## Executive Summary
Executive Summary: DISIS-2024-001 Phase 1 Restudy of Power Flow
Pursuant to the Southwest Power Pool (SPP) Open Access Transmission Tariff (OATT), SPP has conducted this Definitive Interconnection System Impact Study (DISIS) for generation interconnection requests received during the DISIS Queue Cluster Window which closed on March 01, 2025. The primary objective of this DISIS is to identify the system constraints, transient instabilities, and over-dutied equipment associated with connecting the generation to the area transmission system. The Impact Study and other subsequent Interconnection Studies are designed to identify required Transmission Owner Interconnection Facilities, Network Upgrades and other Direct Assignment Facilities needed to inject power into the grid at each specific point of interconnection. The study analysis for the generation interconnection requests included in this DISIS are displayed in this workbook. This workbook provides a convenient method to sort and analyze required study data. The DISIS Manual Version 4.4 posted on https://spp.org/engineering/generator-interconnection contains details about the DISIS process, methodology, definitions, and useful links. Please review the DISIS Manual or contact gistudies@spp.org for more information about the study process. DISIS-2024-001 Phase 1 includes study requests in the following cluster groups: (01 NORTH, 02 NEBRASKA, 03 CENTRAL, 04 SOUTHEAST, 05 SOUTHWEST, WECC)
DISIS Manual Version 4.4
https://spp.org/media/2400/gi-manual-business-practice_7250_20251017.pdf
This DISIS analyzes the impact of interconnecting new generation for total of:
38,033.05 MW
The standard cost of interconnecting all requests included in this DISIS is estimated at:
Total Network Upgrade $7,793,385,702.95 Steady State Network Upgrade $6,199,624,276.94 Interconnection Costs: $1,593,761,426.01
Models Used in Steady State Study
2025 ITP Series, WECC Models
Winter: 2029 WECC Winter: 2031
Summer: 2026, 2029 WECC Summer: 2026, 2031
Light: 2029
By: SPP Generator Interconnection Department
Published: July 20, 2026
Costs for Solar/Battery Requests were allocated using the 29SP (summer peak) model.
Costs for Wind Requests were allocated using the 29L (light load) model.
Short Circuit Ratio calculation is provided per group. A value of “N/A” means the request was offline for that scenario.
All analysis was performed iteratively. A “Mitigation Iteration” column is included in the report to indicate the iteration in which each upgrade was identified.
Iterations are defined in study order as follows: ‘SI‑NC’ = system‑intact non‑convergence; ‘N0’ = first contingency non‑convergence iteration; ‘N1’ = second contingency non‑convergence iteration; ‘T0’ = first thermal iteration; ‘T1’ and ‘T2’ = follow‑up thermal iterations; ‘V’ = voltage.
SPP and the consultant team included previously identified and reviewed upgrades to mitigate select system-intact and contingency non-convergence issues. These upgrades are noted as "Contingent" in the report.
Remaining non-converged contingencies were mitigated by parallel-circuiting the contingent elements, using the same approach as described in the Phase 1.
Thermal and voltage upgrades were selected using automated methods consistent with previous DISIS Phase 1 manual review and mitigation selection whitepaper. (Link)
Network upgrades not listed as "Contingent" were not reviewed by SPP or Transmission Owners for viability or optimality.
Interconnection costs were provided by Transmission Owners.
Good‑faith estimates leveraging SPP’s 2025 ITP Conceptual Cost Estimates were used.

## Requests
Gen Number | Group | Queue | Fuel Type | MW Amount | Service | Area | Substation or Line
ASGI-2024-001 | 01 NORTH | DIS-24-1 | Thermal | 17.1 | ER | WAPA | Pine Lake 12.47 kV
ASGI-2024-002 | 05 SOUTHWEST | DIS-24-1 | Hybrid | 30 | ER | SPS | GridLiance's Cougar 69 kV Substation
ASGI-2024-003 | 03 CENTRAL | DIS-24-1 | Solar | 79.8 | ER/NR | SUNC | Rolla 115 kV Substation
ASGI-2024-006 | 03 CENTRAL | DIS-24-1 | Hybrid | 100 | ER/NR | KCPL | Y-road 115 kV switching station
ASGI-2024-007 | 03 CENTRAL | DIS-24-1 | Thermal | 47.99 | ER/NR | KCPL | Marshall Miami 13.2 kV Substation
ASGI-2024-008 | 03 CENTRAL | DIS-24-1 | Thermal | 86 | ER/NR | KCPL | Marshall Miami 161 kV Substation
ASGI-2024-020 | 03 CENTRAL | DIS-24-1 | Thermal | 131.58 | ER/NR | WERE | Johns-Manville 115 kV Substation
ASGI-2024-023 | 04 SOUTHEAST | DIS-24-1 | Hybrid | 120 | ER/NR | AEPW | Hope NW - Fulton 115 kV Line
ASGI-2024-024 | 03 CENTRAL | DIS-24-1 | Battery/Storage | 79 | ER/NR | KCPL | Alabama St 161 kV Substation
GEN-2024-003 | 04 SOUTHEAST | DIS-24-1 | Thermal | 102.2 | ER | AEPW | Fitzhugh 161kV
GEN-2024-013 | 04 SOUTHEAST | DIS-24-1 | Thermal | 496 | ER/NR | OKGE | Norman Hills 345 kV
GEN-2024-015 | 05 SOUTHWEST | DIS-24-1 | Hybrid | 280 | ER/NR | SPS | Sundown-Amaco-Yoakum 230 kV Substation
GEN-2024-017 | 02 NEBRASKA | DIS-24-1 | Thermal | 62 | ER/NR | NPPD | Olive Creek 345 kV Substation
GEN-2024-018 | 02 NEBRASKA | DIS-24-1 | Thermal | 31 | ER/NR | NPPD | New Beatrice Power Station 345 kV
GEN-2024-019 | 02 NEBRASKA | DIS-24-1 | Thermal | 62 | ER/NR | NPPD | New Beatrice Power Station 345 kV Substation
GEN-2024-020 | 02 NEBRASKA | DIS-24-1 | Thermal | 390 | ER/NR | NPPD | Olive Creek 345 kV Substation
GEN-2024-021 | 02 NEBRASKA | DIS-24-1 | Thermal | 540 | ER/NR | NPPD | Olive Creek 345 kV Substation
GEN-2024-022 | 02 NEBRASKA | DIS-24-1 | Thermal | 390 | ER/NR | NPPD | New Beatrice Power Station 345 kV
GEN-2024-023 | 02 NEBRASKA | DIS-24-1 | Thermal | 270 | ER/NR | NPPD | New Beatrice Power Station 345 kV
GEN-2024-025 | 04 SOUTHEAST | DIS-24-1 | Solar | 150 | ER/NR | AEPW | Lydia 345 kV Substation
GEN-2024-035 | 01 NORTH | DIS-24-1 | Hybrid | 270 | ER/NR | WAPA | Groton 345 kV Substation
GEN-2024-041 | 05 SOUTHWEST | DIS-24-1 | Wind | 250 | ER/NR | SPS | Tuco - Whirlwind 345 kV Line
GEN-2024-042 | 05 SOUTHWEST | DIS-24-1 | Wind | 250 | ER/NR | SPS | Tuco - Whirlwind 345 kV line
GEN-2024-043 | 05 SOUTHWEST | DIS-24-1 | Wind | 250 | ER/NR | SPS | Crossroads - Tolk 345 kV Line
GEN-2024-051 | 02 NEBRASKA | DIS-24-1 | Battery/Storage | 170 | ER/NR | LES | Waverly-Alvo 115 kV Line
GEN-2024-054 | 03 CENTRAL | DIS-24-1 | Solar | 120 | ER/NR | KCPL | Overton - Sedalia East 161 kV line
GEN-2024-055 | 03 CENTRAL | DIS-24-1 | Solar | 175 | ER/NR | KCPL | Butler - Nevada 161 kV line
GEN-2024-056 | 04 SOUTHEAST | DIS-24-1 | Solar | 120 | ER/NR | OKGE | Cow Creek - Morrison 138 kV line
GEN-2024-065 | 02 NEBRASKA | DIS-24-1 | Battery/Storage | 150 | ER/NR | NPPD | FREMONT7 115 kV Substation
GEN-2024-067 | 03 CENTRAL | DIS-24-1 | Solar | 380 | ER/NR | SUNC | Cirrus 345 kV Substation
GEN-2024-068 | 04 SOUTHEAST | DIS-24-1 | Solar | 300 | ER/NR | AEPW | Lydia - Welsh 345 kV Line
GEN-2024-071 | 04 SOUTHEAST | DIS-24-1 | Hybrid | 75 | ER/NR | AEPW | West Atlanta - Atlanta 69 kV Line
GEN-2024-074 | 03 CENTRAL | DIS-24-1 | Battery/Storage | 200 | ER/NR | KCPL | Duncan Road 161 kV Substation
GEN-2024-076 | 03 CENTRAL | DIS-24-1 | Solar | 130 | ER/NR | WERE | Neosho - LaCygne 345 kV Line
GEN-2024-081 | 01 NORTH | DIS-24-1 | Thermal | 745 | ER | WAPA | Springbrook - Tande 345 kV Line
GEN-2024-082 | 01 NORTH | DIS-24-1 | Thermal | 745 | ER | WAPA | Springbrook - Tande 345 kV Line
GEN-2024-088 | 03 CENTRAL | DIS-24-1 | Thermal | 144.999 | ER/NR | SPRM | McCartney 161 kV Substation
GEN-2024-090 | 03 CENTRAL | DIS-24-1 | Battery/Storage | 100 | ER/NR | KCPL | Smithville 161 kV Substation
GEN-2024-099 | 05 SOUTHWEST | DIS-24-1 | Solar | 300 | ER/NR | SPS | Newhart 230 kV Substation
GEN-2024-109 | 05 SOUTHWEST | DIS-24-1 | Wind | 400.5 | ER/NR | SPS | Tolk - Crossroads 345 kV line
GEN-2024-113 | 04 SOUTHEAST | DIS-24-1 | Hybrid | 170 | ER/NR | OKGE | Muskogee - Ft. Smith 345 kV Line
GEN-2024-117 | 04 SOUTHEAST | DIS-24-1 | Hybrid | 150 | ER/NR | AEPW | Coffeyville Tap - North Bartlesville 138kV Line
GEN-2024-118 | 04 SOUTHEAST | DIS-24-1 | Battery/Storage | 199 | ER/NR | AEPW | East 11th Street 138kV Substation
GEN-2024-120 | 04 SOUTHEAST | DIS-24-1 | Battery/Storage | 199 | ER/NR | OKGE | JNS KAMO 138 kV Substation
GEN-2024-122 | 04 SOUTHEAST | DIS-24-1 | Hybrid | 160 | ER/NR | AEPW | Lieberman - IPC Jefferson 138 kV Line
GEN-2024-125 | 03 CENTRAL | DIS-24-1 | Solar | 400 | ER/NR | WERE | Neosho Ridge - Caney River 345 kV Line
GEN-2024-128 | 04 SOUTHEAST | DIS-24-1 | Thermal | 690 | ER/NR | OKGE | Gracemont - Lawton 345 kV Line
GEN-2024-129 | 03 CENTRAL | DIS-24-1 | Thermal | 910 | ER/NR | WERE | Caney River - Neosho 345 kV Line
GEN-2024-139 | 03 CENTRAL | DIS-24-1 | Solar | 250 | ER/NR | WERE | Wolf Creek - Blackberry 345 kV Line
GEN-2024-140 | 02 NEBRASKA | DIS-24-1 | Solar | 250 | ER/NR | NPPD | Antelope - Hoskins 345 kV line
GEN-2024-141 | 01 NORTH | DIS-24-1 | Wind | 212 | ER | WAPA | BASIN__-BE4 230 kV Substation
GEN-2024-143 | 05 SOUTHWEST | DIS-24-1 | Wind | 250 | ER/NR | SPS | XIT Interchange 230 kV Substation
GEN-2024-145 | 05 SOUTHWEST | DIS-24-1 | Wind | 250 | ER/NR | SPS | XIT Interchange 230 kV Substation
GEN-2024-154 | 04 SOUTHEAST | DIS-24-1 | Solar | 200 | ER/NR | AEPW | Chisholm 345 kV Substation
GEN-2024-159 | 05 SOUTHWEST | DIS-24-1 | Solar | 300 | ER/NR | SPS | Oasis to San Juan Mesa Wind Project 230 kV
GEN-2024-162 | 02 NEBRASKA | DIS-24-1 | Hybrid | 110 | ER/NR | NPPD | Twin Church 230 kV Substation
GEN-2024-166 | 03 CENTRAL | DIS-24-1 | Hybrid | 200 | ER/NR | WERE | Murray Gill 138 kV Substation
GEN-2024-168 | 02 NEBRASKA | DIS-24-1 | Solar | 200 | ER/NR | NPPD | Geneva 115 kV Substation
GEN-2024-170 | 03 CENTRAL | DIS-24-1 | Battery/Storage | 280 | ER/NR | KCPL | Pleasant Hill 345 kV Substation
GEN-2024-171 | 04 SOUTHEAST | DIS-24-1 | Battery/Storage | 250 | ER/NR | AEPW | Tulsa North - Grand River Energy Center 345 kV Line
GEN-2024-173 | 02 NEBRASKA | DIS-24-1 | Battery/Storage | 200 | ER/NR | NPPD | Pawnee Lake 115 kV Substation
GEN-2024-177 | 04 SOUTHEAST | DIS-24-1 | Battery/Storage | 199 | ER/NR | AEPW | Red Point 138 kV Substation
GEN-2024-178 | 04 SOUTHEAST | DIS-24-1 | Battery/Storage | 199 | ER/NR | AEPW | Pirkey 138 kV Substation
GEN-2024-181 | 03 CENTRAL | DIS-24-1 | Battery/Storage | 199 | ER/NR | SPRM | Brookline 161 kV Substation
GEN-2024-204 | 04 SOUTHEAST | DIS-24-1 | Battery/Storage | 100 | ER/NR | OKGE | Brown 138 kV Substation
GEN-2024-205 | 03 CENTRAL | DIS-24-1 | Hybrid | 155 | ER/NR | SUNC | St. John 115 kV Substation
GEN-2024-206 | 03 CENTRAL | DIS-24-1 | Thermal | 226.3 | ER/NR | INDN | Blue Valley 161 kV Substation
GEN-2024-207 | 03 CENTRAL | DIS-24-1 | Thermal | 778.6 | ER/NR | INDN | Blue Valley - Blumil 161 kV Line
GEN-2024-211 | 02 NEBRASKA | DIS-24-1 | Thermal | 303 | ER | OPPD | Substation 3740 345 kV
GEN-2024-212 | 02 NEBRASKA | DIS-24-1 | Thermal | 303 | ER | OPPD | Substation 3740 345 kV
GEN-2024-213 | 02 NEBRASKA | DIS-24-1 | Thermal | 360 | ER | OPPD | Substation 3740 345 kV
GEN-2024-215 | 03 CENTRAL | DIS-24-1 | Hybrid | 300 | ER/NR | SUNC | Elm Creek 345 kV Substation
GEN-2024-219 | 04 SOUTHEAST | DIS-24-1 | Hybrid | 160 | ER/NR | OKGE | Chigley - Oaklawn 138 kV Line
GEN-2024-220 | 04 SOUTHEAST | DIS-24-1 | Hybrid | 55 | ER/NR | AEPW | Rodessa - Bloomberg 69 kV Line
GEN-2024-221 | 05 SOUTHWEST | DIS-24-1 | Wind | 400 | ER/NR | SPS | 345 kV Crossroads - Eddy County 345 kV Line
GEN-2024-232 | 04 SOUTHEAST | DIS-24-1 | Solar | 250 | ER/NR | AEPW | Crockett - Rocky Creek 345 kV line
GEN-2024-234 | 02 NEBRASKA | DIS-24-1 | Solar | 200 | ER/NR | OPPD | Raun - Tekamah 161 kV line
GEN-2024-235 | 04 SOUTHEAST | DIS-24-1 | Wind | 250 | ER/NR | AEPW | Sooner - Wekiwa 345 kV line
GEN-2024-236 | 04 SOUTHEAST | DIS-24-1 | Wind | 241.4 | ER/NR | OKGE | Seminole - Muskogee 345 kV line
GEN-2024-239 | 04 SOUTHEAST | DIS-24-1 | Battery/Storage | 200 | ER/NR | OKGE | Cimarron 345 kV Substation
GEN-2024-240 | 04 SOUTHEAST | DIS-24-1 | Wind | 150 | ER/NR | AEPW | Neosho - Delaware 345 kV line
GEN-2024-241 | 04 SOUTHEAST | DIS-24-1 | Solar | 100 | ER/NR | AEPW | Lydia 345 kV Substation
GEN-2024-249 | 03 CENTRAL | DIS-24-1 | Thermal | 721.2 | ER/NR | WERE | Jeffrey EC 345 kV Substation
GEN-2024-252 | 04 SOUTHEAST | DIS-24-1 | Hybrid | 300 | ER/NR | OKGE | Cimmaron 345 kV Substation
GEN-2024-253 | 03 CENTRAL | DIS-24-1 | Hybrid | 300 | ER/NR | WERE | Stranger Creek - 87th Street 345 kV line
GEN-2024-254 | 04 SOUTHEAST | DIS-24-1 | Hybrid | 300 | ER/NR | OKGE | Mathewson 345 kV Substation
GEN-2024-255 | 04 SOUTHEAST | DIS-24-1 | Hybrid | 300 | ER/NR | OKGE | Spring Creek 345 kV Substation
GEN-2024-258 | 03 CENTRAL | DIS-24-1 | Wind | 300 | ER/NR | WERE | Wolf Creek - Blackberry 345 kV Line
GEN-2024-259 | 03 CENTRAL | DIS-24-1 | Hybrid | 199.8 | ER/NR | WERE | Asbury 161 kV Substation
GEN-2024-260 | 03 CENTRAL | DIS-24-1 | Storage | 199.8 | ER/NR | KCPL | East Town 161 kV Substation
GEN-2024-261 | 05 SOUTHWEST | DIS-24-1 | Hybrid | 140 | ER/NR | SPS | Hobbs - LCEC West 115 kV Line
GEN-2024-265 | 05 SOUTHWEST | DIS-24-1 | Hybrid | 155 | ER/NR | SPS | Bensing 115 kV Substation
GEN-2024-268 | 04 SOUTHEAST | DIS-24-1 | Solar | 390 | ER/NR | OKGE | Keefton 345 kV Substation
GEN-2024-276 | 03 CENTRAL | DIS-24-1 | Battery/Storage | 135 | ER/NR | WERE | Tecumseh Hill - Swissvale 230kV Line
GEN-2024-277 | 03 CENTRAL | DIS-24-1 | Battery/Storage | 135 | ER/NR | WERE | Tecumseh Hill - Swissvale 230kV Line
GEN-2024-280 | 05 SOUTHWEST | DIS-24-1 | Hybrid | 350 | ER/NR | SPS | Andrews County 345 kV Substation
GEN-2024-281 | 05 SOUTHWEST | DIS-24-1 | Hybrid | 250 | ER/NR | SPS | Jal - Teague 115 kV Line
GEN-2024-286 | 04 SOUTHEAST | DIS-24-1 | Thermal | 136 | ER | OKGE | AES 5 161 kV Substation
GEN-2024-287 | 03 CENTRAL | DIS-24-1 | Solar | 199.8 | ER/NR | WERE | Wolf Creek - Blackberry 345 kV Line
GEN-2024-293 | 04 SOUTHEAST | DIS-24-1 | Thermal | 248 | ER | OKGE | Muskoge7 345 kV Substation
GEN-2024-294 | 04 SOUTHEAST | DIS-24-1 | Hybrid | 500 | ER/NR | AEPW | Tulsa North - Igloo Valley 345 kV line
GEN-2024-295 | 05 SOUTHWEST | DIS-24-1 | Battery/Storage | 115 | ER/NR | SPS | S Loving 115 kV Substation
GEN-2024-296 | 04 SOUTHEAST | DIS-24-1 | Solar | 167 | ER/NR | AEPW | Muskogee - Pittsburg 345 kV Line
GEN-2024-297 | 04 SOUTHEAST | DIS-24-1 | Solar | 167 | ER/NR | AEPW | Muskogee - Pittsburg 345 kV Line
GEN-2024-299 | 04 SOUTHEAST | DIS-24-1 | Thermal | 744 | ER | OKGE | AES 5 345 kV Substation
GEN-2024-303 | 05 SOUTHWEST | DIS-24-1 | Hybrid | 500 | ER/NR | SPS | Crossroads 345 kV Substation
GEN-2024-304 | 05 SOUTHWEST | DIS-24-1 | Hybrid | 500 | ER/NR | SPS | Crossroads 345 kV Substation
GEN-2024-310 | 05 SOUTHWEST | DIS-24-1 | Battery/Storage | 75 | ER | SPS | Eddy - Chaves 230 kV line
GEN-2024-311 | 05 SOUTHWEST | DIS-24-1 | Solar | 225 | ER/NR | SPS | Eddy - Chaves 230 kV line
GEN-2024-317 | 05 SOUTHWEST | DIS-24-1 | Solar | 250 | ER/NR | SPS | Dragon 345 kV Substation
GEN-2024-318 | 04 SOUTHEAST | DIS-24-1 | Battery/Storage | 199 | ER/NR | AEPW | Tulsa North - American Airlines 138 kV Line
GEN-2024-319 | 03 CENTRAL | DIS-24-1 | Battery/Storage | 199 | ER/NR | KACY | Metro 5 161 kV Substation
GEN-2024-320 | 03 CENTRAL | DIS-24-1 | Battery/Storage | 199 | ER/NR | WERE | Jaggard 115 kV Substation
GEN-2024-321 | 04 SOUTHEAST | DIS-24-1 | Thermal | 493 | ER/NR | OKGE | Seminole 345 kV Substation
GEN-2024-323 | 04 SOUTHEAST | DIS-24-1 | Thermal | 356.8 | ER | WFEC | ITC Hugo 7 345 kV Substation
GEN-2024-327 | 01 NORTH | DIS-24-1 | Battery/Storage | 200 | ER/NR | WAPA | Berthold 115 kV Substation
GEN-2024-329 | 01 NORTH | DIS-24-1 | Battery/Storage | 200 | ER/NR | WAPA | Pleasant Valley 115 kV Substation
GEN-2024-330 | 03 CENTRAL | DIS-24-1 | Battery/Storage | 225 | ER/NR | WERE | Midian 138 kV Substation
GEN-2024-333 | 04 SOUTHEAST | DIS-24-1 | Battery/Storage | 100 | ER/NR | OKGE | Kelley Avenue 138 kV
GEN-2024-334 | 04 SOUTHEAST | DIS-24-1 | Thermal | 103 | ER/NR | OKGE | Ranch Road 345 kV Substation
GEN-2024-336 | 05 SOUTHWEST | DIS-24-1 | Hybrid | 300 | ER/NR | SPS | Ink Basin 230 kV Substation
GEN-2024-338 | 04 SOUTHEAST | DIS-24-1 | Solar | 350 | ER/NR | OKGE | Pittsburg - Johnston County 345 kV line
GEN-2024-339 | 03 CENTRAL | DIS-24-1 | Battery/Storage | 300 | ER/NR | WERE | Stranger Creek 115 kV Substation
GEN-2024-340 | 04 SOUTHEAST | DIS-24-1 | Thermal | 1400 | ER/NR | OKGE | Riverside – Redbud 345 kV line
GEN-2024-341 | 04 SOUTHEAST | DIS-24-1 | Thermal | 1045 | ER/NR | AEPW | Pittsburgh 345 kV Substation
GEN-2024-343 | 04 SOUTHEAST | DIS-24-1 | Thermal | 235 | ER/NR | AEPW | LeBrock 345 kV Substation
GEN-2024-344 | 04 SOUTHEAST | DIS-24-1 | Wind | 200 | ER | OKGE | Riverside - Redbud Switch 345 kV Line
GEN-2024-352 | 03 CENTRAL | DIS-24-1 | Battery/Storage | 199 | ER/NR | KCPL | Sibley 345 kV Substation
GEN-2024-360 | 04 SOUTHEAST | DIS-24-1 | Hybrid | 160 | ER/NR | OKGE | Seminole - Maud 138 kV Line
GEN-2024-361 | 04 SOUTHEAST | DIS-24-1 | Hybrid | 80 | ER/NR | OKGE | Spring Valley - Warwick 138 kV line
GEN-2024-362 | 04 SOUTHEAST | DIS-24-1 | Hybrid | 120 | ER/NR | AEPW | Leonard 138 kV Substation
GEN-2024-370 | 03 CENTRAL | DIS-24-1 | Battery/Storage | 250 | ER/NR | KCPL | Smithville 161 kV Substation
GEN-2024-372 | 02 NEBRASKA | DIS-24-1 | Battery/Storage | 250 | ER/NR | OPPD | S1247 161 kV Substation
GEN-2024-373 | 04 SOUTHEAST | DIS-24-1 | Hybrid | 100 | ER/NR | WFEC | Unger - West Bank Tap 138 kV Line
GEN-2024-374 | 02 NEBRASKA | DIS-24-1 | Solar | 225 | ER/NR | WAPA | Stegall 345 kV Substation
GEN-2024-376 | 04 SOUTHEAST | DIS-24-1 | Solar | 142.183 | ER/NR | AEPW | Hemphill 138 kV Substation
GEN-2024-377 | 04 SOUTHEAST | DIS-24-1 | Thermal | 1350.001 | ER/NR | AEPW | Pirkey 345 kV Substation
GEN-2024-379 | 04 SOUTHEAST | DIS-24-1 | Thermal | 1350.001 | ER/NR | AEPW | Longwood - El Dorado 345 kV Line
ASGI-2010-010 | 05 SOUTHWEST | DIS-10-1 | Gas | 42.195 | ER | SPS
ASGI-2010-020 | 05 SOUTHWEST | DIS-10-2 | Wind | 30 | ER | SPS
ASGI-2010-021 | 05 SOUTHWEST | DIS-10-2 | Wind | 15 | ER | SPS
ASGI-2011-001 | 05 SOUTHWEST | DIS-10-2 | Wind | 27.3 | ER | SPS
ASGI-2011-002 | 05 SOUTHWEST | DIS-11-1 | Wind | 20 | ER | SPS
ASGI-2011-003 | 05 SOUTHWEST | DIS-11-1 | Wind | 10 | ER | SPS
ASGI-2011-004 | 05 SOUTHWEST | DIS-11-2 | Wind | 19.8 | ER | SPS
ASGI-2013-001 | 05 SOUTHWEST | DIS-13-1 | Wind | 11.5 | ER | SPS
ASGI-2013-004 | 03 CENTRAL | DIS-16-1 | Gas | 36.6 | ER | SUNC | Garden City 115kV substation, bus 531445
ASGI-2016-003 | 03 CENTRAL | DIS-16-1 | Diesel | 12 | ER | KCPL | Paola 161kV
ASGI-2016-007NWE208 | 01 NORTH | DIS-16-1 | Wind | 20 | ER | WAPA
ASGI-2016-011 | 04 SOUTHEAST | DIS-16-2-PQ | Thermal | 7.407 | ER | SWPA
ASGI-2016-012 | 04 SOUTHEAST | DIS-16-2-PQ | Thermal | 61.725 | ER | SWPA
ASGI-2016-013 | 04 SOUTHEAST | DIS-16-2-PQ | Thermal | 4.938 | ER | WFEC
BEPCAyrshire | 01 NORTH | DIS-17-1-PQ | Wind | 21 | ER | BEPC
BEPCGerled | 01 NORTH | DIS-17-1-PQ | Wind | 10.5 | ER | BEPC
BEPCHummel | 01 NORTH | DIS-17-1-PQ | Wind | 10.5 | ER | BEPC
BEPCNDPW0 | 01 NORTH | DIS-17-1-PQ | Wind | 7.5 | ER | BEPC
GEN-2001-014 | 04 SOUTHEAST | PQ | Wind | 94.5 | ER | WFEC | Ft Supply 138kV
GEN-2001-026 | 04 SOUTHEAST | PQ | Wind | 74.25 | ER | WFEC | Washita 138kV
GEN-2001-030 | 03 CENTRAL | PQ | CT | 50 | ER | EMDE | LaRussell Energy Center 161kV
GEN-2001-037_GEN-2023-SR16 | 04 SOUTHEAST | PQ | Wind | 102 | ER | OKGE
GEN-2001-039M | 03 CENTRAL | PQ | Wind | 100 | ER | SUNC | Central Plains Tap 115kV
GEN-2001-040 | 03 CENTRAL | PQ | CT | 50 | ER | EMDE | LaRussell Energy Center 161kV
GEN-2002-005 | 04 SOUTHEAST | PQ | Wind | 123 | ER | WFEC | Red Hills Tap 138kV
GEN-2002-008IS | 01 NORTH | DIS-15-2-PQ | Wind | 40.5 | ER/NR | BEPC
GEN-2002-009 | 05 SOUTHWEST | PQ | Wind | 67.2 | ER | SPS | Hansford 115kV
GEN-2002-009IS | 01 NORTH | DIS-15-2-PQ | Wind | 40.5 | ER/NR | BEPC
GEN-2002-022 | 05 SOUTHWEST | PQ | Wind | 239.2 | ER | SPS | Bushland 230kV
GEN-2003-006A | 03 CENTRAL | PQ | Wind | 201 | ER | SUNC | Elm Creek 230kV
GEN-2003-019 | 03 CENTRAL | PQ | Wind | 249.3 | ER | MIDW | Smoky Hills Tap 230kV
GEN-2003-020_GEN-2016-070 | 05 SOUTHWEST | PQ | Wind | 165.3 | ER | SPS
GEN-2003-022_GEN-2004-020_GEN-2016-051 | 04 SOUTHEAST | DIS-16-1 | Wind | 156.8 | ER | AEPW
GEN-2004-008_GEN-2011-011 | 03 CENTRAL | DIS-11-1 | Coal | 900 | ER | KCPL
GEN-2004-015_GEN-2012-034 | 05 SOUTHWEST | PQ | CT | 157 | ER | SPS
GEN-2004-017_GEN-2014-028 | 03 CENTRAL | DIS-14-2 | CT/ST | 300 | ER/NR | EMDE
GEN-2004-023N | 02 NEBRASKA | PQ | Coal | 75 | ER | NPPD | Columbus Co 115kV
GEN-2005-008 | 04 SOUTHEAST | PQ | Wind | 120 | ER | OKGE | Woodward 138kV
GEN-2005-008IS | 01 NORTH | DIS-16-1 | Wind | 50 | ER/NR | BEPC
GEN-2005-013 | 03 CENTRAL | PQ | Wind | 199.8 | ER | WERE | Caney River 345kV
GEN-2006-002 | 04 SOUTHEAST | PQ | Wind | 100.8 | ER | AEPW | Sweetwater 230kV
GEN-2006-008 | 04 SOUTHEAST | PQ | Thermal | 550 | ER | AEPW | Arsenal Hill 138kV
GEN-2006-015IS | 01 NORTH | DIS-16-1 | Wind | 50 | ER/NR | BEPC
GEN-2006-018 | 05 SOUTHWEST | PQ | CT | 168.1 | ER | SPS | TUCO 230kV
GEN-2006-020S | 05 SOUTHWEST | PQ | Wind | 20 | ER | SPS | DWS Frisco 115kV
GEN-2006-021 | 03 CENTRAL | PQ | Wind | 94 | ER | SUNC | Flat Ridge Tap 138kV
GEN-2006-024S | 04 SOUTHEAST | PQ | Wind | 18.9 | ER | WFEC | Buffalo Bear Tap 69kV
GEN-2006-031 | 03 CENTRAL | DIS-13-2 | Gas | 75.6 | ER | MIDW | Knoll 115kV
GEN-2006-035 | 04 SOUTHEAST | PQ | Wind | 132 | ER | AEPW | Sweetwater 230kV
GEN-2006-038N005 | 02 NEBRASKA | PQ | Wind | 80 | ER | NPPD | Broken Bow 115kV
GEN-2006-038N019 | 02 NEBRASKA | PQ | Wind | 80 | ER | NPPD | Petersburg North 115kV
GEN-2006-043 | 04 SOUTHEAST | PQ | Wind | 99 | ER | AEPW | Sweetwater 230kV
GEN-2006-044N | 02 NEBRASKA | DIS-09-1 | Wind | 40.5 | ER | OPPD | North Petersburg 115kV
GEN-2006-046 | 04 SOUTHEAST | PQ | Wind | 129.6 | ER | OKGE | Dewey 138kV
GEN-2007-011N08 | 02 NEBRASKA | PQ | Wind | 81 | ER | NPPD | Bloomfield 115kV
GEN-2007-015IS | 01 NORTH | DIS-15-2-PQ | Wind | 102 | ER/NR | BEPC
GEN-2007-017IS | 02 NEBRASKA | DIS-15-2-PQ | Wind | 202 | ER/NR | OPPD
GEN-2007-018IS | 02 NEBRASKA | DIS-15-2-PQ | Wind | 198 | ER/NR | OPPD
GEN-2007-021 | 04 SOUTHEAST | ICS1 | Wind | 198.9 | ER | OKGE | Tatonga 345kV
GEN-2007-043_GEN-2016-131_GEN-2023-SR18 | 04 SOUTHEAST | DIS-16-2 | Wind | 202.5 | ER | OKGE
GEN-2007-046 | 05 SOUTHWEST | ICS1 | Wind | 200 | ER | SPS | Hitchland 115kV
GEN-2007-050 | 04 SOUTHEAST | ICS1 | Wind | 151.8 | ER | OKGE | Woodward EHV 138kV
GEN-2007-052 | 04 SOUTHEAST | PQ | Gas | 150 | ER | WFEC | Anadarko 138kV
GEN-2007-062 | 04 SOUTHEAST | PQ | Wind | 424 | ER | OKGE | Woodward EHV 345kV
GEN-2008-013 | 04 SOUTHEAST | ICS1 | Wind | 300 | ER | OKGE | Hunter 345kV
GEN-2008-018 | 03 CENTRAL | ICS1 | Wind | 250 | ER | SPS | Finney 345kV
GEN-2008-023 | 04 SOUTHEAST | DIS-09-1 | Wind | 150 | ER | AEPW | Hobart Junction 138kV
GEN-2008-037 | 04 SOUTHEAST | DIS-10-1 | Wind | 99 | ER | WFEC | Tap Washita - Blue Canyon Wind 138kV
GEN-2008-047 | 05 SOUTHWEST | PQ | Wind | 263.13 | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV
GEN-2008-079 | 03 CENTRAL | DIS-09-1 | Wind | 98.9 | ER | SUNC | Crooked Creek 115kV
GEN-2008-086N02 | 02 NEBRASKA | PQ | Wind | 201 | ER | OPPD | Meadow Grove 230kV
GEN-2008-092 | 03 CENTRAL | PQ | Wind | 200.5 | ER | MIDW | Post Rock 230kV
GEN-2008-119O | 02 NEBRASKA | PQ | Wind | 60 | ER | OPPD | S1399 161kV
GEN-2008-123N | 02 NEBRASKA | DIS-10-1 | Wind | 89.66 | ER | NPPD | Tap Pauline - Hildreth (Rosemont) 115kV
GEN-2008-129 | 03 CENTRAL | PQ | CT | 72 | ER | KCPL | Pleasant Hill 161kV
GEN-2009-008 | 03 CENTRAL | DIS-10-1 | Wind | 198.69 | ER | MIDW | South Hays 230kV
GEN-2009-018IS | 01 NORTH | DIS-16-1 | Wind | 100 | ER | BEPC
GEN-2009-020AIS | 01 NORTH | DIS-16-1 | Wind | 80 | ER/NR | WAPA
GEN-2009-025 | 04 SOUTHEAST | DIS-09-1 | Wind | 59.8 | ER | OKGE | TAP Deer Creek – Sinclair 69kV
GEN-2009-026IS | 01 NORTH | DIS-16-1 | Wind | 110 | ER/NR | BEPC
GEN-2010-001 | 05 SOUTHWEST | PQ | Wind | 300 | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV
GEN-2010-001IS | 01 NORTH | DIS-15-2-PQ | Wind | 99 | ER/NR | BEPC
GEN-2010-003 | 03 CENTRAL | DIS-10-1 | Wind | 99.5 | ER | WERE | Waverly 345kV
GEN-2010-005 | 03 CENTRAL | DIS-10-1 | Wind | 299.2 | ER | WERE | Viola 345kV
GEN-2010-009 | 03 CENTRAL | PQ | Wind | 165.6 | ER | SUNC | Buckner 345kV
GEN-2010-036 | 03 CENTRAL | DIS-10-2 | Hydro | 4.6 | ER | WERE | 6th Street 115kV
GEN-2010-036PQ | 03 CENTRAL | DIS-10-2 | Hydro | 2.7 | ER | WERE
GEN-2010-040 | 04 SOUTHEAST | PQ | Wind | 300 | ER | OKGE | Cimarron 345kV
GEN-2010-057 | 03 CENTRAL | DIS-11-1 | Wind | 201 | ER/NR | MIDW | Rice County 230kV
GEN-2011-008 | 03 CENTRAL | DIS-11-1 | Wind | 600 | ER | SUNC | Clark County 345kV
GEN-2011-010 | 04 SOUTHEAST | DIS-11-1 | Wind | 100.8 | ER | OKGE | Minco 345kV
GEN-2011-014 | 05 SOUTHWEST | DIS-11-1 | Wind | 198 | ER | OKGE | Beaver County-Woodward EHV Dbl Ckt (Badger) 345kV
GEN-2011-025_GEN-2023-SR9 | 05 SOUTHWEST | DIS-11-1 | Wind | 79.96 | ER | SPS
GEN-2011-027 | 02 NEBRASKA | DIS-16-1 | Wind | 120 | ER/NR | NPPD | Wakefield 230kV
GEN-2011-045 | 05 SOUTHWEST | DIS-16-1 | NG CT | 205 | ER | SPS | Jones 230kV
GEN-2011-046 | 05 SOUTHWEST | DIS-16-1 | Diesel CT | 23 | ER | SPS | Tucumcari 115kV
GEN-2011-050 | 04 SOUTHEAST | DIS-11-2 | Wind | 108 | ER | AEPW | Tap Rush Springs - Marlow 138kV
GEN-2011-056APQ | 02 NEBRASKA | DIS-11-2 | Hydro | 20 | ER | NPPD
GEN-2011-056BPQ | 02 NEBRASKA | DIS-11-2 | Hydro | 22 | ER | NPPD
GEN-2011-056PQ | 02 NEBRASKA | DIS-11-2 | Hydro | 20 | ER | NPPD
GEN-2011-057 | 03 CENTRAL | DIS-11-2 | Wind | 150 | ER | WERE | Creswell 138kV
GEN-2012-001 | 05 SOUTHWEST | DIS-12-1 | Wind | 61.2 | ER | SPS | Tap Grassland - Borden County 230 kv
GEN-2012-007 | 03 CENTRAL | DIS-16-1 | Gas | 120 | ER/NR | SUNC | Rubart 115kV
GEN-2012-020 | 05 SOUTHWEST | DIS-12-2 | Wind | 478 | ER | SPS | TUCO 230kV
GEN-2012-021 | 02 NEBRASKA | DIS-12-2 | Gas | 4.8 | ER | LES | Terry Bundy Generating Station 115kV
GEN-2012-024 | 03 CENTRAL | DIS-16-1 | Wind | 180 | ER | SUNC | Clark County 345kV
GEN-2012-028 | 04 SOUTHEAST | DIS-12-2 | Wind | 74 | ER | WFEC | Gotebo 69kV
GEN-2012-032 | 04 SOUTHEAST | DIS-12-2 | Wind | 299 | ER | OKGE | Rose Hill-(Ranch Road) Sooner (Open Sky) 345kV
GEN-2012-041 | 04 SOUTHEAST | DIS-16-1 | CT | 121.5 | ER | OMPA | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV
GEN-2013-007 | 04 SOUTHEAST | DIS-13-1 | Wind | 100 | ER/NR | OKGE | Tap Prices Falls - Carter 138kV
GEN-2013-022 | 05 SOUTHWEST | DIS-13-2 | Solar | 25 | ER/NR | SPS | Norton 115kV Switching Station
GEN-2013-027 | 05 SOUTHWEST | DIS-14-2 | Wind | 148.4 | ER/NR | SPS | Tolk - Yoakum 230kV
GEN-2013-029 | 04 SOUTHEAST | DIS-13-2 | Wind | 299 | ER | OKGE | Renfrow 345kV
GEN-2013-032 | 02 NEBRASKA | DIS-13-2 | Wind | 202.5 | ER | NPPD | Antelope 115kV
GEN-2014-001IS | 01 NORTH | DIS-16-1 | Wind | 103.24 | ER | WAPA | Sulphur 115kV
GEN-2014-006IS | 01 NORTH | DIS-16-1 | Gas | 125 | ER/NR | BEPC
GEN-2014-010IS | 01 NORTH | DIS-16-1 | Wind | 150 | ER/NR | BEPC
GEN-2014-013 | 02 NEBRASKA | DIS-16-1 | Wind | 73.5 | ER/NR | LES | Meadow Grove 230kV
GEN-2014-014IS | 01 NORTH | DIS-16-1 | Wind | 150 | ER/NR | BEPC
GEN-2014-020 | 04 SOUTHEAST | DIS-16-1 | Wind | 100 | ER/NR | AEPW | Tuttle 138kV
GEN-2014-021 | 03 CENTRAL | DIS-16-1 | Wind | 300 | ER/NR | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV
GEN-2014-031 | 02 NEBRASKA | DIS-14-2 | Wind | 35.8 | ER/NR | GRIS | Meadow Grove 230kV
GEN-2014-033 | 05 SOUTHWEST | DIS-14-2 | Solar | 70 | ER | SPS | Chaves County 115kV
GEN-2014-034 | 05 SOUTHWEST | DIS-14-2 | Solar | 70 | ER | SPS | Chaves County 115kV
GEN-2014-035 | 05 SOUTHWEST | DIS-16-1 | Solar | 30 | ER | SPS | Chaves County 115kV
GEN-2014-057 | 04 SOUTHEAST | DIS-14-2 | Wind | 249.9 | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV
GEN-2014-064 | 04 SOUTHEAST | DIS-16-1 | Wind | 248.4 | ER | OKGE | Otter 138kV
GEN-2015-001 | 04 SOUTHEAST | DIS-15-1 | Wind | 200 | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV
GEN-2015-005 | 03 CENTRAL | DIS-16-1 | Wind | 200.1 | ER | KCPL | Mullen Creek-Sibley (Ketchum) 345kV
GEN-2015-007 | 02 NEBRASKA | DIS-15-1 | Wind | 160 | ER | NPPD | Hoskins 345kV
GEN-2015-013 | 04 SOUTHEAST | DIS-16-1 | Solar | 120 | ER/NR | WFEC | Snyder 138kV
GEN-2015-014_GEN-2023-SR12 | 05 SOUTHWEST | DIS-15-1 | Wind | 150 | ER | SPS
GEN-2015-015 | 04 SOUTHEAST | DIS-15-1 | Wind | 154.56 | ER/NR | OKGE | Tap Medford Tap – Coyote 138kV
GEN-2015-016 | 03 CENTRAL | DIS-16-1 | Wind | 200 | ER/NR | KCPL | Tap Marmaton - Centerville 161kV
GEN-2015-021 | 03 CENTRAL | DIS-15-1 | Solar | 20 | ER/NR | SUNC | Johnson Corner 115kV
GEN-2015-023 | 02 NEBRASKA | DIS-16-1 | Wind | 300.7 | ER/NR | NPPD | Grand Prairie-Grand Island (Holt County NE) 345kV
GEN-2015-046 | 01 NORTH | DIS-16-1 | Wind | 300 | ER | BEPC | Tande 345kV
GEN-2015-063 | 04 SOUTHEAST | DIS-16-1 | Wind | 300 | ER | OKGE | Woodring-Matthewson 345kV
GEN-2015-064 | 03 CENTRAL | DIS-16-1 | Wind | 197.8 | ER | SUNC | Mingo 115kV
GEN-2015-065 | 03 CENTRAL | DIS-15-2 | Wind | 202.4 | ER | SUNC | Mingo 345kV
GEN-2015-082 | 05 SOUTHWEST | DIS-16-1 | Wind | 200 | ER | OKGE | Beaver County - Woodward EHV Dbl Ckt (Badger) 345kV
GEN-2015-089 | 01 NORTH | DIS-16-1 | Wind | 200 | ER | BEPC | Utica 230 kV Substation
GEN-2015-090 | 03 CENTRAL | DIS-16-1 | Wind | 220 | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV
GEN-2015-096 | 01 NORTH | DIS-16-1 | Wind | 150 | ER | BEPC | Brady 230kV substation
GEN-2016-003 | 04 SOUTHEAST | DIS-16-1 | Wind | 248.4 | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV
GEN-2016-004 | 01 NORTH | DIS-16-1 | Wind | 202 | ER/NR | BEPC | Basin Electric 230 kV
GEN-2016-017 | 01 NORTH | DIS-16-1 | Wind | 250.24 | ER | BEPC | Chappelle Creek 345kV
GEN-2016-030_GEN-2020-SR2 | 04 SOUTHEAST | DIS-16-1 | Solar | 100 | ER/NR | OKGE
GEN-2016-036 | 01 NORTH | DIS-16-2 | Wind | 44.6 | ER | WAPA | Granite Falls 115kV substation
GEN-2016-043 | 02 NEBRASKA | DIS-16-1 | Wind | 230 | ER | NPPD | Hoskins 345kV
GEN-2016-061 | 04 SOUTHEAST | DIS-16-1 | Wind | 250.7 | ER | OKGE | Sooner-Woodring 345 kV line
GEN-2016-067 | 03 CENTRAL | DIS-16-1 | Wind | 73.6 | ER | SUNC | Mingo 345kV
GEN-2016-068 | 04 SOUTHEAST | DIS-16-1 | Wind | 250 | ER | OKGE | Woodring 345kV
GEN-2016-074 | 02 NEBRASKA | DIS-16-2 | Wind | 200 | ER | NPPD | Sweetwater 345kV
GEN-2016-087 | 01 NORTH | DIS-16-2 | Wind | 98.9 | ER | WAPA | Campbell County 230 kV line
GEN-2016-091 | 04 SOUTHEAST | DIS-16-2 | Wind | 303.6 | ER | AEPW | Gracemont-Lawton East Side 345kV
GEN-2016-115 | 03 CENTRAL | DIS-16-2 | Wind | 300 | ER | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV
GEN-2016-121 | 05 SOUTHWEST | DIS-16-2 | Solar | 110 | ER | SPS | Roadrunner 115kV
GEN-2016-123_GEN-2016-124_GEN-2016-125 | 05 SOUTHWEST | DIS-16-2 | Wind | 522 | ER | SPS
GEN-2016-130 | 01 NORTH | DIS-16-2 | Wind | 202 | ER | BEPC | Leland Olds 345 kV
GEN-2016-139 | 04 SOUTHEAST | DIS-16-2 | Wind | 100 | ER | AEPW | Riverside 345kV Substation
GEN-2016-141 | 04 SOUTHEAST | DIS-16-2 | Wind | 350 | ER | AEPW | Riverside 345kV Substation
GEN-2016-142 | 04 SOUTHEAST | DIS-16-2 | Wind | 350 | ER | AEPW | Riverside 345kV Substation
GEN-2016-145 | 04 SOUTHEAST | DIS-16-2 | Wind | 175 | ER | AEPW | Riverside 345kV Substation
GEN-2016-146 | 04 SOUTHEAST | DIS-16-2 | Wind | 175 | ER | AEPW | Riverside 345kV Substation
GEN-2016-147 | 02 NEBRASKA | DIS-16-2 | Solar | 40 | ER | NPPD | Sidney 115 kV Sub
GEN-2016-149 | 03 CENTRAL | DIS-16-2 | Wind | 302 | ER | WERE | Stranger Creek 345kV
GEN-2016-151_GEN-2023-SR4 | 01 NORTH | DIS-16-2 | Wind | 202 | ER | BEPC
GEN-2016-153_GEN-2021-SR8 | 03 CENTRAL | DIS-16-2 | Wind | 134 | ER | WERE
GEN-2016-174 | 03 CENTRAL | DIS-16-2 | Wind | 302 | ER | WERE | Stranger Creek 345kV
GEN-2017-005 | 03 CENTRAL | DIS-17-1 | Wind | 190 | ER | WERE | Marmaton - Litchfield 161 kV
GEN-2017-009 | 03 CENTRAL | DIS-17-1 | Wind | 302 | ER | WERE | Neosho - Caney River 345 kV
GEN-2017-027 | 04 SOUTHEAST | DIS-17-1 | Wind | 140 | ER | OKGE | Pooleville-Ratliff (Carter County) 138kV
GEN-2017-057 | 04 SOUTHEAST | DIS-17-1 | Solar | 72.5 | ER | AEPW | Hosston 69kV
GEN-2017-060 | 03 CENTRAL | DIS-17-1 | Wind | 149.4 | ER | EMDE | LaRussell Energy Center 161kV
GEN-2017-074 | 04 SOUTHEAST | DIS-17-1 | Solar | 72.5 | ER | AEPW | Pryor Junction 138kV sub
GEN-2017-077 | 04 SOUTHEAST | DIS-17-1 | Solar | 124.7 | ER | AEPW | Explorer Claremore Tap COOYYAH4
GEN-2017-082 | 03 CENTRAL | DIS-17-1 | Wind | 149.4 | ER | EMDE | Asbury Plant 161 kV
IR24 | 02 NEBRASKA | DIS-17-2-PQ | Wind | 57 | ER/NR | ALTW
LlanoEstacadoWhiteDeer | 05 SOUTHWEST | PQ | Wind | 80 | ER | SPS
MPC00100 | 01 NORTH | DIS-15-2-PQ | Wind | 99 | ER | OTP
MPC00200 | 01 NORTH | DIS-15-2-PQ | Wind | 60 | ER | OTP
MPC00300 | 01 NORTH | DIS-15-2-PQ | Wind | 40.5 | ER | OTP
MPC00500 | 01 NORTH | DIS-15-2-PQ | Wind | 327.9 | ER/NR | OTP
MPC00500GRE | 01 NORTH | DIS-15-2-PQ | Wind | 51 | ER/NR | GRE
MPC01200 | 01 NORTH | DIS-15-2-PQ | Wind | 49.5 | ER | OTP
MPC01300 | 01 NORTH | DIS-15-2-PQ | Coal | 493 | ER/NR | OTP
MPC02100 | 01 NORTH | DIS-15-2-PQ | Wind | 99.25 | ER | OTP
NPPDColumbusHydro | 02 NEBRASKA | PQ | Hydro | 45 | ER | NPPD
NPPDOrd | 02 NEBRASKA | PQ | Heat | 10.8 | ER | NPPD
NPPDSpringview | 02 NEBRASKA | DIS-17-1-PQ | Wind | 3 | ER | NPPD
PQOKGEMustang | 04 SOUTHEAST | DIS-16-1 | CT | 287 | ER | OKGE
SPSDumas19thSt | 05 SOUTHWEST | PQ | Wind | 20 | ER | SPS
SPSEtter | 05 SOUTHWEST | PQ | Wind | 20 | ER | SPS
SPSHopi | 05 SOUTHWEST | PQ | Solar | 10 | ER | SPS
SPSJal | 05 SOUTHWEST | PQ | Solar | 10 | ER | SPS
SPSLeaCounty | 05 SOUTHWEST | DIS-17-1-PQ | Solar | 5.5 | ER | SPS
SPSLeaRoad | 05 SOUTHWEST | PQ | Solar | 10 | ER | SPS
SPSMonument | 05 SOUTHWEST | PQ | Solar | 10 | ER | SPS
SPSMooreE | 05 SOUTHWEST | PQ | Wind | 17.5 | ER | SPS
SPSOcotillo | 05 SOUTHWEST | PQ | Solar | 10 | ER | SPS
SPSSherman | 05 SOUTHWEST | PQ | Wind | 20 | ER | SPS
Sunray | 05 SOUTHWEST | PQ | Wind | 34.5 | ER | SPS
SWPANixaSolar | 03 CENTRAL | DIS-17-1-PQ | Solar | 7.9 | ER | SWPA
WAPAMPSWind | 01 NORTH | DIS-17-1-PQ | Wind | 1.5 | ER | WAPA
WAPASEAMSFtRandallHydro | 02 NEBRASKA | PQ | Hydro | 360 | ER | WAPA
WAPASEAMSGavinsPointHydro | 02 NEBRASKA | PQ | Hydro | 102 | ER | WAPA
WAPATitanWind | 01 NORTH | DIS-17-1-PQ | Wind | 25 | ER | WAPA
GEN-2017-230_GEN-2024-SR3 | 04 SOUTHEAST | DIS-17-2 | Solar | 72.5 | ER/NR | OKGE
GEN-2017-231_GEN-2024-SR2 | 04 SOUTHEAST | DIS-17-2 | Solar | 72.5 | ER/NR | OKGE
GEN-2010-014_GEN-2011-022_GEN-2023-SR8 | 05 SOUTHWEST | PQ | Wind | 657.8 | ER | SPS
GEN-2007-044_GEN-2014-003_GEN-2023-SR5 | 04 SOUTHEAST | ICS1 | Wind | 315 | ER | OKGE
FORT DODGE 4_GEN-2023-SR28 | 03 CENTRAL | Surplus | Solar | 175 | ER | SUNC
GEN-2012-033_GEN-2015-062_GEN-2023-SR13 | 04 SOUTHEAST | DIS-16-1 | Wind | 103.32 | ER | OKGE
GEN-2003-021N_GEN-2023-SR1 | 02 NEBRASKA | PQ | Wind | 75 | ER/NR | NPPD
GEN-2023-GR5 | 05 SOUTHWEST | Replacement | Solar | 150 | ER | SPS | Plant X 115 kV Substation
GEN-2023-GR4 | 05 SOUTHWEST | Replacement | Solar | 72 | ER | SPS | Cunningham 115kV
GEN-2023-GR3 | 05 SOUTHWEST | Replacement | Wind | 80 | ER/NR | SPS | Norton 115 kV
GEN-2023-GR2 | 04 SOUTHEAST | Replacement | Thermal | 94.242 | ER | OKGE | Tinker Air Force Base 138kV
GEN-2023-GR1 | 04 SOUTHEAST | Replacement | Thermal | 97.488 | ER | WFEC | Anadarko Power Plant 69 kV
GEN-2022-GR1 | 04 SOUTHEAST | Replacement | Thermal | 513 | ER | AEPW | Pirkey 138 kV
HAWCT_GEN-2021-SR9 | 03 CENTRAL | Surplus | Solar | 96.75 | ER/NR | KCPL
GEN-2003-005_GEN-2011-037 | 04 SOUTHEAST | PQ | Wind | 105.6 | ER | WFEC
GEN-2003-004_GEN-2004-023_GEN-2005-003 | 04 SOUTHEAST | PQ | Wind | 151.2 | ER | WFEC
GEN-2002-025A_GEN-2004-014 | 03 CENTRAL | PQ | Wind | 252.5 | ER | SUNC
GEN-2005-012 | 03 CENTRAL | PQ | Wind | 248.4 | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV
GEN-2006-020N | 02 NEBRASKA | PQ | Wind | 42 | ER | NPPD | Bloomfield 115kV
GEN-2001-039A | 03 CENTRAL | PQ | Wind | 104 | ER | SUNC | Shooting Star Tap 115kV
GEN-2008-003 | 04 SOUTHEAST | PQ | Wind | 101.2 | ER | OKGE | Woodward EHV 138kV
GEN-2008-124 | 03 CENTRAL | PQ | Wind | 200.1 | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV
GEN-2006-037N1 | 02 NEBRASKA | PQ | Wind | 75 | ER | NPPD | Broken Bow 115kV
GEN-2007-040 | 03 CENTRAL | PQ | Wind | 131.1 | ER | SUNC | Buckner 345kV
GEN-2009-020_GEN-2014-025 | 03 CENTRAL | PQ | Wind | 50.72 | ER | MIDW
GEN-2010-051 | 02 NEBRASKA | PQ | Wind | 200 | ER | NPPD | Wakefield 230kV
GEN-2008-044_GEN-2010-011 | 04 SOUTHEAST | PQ | Wind | 227.5 | ER | OKGE
J569 | 01 NORTH | ICS1 | Wind | 100 | ER/NR | XEL
J476 | 03 CENTRAL | ICS1 | Wind | 246 | ER/NR | MEC
GEN-2013-009IS | 01 NORTH | DIS-16-1 | Wind | 19.5 | ER | WAPA
ASGI-2016-005NWE205 | 01 NORTH | DIS-16-1 | Wind | 20 | ER | WAPA
GEN-2017-075 | 04 SOUTHEAST | DIS-17-1 | Solar | 200 | ER | OKGE | Hugo-Sunnyside 345 kV
GEN-2017-010 | 01 NORTH | DIS-17-1 | Wind | 200.1 | ER | BEPC | Rhame 230 kV Sub
GEN-2013-028 | 04 SOUTHEAST | DIS-16-1 | Gas | 538 | ER | GRDA | Tap N Tulsa - GRDA 1 345kV
GEN-2014-002 | 04 SOUTHEAST | DIS-16-1 | Wind | 10.53 | ER | OKGE | Tatonga 345kV
GEN-2014-005 | 04 SOUTHEAST | DIS-16-1 | Wind | 5.7 | ER | OKGE | Minco 345kV
ASGI-2015-001 | 03 CENTRAL | DIS-16-1 | Thermal | 6.13 | ER | SUNC | Ninnescah 115kV
GEN-2008-008IS | 01 NORTH | DIS-16-1 | Wind | 5 | ER/NR | WAPA
GEN-2006-001IS | 01 NORTH | DIS-15-2-PQ | Wind | 10 | ER/NR | XEL
GEN-2006-006IS | 01 NORTH | DIS-15-2-PQ | Wind | 10 | ER/NR | XEL
GEN-2005-003IS | 01 NORTH | DIS-16-1 | Wind | 100 | ER/NR | BEPC
GEN-2006-002IS | 01 NORTH | DIS-16-1 | Wind | 53 | ER/NR | WAPA
GEN-2007-014IS | 01 NORTH | DIS-16-1 | Wind | 50 | ER/NR | BEPC
GEN-2010-003IS | 01 NORTH | DIS-16-1 | Wind | 34 | ER/NR | BEPC
GEN-2015-048 | 04 SOUTHEAST | DIS-16-1 | Wind | 200 | ER | OKGE | Cleo Corner 138kV
ASGI-2016-004 | 05 SOUTHWEST | DIS-16-1 | Wind | 10 | ER | SPS | Palo Buro 115kV substation
GEN-2015-036 | 04 SOUTHEAST | DIS-16-1 | Wind | 303.6 | ER | OKGE | Johnston County 345kV
GEN-2015-041 | 05 SOUTHWEST | DIS-16-1 | CT | 5 | ER | SPS | TUCO 345kV
GEN-2016-009 | 03 CENTRAL | DIS-16-1 | Steam Turbine | 29 | ER | OKGE | Osage 69 kV Sub
GEN-2016-013 | 03 CENTRAL | DIS-16-1 | CT | 10 | ER | EMDE | LaRussell Energy Center 161kV
GEN-2016-014 | 03 CENTRAL | DIS-16-1 | CT | 10 | ER | EMDE | LaRussell Energy Center 161kV
GEN-2016-020 | 04 SOUTHEAST | DIS-16-1 | WIND | 148.4 | ER | WFEC | Moreland 138kV Substation
GEN-2016-021 | 02 NEBRASKA | DIS-16-1 | WIND | 298.47 | ER | NPPD | Hoskins 345kV
GEN-2016-022 | 04 SOUTHEAST | DIS-16-1 | Wind | 151.8 | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV
GEN-2016-031 | 04 SOUTHEAST | DIS-16-1 | Wind | 1.5 | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV
GEN-2016-032 | 04 SOUTHEAST | DIS-16-1 | Wind | 200 | ER/NR | OKGE | Crescent Substation 138 kV
GEN-2016-045 | 04 SOUTHEAST | DIS-16-1 | Wind | 499.1 | ER | OKGE | Mathewson 345kV
GEN-2016-057 | 04 SOUTHEAST | DIS-16-1 | Wind | 499.1 | ER | OKGE | Mathewson 345kV
GEN-2016-046 | 03 CENTRAL | DIS-16-1 | Wind | 299 | ER | SUNC | Clark County-Ironwood 345kV
GEN-2016-047_PQOKGEMustang | 04 SOUTHEAST | DIS-16-1 | CT | 134 | ER | OKGE
GEN-2016-050 | 02 NEBRASKA | DIS-16-1 | Wind | 250.7 | ER | NPPD | Axtell – Post Rock 345 kV
GEN-2016-071 | 04 SOUTHEAST | DIS-16-1 | Wind | 64.6 | ER | OKGE | Middleton Tap 138kV Substation
GEN-2016-075 | 02 NEBRASKA | DIS-16-1 | Wind | 50 | ER | WAPA | Fort Thompson-Grand Island (Grand Prairie) 345kV
GEN-2015-034 | 04 SOUTHEAST | DIS-16-1 | Wind | 200 | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV
GEN-2014-040 | 05 SOUTHWEST | DIS-16-1 | Wind | 320 | ER | SPS | Castro 115kV
GEN-2016-028 | 04 SOUTHEAST | DIS-16-1 | Wind | 100 | ER | AEPW | Clayton 138 kV Sub
GEN-2010-055 | 04 SOUTHEAST | DIS-16-1 | Gas | 4.5 | ER | AEPW | Wekiwa 138kV
GEN-2011-019 | 04 SOUTHEAST | DIS-16-1 | Wind | 175 | ER/NR | OKGE | Woodward EHV 345kV
GEN-2011-020 | 04 SOUTHEAST | DIS-16-1 | Wind | 165.6 | ER/NR | OKGE | Woodward EHV 345kV
GEN-2015-088 | 02 NEBRASKA | DIS-16-1 | Wind | 300 | ER/NR | NPPD | Tobias 345kV Substation
GEN-2011-018 | 02 NEBRASKA | DIS-16-1 | Wind | 73.6 | ER/NR | NPPD | Steele City 115kV
GEN-2011-040 | 04 SOUTHEAST | DIS-16-1 | Wind | 111 | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV
GEN-2011-056 | 02 NEBRASKA | DIS-16-1 | Hydro | 3.6 | ER | NPPD | Jeffrey 115kV
GEN-2011-056A | 02 NEBRASKA | DIS-11-2 | Hydro | 3.6 | ER | NPPD | John 1 115kV
GEN-2011-056B | 02 NEBRASKA | DIS-11-2 | Hydro | 4.5 | ER | NPPD | John 2 115kV
ASGI-2012-006 | 03 CENTRAL | DIS-16-1 | Steam | 22.5 | ER | SUNC
GEN-2012-004 | 04 SOUTHEAST | DIS-16-1 | Wind | 40.8 | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV
ASGI-2012-002 | 05 SOUTHWEST | DIS-16-1 | Wind | 18.15 | ER | SPS | FEC 69kV line
GEN-2014-032 | 02 NEBRASKA | DIS-16-1 | Wind | 10.2 | ER/NR | NPPD | Meadow Grove 230kV
GEN-2015-052 | 03 CENTRAL | DIS-16-1 | Wind | 300 | ER | WERE | Open Sky-Rose Hill 345kV
GEN-2015-066 | 04 SOUTHEAST | DIS-16-1 | Wind | 219.96 | ER | OKGE | Sooner - Cleveland 345kV
GEN-2013-012 | 04 SOUTHEAST | DIS-16-1 | Gas | 147 | ER | OKGE | Redbud 345kV
GEN-2006-010_GEN-2013-011 | 04 SOUTHEAST | DIS-16-1 | Coal | 650 | ER | AEPW
ASGI-2013-005 | 05 SOUTHWEST | DIS-16-1 | Wind | 1.65 | ER | SPS
GEN-2013-002_GEN-2013-019 | 02 NEBRASKA | DIS-16-1 | Wind | 124.2 | ER/NR | NPPD
GEN-2013-008 | 02 NEBRASKA | DIS-16-1 | Wind | 1.2 | ER | NPPD | Steele City 115kV
ASGI-2013-002 | 05 SOUTHWEST | DIS-16-1 | Wind | 18.4 | ER | SPS
ASGI-2013-003 | 05 SOUTHWEST | DIS-16-1 | Wind | 18.4 | ER | SPS
GEN-2013-033 | 03 CENTRAL | DIS-13-2 | Gas | 28 | ER/NR | MIDW | Goodman Energy Center 115kV
GEN-2014-001 | 03 CENTRAL | DIS-16-1 | Wind | 200.6 | ER | WERE | Tap Wichita - Emporia Energy Center 345kV
GEN-2014-056_GEN-2015-057 | 04 SOUTHEAST | DIS-16-1 | Wind | 350 | ER | OKGE
GEN-2016-094 | 01 NORTH | DIS-16-2 | Wind | 200 | ER | BEPC | Tap Ft Thompson - Oahe 230kV Line (Single Circuit)
GEN-2016-111 | 03 CENTRAL | DIS-16-2 | Wind | 302 | ER | WERE | Reno - Summit 345kV
GEN-2016-119 | 04 SOUTHEAST | DIS-16-2 | Wind | 600 | ER | OKGE | Spring Creek-Sooner 345kV
GEN-2016-167 | 04 SOUTHEAST | DIS-16-2 | Solar | 73.5 | ER/NR | AEPW | Lieberman - North Benton 138 kV Line
ASGI-2016-010 | 05 SOUTHWEST | DIS-16-2 | Wind | 90 | ER | SPS | Powell Corner 115kV Substation
GEN-2016-097 | 04 SOUTHEAST | DIS-16-2 | Wind | 100 | ER/NR | AEPW | Tap Southwestern-Fletcher Tap 138kV
GEN-2016-102 | 04 SOUTHEAST | DIS-16-2 | Wind | 147.5 | ER/NR | OKGE | Blue River 138kV
GEN-2016-118 | 04 SOUTHEAST | DIS-16-2 | Wind | 288 | ER | WFEC | Dover Switchyard 138 kV Line
GEN-2016-126 | 04 SOUTHEAST | DIS-16-2 | Wind | 172.5 | ER/NR | OKGE | Arbuckle 138kV substation
GEN-2016-128 | 04 SOUTHEAST | DIS-16-2 | Wind | 176 | ER | OKGE | Woodring 345kV
GEN-2016-133_GEN-2016-134_GEN-2016-137_GEN-2016-138 | 04 SOUTHEAST | DIS-16-2 | Wind | 750 | ER | AEPW
GEN-2016-150 | 03 CENTRAL | DIS-16-2 | Wind | 302 | ER | WERE | Stranger Creek 345kV
GEN-2016-160 | 03 CENTRAL | DIS-16-2 | Battery/Storage | 20 | ER/NR | MIDW | Post Rock 230kV
GEN-2016-176 | 03 CENTRAL | DIS-16-2 | Wind | 302 | ER | WERE | Stranger Creek 345kV
GEN-2016-177 | 05 SOUTHWEST | DIS-16-2 | Gas Turbine | 17 | ER | SPS | XTO-Cornell 115 kV station
GEN-2016-132 | 04 SOUTHEAST | DIS-16-2 | Wind | 6.1 | ER | AEPW | Sweetwater 230kV
GEN-2017-040 | 04 SOUTHEAST | DIS-17-1 | Solar | 200.1 | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV
GEN-2017-061 | 04 SOUTHEAST | DIS-17-1 | Solar | 101.5 | ER | GRDA | GRDA1 to CLARMR 5 161kV line
GEN-2017-073 | 04 SOUTHEAST | DIS-17-1 | Solar | 72.5 | ER | GRDA | Dry Gulch 161kV sub
IR32 | 02 NEBRASKA | DIS-17-2-PQ | Wind | 56 | ER/NR | ALTW
BEPCNDPW1 | 01 NORTH | DIS-17-1 | Wind | 5 | ER | BEPC
GEN-2017-014 | 01 NORTH | DIS-17-1 | Wind | 300 | ER | WAPA | Philip Tap 230 kV
GEN-2017-018 | 03 CENTRAL | DIS-17-1 | Solar | 189 | ER/NR | SUNC | Thistle 345 kV sub
GEN-2017-022 | 03 CENTRAL | DIS-17-1 | Solar | 65 | ER/NR | WERE | Altoona- NE Parson 138kV
GEN-2017-071_GEN-2017-072_GEN-2024-SR5 | 04 SOUTHEAST | DIS-17-1 | Solar | 176.9 | ER | OKGE
GEN-2017-100 | 05 SOUTHWEST | DIS-17-1 | Solar | 102.6 | ER/NR | SPS | Texas County 115kV
GEN-2017-097 | 01 NORTH | DIS-17-1 | Solar | 128 | ER | WAPA | Underwood 115 kV Sub
GEN-2017-092 | 04 SOUTHEAST | DIS-17-1 | Solar | 200 | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV
GEN-2017-036 | 04 SOUTHEAST | DIS-17-1 | Solar | 100 | ER | WFEC | Snyder - Cache 138 kV
GEN-2017-068 | 03 CENTRAL | DIS-17-1 | Solar | 103.5 | ER/NR | WERE | Gordon Evans 138kV Substation
GEN-2017-004 | 03 CENTRAL | DIS-17-1 | Wind | 201.6 | ER | SUNC | Elm Creek - Summit 345 kV
GEN-2017-023 | 04 SOUTHEAST | DIS-17-1 | Solar | 85 | ER/NR | WFEC | Hugo Power Plant 138 kV Sub
GEN-2016-037 | 04 SOUTHEAST | DIS-17-1 | Wind | 300 | ER | AEPW | Chisholm-Gracemont 345kV
GEN-2017-033 | 05 SOUTHWEST | DIS-17-1 | Wind | 200 | ER | AEPW | Oklaunion 345 kV sub
GEN-2017-086 | 03 CENTRAL | DIS-17-1 | Wind | 150 | ER | WERE | Viola 345kV
GEN-2017-094 | 01 NORTH | DIS-17-1 | Wind | 200 | ER | WAPA | Fort Thompson-Huron 230 kV
GEN-2017-047 | 05 SOUTHWEST | DIS-17-1 | Wind | 102 | ER/NR | SPS | Bull Creek 115 kV substation
GEN-2017-105 | 02 NEBRASKA | DIS-17-2 | Wind | 75 | ER/NR | OPPD | Tekamah - Raun 161 kV Line
GEN-2017-108 | 03 CENTRAL | DIS-17-2 | Solar | 400 | ER/NR | KCPL | Stillwell - Clinton 161kV Line
GEN-2017-117 | 04 SOUTHEAST | DIS-17-2 | Battery/Storage | 19.8 | ER/NR | WFEC | El Reno SW 138kV
GEN-2017-121 | 03 CENTRAL | DIS-17-2 | Wind | 200 | ER/NR | WERE | Sumner 138kV
GEN-2017-133 | 04 SOUTHEAST | DIS-17-2 | Wind | 200 | ER/NR | OKGE | Arcadia 345kV
GEN-2017-134 | 04 SOUTHEAST | DIS-17-2 | Wind | 250 | ER/NR | OKGE | Arcadia 345kV
GEN-2017-137 | 04 SOUTHEAST | DIS-17-2 | Wind | 295 | ER/NR | OKGE | Arcadia 345kV
GEN-2017-140 | 04 SOUTHEAST | DIS-17-2 | Solar | 160 | ER/NR | AEPW | Clarksville 345kV Switching Station
GEN-2017-141 | 04 SOUTHEAST | DIS-17-2 | Solar | 241.7 | ER/NR | AEPW | Clarksville 345kV Switching Station
GEN-2017-144 | 02 NEBRASKA | DIS-17-2 | Wind | 200 | ER | NPPD | Holt County 345kV
GEN-2017-146 | 05 SOUTHWEST | DIS-17-2 | Wind | 151.8 | ER | SPS | Deaf Smith-Plant X 230kV
GEN-2017-149 | 04 SOUTHEAST | DIS-17-2 | Wind | 258 | ER/NR | OKGE | Johnson County 345kV Substation
GEN-2017-151 | 05 SOUTHWEST | DIS-17-2 | Wind | 300 | ER | SPS | TUCO-Oklaunion 345kV
GEN-2017-158 | 05 SOUTHWEST | DIS-17-2 | Wind | 265 | ER | SPS | Tolk 230kV Substation
GEN-2017-164 | 04 SOUTHEAST | DIS-17-2 | Solar | 250 | ER/NR | OKGE | Woodring 345kV Substation
GEN-2017-171 | 04 SOUTHEAST | DIS-17-2 | Solar | 150 | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV
GEN-2017-172 | 04 SOUTHEAST | DIS-17-2 | Solar | 50 | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV
GEN-2017-173 | 04 SOUTHEAST | DIS-17-2 | Solar | 50 | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV
GEN-2017-175 | 01 NORTH | DIS-17-2 | Wind | 270 | ER | WAPA | Vfodnes-Utica Jct. 230kV
GEN-2017-178 | 04 SOUTHEAST | DIS-17-2 | Battery/Storage | 52 | ER/NR | OKGE | Woodring 345kV Substation
GEN-2017-181 | 02 NEBRASKA | DIS-17-2 | Wind | 300 | ER/NR | NPPD | Tobias 345kV Substation
GEN-2017-182 | 02 NEBRASKA | DIS-17-2 | Wind | 128 | ER/NR | NPPD | Tobias 345kV Substation
GEN-2007-020IS | 01 NORTH | DIS-16-1 | Wind | 16 | ER/NR | BEPC
GEN-2015-045 | 04 SOUTHEAST | DIS-16-1 | Battery/Storage | 10.3 | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV
GEN-2009-001IS | 01 NORTH | DIS-16-1 | Wind | 200 | ER/NR | BEPC
GEN-2007-013IS | 01 NORTH | DIS-16-1 | Wind | 100 | ER/NR | BEPC
GEN-2017-222 | 01 NORTH | DIS-17-2 | Wind | 180 | ER | WAPA | Denison 230kV Substation
GEN-2017-183 | 03 CENTRAL | DIS-17-2 | Wind | 400 | ER/NR | KCPL | Nashua-St. Joe 345kV
GEN-2017-184 | 03 CENTRAL | DIS-17-2 | Solar | 400 | ER/NR | KCPL | Nashua-St. Joe 345kV
GEN-2017-188 | 03 CENTRAL | DIS-17-2 | Solar | 130 | ER | EMDE | Asbury 161 kV
GEN-2017-195 | 03 CENTRAL | DIS-17-2 | Solar | 500.4 | ER/NR | KCPL | West Gardner 345kV
GEN-2017-196 | 03 CENTRAL | DIS-17-2 | Battery/Storage | 128 | ER/NR | KCPL | West Gardner 345kV
GEN-2017-198 | 02 NEBRASKA | DIS-17-2 | Battery/Storage | 11.64 | ER | OPPD | Jones St. No 1201 69kV substation
GEN-2017-201 | 02 NEBRASKA | DIS-17-2 | Wind | 250 | ER/NR | NPPD | Hoskins 345kV Substation
GEN-2017-214 | 01 NORTH | DIS-17-2 | Wind | 100 | ER/NR | WAPA | Logan 230kV Substation
GEN-2017-215 | 01 NORTH | DIS-17-2 | Wind | 100 | ER/NR | WAPA | Logan 230kV Substation
GEN-2017-220 | 03 CENTRAL | DIS-17-2 | Solar | 201.6 | ER/NR | WERE | Buffalo Flats 345kV Substation
GEN-2017-221 | 03 CENTRAL | DIS-17-2 | Battery/Storage | 152 | ER/NR | WERE | Buffalo Flats 345kV Substation
GEN-2017-226 | 03 CENTRAL | DIS-17-2 | Solar | 201.6 | ER/NR | WERE | Gordon Evans 138kV Substation
GEN-2017-227 | 03 CENTRAL | DIS-17-2 | Storage | 201.6 | ER/NR | WERE | Gordon Evans 138kV Substation
GEN-2017-150 | 04 SOUTHEAST | DIS-17-2 | Solar | 250 | ER/NR | OKGE | Minco 345kV
GEN-2017-232 | 04 SOUTHEAST | DIS-17-2 | Solar | 52.2 | ER/NR | OKGE | Brown 138kV Substation
GEN-2017-233 | 04 SOUTHEAST | DIS-17-2 | Wind | 215 | ER/NR | OKGE | Minco 345kV
GEN-2017-239 | 05 SOUTHWEST | DIS-17-2 | Solar | 300 | ER | SPS | Mahoney 230kV Substation
GEN-2017-234 | 02 NEBRASKA | DIS-17-2 | Wind | 115 | ER | NPPD | Spalding to North Loup 115kV
GEN-2020-083 | 01 NORTH | DIS-20-1 | Solar | 74.5 | ER/NR | WAPA | Fairview 115kV Substation
GEN-2018-026 | 04 SOUTHEAST | DIS-18-1 | Battery/Storage | 100 | ER | OKGE | Mustang 138kV Substation
GEN-2018-027 | 04 SOUTHEAST | DIS-18-1 | Battery/Storage | 100 | ER | OKGE | Tulsa Power Station 138kV Substation
GEN-2018-028 | 04 SOUTHEAST | DIS-18-1 | Battery/Storage | 200 | ER | AEPW | Tulsa North 138kV Substation
GEN-2018-029 | 04 SOUTHEAST | DIS-18-1 | Battery/Storage | 100 | ER | OKGE | Horseshoe Lake 138kV Substation
GEN-2018-031 | 03 CENTRAL | DIS-18-1 | Battery/Storage | 50 | ER | KCPL | Blue Valley 161kV Substation
GEN-2018-033 | 02 NEBRASKA | DIS-18-1 | Battery/Storage | 200 | ER | OPPD | Cass County 345kV Substation
GEN-2018-037 | 02 NEBRASKA | DIS-18-1 | Battery/Storage | 100 | ER | OPPD | Looping in OPPD (S1211) (S1220) (S1211) (S1299) 161kV
GEN-2018-043 | 02 NEBRASKA | DIS-18-1 | Solar | 500 | ER | OPPD | Ft. Calhoun - Raun 345 kV Line Break
GEN-2018-048 | 04 SOUTHEAST | DIS-18-1 | Solar | 300 | ER | OKGE | Pecan Creek 345kV Substation
GEN-2018-049 | 03 CENTRAL | DIS-18-1 | Solar | 120 | ER | SUNC | Thistle 345kV Substation
GEN-2018-050 | 04 SOUTHEAST | DIS-18-1 | Solar | 200 | ER | AEPW | Longwood 345kV Substation
GEN-2018-052 | 05 SOUTHWEST | DIS-18-1 | Battery/Storage | 70 | ER | SPS | Roadrunner 115kV Substation
GEN-2018-055 | 04 SOUTHEAST | DIS-18-1 | Solar | 252 | ER/NR | AEPW | Terry Road 345kV station (shared with Rush Springs Windfarm on a common gentie)
GEN-2018-057 | 03 CENTRAL | DIS-18-1 | Solar | 203.4 | ER/NR | WERE | Gordon Evans 138kV
GEN-2018-064 | 04 SOUTHEAST | DIS-18-2_19-1 | Solar | 80 | ER/NR | GRDA | Tonnece Substation 69kV
GEN-2018-067 | 01 NORTH | DIS-18-2_19-1 | Wind | 255 | ER | BEPC | 115kV Strandahl sub
GEN-2018-071 | 04 SOUTHEAST | DIS-18-2_19-1 | Battery/Storage | 151 | ER/NR | OKGE | Interconnecting into OG&E's Ranch Road 345kV substation by tapping a 0.1 gen tie line into the existing Frontier II gen-tie line
GEN-2018-072 | 04 SOUTHEAST | DIS-18-2_19-1 | Battery/Storage | 151 | ER/NR | OKGE | Interconnecting into OG&E's Ranch Road 345kV substation by tapping a 0.1 gen tie line into the existing Frontier II gen-tie line
GEN-2018-074 | 01 NORTH | DIS-18-2_19-1 | Wind | 72 | ER | WAPA | Denison 230kV Substation
GEN-2018-079 | 04 SOUTHEAST | DIS-18-2_19-1 | Solar | 148 | ER | AEPW | Farmland-Delaware 138kV line
GEN-2018-082 | 04 SOUTHEAST | DIS-18-2_19-1 | Wind | 215 | ER | AEPW | Pittsburg 345kV Substation
GEN-2018-089 | 05 SOUTHWEST | DIS-18-2_19-1 | Wind | 196 | ER | SPS | Newhart 230kV Substation
GEN-2018-099 | 05 SOUTHWEST | DIS-18-2_19-1 | Wind | 300 | ER | SPS | Tolk 230kV Substation
GEN-2018-106 | 04 SOUTHEAST | DIS-18-2_19-1 | Solar | 165 | ER | AEPW | Longwood 345kV substation
GEN-2018-108 | 03 CENTRAL | DIS-18-2_19-1 | Battery/Storage | 95 | ER | SUNC | Thistle 345kV substation
GEN-2018-115 | 04 SOUTHEAST | DIS-18-2_19-1 | Solar | 250 | ER/NR | AEPW | Lawton East Side 345kV/138kv Substation
GEN-2018-125 | 02 NEBRASKA | DIS-18-2_19-1 | Wind | 231 | ER/NR | NPPD | New switching station on Gentleman to Sweetwater 345kV line
GEN-2018-128 | 03 CENTRAL | DIS-18-2_19-1 | Wind | 200.22 | ER/NR | OKGE | Renfrow-Viola 345 kV
GEN-2018-131 | 02 NEBRASKA | DIS-18-2_19-1 | Solar | 221.4 | ER/NR | NPPD | Antelope - Hoskins 345 kV
GEN-2018-132 | 02 NEBRASKA | DIS-18-2_19-1 | Solar | 201.6 | ER/NR | NPPD | Antelope - Hoskins 345 kV
GEN-2019-001 | 03 CENTRAL | DIS-18-2_19-1 | Wind | 25 | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV
GEN-2019-002 | 04 SOUTHEAST | DIS-18-2_19-1 | Battery/Storage | 100 | ER | GRDA | Maid 161kV substation
GEN-2019-003 | 05 SOUTHWEST | DIS-18-2_19-1 | Solar | 150 | ER/NR | SPS | Roosevelt 230kV Substation
GEN-2019-011 | 05 SOUTHWEST | DIS-18-2_19-1 | Battery/Storage | 207 | ER/NR | SPS | Yoakum 345kV Substation
GEN-2019-016 | 03 CENTRAL | DIS-18-2_19-1 | Solar | 200 | ER | EMDE | Dadeville 161kV Substation
GEN-2019-021 | 05 SOUTHWEST | DIS-18-2_19-1 | Solar | 50 | ER/NR | SPS | Roosevelt 230kV Substation
GEN-2019-030 | 03 CENTRAL | DIS-18-2_19-1 | Wind | 252 | ER/NR | SUNC | Spearville to Clark County 345 kV line
GEN-2019-037 | 01 NORTH | DIS-18-2_19-1 | Solar | 150 | ER/NR | BEPC | Leland Olds 345kV substation
GEN-2019-039 | 02 NEBRASKA | DIS-18-2_19-1 | Solar | 174.5 | ER/NR | NPPD | Columbus Southeast-Rising City 115kV
GEN-2019-041 | 02 NEBRASKA | DIS-18-2_19-1 | Solar | 78 | ER/NR | NPPD | 115kV Monolith Substation
GEN-2019-044 | 03 CENTRAL | DIS-18-2_19-1 | Solar | 100 | ER | SUNC | North Fort Dodge 115kV Substation
GEN-2019-045 | 04 SOUTHEAST | DIS-18-2_19-1 | Solar | 155 | ER | OKGE | DeGrasse 138kV Substation
GEN-2019-053 | 03 CENTRAL | DIS-18-2_19-1 | Battery/Storage | 50 | ER/NR | SUNC | Great Bend-Spearville 230kV line
GEN-2019-054 | 03 CENTRAL | DIS-18-2_19-1 | Solar | 150 | ER/NR | SUNC | Great Bend- Circle 230kV line
GEN-2019-055 | 03 CENTRAL | DIS-18-2_19-1 | Solar | 150 | ER/NR | SUNC | Great Bend-Spearville 230kV line
GEN-2019-058 | 03 CENTRAL | DIS-18-2_19-1 | Solar | 150 | ER/NR | SUNC | Clark County 345kV substation
GEN-2019-063 | 03 CENTRAL | DIS-18-2_19-1 | Battery/Storage | 50 | ER/NR | SUNC | Clark County 345kV substation
GEN-2019-065 | 04 SOUTHEAST | DIS-18-2_19-1 | Battery/Storage | 180 | ER | AEPW | Overton-Northwest Henderson 138kV
GEN-2019-068 | 03 CENTRAL | DIS-18-2_19-1 | Battery/Storage | 50 | ER/NR | SUNC | Great Bend - Circle 230kV line
GEN-2019-018 | 03 CENTRAL | DIS-18-2_19-1 | Thermal | 15.56 | ER/NR | MIDW | Saxman 115kV substation
GEN-2019-019 | 01 NORTH | DIS-18-2_19-1 | Thermal | 15.15 | ER/NR | BEPC | Siouxland 69kV
GEN-2018-004 | 05 SOUTHWEST | DIS-18-1 | Solar | 74.99 | ER | SPS | T14 Circuit 115kV line
ASGI-2018-003 | 03 CENTRAL | DIS-18-1 | Solar | 20 | ER | KCPL | Tap Appleton - Rockbille 34.5kV
ASGI-2018-006 | 03 CENTRAL | DIS-18-1 | Solar | 20 | ER | KCPL | Tap Metz-Dederick Junction 34.5kV
ASGI-2018-007 | 03 CENTRAL | DIS-18-1 | Solar | 20 | ER | KCPL | Tap Salisbury - Glasgow 34.5kV
ASGI-2018-010 | 03 CENTRAL | DIS-18-1 | Solar | 35 | ER | KCPL | Tap Wal-Mart-Rock Creek 34.5kV
ASGI-2018-011 | 03 CENTRAL | DIS-18-1 | Solar | 35 | ER | KCPL | Tap Rock Creek-Lane 34.5kV
GEN-2018-009 | 03 CENTRAL | DIS-18-1 | Wind | 150 | ER | SUNC | Cimarron 115kV Substation
GEN-2018-011 | 04 SOUTHEAST | DIS-18-1 | Battery/Storage | 74.1 | ER/NR | WFEC | Dover 138 kV Switching Station
GEN-2018-025 | 02 NEBRASKA | DIS-18-1 | Battery/Storage | 200 | ER | OPPD | Fort Calhoun 345kV Substation
GEN-2018-003 | 04 SOUTHEAST | DIS-18-1 | Solar | 150 | ER/NR | AEPW | North Boston-Bann 138kV Line
GEN-2020-078 | 02 NEBRASKA | DIS-20-1 | Solar | 100 | ER/NR | OPPD | Substation 1226 to Substation 1237, 161kV Tap
GEN-2020-079 | 03 CENTRAL | DIS-20-1 | Solar | 225 | ER/NR | EMDE | Riverton-Neosho 161kV line
GEN-2020-081 | 04 SOUTHEAST | DIS-20-1 | Battery/Storage | 200 | ER/NR | AEPW | Tenaska Switching Substation 345kV
GEN-2020-088 | 03 CENTRAL | DIS-20-1 | Solar | 150 | ER/NR | EMDE | La Russell 161 kV Substation
GEN-2020-090 | 03 CENTRAL | DIS-20-1 | Battery/Storage | 204.3 | ER/NR | WERE | Wolf Creek - Blackberry 345 kV Substation
GEN-2020-092 | 04 SOUTHEAST | DIS-20-1 | Solar | 100 | ER/NR | AEPW | Pryor Junction - Midwest Carbide 138kV line
GEN-2020-094 | 02 NEBRASKA | DIS-20-1 | Solar | 250 | ER/NR | OPPD | Neb. City - 103rd & Rokeby 345 kV
MPC03600 | 01 NORTH | DIS-18-1-PQ | Solar | 167.2 | ER | OTP
MPC03700 | 01 NORTH | DIS-18-1-PQ | Solar | 127.9 | ER | OTP
GEN-2016-095 | 04 SOUTHEAST | DIS-16-2 | Wind | 200 | ER/NR | AEPW | Gracemont-Lawton East Side 345kV
GEN-2017-187 | 05 SOUTHWEST | DIS-17-2 | Solar | 150 | ER | SPS | Flatland 115 kV Substation
GEN-2018-015 | 05 SOUTHWEST | DIS-18-1 | Solar | 252 | ER/NR | SPS | Tuco-Oklaunion 345kV Line
MPC03800 | 01 NORTH | DIS-18-1-PQ | Wind | 230 | ER/NR | OTP
MPC03900 | 01 NORTH | DIS-18-1-PQ | Wind | 140 | ER/NR | OTP
MPC04000 | 01 NORTH | DIS-18-1-PQ | Wind | 284 | ER/NR | OTP
GEN-2021-052 | 04 SOUTHEAST | DIS-21-1 | Battery/Storage | 75 | ER | OKGE | Pecan Creek 345kV substation
GEN-2021-053 | 04 SOUTHEAST | DIS-21-1 | Solar | 300 | ER | OKGE | Pecan Creek 345 kV Substation
GEN-2021-063 | 04 SOUTHEAST | DIS-21-1 | Solar | 155 | ER/NR | AEPW | Craig JCT 138kV
GEN-2021-064 | 04 SOUTHEAST | DIS-21-1 | Solar | 100 | ER/NR | AEPW | Carnegie South 138kV
GEN-2021-068 | 03 CENTRAL | DIS-21-1 | Wind | 249.6 | ER | SUNC | SUNC Spearville - Holcomb 345kV
GEN-2021-069 | 03 CENTRAL | DIS-21-1 | Wind | 249.6 | ER | SUNC | SUNC Spearville - Holcomb 345kV
GEN-2021-070 | 03 CENTRAL | DIS-21-1 | Wind | 504 | ER | SUNC | SUNC Spearville - Holcomb 345kV
GEN-2021-077 | 03 CENTRAL | DIS-21-1 | Solar | 95 | ER/NR | KCPL | Windsor to AEC Sedalia 161 kV
GEN-2021-088 | 04 SOUTHEAST | DIS-21-1 | Battery/Storage | 100 | ER/NR | OKGE | Cedar Lane - Canadian 138 kV Transmission Line
GEN-2021-090 | 05 SOUTHWEST | DIS-21-1 | Solar | 400 | ER/NR | SPS | Yoakum 345kV Substation
GEN-2021-096 | 03 CENTRAL | DIS-21-1 | Solar | 500 | ER/NR | WERE | Wolf Creek - Benton 345 kV
GEN-2021-101 | 03 CENTRAL | DIS-21-1 | Solar | 159 | ER/NR | WERE | Evergy's Midland Substation 115kV bus
GEN-2021-103 | 03 CENTRAL | DIS-21-1 | Battery/Storage | 150 | ER/NR | WERE | Evergy's Atlantic Substation115kV bus
GEN-2021-107 | 03 CENTRAL | DIS-21-1 | Solar | 201.6 | ER | WERE | Evergy 345kV Jeffrey Energy Center
GEN-2021-108 | 02 NEBRASKA | DIS-21-1 | Solar | 182.25 | ER/NR | OPPD | OPPD 345KV Cass County Substation
GEN-2020-084 | 02 NEBRASKA | DIS-20-1 | Solar | 350 | ER/NR | OPPD | Raun - Fort Calhoun 345 kV
ASGI-2020-001 | 03 CENTRAL | DIS-20-1 | Solar | 35 | ER | KCPL
ASGI-2020-003 | 03 CENTRAL | DIS-20-1 | Solar | 35 | ER | KCPL
GEN-2020-003 | 03 CENTRAL | DIS-20-1 | Thermal | 58 | ER/NR | WERE | East Substation 69 kV
GEN-2020-007 | 03 CENTRAL | DIS-20-1 | Solar | 650 | ER/NR | KCPL | Evergy La Cygne to Wolf Creek 345kV Substation
GEN-2020-008 | 03 CENTRAL | DIS-20-1 | Solar | 250 | ER | SPS | Corporation Carpenter 345kV Substation
GEN-2020-010 | 04 SOUTHEAST | DIS-20-1 | Solar | 140 | ER/NR | WFEC | Seiling-Taloga Substations 138kV
GEN-2020-011 | 02 NEBRASKA | DIS-20-1 | Solar | 320 | ER/NR | NPPD | Axtell 345 kV Substation
GEN-2020-012 | 04 SOUTHEAST | DIS-20-1 | Solar | 113 | ER/NR | AEPW | Snyder – Altus Jct. 138kV
GEN-2020-013 | 02 NEBRASKA | DIS-20-1 | Solar | 215 | ER/NR | NPPD | Orleans-Holdrege Substation 115kV
GEN-2020-014 | 01 NORTH | DIS-20-1 | Thermal | 45 | ER/NR | WAPA | Lonesome Creek 115kV
GEN-2020-020 | 04 SOUTHEAST | DIS-20-1 | Solar | 201.6 | ER/NR | AEPW | Tap the 345 kV Northwest Texarkana - Valliant line
GEN-2020-025 | 02 NEBRASKA | DIS-20-1 | Thermal | 255 | ER | OPPD | Substation 1363; 161kV Substation
GEN-2020-028 | 02 NEBRASKA | DIS-20-1 | Thermal | 255 | ER | OPPD | Substation 1363; 161kV Substation
GEN-2020-031 | 02 NEBRASKA | DIS-20-1 | Thermal | 272.7 | ER | OPPD | Substation 1363; 161kV Substation
GEN-2020-038 | 02 NEBRASKA | DIS-20-1 | Thermal | 272.7 | ER | OPPD | Substation 3740; 345kV
GEN-2020-043 | 02 NEBRASKA | DIS-20-1 | Thermal | 56.52 | ER | OPPD | Between Substation 1209 and 1252; 161kV
GEN-2020-044 | 02 NEBRASKA | DIS-20-1 | Thermal | 56.52 | ER | OPPD | Between Substation 1209 and 1252; 161kV
GEN-2020-045 | 02 NEBRASKA | DIS-20-1 | Thermal | 56.52 | ER | OPPD | Between Substation 1209 and 1252; 161kV
GEN-2020-054 | 04 SOUTHEAST | DIS-20-1 | Solar | 298 | ER/NR | AEPW | Lydia 345 kV Station
GEN-2020-057 | 03 CENTRAL | DIS-20-1 | Battery/Storage | 424.5 | ER/NR | KCPL | Atlantic 345 kV Substation
GEN-2020-058 | 03 CENTRAL | DIS-20-1 | Solar | 424.5 | ER/NR | KCPL | Atlantic 345 kV Substation
GEN-2020-060 | 05 SOUTHWEST | DIS-20-1 | Battery/Storage | 200 | ER | SPS | Lubbock East Substation 230 kV
GEN-2020-061 | 03 CENTRAL | DIS-20-1 | Thermal | 29 | ER/NR | KCPL | Pleasant Hill 345/161/69 kV Substation
GEN-2020-064 | 03 CENTRAL | DIS-20-1 | Thermal | 64 | ER/NR | EMDE | 4544 Stateline CC 161kV Substation
GEN-2020-067 | 05 SOUTHWEST | DIS-20-1 | Wind | 352.5 | ER | SPS | Tuco to Yoakum 345kV line
GEN-2020-069 | 02 NEBRASKA | DIS-20-1 | Wind | 52.85 | ER/NR | NPPD | Cody to Valentine 115kV line
GEN-2020-072 | 03 CENTRAL | DIS-20-1 | Solar | 150 | ER/NR | KCPL | Windsor to AEC Sedalia 161 kV line
GEN-2020-073 | 03 CENTRAL | DIS-20-1 | Solar | 150 | ER/NR | KCPL | SE Ottawa to Pleasant Valley 161kV
ASGI-2021-001 | 05 SOUTHWEST | DIS-21-1 | Solar | 50 | ER/NR | SPS
ASGI-2021-003 | 05 SOUTHWEST | DIS-21-1 | Solar | 40 | ER/NR | SPS
GEN-2021-001 | 04 SOUTHEAST | DIS-21-1 | Battery/Storage | 100 | ER/NR | OKGE | 138kV Brown Substation
GEN-2021-006 | 03 CENTRAL | DIS-21-1 | Battery/Storage | 300 | ER/NR | WERE | Neosho 345kV substation in Labette County, KS
GEN-2021-018 | 04 SOUTHEAST | DIS-21-1 | Solar | 231 | ER | OKGE | Sooner 345 kV
GEN-2021-019 | 04 SOUTHEAST | DIS-21-1 | Battery/Storage | 74.9 | ER/NR | OKGE | Sooner 345 kV
GEN-2021-021 | 03 CENTRAL | DIS-21-1 | Wind | 150 | ER | SPS | Carpenter 345 kV Substation
GEN-2021-023 | 04 SOUTHEAST | DIS-21-1 | Solar | 306.18 | ER | WERE | Wild Plains 345kV Substation
GEN-2021-025 | 04 SOUTHEAST | DIS-21-1 | Wind | 203.04 | ER | WFEC | Western Farmers 138kV Mooreland Substation
GEN-2021-027 | 02 NEBRASKA | DIS-21-1 | Solar | 102.06 | ER | NPPD | Olive Creek 115 kV Substation
GEN-2021-029 | 03 CENTRAL | DIS-21-1 | Battery/Storage | 253.8 | ER | KCPL | Evergy Tap the La Cygne to Stillwel 345 kV Line
GEN-2021-030 | 03 CENTRAL | DIS-21-1 | Solar | 510.3 | ER | KCPL | Evergy Tap the La Cygne to Stillwel 345 kV Line
GEN-2021-033 | 04 SOUTHEAST | DIS-21-1 | Solar | 204.12 | ER | OKGE | Branch 161kV Substation
GEN-2021-034 | 02 NEBRASKA | DIS-21-1 | Solar | 113 | ER | LES | Rokeby 115 kV Substation
GEN-2021-035 | 03 CENTRAL | DIS-21-1 | Solar | 113 | ER | SUNC | Tap Sunflower Santana 115kV Transmission Line
GEN-2021-036 | 04 SOUTHEAST | DIS-21-1 | Solar | 204.12 | ER/NR | AEPW | Craig to Patterson 138 kV Transmission Line
GEN-2021-038 | 04 SOUTHEAST | DIS-21-1 | Battery/Storage | 200 | ER/NR | AEPW | Welsh 345kV Substation
GEN-2021-039 | 02 NEBRASKA | DIS-21-1 | Battery/Storage | 100 | ER | OPPD | New 161kV substation looping in OPPD 161kV lines S1211 to S1220 and S1211 to S1299
GEN-2021-040 | 02 NEBRASKA | DIS-21-1 | Battery/Storage | 200 | ER | OPPD | OPPD District, Cass County Power Plant Substation, 345kV Bus
GEN-2021-041 | 04 SOUTHEAST | DIS-21-1 | Battery/Storage | 100 | ER/NR | OKGE | Mustang 138kV Substation
GEN-2021-042 | 03 CENTRAL | DIS-21-1 | Battery/Storage | 50 | ER/NR | KCPL | Independence Power & Light, Blue Valley Substation, 161kV Bus
GEN-2021-043 | 02 NEBRASKA | DIS-21-1 | Battery/Storage | 250 | ER | LES | 8000 SW 12th (Rokeby) Station, 115kV Bus
GEN-2021-047 | 04 SOUTHEAST | DIS-21-1 | Solar | 250 | ER | GRDA | Tulsa (Bus #509852) - Igloo (Bus #513596) 345kV line
GEN-2021-048 | 02 NEBRASKA | DIS-21-1 | Battery/Storage | 75 | ER/NR | LES | Wagener 115kV Substation
GEN-2021-049 | 02 NEBRASKA | DIS-21-1 | Solar | 225 | ER/NR | LES | Wagener 115kV Substation
GEN-2023-120 | 05 SOUTHWEST | DIS-23-1 | Solar | 130 | ER | SPS | Kress 115 kV Substation
GEN-2023-132 | 04 SOUTHEAST | DIS-23-1 | Solar | 150 | ER/NR | SWPA | Jonesboro - Independence 161 kV
GEN-2023-135 | 04 SOUTHEAST | DIS-23-1 | Solar | 52 | ER/NR | AEPW | Lydia 345kV substation
GEN-2023-153 | 02 NEBRASKA | DIS-23-1 | Solar | 120 | ER/NR | NPPD | Grant 115 kV Substation
GEN-2023-161 | 04 SOUTHEAST | DIS-23-1 | Storage | 74.9 | ER/NR | OKGE | Roman Nose 138 kV Substation
GEN-2023-170 | 03 CENTRAL | DIS-23-1 | Storage | 150 | ER | KCPL | Salisbury 161 kV Substation
GEN-2023-171 | 03 CENTRAL | DIS-23-1 | Storage | 150 | ER/NR | INDN | Sub M 161 kV Substation
GEN-2023-172 | 03 CENTRAL | DIS-23-1 | Wind | 200 | ER/NR | SUNC | Holcomb 345 kV
GEN-2023-173 | 03 CENTRAL | DIS-23-1 | Wind | 100 | ER/NR | SUNC | Holcomb 345 kV
GEN-2023-177 | 04 SOUTHEAST | DIS-23-1 | Solar | 200 | ER/NR | OKGE | Paoli - Seminole 138 kV line tap
GEN-2023-193 | 04 SOUTHEAST | DIS-23-1 | Solar | 175 | ER/NR | AEPW | Pirkey - Whitney 138 kV Line
GEN-2023-199 | 02 NEBRASKA | DIS-23-1 | Solar | 250 | ER/NR | NPPD | Twin Church 230 kV Substation
GEN-2023-204 | 04 SOUTHEAST | DIS-23-1 | Thermal | 914.6 | ER | AEPW | Welsh-Lydia 345kV Line
GEN-2023-205 | 04 SOUTHEAST | DIS-23-1 | Solar | 180 | ER/NR | AEPW | McAlester City - Weleetka 138 kV line
GEN-2023-210 | 04 SOUTHEAST | DIS-23-1 | Solar | 191 | ER/NR | WFEC | Prague - Chernicky 138 kV Line
GEN-2023-220 | 03 CENTRAL | DIS-23-1 | Solar | 250 | ER/NR | WERE | Emporia Energy Center - Swissvale 345 kV Line
GEN-2023-221 | 03 CENTRAL | DIS-23-1 | Solar | 250 | ER/NR | WERE | Emporia Energy Center - Swissvale 345 kV Line
GEN-2023-222 | 02 NEBRASKA | DIS-23-1 | Thermal | 478 | ER/NR | NPPD | New Beatrice Power Station 345 kV
GEN-2023-223 | 02 NEBRASKA | DIS-23-1 | Thermal | 239 | ER/NR | NPPD | New Beatrice Power Station 345 kV
GEN-2023-224 | 02 NEBRASKA | DIS-23-1 | Thermal | 478 | ER | NPPD | Olive Creek 345 kV Substation
GEN-2023-229 | 04 SOUTHEAST | DIS-23-1 | Wind | 230 | ER/NR | AEPW | Southwestern Power Station 138 kV Substation (SWS4)
GEN-2023-230 | 04 SOUTHEAST | DIS-23-1 | Solar | 150 | ER/NR | WAPA | Red Pointe 138 kV Substation
GEN-2023-241 | 04 SOUTHEAST | DIS-23-1 | Solar | 93 | ER | AEPW | Winnsboro 138 kV Substation
GEN-2020-087 | 04 SOUTHEAST | DIS-20-1 | Solar | 500 | ER/NR | AEPW | Cimmarron to Lawton 345 kV Line
GEN-2022-235 | 04 SOUTHEAST | DIS-22-1 | Battery/Storage | 150 | ER/NR | WFEC | El Reno SW 138 kV
GEN-2022-083 | 01 NORTH | DIS-22-1 | Thermal | 250 | ER | BEPC | Judson Substation 345 kV
GEN-2022-139 | 04 SOUTHEAST | DIS-22-1 | Battery/Storage | 300 | ER | AEPW | Pirkey 345kV Substation
GEN-2022-142 | 03 CENTRAL | DIS-22-1 | Battery/Storage | 200 | ER | KCPL | Shoal Creek 161 kV Substation
GEN-2022-143 | 04 SOUTHEAST | DIS-22-1 | Battery/Storage | 200 | ER | OKGE | Caney Creek 138 kV Substation
GEN-2022-144 | 03 CENTRAL | DIS-22-1 | Battery/Storage | 200 | ER | KCPL | Blue Mills BESS 161kV Substation
GEN-2022-071 | 04 SOUTHEAST | DIS-22-1 | Solar | 90.824 | ER/NR | AEPW | Talawanda to Canadian River 138 kV Line Tap
GEN-2022-073 | 03 CENTRAL | DIS-22-1 | Battery/Storage | 300 | ER/NR | KCPL | Nashua-Smithville 161kV
GEN-2022-075 | 03 CENTRAL | DIS-22-1 | Solar | 175 | ER/NR | MIDW | Tap on the Spearville - Post Rock 345kV line
GEN-2022-098 | 04 SOUTHEAST | DIS-22-1 | Solar | 200 | ER/NR | OKGE | Bison 345kV Substation
GEN-2022-100 | 03 CENTRAL | DIS-22-1 | Solar | 80 | ER/NR | KCPL | Overton - Sedalia East 161 kV Substation
GEN-2022-102 | 03 CENTRAL | DIS-22-1 | Battery/Storage | 100 | ER/NR | KCPL | Liberty West 161 kV
GEN-2022-104 | 04 SOUTHEAST | DIS-22-1 | Solar | 113.078 | ER/NR | WFEC | Brown - South Coleman Junction 138kV line
GEN-2022-130 | 04 SOUTHEAST | DIS-22-1 | Battery/Storage | 200 | ER/NR | OKGE | Battlefield BESS 161kV
GEN-2022-154 | 04 SOUTHEAST | DIS-22-1 | Battery/Storage | 100 | ER | WFEC | Canadian Switch 138 kV Substation
GEN-2022-155 | 04 SOUTHEAST | DIS-22-1 | Battery/Storage | 200 | ER | OKGE | Horseshoe Lake 138 kV Substation
GEN-2022-156 | 04 SOUTHEAST | DIS-22-1 | Battery/Storage | 100 | ER | GRDA | Silver City 138 kV Substation
GEN-2022-176 | 04 SOUTHEAST | DIS-22-1 | Wind | 215 | ER/NR | AEPW | Northeastern - Delaware 345 kV transmission line
GEN-2022-214 | 03 CENTRAL | DIS-22-1 | Solar | 239 | ER | WERE | Gill - Viola 138 kV Line Break
GEN-2022-238 | 04 SOUTHEAST | DIS-22-1 | Battery/Storage | 150 | ER/NR | OKGE | Maud 138 kV substation
GEN-2023-225 | 02 NEBRASKA | DIS-23-1 | Thermal | 217 | ER | NPPD | Olive Creek 345 kV Substation
J1846 | 01 NORTH | DIS-22-1-PQ | Battery/Storage | 200 | ER/NR | XEL
J1867 | 04 SOUTHEAST | DIS-22-1-PQ | Wind | 200 | ER/NR | ALTW
J1889 | 02 NEBRASKA | DIS-22-1-PQ | Solar | 60 | ER/NR | ALTW
J1898 | 01 NORTH | DIS-22-1-PQ | Battery/Storage | 200 | ER/NR | XEL
J2027 | 01 NORTH | DIS-22-1-PQ | Solar | 150 | ER/NR | GRE
J2031 | 02 NEBRASKA | DIS-22-1-PQ | Wind | 100 | ER/NR | ALTW
J2053 | 01 NORTH | DIS-22-1-PQ | Wind | 151.47 | ER/NR | XEL
J2068 | 01 NORTH | DIS-22-1-PQ | Solar | 75 | ER/NR | XEL
J2078 | 02 NEBRASKA | DIS-22-1-PQ | Solar | 200 | ER/NR | ALTW
J2080 | 01 NORTH | DIS-22-1-PQ | Wind | 200 | ER/NR | MP
J2087 | 01 NORTH | DIS-22-1-PQ | Solar | 125 | ER/NR | XEL
J2097 | 01 NORTH | DIS-22-1-PQ | Wind | 100 | ER/NR | MP
J2104 | 01 NORTH | DIS-22-1-PQ | Wind | 230.01 | ER/NR | XEL
J2120 | 02 NEBRASKA | DIS-22-1-PQ | Battery/Storage | 100 | ER/NR | ALTW
J2157 | 01 NORTH | DIS-22-1-PQ | Wind | 100 | ER/NR | MP
J2219 | 01 NORTH | DIS-22-1-PQ | Battery/Storage | 180 | ER/NR | DPC
J2227 | 01 NORTH | DIS-22-1-PQ | Solar | 80.1 | ER/NR | DPC
J2250 | 01 NORTH | DIS-22-1-PQ | Wind | 200 | ER/NR | OTP
J2268 | 02 NEBRASKA | DIS-22-1-PQ | Solar | 370 | ER/NR | ALTW
J2276 | 01 NORTH | DIS-22-1-PQ | Solar | 39.5 | ER/NR | OTP
J2309 | 01 NORTH | DIS-22-1-PQ | Solar | 100 | ER/NR | XEL
MPC04500 | 01 NORTH | DIS-22-PQ | Wind | 250 | ER/NR | OTP
GEN-2022-111 | 04 SOUTHEAST | DIS-22-1 | Solar | 150 | ER/NR | AEPW | Wilkes 345 kV Substation
GEN-2022-136 | 04 SOUTHEAST | DIS-22-1 | Battery/Storage | 180 | ER | WFEC | Colbert 138 kV Substation
GEN-2022-145 | 04 SOUTHEAST | DIS-22-1 | Battery/Storage | 180 | ER | AEPW | Weatherford Jct. to Hinton 138 kV line
GEN-2022-004 | 03 CENTRAL | DIS-22-1 | Solar | 33 | ER/NR | WERE | Murray Gill 138 kV Substation
GEN-2022-006 | 03 CENTRAL | DIS-22-1 | Solar | 200 | ER/NR | WERE | Neosho 161 kV Substation (532937 NEOSHO 5)
GEN-2022-007 | 03 CENTRAL | DIS-22-1 | Solar | 135 | ER/NR | WERE | Lang - Reading 115 kV Transmission Line
GEN-2022-009 | 01 NORTH | DIS-22-1 | Thermal | 125 | ER | BEPC | Judson Substation 345 kV
GEN-2022-010 | 01 NORTH | DIS-22-1 | Thermal | 250 | ER | BEPC | Judson Substation 345 kV
GEN-2022-012 | 04 SOUTHEAST | DIS-22-1 | Battery/Storage | 100 | ER/NR | OKGE | Woodward 345 kV Substation
GEN-2022-013 | 03 CENTRAL | DIS-22-1 | Solar | 300 | ER/NR | WERE | Tap of Neosho - LaCygne 345 kV Line
GEN-2022-015 | 03 CENTRAL | DIS-22-1 | Solar | 270 | ER/NR | SUNC | Tap of Mingo - Red Willow 345 kV Line
GEN-2022-016 | 04 SOUTHEAST | DIS-22-1 | Solar | 288 | ER/NR | OKGE | Woodward 345kV Substation
GEN-2022-017 | 04 SOUTHEAST | DIS-22-1 | Battery/Storage | 150 | ER/NR | OKGE | Woodward 345kV Substation
GEN-2022-024 | 03 CENTRAL | DIS-22-1 | Battery/Storage | 200 | ER/NR | WERE | Tap of Neosho - LaCygne 345 kV Line
GEN-2022-038 | 04 SOUTHEAST | DIS-22-1 | Solar | 180 | ER | AEPW | Longwood to Scottville 138 kV line
GEN-2022-054 | 03 CENTRAL | DIS-22-1 | Solar | 200 | ER | WERE | Wolf Creek - Blackberry 345 kV Tap
GEN-2022-055 | 04 SOUTHEAST | DIS-22-1 | Solar | 200 | ER | WFEC | Sunshine North to Anadarko 138 kV
GEN-2022-065 | 03 CENTRAL | DIS-22-1 | Solar | 145 | ER/NR | SUNC | tap on Arthur Mullergreen-Spearville 230 kV line
ASGI-2023-001 | 05 SOUTHWEST | DIS-23-1 | Solar | 20 | ER/NR | SPS | Chevron Green 115 kV Substation
GEN-2023-015 | 03 CENTRAL | DIS-23-1 | Solar | 330 | ER/NR | SPS | Finney-Carpenter 345 KV line
GEN-2023-033 | 03 CENTRAL | DIS-23-1 | Storage | 200 | ER/NR | KCPL | Liberty South 161 kV Substation
GEN-2023-034 | 03 CENTRAL | DIS-23-1 | Solar | 130 | ER/NR | WERE | Clear Water - Waco 138 kV line
GEN-2023-035 | 04 SOUTHEAST | DIS-23-1 | Solar | 200 | ER/NR | WFEC | Cleveland - Amber Tap 138 kV Line
GEN-2023-037 | 03 CENTRAL | DIS-23-1 | Storage | 200 | ER/NR | KACY | Nearman 161 kV Substation
GEN-2023-038 | 04 SOUTHEAST | DIS-23-1 | Solar | 200 | ER/NR | OKGE | Lula 138 kV Substation
GEN-2023-055 | 04 SOUTHEAST | DIS-23-1 | Storage | 100 | ER/NR | GRDA | Kerr Grove 161 kV
GEN-2023-057 | 04 SOUTHEAST | DIS-23-1 | Storage | 150 | ER/NR | GRDA | Pawnee Switch 138 kV
GEN-2023-059 | 04 SOUTHEAST | DIS-23-1 | Solar | 200 | ER/NR | AEPW | Tap Rockhill to South Shreveport 138 kV line
GEN-2023-061 | 03 CENTRAL | DIS-23-1 | Storage | 100 | ER/NR | SWPA | Carthage 161 kV Substation
GEN-2023-063 | 04 SOUTHEAST | DIS-23-1 | Solar | 135 | ER/NR | AEPW | Catoosa - Owasso 88th 138 kV line
GEN-2023-064 | 04 SOUTHEAST | DIS-23-1 | Solar | 200 | ER/NR | SWPA | RS Kerr-Stigler 161 kV line
GEN-2023-069 | 04 SOUTHEAST | DIS-23-1 | Solar | 100 | ER/NR | WFEC | Tupelo - Atoka 138 kV Line
GEN-2023-077 | 02 NEBRASKA | DIS-23-1 | Thermal | 255 | ER | OPPD | Substation 3740 345 kV
GEN-2023-078 | 02 NEBRASKA | DIS-23-1 | Thermal | 255 | ER | OPPD | Substation 3740 345 kV
GEN-2023-079 | 02 NEBRASKA | DIS-23-1 | Thermal | 272.7 | ER | OPPD | Substation 3740 345 kV
GEN-2023-088 | 04 SOUTHEAST | DIS-23-1 | Wind | 117 | ER/NR | WFEC | Pharaoh 138 kV Substation
GEN-2023-092 | 04 SOUTHEAST | DIS-23-1 | Solar | 125 | ER/NR | WFEC | Unger - Frogville 138 kV line
GEN-2023-099 | 03 CENTRAL | DIS-23-1 | Solar | 300 | ER | WERE | Jeffery Energy Center 345 kV Substation
GEN-2023-102 | 04 SOUTHEAST | DIS-23-1 | Solar | 475 | ER/NR | OKGE | Degrasse 345 kV Substation
GEN-2023-104 | 04 SOUTHEAST | DIS-23-1 | Solar | 100 | ER/NR | WFEC | Mooreland - Noel 138 kV Line
GEN-2023-107 | 03 CENTRAL | DIS-23-1 | Wind | 300 | ER | SUNC | Setab 345 kV
GEN-2020-065 | 05 SOUTHWEST | DIS-20-1 | Thermal | 1003 | ER | SPS | Hobbs-Andrews 345 kV Line
GEN-2018-024 | 04 SOUTHEAST | DIS-17-1 | Battery/Storage | 100 | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV
GEN-2023-206 | 04 SOUTHEAST | DIS-23-1 | Storage | 50 | ER/NR | OKGE | Battlefield BESS 161 kV Substation
GEN-2021-056 | 03 CENTRAL | DIS-21-1 | Wind | 300 | ER | WERE | Viola 345kV Substation
GEN-2022-147 | 05 SOUTHWEST | DIS-22-1 | Thermal | 203 | ER | SPS | Tuco 345kV
GEN-2022-161 | 03 CENTRAL | DIS-22-1 | Wind | 360 | ER | WERE | Burns 345kV Substation
J1998 | 02 NEBRASKA | DIS-22-1-PQ | Wind | 66 | ER/NR | ALTW
J2122 | 02 NEBRASKA | DIS-22-1-PQ | Wind | 33 | ER/NR | ALTW
GEN-2006-044 | 05 SOUTHWEST | PQ | Wind | 370 | ER | SPS | Hitchland 345kV
GEN-2020-056 | 03 CENTRAL | DIS-20-1 | Solar | 20 | ER/NR | SUNC | Russell 115 kV Substation

## Revision History
Revision History
Date | Author | Change Description
2026-03-13 | SPP | Phase 1 Draft Posting
2026-04-01 | SPP | Phase 1 Draft Posting#2
2026-04-08 | SPP | Phase 1 Final Posting
2026-07-14 | SPP | Phase 1 Restudy Draft Posting
2026-07-20 | SPP | Phase 1 Restudy Final Posting

## Constraints Summary
Group | Service Type | Constraint Type | Constraints | Season | Mitigation Iteration | Most Severe Contingency | Rating Type | Rating (MVA) | BC Loading % | TC Loading % | TC Voltage | VMIN | VMAX | Upgrade Name
00ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | [7 empty] | 21ITP_Multi - Tande - Finstad - Leland Olds 345 kV.idv : 2021 ITP, PID: 92168, NTC, ISD: 11/30/2026
00ALL | ERIS | Thermal | 337361 3MINDEN_LA! 115 337363 3SAREPTA! 115 1 | 26S, 29S, 29W | JTIQ Expanded Scope Analysis | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | B | 176 | <90% | 129.19 |  |  |  | Rebuild the 3MINDEN_LA! to 3SAREPTA! 115kV Line 1
00ALL | ERIS | Thermal | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | 26SP | T0 | Single 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 227 | 28.926 | 149.0441 |  |  |  | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
00ALL | ERIS | Thermal | 337376 7SAREPTA% 345 788340 G24-379-TAP 345 1 | 26SP | T0 | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | B | 1195 | -1.8067 | 107.5536 |  |  |  | Rebuild line 337376 7SAREPTA% 345 788340 G24-379-TAP 345 1
00ALL | ERIS | Thermal | 337904 5RUSSELVL.S 161 505508 DARDANE5 161 1 | 26SP | T0 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | B | 396 | 77.8955 | 111.3177 |  |  |  | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
00ALL | ERIS | Thermal | 507727 FLOURNY4 138 508816 OAKPH 4 138 1 | 26SP | T0 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | B | 188 | 121.2021 | 154.8742 |  |  |  | Rebuild line 507727 FLOURNY4 138 508816 OAKPH 4 138 1
00ALL | ERIS | Thermal | 508072 NWTXARK7 345 508359 WELSH 7 345 1 | 26SP | T0 | Single 508298 LYDIA7 345 779010 G24-068-TAP 345 1 | B | 927 | 24.4083 | 102.4055 |  |  |  | Rebuild line 508072 NWTXARK7 345 508359 WELSH 7 345 1
00ALL | ERIS | Thermal | 508298 LYDIA 7 345 510911 VALIANT7 345 1 | 26SP | T0 | Single 510911 VALIANT7 345 764520 G20-020-TAP 345 1 | B | 1176 | 46.4292 | 103.2181 |  |  |  | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
00ALL | ERIS | Thermal | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | 26SP | T0 | P23:345:AEPW:WELSH CB 10610 NBTB:::: | B | 1059 | 45.0866 | 122.6891 |  |  |  | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
00ALL | ERIS | Thermal | 508548 KNOXLEE4 138 509092 EASTON 4 138 1 | 26SP | T0 | P23:345:AEPW:PIRKEY CB 13430 NBTB:::: | B | 547 | 46.1251 | 119.4926 |  |  |  | Rebuild line 508548 KNOXLEE4 138 509092 EASTON 4 138 1
00ALL | ERIS | Thermal | 508562 PIRKEY 4 138 3WXFMR 520:PIRKEY 1 345 1 | 26SP | T0 | P23:345:AEPW:PIRKEY CB 13430 NBTB:::: | B | 600 | 16.8468 | 106.4715 |  |  |  | Add 3-winding transformer 508562 PIRKEY 4 138 508563 PIRKEY 7 345 508587 PIRKY1-1 13 M2
00ALL | ERIS | Thermal | 508562 PIRKEY 4 138 508566 SABMINT4 138 1 | 26SP | T0 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | B | 340 | 49.6251 | 101.0119 |  |  |  | Rebuild line 508562 PIRKEY 4 138 508566 SABMINT4 138 1
00ALL | ERIS | Thermal | 508562 PIRKEY 4 138 508596 BRANDYBR4 138 1 | 26SP | T0 | P23:345:AEPW:PIRKEY CB 13430 NBTB:::: | B | 575 | 45.1057 | 114.8987 |  |  |  | Rebuild line 508562 PIRKEY 4 138 508596 BRANDYBR4 138 1
00ALL | ERIS | Thermal | 508563 PIRKEY 7 345 3WXFMR 520:PIRKEY 1 345 1 | 26SP | T0 | P23:345:AEPW:PIRKEY CB 13430 NBTB:::: | B | 600 | 16.9424 | 108.3741 |  |  |  | Add 3-winding transformer 508562 PIRKEY 4 138 508563 PIRKEY 7 345 508587 PIRKY1-1 13 M2
00ALL | ERIS | Thermal | 508563 PIRKEY 7 345 508832 DIANA 7 345 1 | 26SP | T0 | Single 334197 7ROCKYCRK% 345 783930 G24-232-TAP 345 1 | B | 1306 | 31.6347 | 104.1965 |  |  |  | Rebuild line 508563 PIRKEY 7 345 508832 DIANA 7 345 1
00ALL | ERIS | Thermal | 508566 SABMINT4 138 508569 SEMRSHL4 138 1 | 26SP | T0 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | B | 272 | 58.1187 | 122.2855 |  |  |  | Rebuild line 508566 SABMINT4 138 508569 SEMRSHL4 138 1
00ALL | ERIS | Thermal | 508567 SCOTTSV4 138 508569 SEMRSHL4 138 1 | 26SP | T0 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | B | 272 | 47.4652 | 111.3473 |  |  |  | Rebuild line 508567 SCOTTSV4 138 508569 SEMRSHL4 138 1
00ALL | ERIS | Thermal | 508596 BRANDYBR4 138 509092 EASTON 4 138 1 | 26SP | T0 | P23:345:AEPW:PIRKEY CB 13430 NBTB:::: | B | 575 | 45.014 | 114.8054 |  |  |  | Rebuild line 508596 BRANDYBR4 138 509092 EASTON 4 138 1
00ALL | ERIS | Thermal | 508808 LONGWD 4 138 508816 OAKPH 4 138 1 | 26SP | T0 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | B | 188 | 123.1163 | 156.8154 |  |  |  | Rebuild line 508808 LONGWD 4 138 508816 OAKPH 4 138 1
00ALL | ERIS | Thermal | 508809 LONGWD 7 345 788340 G24-379-TAP 345 1 | 26SP | T0 | Single 337376 7SAREPTA% 345 788340 G24-379-TAP 345 1 | B | 1195 | -1.5881 | 107.7877 |  |  |  | Rebuild line 508809 LONGWD 7 345 788340 G24-379-TAP 345 1
00ALL | ERIS | Thermal | 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1 | 26SP | T0 | P42:345:OKGE:SB_REUD7389:::EHV: | B | 1055 | -6.5015 | 137.0482 |  |  |  | Rebuild line 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1
00ALL | ERIS | Thermal | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 26SP | T0 | Single 510907 PITTSB-7 345 515422 C-RIVER7 345 1 | B | 956 | 41.1502 | 121.1336 |  |  |  | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
00ALL | ERIS | Thermal | 511467 L.E.S.-4 138 3WXFMR 520:LES 5 345 2 | 26SP | T0 | P42:345:OKGE:SB_GRNT7313:::EHV: | B | 515 | 50.0946 | 101.3128 |  |  |  | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
00ALL | ERIS | Thermal | 511468 L.E.S.-7 345 3WXFMR 520:LES 5 345 2 | 26SP | T0 | P42:345:OKGE:SB_GRNT7313:::EHV: | B | 515 | 51.2496 | 101.4646 |  |  |  | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
00ALL | ERIS | Thermal | 514808 JOHNCO 4 138 3WXFMR 524:524:JOHNCOT3 345 3 | 26SP | T0 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 478 | 32.4384 | 100.3203 |  |  |  | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
00ALL | ERIS | Thermal | 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 | 26SP | T0 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 222 | 68.3533 | 126.6708 |  |  |  | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
00ALL | ERIS | Thermal | 514809 JOHNCO 7 345 3WXFMR 524:524:JOHNCOT3 345 3 | 26SP | T0 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 478 | 32.4906 | 100.3203 |  |  |  | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
00ALL | ERIS | Thermal | 514809 JOHNCO 7 345 787110 G24-338-TAP 345 1 | 26SP | T0 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 1195 | 15.59 | 101.4771 |  |  |  | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
00ALL | ERIS | Thermal | 514907 ARCADIA4 138 3WXFMR 524:524:ARCADIA4 345 4 | 26SP | T0 | P13:138:OKGE:BKRBKR_3W024:::HV: | B | 448 | 94.1149 | 100.482 |  |  |  | Add 3-winding transformer 514907 ARCADIA4 138 514908 ARCADIA7 345 515700 ARCADI41 13 M2
00ALL | ERIS | Thermal | 514908 ARCADIA7 345 3WXFMR 524:524:ARCADIA4 345 4 | 26SP | T0 | P13:138:OKGE:BKRBKR_3W024:::HV: | B | 448 | 97.2965 | 103.8945 |  |  |  | Add 3-winding transformer 514907 ARCADIA4 138 514908 ARCADIA7 345 515700 ARCADI41 13 M2
00ALL | ERIS | Thermal | 514909 REDBUD 7 345 787290 G24-344-TAP 345 1 | 26SP | T0 | Single 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1 | B | 1055 | -5.5694 | 133.208 |  |  |  | Rebuild line 514909 REDBUD 7 345 787290 G24-344-TAP 345 1
00ALL | ERIS | Thermal | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 | 26SP | T0 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 191 | 74.1227 | 141.9099 |  |  |  | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
00ALL | ERIS | Thermal | 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 | 26SP | T0 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 222 | 67.5109 | 125.8151 |  |  |  | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
00ALL | ERIS | Thermal | 515301 FTSMTHW5 161 3WXFMR 524:524:FTSMITH5 345 5 | 26SP | T0 | P42:500:OKGE:SB_FTTH8585:::EHV: | B | 493 | 44.8577 | 103.9313 |  |  |  | Add 3-winding transformer 515301 FTSMTHW5 161 515302 FTSMITH7 345 515728 FTSMTH51 13 M2
00ALL | ERIS | Thermal | 515301 FTSMTHW5 161 515306 ARKOMA 5 161 1 | 26SP | T0 | Single 515231 KEEFTON7 345 780360 G24-113-TAP 345 1 | B | 359 | 60.8127 | 113.1202 |  |  |  | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
00ALL | ERIS | Thermal | 515302 FTSMITH7 345 3WXFMR 524:524:FTSMITH5 345 5 | 26SP | T0 | P42:500:OKGE:SB_FTTH8585:::EHV: | B | 493 | 45.2332 | 104.5961 |  |  |  | Add 3-winding transformer 515301 FTSMTHW5 161 515302 FTSMITH7 345 515728 FTSMTH51 13 M2
00ALL | ERIS | Thermal | 515306 ARKOMA 5 161 515308 3RDST 5 161 1 | 26SP | T0 | Single 515231 KEEFTON7 345 780360 G24-113-TAP 345 1 | B | 335 | 57.281 | 113.225 |  |  |  | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
00ALL | ERIS | Thermal | 515308 3RDST 5 161 515356 JSTREET5 161 1 | 26SP | T0 | Single 515231 KEEFTON7 345 780360 G24-113-TAP 345 1 | B | 223 | 44.0698 | 110.2081 |  |  |  | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
00ALL | ERIS | Thermal | 515336 VBI 2 69 3WXFMR 524:524:VBI2 161 2 | 26SP | T0 | System Intact | A | 76 | 91.2392 | 108.2991 |  |  |  | Rebuild 3-winding transformer 515336 VBI 2 69 515339 VBI 5 161 515769 VBI 1 13 2
00ALL | ERIS | Thermal | 515339 VBI 5 161 3WXFMR 524:524:VBI2 161 2 | 26SP | T0 | System Intact | A | 76 | 91.2392 | 108.2991 |  |  |  | Rebuild 3-winding transformer 515336 VBI 2 69 515339 VBI 5 161 515769 VBI 1 13 2
00ALL | ERIS | Thermal | 515339 VBI 5 161 515406 ADABELL5 161 1 | 26SP | T0 | Single 515231 KEEFTON7 345 780360 G24-113-TAP 345 1 | B | 223 | 33.5178 | 128.9573 |  |  |  | Rebuild line 515339 VBI 5 161 515406 ADABELL5 161 1
00ALL | ERIS | Thermal | 515800 GRACMNT7 345 3WXFMR 524:524:GRACMNT3 345 3 | 26SP | T0 | P42:345:OKGE:SB_GRNT7381:::EHV: | B | 478 | 37.9664 | 111.6521 |  |  |  | Add 3-winding transformer 515800 GRACMNT7 345 515801 GRCMNT11 13 515802 GRACMNT4 138 M2
00ALL | ERIS | Thermal | 515802 GRACMNT4 138 3WXFMR 524:524:GRACMNT3 345 3 | 26SP | T0 | P42:345:OKGE:SB_GRNT7381:::EHV: | B | 478 | 37.9309 | 111.6521 |  |  |  | Add 3-winding transformer 515800 GRACMNT7 345 515801 GRCMNT11 13 515802 GRACMNT4 138 M2
00ALL | ERIS | Thermal | 532780 CANEYRV7 345 532800 LATHAMS7 345 1 | 26SP | T0 | P23:345:WERE:N345-345-20:EHV: | B | 1159 | 11.2641 | 100.8309 |  |  |  | Rebuild line 532780 CANEYRV7 345 532800 LATHAMS7 345 1
00ALL | ERIS | Thermal | 532793 NEOSHO 7 345 3WXFMR 536:N345 TX-1 138 1 | 26SP | T0 | Single 532793 NEOSHO7 345 532939 N34545 161 532825 'N345 2 1 ' 13 2 | B | 400 | 103.2811 | 123.3093 |  |  |  | Add 3-winding transformer 532793 NEOSHO 7 345 532824 N345 1 1 13 533023 N345 3 4 138 M2
00ALL | ERIS | Thermal | 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 | 26SP | T0 | P23:345:WERE:N345-345-20:EHV: | B | 956 | 16.2247 | 122.6952 |  |  |  | Rebuild line 532794 ROSEHIL7 345 532800 LATHAMS7 345 1
00ALL | ERIS | Thermal | 533023 N345 3 4 138 3WXFMR 536:N345 TX-1 138 1 | 26SP | T0 | Single 532793 NEOSHO7 345 532939 N34545 161 532825 'N345 2 1 ' 13 2 | B | 400 | 107.2969 | 127.6279 |  |  |  | Add 3-winding transformer 532793 NEOSHO 7 345 532824 N345 1 1 13 533023 N345 3 4 138 M2
00ALL | ERIS | Thermal | 533417 EMCPHER3 115 533426 MANVILE3 115 1 | 26SP | T0 | Single 533426 MANVILE3 115 533437 MOHAWK3 115 1 | B | 128 | 8.294 | 107.8314 |  |  |  | Rebuild line 533417 EMCPHER3 115 533426 MANVILE3 115 1
00ALL | ERIS | Thermal | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 | 26SP | T0 | Single 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 334 | 22.2477 | 142.1462 |  |  |  | Rebuild line 541250 SIBLEYPL 161 548808 ECKLES-161 161 1
00ALL | ERIS | Thermal | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | 26SP | T0 | Single 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 334 | 56.2228 | 251.3484 |  |  |  | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
00ALL | ERIS | Thermal | 542987 GRAND 5 161 542989 NAVY 5 161 1 | 26SP | T0 | Single 542985 NEASTS5 161 542988 GRANDW5 161 1 | B | 259 | 64.0027 | 104.6104 |  |  |  | Line - Crosstown - Blue Valley Station 161 kV New Line.idv : 2025 ITP upgrade, PID : 900341, NO NTC
00ALL | ERIS | Thermal | 542987 GRAND 5 161 543666 NEASTN5 161 1 | 26SP | T0 | Single 542985 NEASTS5 161 542988 GRANDW5 161 1 | B | 259 | 63.9175 | 104.5925 |  |  |  | Line - Crosstown - Blue Valley Station 161 kV New Line.idv : 2025 ITP upgrade, PID : 900341, NO NTC
00ALL | ERIS | Thermal | 542988 GRAND W5 161 542990 CROSTWN5 161 1 | 26SP | T0 | Single 542985 NEASTS5 161 543133 CHARLOT5 161 1 | B | 259 | 87.1867 | 112.18 |  |  |  | Line - Crosstown - Blue Valley Station 161 kV New Line.idv : 2025 ITP upgrade, PID : 900341, NO NTC
00ALL | ERIS | Thermal | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | 26SP | T0 | Single 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 309 | 58.9029 | 302.4555 |  |  |  | Add line 543004 BLUMILS5 161 548808 ECKLES-161 161 M2
00ALL | ERIS | Thermal | 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | 26SP | T0 | Single 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 309 | -0.48658 | 242.7931 |  |  |  | Rebuild line 543004 BLUMILS5 161 783180 G24-207-TAP 161 1
00ALL | ERIS | Thermal | 543085 COURTNY2 69 548802 SUB H 69 1 | 26SP | T0 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | B | 58 | 19.3758 | 105.2667 |  |  |  | Rebuild line 543085 COURTNY2 69 548802 SUB H 69 1
00ALL | ERIS | Thermal | 543164 SUGRCK_TP_W2 69 543165 SUGRCK_TP_E2 69 1 | 26SP | T0 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | B | 53 | -13.6476 | 108.8766 |  |  |  | Rebuild line 543164 SUGRCK_TP_W2 69 543165 SUGRCK_TP_E2 69 1
00ALL | ERIS | Thermal | 548802 SUB H 69 548806 BLUVLY 69 1 | 26SP | T0 | P12:161:INDN:BLUVLY-SUB M:::HV: | B | 58 | 22.6999 | 173.8468 |  |  |  | Rebuild line 548802 SUB H 69 548806 BLUVLY 69 1
00ALL | ERIS | Thermal | 548802 SUB H 69 548815 SUB M 69 1 | 26SP | T0 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | B | 79 | 31.9904 | 114.1517 |  |  |  | Rebuild line 548802 SUB H 69 548815 SUB M 69 1
00ALL | ERIS | Thermal | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | 26SP | T0 | P12:161:INDN:BLUVLY-SUB M:::HV: | B | 112 | 68.7382 | 191.8914 |  |  |  | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
00ALL | ERIS | Thermal | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | 26SP | T0 | P12:161:INDN:BLUVLY-SUB M:::HV: | B | 112 | 70.6201 | 197.1448 |  |  |  | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
00ALL | ERIS | Thermal | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | 26SP | T0 | Single 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 335 | 35.2278 | 276.5048 |  |  |  | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
00ALL | ERIS | Thermal | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | 26SP | T0 | Single 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 309 | 59.2307 | 302.2631 |  |  |  | Add line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 M2
00ALL | ERIS | Thermal | 548815 SUB M 69 548814 SUB M-161 161 1 | 26SP | T0 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | B | 112 | 82.7907 | 147.8714 |  |  |  | Rebuild 2-winding transformer 548814 SUB M-161 161 548815 SUB M 69 1
00ALL | ERIS | Thermal | 640076 BEATRCE7 115 640088 BPS SUB7 115 1 | 26SP | T0 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | B | 193 | 74.3636 | 152.117 |  |  |  | DIS2301_P2_G00_ERIS_2_640_NPPD_TO_1000_DAYKIN_345KV_SUB.idv : DISIS_2023 Identified Upgrade
00ALL | ERIS | Thermal | 640076 BEATRCE7 115 640088 BPS SUB7 115 1 | 26SP | T0 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | B | 193 | 74.3636 | 152.117 |  |  |  | DIS2301_P2_G00_ERIS_3_640_NPPD_TO_2000_add_BPS_345_Lines_Rev34.idv : DISIS_2023 Identified Upgrade
00ALL | ERIS | Thermal | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 26SP | T0 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | B | 99 | 153.6016 | 337.5032 |  |  |  | DIS2301_P2_G00_ERIS_2_640_NPPD_TO_1000_DAYKIN_345KV_SUB.idv : DISIS_2023 Identified Upgrade
00ALL | ERIS | Thermal | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 26SP | T0 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | B | 99 | 153.6016 | 337.5032 |  |  |  | DIS2301_P2_G00_ERIS_3_640_NPPD_TO_2000_add_BPS_345_Lines_Rev34.idv : DISIS_2023 Identified Upgrade
00ALL | ERIS | Thermal | 640076 BEATRCE7 115 640361 STEINER7 115 1 | 26SP | T0 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | B | 121 | 62.4527 | 154.0683 |  |  |  | Rebuild line 640076 BEATRCE7 115 640361 STEINER7 115 1
00ALL | ERIS | Thermal | 640088 BPS SUB7 115 3WXFMR 640:BPS_345_115 T1 345 1 | 26SP | T0 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | B | 417 | 173.9551 | 354.6039 |  |  |  | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2
00ALL | ERIS | Thermal | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 26SP | T0 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | B | 140 | 123.5196 | 354.8766 |  |  |  | Rebuild line 640088 BPS SUB7 115 640111 CLATONA7 115 1
00ALL | ERIS | Thermal | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 26SP | T0 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | B | 193 | 114.4061 | 336.4692 |  |  |  | Add line 640088 BPS SUB7 115 640278 SHELDON7 115 M2
00ALL | ERIS | Thermal | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 26SP | T0 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | B | 140 | 116.4126 | 348.4283 |  |  |  | Rebuild line 640111 CLATONA7 115 640278 SHELDON7 115 1
00ALL | ERIS | Thermal | 640139 COOPER 3 345 640590 OLIVECREEK 3 345 1 | 26SP | T0 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | B | 956 | 45.9929 | 111.8885 |  |  |  | Rebuild line 640139 COOPER 3 345 640590 OLIVECREEK 3 345 1
00ALL | ERIS | Thermal | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 | 26SP | T0 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | B | 99 | 89.8695 | 179.5021 |  |  |  | Rebuild line 640169 FAIRBRY7 115 640208 HARBINE7 115 1
00ALL | ERIS | Thermal | 640169 FAIRBRY7 115 640218 HEBRN N7 115 1 | 26SP | T0 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | B | 99 | 61.3915 | 155.7041 |  |  |  | Rebuild line 640169 FAIRBRY7 115 640218 HEBRN N7 115 1
00ALL | ERIS | Thermal | 640234 HUMBOLT5 161 3WXFMR 640:HUMBOLDT T2 161 1 | 26SP | T0 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | B | 126 | 56.5821 | 149.6902 |  |  |  | Add 3-winding transformer 640234 HUMBOLT5 161 640235 HUMBOLT7 115 643087 HUMBOLDT T29 13 M2
00ALL | ERIS | Thermal | 640235 HUMBOLT7 115 3WXFMR 640:HUMBOLDT T2 161 1 | 26SP | T0 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | B | 126 | 55.704 | 137.8984 |  |  |  | Add 3-winding transformer 640234 HUMBOLT5 161 640235 HUMBOLT7 115 643087 HUMBOLDT T29 13 M2
00ALL | ERIS | Thermal | 640235 HUMBOLT7 115 640361 STEINER7 115 1 | 26SP | T0 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | B | 121 | 60.3705 | 152.1307 |  |  |  | Rebuild line 640235 HUMBOLT7 115 640361 STEINER7 115 1
00ALL | ERIS | Thermal | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | 26SP | T0 | P42:345:NPPD:BKR-MOR-3312:::: | B | 956 | 39.4188 | 102.2146 |  |  |  | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
00ALL | ERIS | Thermal | 640277 MOORE 3 345 3WXFMR 640:MOORE T1 345 1 | 26SP | T0 | P42:345:NPPD:BKR-MOR-3308:::: | B | 400 | 81.9949 | 195.4671 |  |  |  | Add 3-winding transformer 640277 MOORE 3 345 640278 SHELDON7 115 640280 MOORE 9 13 M2
00ALL | ERIS | Thermal | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | 26SP | T0 | Single 640088 BPSSUB7 115 771999 G23-222-POI 345 771998 'NEW_TER_BPS ' 13 1 | B | 956 | 112.0537 | 260.7181 |  |  |  | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
00ALL | ERIS | Thermal | 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 | 26SP | T0 | P42:345:NPPD:BKR-MOR-3306:::: | B | 956 | 61.506 | 100.5447 |  |  |  | Rebuild line 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1
00ALL | ERIS | Thermal | 640278 SHELDON7 115 3WXFMR 640:MOORE T1 345 1 | 26SP | T0 | P42:345:NPPD:BKR-MOR-3308:::: | B | 400 | 81.9949 | 195.4671 |  |  |  | Add 3-winding transformer 640277 MOORE 3 345 640278 SHELDON7 115 640280 MOORE 9 13 M2
00ALL | ERIS | Thermal | 640278 SHELDON7 115 640591 OLIVECREEK 7 115 1 | 26SP | T0 | P42:345:NPPD:BKR-MOR-3308:::: | B | 400 | 49.7356 | 107.3677 |  |  |  | Rebuild line 640278 SHELDON7 115 640591 OLIVECREEK 7 115 1
00ALL | ERIS | Thermal | 640278 SHELDON7 115 640591 OLIVECREEK 7 115 2 | 26SP | T0 | P42:345:NPPD:BKR-MOR-3308:::: | B | 400 | 49.7356 | 107.3677 |  |  |  | Rebuild line 640278 SHELDON7 115 640591 OLIVECREEK 7 115 2
00ALL | ERIS | Thermal | 640278 SHELDON7 115 650242 FOLSM&PHIL7 115 1 | 26SP | T0 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | B | 300 | 46.8682 | 101.775 |  |  |  | Rebuild line 640278 SHELDON7 115 650242 FOLSM&PHIL7 115 1
00ALL | ERIS | Thermal | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T1 345 1 | 26SP | T0 | P42:345:NPPD:BKR-MOR-3308:::: | B | 417 | 78.012 | 183.9678 |  |  |  | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
00ALL | ERIS | Thermal | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T2 345 1 | 26SP | T0 | P42:345:NPPD:BKR-MOR-3308:::: | B | 417 | 78.012 | 183.9678 |  |  |  | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
00ALL | ERIS | Thermal | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T1 345 1 | 26SP | T0 | P42:345:NPPD:BKR-MOR-3308:::: | B | 417 | 77.3928 | 173.7124 |  |  |  | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
00ALL | ERIS | Thermal | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T2 345 1 | 26SP | T0 | P42:345:NPPD:BKR-MOR-3308:::: | B | 417 | 77.3929 | 173.713 |  |  |  | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
00ALL | ERIS | Thermal | 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1 | 26SP | T0 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | B | 240 | 79.0493 | 166.5845 |  |  |  | Rebuild line 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1
00ALL | ERIS | Thermal | 645454 S3454 3 345 645740 S3740 3 345 1 | 26SP | T0 | P12:345:OPPD:S3455-S3740:::EHV: | B | 1792 | 67.0566 | 100.7287 |  |  |  | Rebuild line 645454 S3454 3 345 645740 S3740 3 345 1
00ALL | ERIS | Thermal | 645455 S3455 3 345 645740 S3740 3 345 1 | 26SP | T0 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | B | 1195 | 108.9363 | 164.1197 |  |  |  | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
00ALL | ERIS | Thermal | 646221 S1221 5 161 646231 S1231 5 161 1 | 26SP | T0 | P23:345:OPPD:FUTURE 56-55&56-58:::EHV: | B | 217 | 110.5096 | 119.4065 |  |  |  | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
00ALL | ERIS | Thermal | 646259 S1259 5 161 646278 S1278 5 161 1 | 26SP | T0 | P23:345:OPPD:FUTURE 56-55&56-58:::EHV: | B | 215 | 114.9316 | 106.7879 |  |  |  | Rebuild line 646259 S1259 5 161 646278 S1278 5 161 1
00ALL | ERIS | Thermal | 652391 WILLISTON27 115 652421 WILISTN7 115 Z1 | 26SP | T0 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | B | 201 | 13.6691 | 127.8644 |  |  |  | Rebuild line 652391 WILLISTON27 115 652421 WILISTN7 115 Z1
00ALL | ERIS | Thermal | 652400 WILISTN4 230 659334 JUDSON__-BE4 230 1 | 26SP | T0 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | B | 482 | -21.4902 | 110.6312 |  |  |  | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
00ALL | ERIS | Thermal | 652400 WILISTN4 230 659334 JUDSON__-BE4 230 1 | 26SP | T0 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | B | 482 | -21.4902 | 110.6312 |  |  |  | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
00ALL | ERIS | Thermal | 652400 WILISTN4 230 659334 JUDSON__-BE4 230 1 | 26SP | T0 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | B | 482 | -21.4902 | 110.6312 |  |  |  | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
00ALL | ERIS | Thermal | 652400 WILISTN4 230 659362 WHEELOCK-BE4 230 1 | 26SP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 406 | 8.069 | 133.1912 |  |  |  | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
00ALL | ERIS | Thermal | 652400 WILISTN4 230 659362 WHEELOCK-BE4 230 1 | 26SP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 406 | 8.069 | 133.1912 |  |  |  | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
00ALL | ERIS | Thermal | 652400 WILISTN4 230 659362 WHEELOCK-BE4 230 1 | 26SP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 406 | 8.069 | 133.1912 |  |  |  | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
00ALL | ERIS | Thermal | 655933 N.MISRDG-MW7 115 655957 EASTFORK-MW7 115 1 | 26SP | T0 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | B | 189 | 11.0407 | 142.6232 |  |  |  | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
00ALL | ERIS | Thermal | 655933 N.MISRDG-MW7 115 655957 EASTFORK-MW7 115 1 | 26SP | T0 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | B | 189 | 11.0407 | 142.6232 |  |  |  | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
00ALL | ERIS | Thermal | 655933 N.MISRDG-MW7 115 655957 EASTFORK-MW7 115 1 | 26SP | T0 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | B | 189 | 11.0407 | 142.6232 |  |  |  | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
00ALL | ERIS | Thermal | 655957 EASTFORK-MW7 115 659331 SPRNGBRK-BE7 115 1 | 26SP | T0 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | B | 415 | 21.9768 | 132.6347 |  |  |  | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
00ALL | ERIS | Thermal | 655957 EASTFORK-MW7 115 659331 SPRNGBRK-BE7 115 1 | 26SP | T0 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | B | 415 | 21.9768 | 132.6347 |  |  |  | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
00ALL | ERIS | Thermal | 655957 EASTFORK-MW7 115 659331 SPRNGBRK-BE7 115 1 | 26SP | T0 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | B | 415 | 21.9768 | 132.6347 |  |  |  | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
00ALL | ERIS | Thermal | 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1 | 26SP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 506 | 44.2207 | 227.6009 |  |  |  | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
00ALL | ERIS | Thermal | 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1 | 26SP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 506 | 44.2207 | 227.6009 |  |  |  | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
00ALL | ERIS | Thermal | 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1 | 26SP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 506 | 44.2207 | 227.6009 |  |  |  | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
00ALL | ERIS | Thermal | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z | 26SP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 506 | 25.6513 | 190.6179 |  |  |  | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
00ALL | ERIS | Thermal | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z | 26SP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 506 | 25.6513 | 190.6179 |  |  |  | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
00ALL | ERIS | Thermal | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z | 26SP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 506 | 25.6513 | 190.6179 |  |  |  | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
00ALL | ERIS | Thermal | 659330 SPRNGBRK-BE3 345 3WXFMR 659:652: SPRNGBRK KUXA 115 1 | 26SP | T0 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | B | 416 | 22.5939 | 132.3291 |  |  |  | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
00ALL | ERIS | Thermal | 659330 SPRNGBRK-BE3 345 3WXFMR 659:652: SPRNGBRK KUXA 115 1 | 26SP | T0 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | B | 416 | 22.5939 | 132.3291 |  |  |  | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
00ALL | ERIS | Thermal | 659330 SPRNGBRK-BE3 345 3WXFMR 659:652: SPRNGBRK KUXA 115 1 | 26SP | T0 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | B | 416 | 22.5939 | 132.3291 |  |  |  | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
00ALL | ERIS | Thermal | 659330 SPRNGBRK-BE3 345 659333 JUDSON__-BE3 345 1 | 26SP | T0 | Single 659427 TN.LS-JD-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | -7.339 | 111.0855 |  |  |  | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
00ALL | ERIS | Thermal | 659330 SPRNGBRK-BE3 345 659333 JUDSON__-BE3 345 1 | 26SP | T0 | Single 659427 TN.LS-JD-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | -7.339 | 111.0855 |  |  |  | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
00ALL | ERIS | Thermal | 659330 SPRNGBRK-BE3 345 659333 JUDSON__-BE3 345 1 | 26SP | T0 | Single 659427 TN.LS-JD-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | -7.339 | 111.0855 |  |  |  | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
00ALL | ERIS | Thermal | 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | 26SP | T0 | Single 659427 TN.LS-JD-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | -0.59335 | 135.4147 |  |  |  | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1
00ALL | ERIS | Thermal | 659331 SPRNGBRK-BE7 115 3WXFMR 659:652: SPRNGBRK KUXA 115 1 | 26SP | T0 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | B | 416 | 22.4716 | 129.7201 |  |  |  | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
00ALL | ERIS | Thermal | 659331 SPRNGBRK-BE7 115 3WXFMR 659:652: SPRNGBRK KUXA 115 1 | 26SP | T0 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | B | 416 | 22.4716 | 129.7201 |  |  |  | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
00ALL | ERIS | Thermal | 659331 SPRNGBRK-BE7 115 3WXFMR 659:652: SPRNGBRK KUXA 115 1 | 26SP | T0 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | B | 416 | 22.4716 | 129.7201 |  |  |  | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
00ALL | ERIS | Thermal | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | 26SP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 637 | 36.4829 | 172.61 |  |  |  | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
00ALL | ERIS | Thermal | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | 26SP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 637 | 36.4829 | 172.61 |  |  |  | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
00ALL | ERIS | Thermal | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | 26SP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 637 | 36.4829 | 172.61 |  |  |  | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
00ALL | ERIS | Thermal | 659336 TANDE___-BE3 345 659427 TN.LS-JD-BE3 345 Z | 26SP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | -2.574 | 141.3444 |  |  |  | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
00ALL | ERIS | Thermal | 659336 TANDE___-BE3 345 659427 TN.LS-JD-BE3 345 Z | 26SP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | -2.574 | 141.3444 |  |  |  | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
00ALL | ERIS | Thermal | 659336 TANDE___-BE3 345 659427 TN.LS-JD-BE3 345 Z | 26SP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | -2.574 | 141.3444 |  |  |  | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
00ALL | ERIS | Thermal | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | 26SP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 637 | 36.3771 | 172.61 |  |  |  | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
00ALL | ERIS | Thermal | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | 26SP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 637 | 36.3771 | 172.61 |  |  |  | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
00ALL | ERIS | Thermal | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | 26SP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 637 | 36.3771 | 172.61 |  |  |  | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
00ALL | ERIS | Thermal | 659362 WHEELOCK-BE4 230 661084 TIOGA4 4 230 1 | 26SP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 506 | 21.8826 | 130.9507 |  |  |  | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
00ALL | ERIS | Thermal | 659362 WHEELOCK-BE4 230 661084 TIOGA4 4 230 1 | 26SP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 506 | 21.8826 | 130.9507 |  |  |  | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
00ALL | ERIS | Thermal | 659362 WHEELOCK-BE4 230 661084 TIOGA4 4 230 1 | 26SP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 506 | 21.8826 | 130.9507 |  |  |  | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
00ALL | ERIS | Thermal | 659427 TN.LS-JD-BE3 345 779400 G24-081-TAP 345 1 | 26SP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | -2.2038 | 141.3444 |  |  |  | Rebuild line 659427 TN.LS-JD-BE3 345 779400 G24-081-TAP 345 1
00ALL | ERIS | Thermal | 771999 G23-222-POI 345 3WXFMR 640:BPS_345_115 T1 345 1 | 26SP | T0 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | B | 417 | 173.9551 | 393.5711 |  |  |  | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2
00ALL | ERIS | Thermal | 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1 | 26SP | T0 | P23:345:AEPW:WELSH CB 10610 NBTB:::: | B | 1059 | 45.1141 | 111.4242 |  |  |  | Rebuild line 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1
00ALL | ERIS | Thermal | 787170 G24-340-TAP 345 787290 G24-344-TAP 345 1 | 26SP | T0 | Single 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1 | B | 1055 | -0.55776 | 129.5722 |  |  |  | Rebuild line 787170 G24-340-TAP 345 787290 G24-344-TAP 345 1
00ALL | ERIS | Thermal | 507711 ARSHILL4 138 507742 MCWILLI4 138 1 | 26SP | T1 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | B | 308 | 52.2184 | 103.6738 |  |  |  | Rebuild line 507711 ARSHILL4 138 507742 MCWILLI4 138 1
00ALL | ERIS | Thermal | 507727 FLOURNY4 138 507732 GENMOTR4 138 1 | 26SP | T1 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | B | 188 | 82.5364 | 178.6318 |  |  |  | Rebuild line 507727 FLOURNY4 138 507732 GENMOTR4 138 1
00ALL | ERIS | Thermal | 507732 GENMOTR4 138 507759 SW SHV 4 138 1 | 26SP | T1 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | B | 188 | 81.9313 | 177.8938 |  |  |  | Rebuild line 507732 GENMOTR4 138 507759 SW SHV 4 138 1
00ALL | ERIS | Thermal | 507760 SW SHV 7 345 508809 LONGWD 7 345 1 | 26SP | T1 | Single 337376 7SAREPTA% 345 788340 G24-379-TAP 345 1 | B | 1195 | 39.169 | 104.4813 |  |  |  | Rebuild line 507760 SW SHV 7 345 508809 LONGWD 7 345 1
00ALL | ERIS | Thermal | 507774 NORAM 4 138 508808 LONGWD 4 138 1 | 26SP | T1 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | B | 265 | 84.6481 | 120.8439 |  |  |  | Rebuild line 507774 NORAM 4 138 508808 LONGWD 4 138 1
00ALL | ERIS | Thermal | 508548 KNOXLEE4 138 509059 CHEROKE4 138 1 | 26SP | T1 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | B | 395 | 56.1131 | 103.881 |  |  |  | Rebuild line 508548 KNOXLEE4 138 509059 CHEROKE4 138 1
00ALL | ERIS | Thermal | 508808 LONGWD 4 138 3WXFMR 520:LONGWOOD 345 1 | 26SP | T1 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | B | 580 | 71.3651 | 114.6946 |  |  |  | Add 3-winding transformer 508808 LONGWD 4 138 508809 LONGWD 7 345 508819 LONGW1-1 13 M2
00ALL | ERIS | Thermal | 508808 LONGWD 4 138 508816 OAKPH 4 138 1 | 26SP | T1 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | B | 395 | 54.9111 | 100.8572 |  |  |  | Rebuild line 508808 LONGWD 4 138 508816 OAKPH 4 138 1
00ALL | ERIS | Thermal | 508809 LONGWD 7 345 3WXFMR 520:LONGWOOD 345 1 | 26SP | T1 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | B | 580 | 73.2371 | 115.4467 |  |  |  | Add 3-winding transformer 508808 LONGWD 4 138 508809 LONGWD 7 345 508819 LONGW1-1 13 M2
00ALL | ERIS | Thermal | 509059 CHEROKE4 138 509087 TATUM 4 138 1 | 26SP | T1 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | B | 350 | 60.7849 | 114.6003 |  |  |  | Rebuild line 509059 CHEROKE4 138 509087 TATUM 4 138 1
00ALL | ERIS | Thermal | 509083 ROKHILL4 138 509087 TATUM 4 138 1 | 26SP | T1 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | B | 350 | 59.6974 | 113.4766 |  |  |  | Rebuild line 509083 ROKHILL4 138 509087 TATUM 4 138 1
00ALL | ERIS | Thermal | 514934 DRAPER 7 345 515045 SEMINOL7 345 2 | 26SP | T1 | P42:345:OKGE:SB_SEOL7385:::EHV: | B | 717 | 22.5314 | 104.675 |  |  |  | Rebuild line 514934 DRAPER 7 345 515045 SEMINOL7 345 2
00ALL | ERIS | Thermal | 515301 FTSMTHW5 161 515306 ARKOMA 5 161 1 | 26SP | T1 | Single 515231 KEEFTON7 345 780360 G24-113-TAP 345 1 | B | 359 | 59.9336 | 103.2993 |  |  |  | Rebuild line 515301 FTSMTHW5 161 515306 ARKOMA 5 161 1
00ALL | ERIS | Thermal | 515306 ARKOMA 5 161 515308 3RDST 5 161 1 | 26SP | T1 | Single 515231 KEEFTON7 345 780360 G24-113-TAP 345 1 | B | 335 | 56.334 | 102.7878 |  |  |  | Rebuild line 515306 ARKOMA 5 161 515308 3RDST 5 161 1
00ALL | ERIS | Thermal | 515308 3RDST 5 161 515356 JSTREET5 161 1 | 26SP | T1 | P22:345:EES:MUSKOGE7!:::EHV: | B | 223 | 49.329 | 101.2281 |  |  |  | Rebuild line 515308 3RDST 5 161 515356 JSTREET5 161 1
00ALL | ERIS | Thermal | 533021 NEOSHO 4 138 533023 N345 3 4 138 1 | 26SP | T1 | Single 532793 NEOSHO7 345 532939 N34545 161 532825 'N345 2 1 ' 13 2 | B | 478 | 113.2057 | 134.2441 |  |  |  | Rebuild line 533021 NEOSHO 4 138 533023 N345 3 4 138 1
00ALL | ERIS | Thermal | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | 26SP | T1 | P12:161:INDN:BLUVLY-ECKLES:::HV: | B | 335 | -6.7842 | 107.0434 |  |  |  | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
00ALL | ERIS | Thermal | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | 26SP | T1 | P42:345:NPPD:BKR-TOB-3304:::: | B | 956 | 48.9487 | 103.5564 |  |  |  | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
00ALL | ERIS | Thermal | 645455 S3455 3 345 645740 S3740 3 345 1 | 26SP | T1 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | B | 1195 | 98.9937 | 150.0028 |  |  |  | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
00ALL | ERIS | Thermal | 646221 S1221 5 161 646231 S1231 5 161 1 | 26SP | T1 | P23:345:OPPD:FUTURE 56-55&56-58:::EHV: | B | 217 | 107.1847 | 117.252 |  |  |  | Rebuild line 646221 S1221 5 161 646231 S1231 5 161 1
00ALL | ERIS | Thermal | 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1 | 26SP | T1 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 506 | 31.469 | 110.8229 |  |  |  | Rebuild line 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1
00ALL | ERIS | Thermal | 659336 TANDE___-BE3 345 659427 TN.LS-JD-BE3 345 Z | 26SP | T1 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | -2.5863 | 136.8399 |  |  |  | Rebuild line 659336 TANDE___-BE3 345 659427 TN.LS-JD-BE3 345 Z
00ALL | ERIS | Thermal | 507711 ARSHILL4 138 507749 RAINES 4 138 1 | 26SP | T2 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | B | 289 | 70.0024 | 105.0342 |  |  |  | Rebuild line 507711 ARSHILL4 138 507749 RAINES 4 138 1
00ALL | ERIS | Thermal | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | 29SP | T0 | Single 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 227 | 38.6513 | 156.472 |  |  |  | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
00ALL | ERIS | Thermal | 337376 7SAREPTA% 345 788340 G24-379-TAP 345 1 | 29SP | T0 | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | B | 1195 | -1.8063 | 107.6241 |  |  |  | Rebuild line 337376 7SAREPTA% 345 788340 G24-379-TAP 345 1
00ALL | ERIS | Thermal | 337904 5RUSSELVL.S 161 505508 DARDANE5 161 1 | 29SP | T0 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | B | 396 | 64.8927 | 114.7438 |  |  |  | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
00ALL | ERIS | Thermal | 337909 8ANO% 500 515305 FTSMITH8 500 1 | 29SP | T0 | P52:345:AEPW:NR4PITTSB-7:::: | B | 1299 | 63.9128 | 102.9598 |  |  |  | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
00ALL | ERIS | Thermal | 505522 VAN BUR5 161 505524 LIBERTY5 161 1 | 29SP | T0 | P22:345:EES:MUSKOGE7!:::EHV: | B | 222 | 52.3232 | 117.409 |  |  |  | Rebuild line 505522 VAN BUR5 161 505524 LIBERTY5 161 1
00ALL | ERIS | Thermal | 505552 GORE 5 161 505558 MUSKTAP5 161 1 | 29SP | T0 | P22:345:EES:MUSKOGE7!:::EHV: | B | 201 | 75.0584 | 117.908 |  |  |  | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
00ALL | ERIS | Thermal | 507727 FLOURNY4 138 508816 OAKPH 4 138 1 | 29SP | T0 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | B | 287 | 81.0221 | 102.0609 |  |  |  | Rebuild line 507727 FLOURNY4 138 508816 OAKPH 4 138 1
00ALL | ERIS | Thermal | 508072 NWTXARK7 345 508359 WELSH 7 345 1 | 29SP | T0 | Single 508298 LYDIA7 345 779010 G24-068-TAP 345 1 | B | 927 | 31.0969 | 105.1339 |  |  |  | Rebuild line 508072 NWTXARK7 345 508359 WELSH 7 345 1
00ALL | ERIS | Thermal | 508298 LYDIA 7 345 510911 VALIANT7 345 1 | 29SP | T0 | Single 510911 VALIANT7 345 764520 G20-020-TAP 345 1 | B | 1176 | 52.1938 | 107.4903 |  |  |  | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
00ALL | ERIS | Thermal | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | 29SP | T0 | P23:345:AEPW:WELSH CB 10610 NBTB:::: | B | 1059 | 52.4447 | 126.1457 |  |  |  | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
00ALL | ERIS | Thermal | 508548 KNOXLEE4 138 509059 CHEROKE4 138 1 | 29SP | T0 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | B | 350 | 76.8081 | 100.1039 |  |  |  | Rebuild line 508548 KNOXLEE4 138 509059 CHEROKE4 138 1
00ALL | ERIS | Thermal | 508548 KNOXLEE4 138 509092 EASTON 4 138 1 | 29SP | T0 | P23:345:AEPW:PIRKEY CB 13430 NBTB:::: | B | 547 | 47.4982 | 116.2431 |  |  |  | Rebuild line 508548 KNOXLEE4 138 509092 EASTON 4 138 1
00ALL | ERIS | Thermal | 508557 MARSHL-4 138 508562 PIRKEY 4 138 1 | 29SP | T0 | P23:345:AEPW:PIRKEY CB 13430 NBTB:::: | B | 491 | 46.194 | 100.2536 |  |  |  | Rebuild line 508557 MARSHL-4 138 508562 PIRKEY 4 138 1
00ALL | ERIS | Thermal | 508562 PIRKEY 4 138 3WXFMR 520:PIRKEY 1 345 1 | 29SP | T0 | P23:345:AEPW:PIRKEY CB 13430 NBTB:::: | B | 600 | 21.4179 | 103.9699 |  |  |  | Add 3-winding transformer 508562 PIRKEY 4 138 508563 PIRKEY 7 345 508587 PIRKY1-1 13 M2
00ALL | ERIS | Thermal | 508562 PIRKEY 4 138 508566 SABMINT4 138 1 | 29SP | T0 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | B | 340 | 60.0836 | 105.1363 |  |  |  | Rebuild line 508562 PIRKEY 4 138 508566 SABMINT4 138 1
00ALL | ERIS | Thermal | 508562 PIRKEY 4 138 508596 BRANDYBR4 138 1 | 29SP | T0 | P23:345:AEPW:PIRKEY CB 13430 NBTB:::: | B | 575 | 46.4214 | 111.8135 |  |  |  | Rebuild line 508562 PIRKEY 4 138 508596 BRANDYBR4 138 1
00ALL | ERIS | Thermal | 508563 PIRKEY 7 345 3WXFMR 520:PIRKEY 1 345 1 | 29SP | T0 | P23:345:AEPW:PIRKEY CB 13430 NBTB:::: | B | 600 | 21.5041 | 105.7524 |  |  |  | Add 3-winding transformer 508562 PIRKEY 4 138 508563 PIRKEY 7 345 508587 PIRKY1-1 13 M2
00ALL | ERIS | Thermal | 508563 PIRKEY 7 345 508832 DIANA 7 345 1 | 29SP | T0 | Single 334197 7ROCKYCRK% 345 783930 G24-232-TAP 345 1 | B | 1306 | 43.7277 | 109.3236 |  |  |  | Rebuild line 508563 PIRKEY 7 345 508832 DIANA 7 345 1
00ALL | ERIS | Thermal | 508566 SABMINT4 138 508569 SEMRSHL4 138 1 | 29SP | T0 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | B | 272 | 71.1609 | 127.4298 |  |  |  | Rebuild line 508566 SABMINT4 138 508569 SEMRSHL4 138 1
00ALL | ERIS | Thermal | 508567 SCOTTSV4 138 508569 SEMRSHL4 138 1 | 29SP | T0 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | B | 272 | 59.6265 | 115.6232 |  |  |  | Rebuild line 508567 SCOTTSV4 138 508569 SEMRSHL4 138 1
00ALL | ERIS | Thermal | 508596 BRANDYBR4 138 509092 EASTON 4 138 1 | 29SP | T0 | P23:345:AEPW:PIRKEY CB 13430 NBTB:::: | B | 575 | 46.3278 | 111.7191 |  |  |  | Rebuild line 508596 BRANDYBR4 138 509092 EASTON 4 138 1
00ALL | ERIS | Thermal | 508809 LONGWD 7 345 788340 G24-379-TAP 345 1 | 29SP | T0 | Single 337376 7SAREPTA% 345 788340 G24-379-TAP 345 1 | B | 1195 | -1.5829 | 108.098 |  |  |  | Rebuild line 508809 LONGWD 7 345 788340 G24-379-TAP 345 1
00ALL | ERIS | Thermal | 509083 ROKHILL4 138 509102 NEWPROS4 138 1 | 29SP | T0 | P23:345:EES::7ROCKYCRK%:1:EHV: | B | 289 | 101.3707 | 100.4359 |  |  |  | Rebuild line 509083 ROKHILL4 138 509102 NEWPROS4 138 1
00ALL | ERIS | Thermal | 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1 | 29SP | T0 | P42:345:OKGE:SB_REUD7389:::EHV: | B | 1055 | -6.4924 | 137.0949 |  |  |  | Rebuild line 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1
00ALL | ERIS | Thermal | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 29SP | T0 | Single 510907 PITTSB-7 345 515422 C-RIVER7 345 1 | B | 956 | 50.6954 | 126.6467 |  |  |  | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
00ALL | ERIS | Thermal | 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 | 29SP | T0 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 222 | 70.8429 | 130.823 |  |  |  | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
00ALL | ERIS | Thermal | 514809 JOHNCO 7 345 787110 G24-338-TAP 345 1 | 29SP | T0 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 1195 | 26.5345 | 103.3869 |  |  |  | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
00ALL | ERIS | Thermal | 514909 REDBUD 7 345 787290 G24-344-TAP 345 1 | 29SP | T0 | Single 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1 | B | 1055 | -5.5591 | 133.2787 |  |  |  | Rebuild line 514909 REDBUD 7 345 787290 G24-344-TAP 345 1
00ALL | ERIS | Thermal | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 | 29SP | T0 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 191 | 77.083 | 146.7539 |  |  |  | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
00ALL | ERIS | Thermal | 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 | 29SP | T0 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 222 | 70.0015 | 129.9677 |  |  |  | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
00ALL | ERIS | Thermal | 515336 VBI 2 69 3WXFMR 524:524:VBI2 161 2 | 29SP | T0 | System Intact | A | 76 | 103.847 | 117.4893 |  |  |  | Rebuild 3-winding transformer 515336 VBI 2 69 515339 VBI 5 161 515769 VBI 1 13 2
00ALL | ERIS | Thermal | 515339 VBI 5 161 3WXFMR 524:524:VBI2 161 2 | 29SP | T0 | System Intact | A | 76 | 103.847 | 117.4893 |  |  |  | Rebuild 3-winding transformer 515336 VBI 2 69 515339 VBI 5 161 515769 VBI 1 13 2
00ALL | ERIS | Thermal | 515339 VBI 5 161 515406 ADABELL5 161 1 | 29SP | T0 | P22:345:EES:MUSKOGE7!:::EHV: | B | 223 | 32.9382 | 100.0239 |  |  |  | Rebuild line 515339 VBI 5 161 515406 ADABELL5 161 1
00ALL | ERIS | Thermal | 515800 GRACMNT7 345 3WXFMR 524:524:GRACMNT3 345 3 | 29SP | T0 | P42:345:OKGE:SB_GRNT7381:::EHV: | B | 478 | 26.4834 | 105.3618 |  |  |  | Add 3-winding transformer 515800 GRACMNT7 345 515801 GRCMNT11 13 515802 GRACMNT4 138 M2
00ALL | ERIS | Thermal | 515802 GRACMNT4 138 3WXFMR 524:524:GRACMNT3 345 3 | 29SP | T0 | P42:345:OKGE:SB_GRNT7381:::EHV: | B | 478 | 26.3801 | 105.3618 |  |  |  | Add 3-winding transformer 515800 GRACMNT7 345 515801 GRCMNT11 13 515802 GRACMNT4 138 M2
00ALL | ERIS | Thermal | 532793 NEOSHO 7 345 3WXFMR 536:N345 TX-1 138 1 | 29SP | T0 | Single 532793 NEOSHO7 345 532939 N34545 161 532825 'N345 2 1 ' 13 2 | B | 400 | 91.6388 | 117.1612 |  |  |  | Add 3-winding transformer 532793 NEOSHO 7 345 532824 N345 1 1 13 533023 N345 3 4 138 M2
00ALL | ERIS | Thermal | 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 | 29SP | T0 | P23:345:WERE:N345-345-20:EHV: | B | 956 | 16.4263 | 121.5852 |  |  |  | Rebuild line 532794 ROSEHIL7 345 532800 LATHAMS7 345 1
00ALL | ERIS | Thermal | 533023 N345 3 4 138 3WXFMR 536:N345 TX-1 138 1 | 29SP | T0 | Single 532793 NEOSHO7 345 532939 N34545 161 532825 'N345 2 1 ' 13 2 | B | 400 | 91.5377 | 117.0158 |  |  |  | Add 3-winding transformer 532793 NEOSHO 7 345 532824 N345 1 1 13 533023 N345 3 4 138 M2
00ALL | ERIS | Thermal | 533417 EMCPHER3 115 533426 MANVILE3 115 1 | 29SP | T0 | Single 533426 MANVILE3 115 533437 MOHAWK3 115 1 | B | 128 | 6.5416 | 106.5478 |  |  |  | Rebuild line 533417 EMCPHER3 115 533426 MANVILE3 115 1
00ALL | ERIS | Thermal | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 | 29SP | T0 | Single 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 334 | 22.7355 | 142.2515 |  |  |  | Rebuild line 541250 SIBLEYPL 161 548808 ECKLES-161 161 1
00ALL | ERIS | Thermal | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | 29SP | T0 | Single 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 334 | 55.9601 | 256.1148 |  |  |  | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
00ALL | ERIS | Thermal | 542988 GRAND W5 161 542990 CROSTWN5 161 1 | 29SP | T0 | Single 542985 NEASTS5 161 543133 CHARLOT5 161 1 | B | 259 | 80.7531 | 104.6173 |  |  |  | Line - Crosstown - Blue Valley Station 161 kV New Line.idv : 2025 ITP upgrade, PID : 900341, NO NTC
00ALL | ERIS | Thermal | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | 29SP | T0 | Single 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 309 | 58.9042 | 302.3771 |  |  |  | Add line 543004 BLUMILS5 161 548808 ECKLES-161 161 M2
00ALL | ERIS | Thermal | 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | 29SP | T0 | Single 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 309 | -0.4861 | 242.7652 |  |  |  | Rebuild line 543004 BLUMILS5 161 783180 G24-207-TAP 161 1
00ALL | ERIS | Thermal | 543085 COURTNY2 69 548802 SUB H 69 1 | 29SP | T0 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | B | 58 | 21.1449 | 107.2237 |  |  |  | Rebuild line 543085 COURTNY2 69 548802 SUB H 69 1
00ALL | ERIS | Thermal | 543164 SUGRCK_TP_W2 69 543165 SUGRCK_TP_E2 69 1 | 29SP | T0 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | B | 53 | -12.6077 | 110.2063 |  |  |  | Rebuild line 543164 SUGRCK_TP_W2 69 543165 SUGRCK_TP_E2 69 1
00ALL | ERIS | Thermal | 548802 SUB H 69 548806 BLUVLY 69 1 | 29SP | T0 | P12:161:INDN:BLUVLY-SUB M:::HV: | B | 58 | 23.948 | 171.565 |  |  |  | Rebuild line 548802 SUB H 69 548806 BLUVLY 69 1
00ALL | ERIS | Thermal | 548802 SUB H 69 548815 SUB M 69 1 | 29SP | T0 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | B | 79 | 34.0736 | 117.5648 |  |  |  | Rebuild line 548802 SUB H 69 548815 SUB M 69 1
00ALL | ERIS | Thermal | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | 29SP | T0 | P12:161:INDN:BLUVLY-SUB M:::HV: | B | 112 | 69.5761 | 191.6339 |  |  |  | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
00ALL | ERIS | Thermal | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | 29SP | T0 | P12:161:INDN:BLUVLY-SUB M:::HV: | B | 112 | 71.4809 | 196.8803 |  |  |  | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
00ALL | ERIS | Thermal | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | 29SP | T0 | Single 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 335 | 35.7518 | 276.0338 |  |  |  | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
00ALL | ERIS | Thermal | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | 29SP | T0 | Single 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 309 | 59.1883 | 302.1205 |  |  |  | Add line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 M2
00ALL | ERIS | Thermal | 548815 SUB M 69 548814 SUB M-161 161 1 | 29SP | T0 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | B | 112 | 82.6625 | 150.5222 |  |  |  | Rebuild 2-winding transformer 548814 SUB M-161 161 548815 SUB M 69 1
00ALL | ERIS | Thermal | 640088 BPS SUB7 115 3WXFMR 640:BPS_345_115 T1 345 1 | 29SP | T0 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | B | 417 | 68.8908 | 105.8248 |  |  |  | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2
00ALL | ERIS | Thermal | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | 29SP | T0 | Single 640312 PAULINE3 345 640525 TOBIAS3 345 1 | B | 956 | 44.5763 | 104.1025 |  |  |  | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
00ALL | ERIS | Thermal | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | 29SP | T0 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | B | 956 | 108.8674 | 248.1828 |  |  |  | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
00ALL | ERIS | Thermal | 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 | 29SP | T0 | P42:345:NPPD:BKR-MOR-3306:::: | B | 956 | 70.3698 | 115.201 |  |  |  | Rebuild line 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1
00ALL | ERIS | Thermal | 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 | 29SP | T0 | P42:345:NPPD:L3502A.MOORE.MCCOOL.CB3310:::: | B | 956 | 63.3424 | 108.5368 |  |  |  | Rebuild line 640277 MOORE 3 345 650189 103&ROKEBY3 345 1
00ALL | ERIS | Thermal | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T1 345 1 | 29SP | T0 | P42:345:NPPD:BKR-MOR-3308:::: | B | 417 | 66.7547 | 130.1714 |  |  |  | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
00ALL | ERIS | Thermal | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T2 345 1 | 29SP | T0 | P42:345:NPPD:BKR-MOR-3308:::: | B | 417 | 66.7547 | 130.1714 |  |  |  | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
00ALL | ERIS | Thermal | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T1 345 1 | 29SP | T0 | P42:345:NPPD:BKR-MOR-3308:::: | B | 417 | 65.6073 | 125.7875 |  |  |  | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
00ALL | ERIS | Thermal | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T2 345 1 | 29SP | T0 | P42:345:NPPD:BKR-MOR-3308:::: | B | 417 | 65.6073 | 125.7878 |  |  |  | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
00ALL | ERIS | Thermal | 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1 | 29SP | T0 | P42:345:NPPD:BKR-MOR-3308:::: | B | 240 | 59.8063 | 111.1518 |  |  |  | Rebuild line 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1
00ALL | ERIS | Thermal | 645455 S3455 3 345 645740 S3740 3 345 1 | 29SP | T0 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | B | 1195 | 116.3217 | 167.3859 |  |  |  | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
00ALL | ERIS | Thermal | 646221 S1221 5 161 646231 S1231 5 161 1 | 29SP | T0 | P23:345:OPPD:FUTURE 56-55&56-58:::EHV: | B | 217 | 129.9033 | 145.0025 |  |  |  | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
00ALL | ERIS | Thermal | 652391 WILLISTON27 115 652421 WILISTN7 115 Z1 | 29SP | T0 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | B | 201 | 7.6843 | 112.6538 |  |  |  | Rebuild line 652391 WILLISTON27 115 652421 WILISTN7 115 Z1
00ALL | ERIS | Thermal | 652400 WILISTN4 230 659334 JUDSON__-BE4 230 1 | 29SP | T0 | P23:345:UMZB:# 7148 #:: TND IN ND. BREAKER FAULT (296):EHV: | B | 482 | 59.2387 | 115.4285 |  |  |  | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
00ALL | ERIS | Thermal | 652400 WILISTN4 230 659334 JUDSON__-BE4 230 1 | 29SP | T0 | P23:345:UMZB:# 7148 #:: TND IN ND. BREAKER FAULT (296):EHV: | B | 482 | 59.2387 | 115.4285 |  |  |  | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
00ALL | ERIS | Thermal | 652400 WILISTN4 230 659334 JUDSON__-BE4 230 1 | 29SP | T0 | P23:345:UMZB:# 7148 #:: TND IN ND. BREAKER FAULT (296):EHV: | B | 482 | 59.2387 | 115.4285 |  |  |  | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
00ALL | ERIS | Thermal | 655933 N.MISRDG-MW7 115 655957 EASTFORK-MW7 115 1 | 29SP | T0 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | B | 189 | 5.5596 | 137.3456 |  |  |  | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
00ALL | ERIS | Thermal | 655933 N.MISRDG-MW7 115 655957 EASTFORK-MW7 115 1 | 29SP | T0 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | B | 189 | 5.5596 | 137.3456 |  |  |  | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
00ALL | ERIS | Thermal | 655933 N.MISRDG-MW7 115 655957 EASTFORK-MW7 115 1 | 29SP | T0 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | B | 189 | 5.5596 | 137.3456 |  |  |  | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
00ALL | ERIS | Thermal | 655957 EASTFORK-MW7 115 659331 SPRNGBRK-BE7 115 1 | 29SP | T0 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | B | 415 | 20.771 | 130.4722 |  |  |  | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
00ALL | ERIS | Thermal | 655957 EASTFORK-MW7 115 659331 SPRNGBRK-BE7 115 1 | 29SP | T0 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | B | 415 | 20.771 | 130.4722 |  |  |  | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
00ALL | ERIS | Thermal | 655957 EASTFORK-MW7 115 659331 SPRNGBRK-BE7 115 1 | 29SP | T0 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | B | 415 | 20.771 | 130.4722 |  |  |  | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
00ALL | ERIS | Thermal | 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1 | 29SP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 506 | 33.1765 | 213.4091 |  |  |  | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
00ALL | ERIS | Thermal | 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1 | 29SP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 506 | 33.1765 | 213.4091 |  |  |  | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
00ALL | ERIS | Thermal | 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1 | 29SP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 506 | 33.1765 | 213.4091 |  |  |  | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
00ALL | ERIS | Thermal | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z | 29SP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 506 | 23.9278 | 184.5908 |  |  |  | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
00ALL | ERIS | Thermal | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z | 29SP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 506 | 23.9278 | 184.5908 |  |  |  | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
00ALL | ERIS | Thermal | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z | 29SP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 506 | 23.9278 | 184.5908 |  |  |  | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
00ALL | ERIS | Thermal | 659330 SPRNGBRK-BE3 345 3WXFMR 659:652: SPRNGBRK KUXA 115 1 | 29SP | T0 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | B | 416 | 20.876 | 130.276 |  |  |  | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
00ALL | ERIS | Thermal | 659330 SPRNGBRK-BE3 345 3WXFMR 659:652: SPRNGBRK KUXA 115 1 | 29SP | T0 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | B | 416 | 20.876 | 130.276 |  |  |  | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
00ALL | ERIS | Thermal | 659330 SPRNGBRK-BE3 345 3WXFMR 659:652: SPRNGBRK KUXA 115 1 | 29SP | T0 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | B | 416 | 20.876 | 130.276 |  |  |  | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
00ALL | ERIS | Thermal | 659330 SPRNGBRK-BE3 345 659333 JUDSON__-BE3 345 1 | 29SP | T0 | P12:345.0:UMZ:# N-1 #:: LINE TANDE___-BE3-TN.LS-JD-BE3-Z :EHV: | B | 1087 | -14.0946 | 104.9387 |  |  |  | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
00ALL | ERIS | Thermal | 659330 SPRNGBRK-BE3 345 659333 JUDSON__-BE3 345 1 | 29SP | T0 | P12:345.0:UMZ:# N-1 #:: LINE TANDE___-BE3-TN.LS-JD-BE3-Z :EHV: | B | 1087 | -14.0946 | 104.9387 |  |  |  | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
00ALL | ERIS | Thermal | 659330 SPRNGBRK-BE3 345 659333 JUDSON__-BE3 345 1 | 29SP | T0 | P12:345.0:UMZ:# N-1 #:: LINE TANDE___-BE3-TN.LS-JD-BE3-Z :EHV: | B | 1087 | -14.0946 | 104.9387 |  |  |  | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
00ALL | ERIS | Thermal | 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | 29SP | T0 | P12:345.0:UMZ:# N-1 #:: LINE TANDE___-BE3-TN.LS-JD-BE3-Z :EHV: | B | 1087 | -2.484 | 135.101 |  |  |  | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1
00ALL | ERIS | Thermal | 659331 SPRNGBRK-BE7 115 3WXFMR 659:652: SPRNGBRK KUXA 115 1 | 29SP | T0 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | B | 416 | 20.8384 | 128.3005 |  |  |  | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
00ALL | ERIS | Thermal | 659331 SPRNGBRK-BE7 115 3WXFMR 659:652: SPRNGBRK KUXA 115 1 | 29SP | T0 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | B | 416 | 20.8384 | 128.3005 |  |  |  | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
00ALL | ERIS | Thermal | 659331 SPRNGBRK-BE7 115 3WXFMR 659:652: SPRNGBRK KUXA 115 1 | 29SP | T0 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | B | 416 | 20.8384 | 128.3005 |  |  |  | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
00ALL | ERIS | Thermal | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | 29SP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 637 | 66.916 | 204.6432 |  |  |  | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
00ALL | ERIS | Thermal | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | 29SP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 637 | 66.916 | 204.6432 |  |  |  | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
00ALL | ERIS | Thermal | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | 29SP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 637 | 66.916 | 204.6432 |  |  |  | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
00ALL | ERIS | Thermal | 659336 TANDE___-BE3 345 659427 TN.LS-JD-BE3 345 Z | 29SP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | -2.5032 | 140.2416 |  |  |  | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
00ALL | ERIS | Thermal | 659336 TANDE___-BE3 345 659427 TN.LS-JD-BE3 345 Z | 29SP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | -2.5032 | 140.2416 |  |  |  | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
00ALL | ERIS | Thermal | 659336 TANDE___-BE3 345 659427 TN.LS-JD-BE3 345 Z | 29SP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | -2.5032 | 140.2416 |  |  |  | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
00ALL | ERIS | Thermal | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | 29SP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 637 | 66.588 | 204.6432 |  |  |  | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
00ALL | ERIS | Thermal | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | 29SP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 637 | 66.588 | 204.6432 |  |  |  | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
00ALL | ERIS | Thermal | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | 29SP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 637 | 66.588 | 204.6432 |  |  |  | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
00ALL | ERIS | Thermal | 659362 WHEELOCK-BE4 230 661084 TIOGA4 4 230 1 | 29SP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 506 | 23.1015 | 125.5606 |  |  |  | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
00ALL | ERIS | Thermal | 659362 WHEELOCK-BE4 230 661084 TIOGA4 4 230 1 | 29SP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 506 | 23.1015 | 125.5606 |  |  |  | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
00ALL | ERIS | Thermal | 659362 WHEELOCK-BE4 230 661084 TIOGA4 4 230 1 | 29SP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 506 | 23.1015 | 125.5606 |  |  |  | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
00ALL | ERIS | Thermal | 659427 TN.LS-JD-BE3 345 779400 G24-081-TAP 345 1 | 29SP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | -2.1433 | 140.2416 |  |  |  | Rebuild line 659427 TN.LS-JD-BE3 345 779400 G24-081-TAP 345 1
00ALL | ERIS | Thermal | 771999 G23-222-POI 345 3WXFMR 640:BPS_345_115 T1 345 1 | 29SP | T0 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | B | 417 | 68.9284 | 105.8248 |  |  |  | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2
00ALL | ERIS | Thermal | 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1 | 29SP | T0 | P23:345:AEPW:WELSH CB 10610 NBTB:::: | B | 1059 | 52.4643 | 114.8273 |  |  |  | Rebuild line 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1
00ALL | ERIS | Thermal | 787170 G24-340-TAP 345 787290 G24-344-TAP 345 1 | 29SP | T0 | Single 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1 | B | 1055 | 0.55673 | 129.6354 |  |  |  | Rebuild line 787170 G24-340-TAP 345 787290 G24-344-TAP 345 1
00ALL | ERIS | Thermal | 505552 GORE 5 161 505558 MUSKTAP5 161 1 | 29SP | T1 | P22:345:EES:MUSKOGE7!:::EHV: | B | 201 | 73.1209 | 111.1438 |  |  |  | Rebuild line 505552 GORE 5 161 505558 MUSKTAP5 161 1
00ALL | ERIS | Thermal | 507711 ARSHILL4 138 507742 MCWILLI4 138 1 | 29SP | T1 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | B | 308 | 58.7175 | 108.5009 |  |  |  | Rebuild line 507711 ARSHILL4 138 507742 MCWILLI4 138 1
00ALL | ERIS | Thermal | 507727 FLOURNY4 138 507732 GENMOTR4 138 1 | 29SP | T1 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | B | 188 | 91.8229 | 185.8438 |  |  |  | Rebuild line 507727 FLOURNY4 138 507732 GENMOTR4 138 1
00ALL | ERIS | Thermal | 507727 FLOURNY4 138 508816 OAKPH 4 138 1 | 29SP | T1 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | B | 395 | 56.2966 | 101.2557 |  |  |  | Rebuild line 507727 FLOURNY4 138 508816 OAKPH 4 138 1
00ALL | ERIS | Thermal | 507732 GENMOTR4 138 507759 SW SHV 4 138 1 | 29SP | T1 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | B | 188 | 91.381 | 185.2751 |  |  |  | Rebuild line 507732 GENMOTR4 138 507759 SW SHV 4 138 1
00ALL | ERIS | Thermal | 507760 SW SHV 7 345 508809 LONGWD 7 345 1 | 29SP | T1 | Single 337376 7SAREPTA% 345 788340 G24-379-TAP 345 1 | B | 1195 | 43.0829 | 109.0412 |  |  |  | Rebuild line 507760 SW SHV 7 345 508809 LONGWD 7 345 1
00ALL | ERIS | Thermal | 507774 NORAM 4 138 508808 LONGWD 4 138 1 | 29SP | T1 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | B | 265 | 81.7637 | 117.6238 |  |  |  | Rebuild line 507774 NORAM 4 138 508808 LONGWD 4 138 1
00ALL | ERIS | Thermal | 508548 KNOXLEE4 138 509059 CHEROKE4 138 1 | 29SP | T1 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | B | 395 | 66.7557 | 108.1364 |  |  |  | Rebuild line 508548 KNOXLEE4 138 509059 CHEROKE4 138 1
00ALL | ERIS | Thermal | 508562 PIRKEY 4 138 508566 SABMINT4 138 1 | 29SP | T1 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | B | 395 | 53.4519 | 101.7389 |  |  |  | Rebuild line 508562 PIRKEY 4 138 508566 SABMINT4 138 1
00ALL | ERIS | Thermal | 508808 LONGWD 4 138 3WXFMR 520:LONGWOOD 345 1 | 29SP | T1 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | B | 580 | 71.0833 | 113.9863 |  |  |  | Add 3-winding transformer 508808 LONGWD 4 138 508809 LONGWD 7 345 508819 LONGW1-1 13 M2
00ALL | ERIS | Thermal | 508808 LONGWD 4 138 508816 OAKPH 4 138 1 | 29SP | T1 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | B | 395 | 57.2108 | 102.188 |  |  |  | Rebuild line 508808 LONGWD 4 138 508816 OAKPH 4 138 1
00ALL | ERIS | Thermal | 508809 LONGWD 7 345 3WXFMR 520:LONGWOOD 345 1 | 29SP | T1 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | B | 580 | 73.0784 | 116.5224 |  |  |  | Add 3-winding transformer 508808 LONGWD 4 138 508809 LONGWD 7 345 508819 LONGW1-1 13 M2
00ALL | ERIS | Thermal | 509059 CHEROKE4 138 509087 TATUM 4 138 1 | 29SP | T1 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | B | 350 | 72.7574 | 119.3858 |  |  |  | Rebuild line 509059 CHEROKE4 138 509087 TATUM 4 138 1
00ALL | ERIS | Thermal | 509083 ROKHILL4 138 509087 TATUM 4 138 1 | 29SP | T1 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | B | 350 | 71.6444 | 118.2437 |  |  |  | Rebuild line 509083 ROKHILL4 138 509087 TATUM 4 138 1
00ALL | ERIS | Thermal | 514934 DRAPER 7 345 515045 SEMINOL7 345 2 | 29SP | T1 | P42:345:OKGE:SB_SEOL7385:::EHV: | B | 717 | 40.7232 | 109.0105 |  |  |  | Rebuild line 514934 DRAPER 7 345 515045 SEMINOL7 345 2
00ALL | ERIS | Thermal | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 | 29SP | T1 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 191 | 66.9209 | 102.6582 |  |  |  | Rebuild line 515117 ARBUCKL4 138 515121 MILLCKT4 138 1
00ALL | ERIS | Thermal | 533021 NEOSHO 4 138 533023 N345 3 4 138 1 | 29SP | T1 | Single 532793 NEOSHO7 345 532939 N34545 161 532825 'N345 2 1 ' 13 2 | B | 478 | 92.8465 | 117.99 |  |  |  | Rebuild line 533021 NEOSHO 4 138 533023 N345 3 4 138 1
00ALL | ERIS | Thermal | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | 29SP | T1 | P12:161:INDN:BLUVLY-ECKLES:::HV: | B | 335 | -7.1041 | 107.0069 |  |  |  | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
00ALL | ERIS | Thermal | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | 29SP | T1 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | B | 956 | 52.7149 | 121.9917 |  |  |  | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
00ALL | ERIS | Thermal | 645454 S3454 3 345 645455 S3455 3 345 1 | 29SP | T1 | P12:345:OPPD:S3455-S3740:::EHV: | B | 1195 | 74.0258 | 100.6765 |  |  |  | Rebuild line 645454 S3454 3 345 645455 S3455 3 345 1
00ALL | ERIS | Thermal | 645455 S3455 3 345 645740 S3740 3 345 1 | 29SP | T1 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | B | 1195 | 116.0916 | 168.2571 |  |  |  | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
00ALL | ERIS | Thermal | 646221 S1221 5 161 646231 S1231 5 161 1 | 29SP | T1 | P23:345:OPPD:FUTURE 56-55&56-58:::EHV: | B | 217 | 129.7285 | 147.401 |  |  |  | Rebuild line 646221 S1221 5 161 646231 S1231 5 161 1
00ALL | ERIS | Thermal | 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1 | 29SP | T1 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 506 | 34.6907 | 115.9626 |  |  |  | Rebuild line 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1
00ALL | ERIS | Thermal | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z | 29SP | T1 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 506 | 27.4471 | 100.5821 |  |  |  | Rebuild line 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z
00ALL | ERIS | Thermal | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | 29SP | T1 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 637 | 69.2297 | 132.5403 |  |  |  | Add 3-winding transformer 659336 TANDE___-BE3 345 659337 TANDE___-BE4 230 659338 TND.KU3A-BE9 13 M2
00ALL | ERIS | Thermal | 659336 TANDE___-BE3 345 659427 TN.LS-JD-BE3 345 Z | 29SP | T1 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | -2.5375 | 138.039 |  |  |  | Rebuild line 659336 TANDE___-BE3 345 659427 TN.LS-JD-BE3 345 Z
00ALL | ERIS | Thermal | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | 29SP | T1 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 637 | 68.9132 | 132.5403 |  |  |  | Add 3-winding transformer 659336 TANDE___-BE3 345 659337 TANDE___-BE4 230 659338 TND.KU3A-BE9 13 M2
00ALL | ERIS | Thermal | 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1 | 29SP | T2 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 637 | 35.1985 | 106.461 |  |  |  | Rebuild line 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1
00ALL | ERIS | Thermal | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z | 29SP | T2 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 509 | 34.1408 | 112.6519 |  |  |  | Rebuild line 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z
00ALL | ERIS | Thermal | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 29WP | T0 | System Intact | A | 334 | 96.6246 | 103.3014 |  |  |  | Rebuild line 300071 5CLINTN 161 761278 G17-108-TAP 161 1
00ALL | ERIS | Thermal | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | 29WP | T0 | Single 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 277 | 14.1631 | 111.917 |  |  |  | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
00ALL | ERIS | Thermal | 337376 7SAREPTA% 345 788340 G24-379-TAP 345 1 | 29WP | T0 | Single 508809 LONGWD7 345 788340 G24-379-TAP 345 1 | B | 1195 | -1.7993 | 111.4105 |  |  |  | Rebuild line 337376 7SAREPTA% 345 788340 G24-379-TAP 345 1
00ALL | ERIS | Thermal | 508548 KNOXLEE4 138 509092 EASTON 4 138 1 | 29WP | T0 | P23:345:AEPW:PIRKEY CB 13430 NBTB:::: | B | 618 | 40.2213 | 105.8681 |  |  |  | Rebuild line 508548 KNOXLEE4 138 509092 EASTON 4 138 1
00ALL | ERIS | Thermal | 508562 PIRKEY 4 138 3WXFMR 520:PIRKEY 1 345 1 | 29WP | T0 | P23:345:AEPW:PIRKEY CB 13430 NBTB:::: | B | 600 | 17.5545 | 105.7103 |  |  |  | Add 3-winding transformer 508562 PIRKEY 4 138 508563 PIRKEY 7 345 508587 PIRKY1-1 13 M2
00ALL | ERIS | Thermal | 508563 PIRKEY 7 345 3WXFMR 520:PIRKEY 1 345 1 | 29WP | T0 | P23:345:AEPW:PIRKEY CB 13430 NBTB:::: | B | 600 | 17.6417 | 107.566 |  |  |  | Add 3-winding transformer 508562 PIRKEY 4 138 508563 PIRKEY 7 345 508587 PIRKY1-1 13 M2
00ALL | ERIS | Thermal | 508566 SABMINT4 138 508569 SEMRSHL4 138 1 | 29WP | T0 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | B | 333 | 57.2357 | 102.9158 |  |  |  | Rebuild line 508566 SABMINT4 138 508569 SEMRSHL4 138 1
00ALL | ERIS | Thermal | 508809 LONGWD 7 345 788340 G24-379-TAP 345 1 | 29WP | T0 | Single 337376 7SAREPTA% 345 788340 G24-379-TAP 345 1 | B | 1195 | -1.5798 | 111.4957 |  |  |  | Rebuild line 508809 LONGWD 7 345 788340 G24-379-TAP 345 1
00ALL | ERIS | Thermal | 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1 | 29WP | T0 | P42:345:OKGE:SB_REUD7389:::EHV: | B | 1143 | -5.9977 | 126.4144 |  |  |  | Rebuild line 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1
00ALL | ERIS | Thermal | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 29WP | T0 | Single 510907 PITTSB-7 345 515422 C-RIVER7 345 1 | B | 956 | 8.5669 | 100.5325 |  |  |  | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
00ALL | ERIS | Thermal | 514909 REDBUD 7 345 787290 G24-344-TAP 345 1 | 29WP | T0 | Single 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1 | B | 1143 | -5.1352 | 122.9331 |  |  |  | Rebuild line 514909 REDBUD 7 345 787290 G24-344-TAP 345 1
00ALL | ERIS | Thermal | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 | 29WP | T0 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 191 | 27.2337 | 112.3457 |  |  |  | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
00ALL | ERIS | Thermal | 532793 NEOSHO 7 345 3WXFMR 536:N345 TX-1 138 1 | 29WP | T0 | Single 532793 NEOSHO7 345 532939 N34545 161 532825 'N345 2 1 ' 13 2 | B | 400 | 86.1791 | 105.5635 |  |  |  | Add 3-winding transformer 532793 NEOSHO 7 345 532824 N345 1 1 13 533023 N345 3 4 138 M2
00ALL | ERIS | Thermal | 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 | 29WP | T0 | P23:345:WERE:N345-345-20:EHV: | B | 956 | 19.1442 | 112.4564 |  |  |  | Rebuild line 532794 ROSEHIL7 345 532800 LATHAMS7 345 1
00ALL | ERIS | Thermal | 533023 N345 3 4 138 3WXFMR 536:N345 TX-1 138 1 | 29WP | T0 | Single 532937 NEOSHO5 161 532939 N34545 161 1 | B | 400 | 93.7718 | 112.6182 |  |  |  | Add 3-winding transformer 532793 NEOSHO 7 345 532824 N345 1 1 13 533023 N345 3 4 138 M2
00ALL | ERIS | Thermal | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 | 29WP | T0 | Single 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 334 | 21.3163 | 141.2841 |  |  |  | Rebuild line 541250 SIBLEYPL 161 548808 ECKLES-161 161 1
00ALL | ERIS | Thermal | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | 29WP | T0 | Single 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 334 | 67.6109 | 267.3731 |  |  |  | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
00ALL | ERIS | Thermal | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | 29WP | T0 | Single 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 334 | 54.3269 | 279.2988 |  |  |  | Add line 543004 BLUMILS5 161 548808 ECKLES-161 161 M2
00ALL | ERIS | Thermal | 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | 29WP | T0 | Single 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 334 | -0.45183 | 224.2817 |  |  |  | Rebuild line 543004 BLUMILS5 161 783180 G24-207-TAP 161 1
00ALL | ERIS | Thermal | 543164 SUGRCK_TP_W2 69 543165 SUGRCK_TP_E2 69 1 | 29WP | T0 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | B | 53 | 19.6703 | 125.9223 |  |  |  | Rebuild line 543164 SUGRCK_TP_W2 69 543165 SUGRCK_TP_E2 69 1
00ALL | ERIS | Thermal | 548802 SUB H 69 548806 BLUVLY 69 1 | 29WP | T0 | P12:161:INDN:BLUVLY-SUB M:::HV: | B | 72 | 16.0279 | 136.8184 |  |  |  | Rebuild line 548802 SUB H 69 548806 BLUVLY 69 1
00ALL | ERIS | Thermal | 548802 SUB H 69 548815 SUB M 69 1 | 29WP | T0 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | B | 96 | 33.934 | 102.4189 |  |  |  | Rebuild line 548802 SUB H 69 548815 SUB M 69 1
00ALL | ERIS | Thermal | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | 29WP | T0 | P12:161:INDN:BLUVLY-SUB M:::HV: | B | 112 | 50.9085 | 173.2062 |  |  |  | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
00ALL | ERIS | Thermal | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | 29WP | T0 | P12:161:INDN:BLUVLY-SUB M:::HV: | B | 112 | 52.3022 | 177.948 |  |  |  | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
00ALL | ERIS | Thermal | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | 29WP | T0 | Single 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 335 | 42.003 | 282.9433 |  |  |  | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
00ALL | ERIS | Thermal | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | 29WP | T0 | Single 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 334 | 54.2753 | 277.815 |  |  |  | Add line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 M2
00ALL | ERIS | Thermal | 548815 SUB M 69 548814 SUB M-161 161 1 | 29WP | T0 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | B | 112 | 68.8874 | 136.1066 |  |  |  | Rebuild 2-winding transformer 548814 SUB M-161 161 548815 SUB M 69 1
00ALL | ERIS | Thermal | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | 29WP | T0 | Single 640312 PAULINE3 345 640525 TOBIAS3 345 1 | B | 956 | 37.2352 | 101.3156 |  |  |  | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
00ALL | ERIS | Thermal | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | 29WP | T0 | Single 640600 DAYKIN3 345 771999 G23-222-POI 345 1 | B | 956 | 99.5227 | 248.2416 |  |  |  | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
00ALL | ERIS | Thermal | 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 | 29WP | T0 | P42:345:NPPD:BKR-MOR-3306:::: | B | 956 | 60.1157 | 102.9523 |  |  |  | Rebuild line 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1
00ALL | ERIS | Thermal | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T1 345 1 | 29WP | T0 | P42:345:NPPD:BKR-MOR-3308:::: | B | 417 | 64.531 | 124.734 |  |  |  | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
00ALL | ERIS | Thermal | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T2 345 1 | 29WP | T0 | P42:345:NPPD:BKR-MOR-3308:::: | B | 417 | 64.531 | 124.734 |  |  |  | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
00ALL | ERIS | Thermal | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T1 345 1 | 29WP | T0 | P42:345:NPPD:BKR-MOR-3308:::: | B | 417 | 63.4491 | 121.5754 |  |  |  | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
00ALL | ERIS | Thermal | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T2 345 1 | 29WP | T0 | P42:345:NPPD:BKR-MOR-3308:::: | B | 417 | 63.4491 | 121.5756 |  |  |  | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
00ALL | ERIS | Thermal | 645455 S3455 3 345 645740 S3740 3 345 1 | 29WP | T0 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | B | 1195 | 100.0875 | 155.7815 |  |  |  | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
00ALL | ERIS | Thermal | 646221 S1221 5 161 646231 S1231 5 161 1 | 29WP | T0 | P23:345:OPPD:FUTURE 56-55&56-58:::EHV: | B | 217 | 109.8952 | 127.9376 |  |  |  | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
00ALL | ERIS | Thermal | 655933 N.MISRDG-MW7 115 655957 EASTFORK-MW7 115 1 | 29WP | T0 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | B | 189 | 4.2245 | 137.4246 |  |  |  | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
00ALL | ERIS | Thermal | 655933 N.MISRDG-MW7 115 655957 EASTFORK-MW7 115 1 | 29WP | T0 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | B | 189 | 4.2245 | 137.4246 |  |  |  | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
00ALL | ERIS | Thermal | 655933 N.MISRDG-MW7 115 655957 EASTFORK-MW7 115 1 | 29WP | T0 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | B | 189 | 4.2245 | 137.4246 |  |  |  | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
00ALL | ERIS | Thermal | 655957 EASTFORK-MW7 115 659331 SPRNGBRK-BE7 115 1 | 29WP | T0 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | B | 415 | 24.3267 | 134.8503 |  |  |  | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
00ALL | ERIS | Thermal | 655957 EASTFORK-MW7 115 659331 SPRNGBRK-BE7 115 1 | 29WP | T0 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | B | 415 | 24.3267 | 134.8503 |  |  |  | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
00ALL | ERIS | Thermal | 655957 EASTFORK-MW7 115 659331 SPRNGBRK-BE7 115 1 | 29WP | T0 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | B | 415 | 24.3267 | 134.8503 |  |  |  | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
00ALL | ERIS | Thermal | 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1 | 29WP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 637 | 30.8843 | 173.7597 |  |  |  | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
00ALL | ERIS | Thermal | 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1 | 29WP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 637 | 30.8843 | 173.7597 |  |  |  | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
00ALL | ERIS | Thermal | 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1 | 29WP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 637 | 30.8843 | 173.7597 |  |  |  | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
00ALL | ERIS | Thermal | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z | 29WP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 526 | 22.1882 | 177.0036 |  |  |  | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
00ALL | ERIS | Thermal | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z | 29WP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 526 | 22.1882 | 177.0036 |  |  |  | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
00ALL | ERIS | Thermal | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z | 29WP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 526 | 22.1882 | 177.0036 |  |  |  | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
00ALL | ERIS | Thermal | 659330 SPRNGBRK-BE3 345 3WXFMR 659:652: SPRNGBRK KUXA 115 1 | 29WP | T0 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | B | 416 | 24.3736 | 134.7044 |  |  |  | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
00ALL | ERIS | Thermal | 659330 SPRNGBRK-BE3 345 3WXFMR 659:652: SPRNGBRK KUXA 115 1 | 29WP | T0 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | B | 416 | 24.3736 | 134.7044 |  |  |  | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
00ALL | ERIS | Thermal | 659330 SPRNGBRK-BE3 345 3WXFMR 659:652: SPRNGBRK KUXA 115 1 | 29WP | T0 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | B | 416 | 24.3736 | 134.7044 |  |  |  | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
00ALL | ERIS | Thermal | 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | 29WP | T0 | P23:345:UMZB:# 7148 #:: TND IN ND. BREAKER FAULT (296):EHV: | B | 1195 | -0.52553 | 123.2148 |  |  |  | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1
00ALL | ERIS | Thermal | 659331 SPRNGBRK-BE7 115 3WXFMR 659:652: SPRNGBRK KUXA 115 1 | 29WP | T0 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | B | 416 | 24.3284 | 132.4544 |  |  |  | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
00ALL | ERIS | Thermal | 659331 SPRNGBRK-BE7 115 3WXFMR 659:652: SPRNGBRK KUXA 115 1 | 29WP | T0 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | B | 416 | 24.3284 | 132.4544 |  |  |  | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
00ALL | ERIS | Thermal | 659331 SPRNGBRK-BE7 115 3WXFMR 659:652: SPRNGBRK KUXA 115 1 | 29WP | T0 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | B | 416 | 24.3284 | 132.4544 |  |  |  | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
00ALL | ERIS | Thermal | 659333 JUDSON__-BE3 345 3WXFMR 659:652: JUDSON KUXA 230 1 | 29WP | T0 | P13:345-230.0:UMZ:# N-1 #:: 3WND JUDSON__-BE3-JUDSON__-BE4-JDS.KU6A-BE9-1 JUDSON KU3A:EHV: | B | 717 | 93.6334 | 104.5457 |  |  |  | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
00ALL | ERIS | Thermal | 659333 JUDSON__-BE3 345 3WXFMR 659:652: JUDSON KUXA 230 1 | 29WP | T0 | P13:345-230.0:UMZ:# N-1 #:: 3WND JUDSON__-BE3-JUDSON__-BE4-JDS.KU6A-BE9-1 JUDSON KU3A:EHV: | B | 717 | 93.6334 | 104.5457 |  |  |  | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
00ALL | ERIS | Thermal | 659333 JUDSON__-BE3 345 3WXFMR 659:652: JUDSON KUXA 230 1 | 29WP | T0 | P13:345-230.0:UMZ:# N-1 #:: 3WND JUDSON__-BE3-JUDSON__-BE4-JDS.KU6A-BE9-1 JUDSON KU3A:EHV: | B | 717 | 93.6334 | 104.5457 |  |  |  | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
00ALL | ERIS | Thermal | 659333 JUDSON__-BE3 345 3WXFMR 659:JUDSON KU3A 230 1 | 29WP | T0 | Single 659333 JUDSON__-BE3 345 659334 JUDSON__-BE4 230 659329 'JDS.KUXA-BE9' 13 1 | B | 717 | 93.6334 | 104.5457 |  |  |  | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
00ALL | ERIS | Thermal | 659333 JUDSON__-BE3 345 3WXFMR 659:JUDSON KU3A 230 1 | 29WP | T0 | Single 659333 JUDSON__-BE3 345 659334 JUDSON__-BE4 230 659329 'JDS.KUXA-BE9' 13 1 | B | 717 | 93.6334 | 104.5457 |  |  |  | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
00ALL | ERIS | Thermal | 659333 JUDSON__-BE3 345 3WXFMR 659:JUDSON KU3A 230 1 | 29WP | T0 | Single 659333 JUDSON__-BE3 345 659334 JUDSON__-BE4 230 659329 'JDS.KUXA-BE9' 13 1 | B | 717 | 93.6334 | 104.5457 |  |  |  | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
00ALL | ERIS | Thermal | 659334 JUDSON__-BE4 230 3WXFMR 659:652: JUDSON KUXA 230 1 | 29WP | T0 | P13:345-230.0:UMZ:# N-1 #:: 3WND JUDSON__-BE3-JUDSON__-BE4-JDS.KU6A-BE9-1 JUDSON KU3A:EHV: | B | 717 | 93.6334 | 104.5457 |  |  |  | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
00ALL | ERIS | Thermal | 659334 JUDSON__-BE4 230 3WXFMR 659:652: JUDSON KUXA 230 1 | 29WP | T0 | P13:345-230.0:UMZ:# N-1 #:: 3WND JUDSON__-BE3-JUDSON__-BE4-JDS.KU6A-BE9-1 JUDSON KU3A:EHV: | B | 717 | 93.6334 | 104.5457 |  |  |  | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
00ALL | ERIS | Thermal | 659334 JUDSON__-BE4 230 3WXFMR 659:652: JUDSON KUXA 230 1 | 29WP | T0 | P13:345-230.0:UMZ:# N-1 #:: 3WND JUDSON__-BE3-JUDSON__-BE4-JDS.KU6A-BE9-1 JUDSON KU3A:EHV: | B | 717 | 93.6334 | 104.5457 |  |  |  | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
00ALL | ERIS | Thermal | 659334 JUDSON__-BE4 230 3WXFMR 659:JUDSON KU3A 230 1 | 29WP | T0 | Single 659333 JUDSON__-BE3 345 659334 JUDSON__-BE4 230 659329 'JDS.KUXA-BE9' 13 1 | B | 717 | 93.6334 | 104.5457 |  |  |  | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
00ALL | ERIS | Thermal | 659334 JUDSON__-BE4 230 3WXFMR 659:JUDSON KU3A 230 1 | 29WP | T0 | Single 659333 JUDSON__-BE3 345 659334 JUDSON__-BE4 230 659329 'JDS.KUXA-BE9' 13 1 | B | 717 | 93.6334 | 104.5457 |  |  |  | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
00ALL | ERIS | Thermal | 659334 JUDSON__-BE4 230 3WXFMR 659:JUDSON KU3A 230 1 | 29WP | T0 | Single 659333 JUDSON__-BE3 345 659334 JUDSON__-BE4 230 659329 'JDS.KUXA-BE9' 13 1 | B | 717 | 93.6334 | 104.5457 |  |  |  | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
00ALL | ERIS | Thermal | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | 29WP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 637 | 70.423 | 208.6129 |  |  |  | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
00ALL | ERIS | Thermal | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | 29WP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 637 | 70.423 | 208.6129 |  |  |  | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
00ALL | ERIS | Thermal | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | 29WP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 637 | 70.423 | 208.6129 |  |  |  | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
00ALL | ERIS | Thermal | 659336 TANDE___-BE3 345 659427 TN.LS-JD-BE3 345 Z | 29WP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1195 | -1.9491 | 127.7361 |  |  |  | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
00ALL | ERIS | Thermal | 659336 TANDE___-BE3 345 659427 TN.LS-JD-BE3 345 Z | 29WP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1195 | -1.9491 | 127.7361 |  |  |  | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
00ALL | ERIS | Thermal | 659336 TANDE___-BE3 345 659427 TN.LS-JD-BE3 345 Z | 29WP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1195 | -1.9491 | 127.7361 |  |  |  | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
00ALL | ERIS | Thermal | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | 29WP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 637 | 69.9163 | 208.6129 |  |  |  | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
00ALL | ERIS | Thermal | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | 29WP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 637 | 69.9163 | 208.6129 |  |  |  | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
00ALL | ERIS | Thermal | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | 29WP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 637 | 69.9163 | 208.6129 |  |  |  | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
00ALL | ERIS | Thermal | 659362 WHEELOCK-BE4 230 661084 TIOGA4 4 230 1 | 29WP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 526 | 20.7348 | 120.1453 |  |  |  | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
00ALL | ERIS | Thermal | 659362 WHEELOCK-BE4 230 661084 TIOGA4 4 230 1 | 29WP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 526 | 20.7348 | 120.1453 |  |  |  | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
00ALL | ERIS | Thermal | 659362 WHEELOCK-BE4 230 661084 TIOGA4 4 230 1 | 29WP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 526 | 20.7348 | 120.1453 |  |  |  | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
00ALL | ERIS | Thermal | 659427 TN.LS-JD-BE3 345 779400 G24-081-TAP 345 1 | 29WP | T0 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1195 | -1.9493 | 127.736 |  |  |  | Rebuild line 659427 TN.LS-JD-BE3 345 779400 G24-081-TAP 345 1
00ALL | ERIS | Thermal | 787170 G24-340-TAP 345 787290 G24-344-TAP 345 1 | 29WP | T0 | Single 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1 | B | 1143 | 0.51428 | 119.5812 |  |  |  | Rebuild line 787170 G24-340-TAP 345 787290 G24-344-TAP 345 1
00ALL | ERIS | Thermal | 507727 FLOURNY4 138 507732 GENMOTR4 138 1 | 29WP | T1 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | B | 234 | 42.0336 | 131.1509 |  |  |  | Rebuild line 507727 FLOURNY4 138 507732 GENMOTR4 138 1
00ALL | ERIS | Thermal | 507732 GENMOTR4 138 507759 SW SHV 4 138 1 | 29WP | T1 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | B | 234 | 41.815 | 130.7071 |  |  |  | Rebuild line 507732 GENMOTR4 138 507759 SW SHV 4 138 1
00ALL | ERIS | Thermal | 508548 KNOXLEE4 138 509059 CHEROKE4 138 1 | 29WP | T1 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | B | 395 | 55.4207 | 102.6963 |  |  |  | Rebuild line 508548 KNOXLEE4 138 509059 CHEROKE4 138 1
00ALL | ERIS | Thermal | 509059 CHEROKE4 138 509087 TATUM 4 138 1 | 29WP | T1 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | B | 379 | 54.6163 | 103.8167 |  |  |  | Rebuild line 509059 CHEROKE4 138 509087 TATUM 4 138 1
00ALL | ERIS | Thermal | 509083 ROKHILL4 138 509087 TATUM 4 138 1 | 29WP | T1 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | B | 379 | 53.7266 | 102.9027 |  |  |  | Rebuild line 509083 ROKHILL4 138 509087 TATUM 4 138 1
00ALL | ERIS | Thermal | 533021 NEOSHO 4 138 533023 N345 3 4 138 1 | 29WP | T1 | Single 532937 NEOSHO5 161 532939 N34545 161 1 | B | 478 | 98.4396 | 118.9931 |  |  |  | Rebuild line 533021 NEOSHO 4 138 533023 N345 3 4 138 1
00ALL | ERIS | Thermal | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | 29WP | T1 | P12:161:INDN:BLUVLY-ECKLES:::HV: | B | 334 | 11.6595 | 104.3267 |  |  |  | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
00ALL | ERIS | Thermal | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | 29WP | T1 | P12:161:INDN:BLUVLY-ECKLES:::HV: | B | 335 | -1.5155 | 110.7789 |  |  |  | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
00ALL | ERIS | Thermal | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | 29WP | T1 | Single 640600 DAYKIN3 345 771999 G23-222-POI 345 1 | B | 956 | 47.9037 | 120.7011 |  |  |  | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
00ALL | ERIS | Thermal | 645455 S3455 3 345 645740 S3740 3 345 1 | 29WP | T1 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | B | 1195 | 99.5062 | 156.3479 |  |  |  | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
00ALL | ERIS | Thermal | 646221 S1221 5 161 646231 S1231 5 161 1 | 29WP | T1 | P23:345:OPPD:FUTURE 56-55&56-58:::EHV: | B | 217 | 109.0627 | 129.6986 |  |  |  | Rebuild line 646221 S1221 5 161 646231 S1231 5 161 1
00ALL | ERIS | Thermal | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | 29WP | T1 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 637 | 75.3201 | 138.2005 |  |  |  | Add 3-winding transformer 659336 TANDE___-BE3 345 659337 TANDE___-BE4 230 659338 TND.KU3A-BE9 13 M2
00ALL | ERIS | Thermal | 659336 TANDE___-BE3 345 659427 TN.LS-JD-BE3 345 Z | 29WP | T1 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1195 | -1.9742 | 124.5842 |  |  |  | Rebuild line 659336 TANDE___-BE3 345 659427 TN.LS-JD-BE3 345 Z
00ALL | ERIS | Thermal | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | 29WP | T1 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 637 | 74.8941 | 138.2005 |  |  |  | Add 3-winding transformer 659336 TANDE___-BE3 345 659337 TANDE___-BE4 230 659338 TND.KU3A-BE9 13 M2
00ALL | ERIS | Thermal | 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1 | 29WP | T2 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 637 | 41.2992 | 111.713 |  |  |  | Rebuild line 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1
00ALL | ERIS | Thermal | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z | 29WP | T2 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 509 | 35.993 | 113.8469 |  |  |  | Rebuild line 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z
00ALL | ERIS | Voltage | FINNEY 7 | 26SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 1.0633 | 0.9 | 1.05 | Add 23 MVAR switched shunt at FINNEY 7 345 kV
00ALL | ERIS | Voltage | G17-140-BUS | 26SP | V | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: |  |  |  |  | 1.2288 | 0.92 | 1.05 | Mitigated at another bus
00ALL | ERIS | Voltage | G23-015-TAP | 26SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 1.0619 | 0.9 | 1.05 | Mitigated at another bus
00ALL | ERIS | Voltage | GEN-2017-140 | 26SP | V | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: |  |  |  |  | 1.2288 | 0.92 | 1.05 | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
00ALL | ERIS | Voltage | GEN-2023-015 | 26SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 1.0619 | 0.9 | 1.05 | Mitigated at another bus
00ALL | ERIS | Voltage | MALTABN5 | 26SP | V | Single 543059 MALTABN5 161 543064 NORTON5 161 1 |  |  |  |  | 0.89774 | 0.93 | 1.05 | Mitigated at another bus
00ALL | ERIS | Voltage | SWAVCAP5 | 26SP | V | Single 543059 MALTABN5 161 543064 NORTON5 161 1 |  |  |  |  | 0.89836 | 0.93 | 1.05 | Mitigated at another bus
00ALL | ERIS | Voltage | SWAVRLY5 | 26SP | V | Single 543059 MALTABN5 161 543064 NORTON5 161 1 |  |  |  |  | 0.89817 | 0.93 | 1.05 | Add 7 MVAR switched shunt at SWAVRLY5 161 kV
00ALL | ERIS | Voltage | G17-140-BUS | 29SP | V | P22:345:EES:MUSKOGE7!:::EHV: |  |  |  |  | 1.2099 | 0.92 | 1.05 | Mitigated at another bus
00ALL | ERIS | Voltage | GEN-2017-140 | 29SP | V | P22:345:EES:MUSKOGE7!:::EHV: |  |  |  |  | 1.2099 | 0.92 | 1.05 | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
00ALL | ERIS | Voltage | GEN-2017-214 | 29SP | V | P13:230-115.0:UMZ:# N-1 #:: 3WND LOGAN___-BE4-LOGAN___-BE7-LGN.KW1A-BE9-1 KW1A:HV: |  |  |  |  | 1.0522 | 0.9 | 1.05 | Add 0.02 MVAR switched shunt at GEN-2017-214 230 kV
00ALL | ERIS | Voltage | MALTABN5 | 29SP | V | Single 543059 MALTABN5 161 543064 NORTON5 161 1 |  |  |  |  | 0.90596 | 0.93 | 1.05 | Mitigated at another bus
00ALL | ERIS | Voltage | NP-GLAZIR_G2 | 29SP | V | P42:345:SPS:CARPENTER-OR335:::EHV: |  |  |  |  | 0.66129 | 0.9 | 1.05 | Mitigated at another bus
00ALL | ERIS | Voltage | NP-LIPSCOMB2 | 29SP | V | P42:345:SPS:CARPENTER-OR335:::EHV: |  |  |  |  | 0.61984 | 0.9 | 1.05 | Mitigated at another bus
00ALL | ERIS | Voltage | NP-LIPS_SHA2 | 29SP | V | P42:345:SPS:CARPENTER-OR335:::EHV: |  |  |  |  | 0.61984 | 0.9 | 1.05 | Mitigated at another bus
00ALL | ERIS | Voltage | NP-LUCKY_CR2 | 29SP | V | P42:345:SPS:CARPENTER-OR335:::EHV: |  |  |  |  | 0.75863 | 0.9 | 1.05 | Mitigated at another bus
00ALL | ERIS | Voltage | NP-LUCKY_G 2 | 29SP | V | P42:345:SPS:CARPENTER-OR335:::EHV: |  |  |  |  | 0.75879 | 0.9 | 1.05 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
00ALL | ERIS | Voltage | NP-SHATTUCK2 | 29SP | V | P42:345:SPS:CARPENTER-OR335:::EHV: |  |  |  |  | 0.59682 | 0.9 | 1.05 | Mitigated at another bus
00ALL | ERIS | Voltage | NP-SUB_A 2 | 29SP | V | P42:345:SPS:CARPENTER-OR335:::EHV: |  |  |  |  | 0.83009 | 0.9 | 1.05 | Mitigated at another bus
00ALL | ERIS | Voltage | NP-VALERO_P2 | 29SP | V | P42:345:SPS:CARPENTER-OR335:::EHV: |  |  |  |  | 0.62853 | 0.9 | 1.05 | Mitigated at another bus
00ALL | ERIS | Voltage | RB-NMO1_SW 2 | 29SP | V | P12:345:OKGE:BKRBKR3360:::EHV: |  |  |  |  | 0.89929 | 0.9 | 1.05 | None
00ALL | ERIS | Voltage | RB-TEXLINE 2 | 29SP | V | P12:345:OKGE:BKRBKR3360:::EHV: |  |  |  |  | 0.89929 | 0.9 | 1.05 | None
00ALL | ERIS | Voltage | SWAVCAP5 | 29SP | V | Single 543059 MALTABN5 161 543064 NORTON5 161 1 |  |  |  |  | 0.90657 | 0.93 | 1.05 | Mitigated at another bus
00ALL | ERIS | Voltage | SWAVRLY5 | 29SP | V | Single 543059 MALTABN5 161 543064 NORTON5 161 1 |  |  |  |  | 0.90638 | 0.93 | 1.05 | Add 7 MVAR switched shunt at SWAVRLY5 161 kV
00ALL | ERIS | Voltage | BELFELD3 | 29WP | V | 259690 |  |  |  |  | 1.0511 | 0.9 | 1.05 | None
00ALL | ERIS | Voltage | FINNEY 7 | 29WP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 1.0985 | 0.9 | 1.05 | Add 23 MVAR switched shunt at FINNEY 7 345 kV
00ALL | ERIS | Voltage | G23-015-TAP | 29WP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 1.0953 | 0.9 | 1.05 | Mitigated at another bus
00ALL | ERIS | Voltage | GEN-2017-214 | 29WP | V | P13:230-115.0:UMZ:# N-1 #:: 3WND LOGAN___-BE4-LOGAN___-BE7-LGN.KW1A-BE9-1 KW1A:HV: |  |  |  |  | 1.0513 | 0.9 | 1.05 | Add 0.02 MVAR switched shunt at GEN-2017-214 230 kV
00ALL | ERIS | Voltage | GEN-2023-015 | 29WP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 1.0953 | 0.9 | 1.05 | Mitigated at another bus
00ALL | ERIS | Voltage | MAURINE4 | 29WP | V | 259690 |  |  |  |  | 1.0618 | 0.9 | 1.05 | None
00ALL | ERIS | Voltage | RUSHMORE-RM8 | 29WP | V | 259690 |  |  |  |  | 1.0504 | 0.9 | 1.05 | Add 0.02 MVAR switched shunt at RUSHMORE-RM8 69 kV
00NR | NRIS | Thermal | 505488 CARTHAG5 161 3WXFMR 300:CRG X1 161 1 | 26SP | T0 | Single 505490 CARTHG2 69 505488 CARTHAG5 161 505489 'CRG X2 1 ' 13 1 | B | 84 | 105.1209 | 102.3328 |  |  |  | Carthage_Add_transformer_fixed.idv :
00NR | NRIS | Thermal | 505488 CARTHAG5 161 3WXFMR 537:CRG X2 161 1 | 26SP | T0 | Single 505490 CARTHG2 69 505488 CARTHAG5 161 505487 'CRG X1 1 ' 13 1 | B | 84 | 104.5027 | 101.7304 |  |  |  | Carthage_Add_transformer_fixed.idv :
00NR | NRIS | Thermal | 509817 T.NO.--4 138 509900 46ST-TP-4 138 1 | 26SP | T0 | Single 509784 A.A.---4 138 786510 G24-318-TAP 138 1 | B | 151 | 91.4427 | 113.7874 |  |  |  | 520_T.NO.4-46ST-TP-PPTAP_rebuild.idv : 2023 ITP, PID: 93019, NTC, ISD: 1/21/2027
00NR | NRIS | Thermal | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 26SP | T0 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | B | 106 | 85.6147 | 133.612 |  |  |  | Rebuild line 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1
00NR | NRIS | Thermal | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 26SP | T0 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | B | 171 | 75.2264 | 113.9786 |  |  |  | Rebuild line 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1
00NR | NRIS | Thermal | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 26SP | T0 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | B | 106 | 78.6229 | 126.6716 |  |  |  | Line - Duncan - Duncan Tap - Duncan Eastside - Rush Springs Tap - Marlow 138 kV Rebuild.idv : 2025 ITP, PID: 900298, NTC, ISD: Unknown
00NR | NRIS | Thermal | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 26SP | T0 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | B | 106 | 69.3354 | 117.3847 |  |  |  | Line - Duncan - Duncan Tap - Duncan Eastside - Rush Springs Tap - Marlow 138 kV Rebuild.idv : 2025 ITP, PID: 900298, NTC, ISD: Unknown
00NR | NRIS | Thermal | 511467 L.E.S.-4 138 3WXFMR 520:LES 5 345 2 | 26SP | T0 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | B | 515 | 56.8963 | 117.1585 |  |  |  | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2
00NR | NRIS | Thermal | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 26SP | T0 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | B | 173 | 52.056 | 104.979 |  |  |  | Rebuild line 511467 L.E.S.-4 138 511494 COMMTAP4 138 1
00NR | NRIS | Thermal | 511468 L.E.S.-7 345 3WXFMR 520:LES 5 345 2 | 26SP | T0 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | B | 515 | 57.8158 | 116.8526 |  |  |  | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2
00NR | NRIS | Thermal | 511468 L.E.S.-7 345 764550 G20-087-TAP 345 1 | 26SP | T0 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | B | 1176 | 57.3041 | 115.0941 |  |  |  | Rebuild line 511468 L.E.S.-7 345 764550 G20-087-TAP 345 1
00NR | NRIS | Thermal | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 26SP | T0 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | B | 171 | 75.3956 | 114.1433 |  |  |  | Rebuild line 511494 COMMTAP4 138 529304 OMDUNCN4 138 1
00NR | NRIS | Thermal | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | 26SP | T0 | Single 514894 CZECHAL4 138 514898 CIMARON4 138 1 | B | 308 | 82.7937 | 104.2764 |  |  |  | Rebuild line 514863 HAYMAKR4 138 514898 CIMARON4 138 1
00NR | NRIS | Thermal | 514887 WESTMOR4 138 514925 PENN 4 138 1 | 26SP | T0 | Single 514953 HOLLYWD4 138 514954 INDNHIL4 138 1 | B | 287 | 90.5388 | 105.2997 |  |  |  | 524_SW134TP4-WESTMOR4_extendLine.idv : 2023 ITP, PID: 92996, NTC, ISD: 12/15/2025 (marked as in service)
00NR | NRIS | Thermal | 514893 XEROX 4 138 514894 CZECHAL4 138 1 | 26SP | T0 | P12:138:OKGE:BKRBKR1250:::HV: | B | 382 | 67.0497 | 103.4879 |  |  |  | Rebuild line 514893 XEROX 4 138 514894 CZECHAL4 138 1
00NR | NRIS | Thermal | 514898 CIMARON4 138 3WXFMR 524:524:CIMARON2 345 2 | 26SP | T0 | P13:138:OKGE:BKRBKR_3W020:::HV: | B | 478 | 73.8301 | 102.3793 |  |  |  | Add 3-winding transformer 514898 CIMARON4 138 514901 CIMARON7 345 515715 CIMARO21 13 M2
00NR | NRIS | Thermal | 514901 CIMARON7 345 3WXFMR 524:524:CIMARON2 345 2 | 26SP | T0 | P13:138:OKGE:BKRBKR_3W020:::HV: | B | 478 | 76.3697 | 105.6405 |  |  |  | Add 3-winding transformer 514898 CIMARON4 138 514901 CIMARON7 345 515715 CIMARO21 13 M2
00NR | NRIS | Thermal | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 26SP | T0 | P42:345:OKGE:SB_GRNT7381:::EHV: | B | 234 | 37.7059 | 110.8778 |  |  |  | Rebuild line 515802 GRACMNT4 138 520814 ANADARK4 138 1
00NR | NRIS | Thermal | 516092 OKTAHA 5 161 3WXFMR OKTAHA 5 69 7 | 26SP | T0 | P22:345:EES:MUSKOGE7!:::EHV: | B | 112 | 79.6987 | 147.7196 |  |  |  | Rebuild 3-winding transformer 516092 OKTAHA 5 161 516093 OKTAHA 2 69 516095 OKTAHA71 13 7
00NR | NRIS | Thermal | 516093 OKTAHA 2 69 3WXFMR OKTAHA 5 69 7 | 26SP | T0 | P22:345:EES:MUSKOGE7!:::EHV: | B | 112 | 78.5594 | 146.2088 |  |  |  | Rebuild 3-winding transformer 516092 OKTAHA 5 161 516093 OKTAHA 2 69 516095 OKTAHA71 13 7
00NR | NRIS | Thermal | 528618 LE-LOVINTON2 69 528334 LE-NRTH_INT3 115 1 | 26SP | T0 | Single 527864 CUNNINHAM3 115 528348 BUCKEYE_TP3 115 1 | B | 100 | 69.0442 | 109.6229 |  |  |  | Rebuild 2-winding transformer 528334 LE-NRTH_INT3 115 528618 LE-LOVINTON2 69 1
00NR | NRIS | Thermal | 530565 SEWARD 2 69 3WXFMR 531:SEWARD T1 69 1 | 26SP | T0 | Single 539666 GBENDTP3 115 539692 SEWARD3 115 1 | B | 44.79 | -32.883 | 105.8778 |  |  |  | Rebuild 3-winding transformer 530565 SEWARD 2 69 530631 SWRD1 1 12 530679 SEWRDMW3 115 1
00NR | NRIS | Thermal | 530679 SEWRDMW3 115 3WXFMR 531:SEWARD T1 69 1 | 26SP | T0 | Single 539666 GBENDTP3 115 539692 SEWARD3 115 1 | B | 44.79 | -33.4128 | 105.8778 |  |  |  | Rebuild 3-winding transformer 530565 SEWARD 2 69 530631 SWRD1 1 12 530679 SEWRDMW3 115 1
00NR | NRIS | Thermal | 530679 SEWRDMW3 115 539692 SEWARD 3 115 1 | 26SP | T0 | Single 539666 GBENDTP3 115 539692 SEWARD3 115 1 | B | 40 | -37.7753 | 115.3002 |  |  |  | Rebuild line 530679 SEWRDMW3 115 539692 SEWARD 3 115 1
00NR | NRIS | Thermal | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | 26SP | T0 | P23:345:SUNC:HLC_BRK188:::EHV: | B | 165.1 | 21.982 | 111.0123 |  |  |  | Rebuild line 531405 WALKMYR3 115 539654 CIM-PLT3 115 1
00NR | NRIS | Thermal | 532777 NRSS7 345 532793 NEOSHO 7 345 1 | 26SP | T0 | P12:345:WERE:LATH-ROSE-345:EHV: | B | 1159 | 11.7171 | 115.6655 |  |  |  | Rebuild line 532777 NRSS7 345 532793 NEOSHO 7 345 1
00NR | NRIS | Thermal | 532777 NRSS7 345 780840 G24-129-TAP 345 1 | 26SP | T0 | P12:345:WERE:LATH-ROSE-345:EHV: | B | 1159 | 7.7023 | 111.3269 |  |  |  | Rebuild line 532777 NRSS7 345 780840 G24-129-TAP 345 1
00NR | NRIS | Thermal | 532780 CANEYRV7 345 780720 G24-125-TAP 345 1 | 26SP | T0 | P23:345:WERE:N345-345-20:EHV: | B | 1159 | 8.7071 | 119.3033 |  |  |  | Rebuild line 532780 CANEYRV7 345 780720 G24-125-TAP 345 1
00NR | NRIS | Thermal | 532793 NEOSHO 7 345 3WXFMR 536:N345 TX-2 161 2 | 26SP | T0 | Single 533021 NEOSHO4 138 533023 N34534 138 1 | B | 550 | 71.8268 | 111.3295 |  |  |  | Add 3-winding transformer 532793 NEOSHO 7 345 532825 N345 2 1 13 532939 N345 4 5 161 M2
00NR | NRIS | Thermal | 532937 NEOSHO 5 161 3WXFMR 536:NEOSHO TX-5 138 1 | 26SP | T0 | Single 532793 NEOSHO7 345 532939 N34545 161 532825 'N345 2 1 ' 13 2 | B | 165 | 47.8607 | 125.6401 |  |  |  | Add 3-winding transformer 532937 NEOSHO 5 161 532959 NEOSH5 1 13 533020 NEOSHOS4 138 M2
00NR | NRIS | Thermal | 532937 NEOSHO 5 161 532939 N345 4 5 161 1 | 26SP | T0 | Single 533021 NEOSHO4 138 533023 N34534 138 1 | B | 557 | 69.6476 | 106.5051 |  |  |  | Rebuild line 532937 NEOSHO 5 161 532939 N345 4 5 161 1
00NR | NRIS | Thermal | 532939 N345 4 5 161 3WXFMR 536:N345 TX-2 161 2 | 26SP | T0 | Single 533021 NEOSHO4 138 533023 N34534 138 1 | B | 550 | 71.8269 | 111.179 |  |  |  | Add 3-winding transformer 532793 NEOSHO 7 345 532825 N345 2 1 13 532939 N345 4 5 161 M2
00NR | NRIS | Thermal | 533020 NEOSHOS4 138 3WXFMR 536:NEOSHO TX-5 138 1 | 26SP | T0 | Single 532793 NEOSHO7 345 532939 N34545 161 532825 'N345 2 1 ' 13 2 | B | 165 | 47.8607 | 124.7681 |  |  |  | Add 3-winding transformer 532937 NEOSHO 5 161 532959 NEOSH5 1 13 533020 NEOSHOS4 138 M2
00NR | NRIS | Thermal | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 26SP | T0 | P12:115:SUNC:SAINTJOHN-SAINTJOHN(MIDWEST):::HV: | B | 101 | -6.8225 | 110.8057 |  |  |  | Rebuild line 539692 SEWARD 3 115 539696 ST-JOHN3 115 1
00NR | NRIS | Thermal | 640080 BELDEN 7 115 640212 HARTGTN7 115 1 | 26SP | T0 | P12:230.0:UMZ:# N-1 #:: LINE TWIN CH4-SIOUXCY4-1 :HV: | B | 123 | 33.2574 | 102.727 |  |  |  | Rebuild line 640080 BELDEN 7 115 640212 HARTGTN7 115 1
00NR | NRIS | Thermal | 640149 CREITON7 115 640521 ANTELOPE 7 115 1 | 26SP | T0 | P42:345:NPPD:BKR-HOS-3308:::: | B | 143 | 65.736 | 103.6591 |  |  |  | Rebuild line 640149 CREITON7 115 640521 ANTELOPE 7 115 1
00NR | NRIS | Thermal | 640227 HOSKINS4 230 3WXFMR 640:HOSKINS T1 230 1 | 26SP | T0 | P13:115-345:NPPD:HOSKINS3:T4::: | B | 187 | 91.9094 | 103.3209 |  |  |  | Add 3-winding transformer 640227 HOSKINS4 230 640228 HOSKINS7 115 643083 HOSKINS T1 9 13 M2
00NR | NRIS | Thermal | 640228 HOSKINS7 115 3WXFMR 640:HOSKINS T1 230 1 | 26SP | T0 | P13:115-345:NPPD:HOSKINS3:T4::: | B | 187 | 91.2321 | 101.793 |  |  |  | Add 3-winding transformer 640227 HOSKINS4 230 640228 HOSKINS7 115 643083 HOSKINS T1 9 13 M2
00NR | NRIS | Thermal | 640338 SCOTBLF 7 115 653313 GERING TAP 115 1 | 26SP | T0 | P12:230.0:UMZ:# N-1 #:: LINE WAYSIDE 4-STEGALL-LNX3-1 :HV: | B | 109 | 83.5739 | 113.076 |  |  |  | 640_NPPD_Rebuild_Scotsbluff_Gering_115.idv : 2024 ITP, PID: 94819, NTC, ISD: Unknown
00NR | NRIS | Thermal | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | 26SP | T0 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | B | 116 | 62.6447 | 132.0705 |  |  |  | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
00NR | NRIS | Thermal | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | 26SP | T0 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | B | 120 | 62.175 | 130.4818 |  |  |  | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
00NR | NRIS | Thermal | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | 26SP | T0 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | B | 120 | 62.175 | 130.4818 |  |  |  | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
00NR | NRIS | Thermal | 652512 GROTON 7 115 660001 ABR SIEBRCHT 115 1 | 26SP | T0 | P12:230:MDU:ELLENDALE:ELLENDALE345:Z: | B | 180.3 | 115.0474 | 133.41 |  |  |  | Rebuild line 652512 GROTON 7 115 660001 ABR SIEBRCHT 115 1
00NR | NRIS | Thermal | 653312 MORRILL 7 115 653313 GERING TAP 115 1 | 26SP | T0 | P12:230.0:UMZ:# N-1 #:: LINE WAYSIDE 4-STEGALL-LNX3-1 :HV: | B | 109 | 83.3722 | 113.0139 |  |  |  | 640_NPPD_Rebuild_Morill_Gering_115.idv : 2024 ITP, PID: TBD, ISD: Unknown
00NR | NRIS | Thermal | 653312 MORRILL 7 115 659814 SNAKECK-TS7 115 1 | 26SP | T0 | P12:230.0:UMZ:# N-1 #:: LINE WAYSIDE 4-STEGALL-LNX3-1 :HV: | B | 109 | 76.5513 | 105.6302 |  |  |  | 640_NPPD_Rebuild_Morill_Gering_115.idv : 2024 ITP, PID: TBD, ISD: Unknown
00NR | NRIS | Thermal | 653570 ALIANCE 7 115 659814 SNAKECK-TS7 115 1 | 26SP | T0 | P12:230.0:UMZ:# N-1 #:: LINE WAYSIDE 4-STEGALL-LNX3-1 :HV: | B | 109 | 71.3208 | 109.5519 |  |  |  | 640_NPPD_Rebuild_Morill_Gering_115.idv : 2024 ITP, PID: TBD, ISD: Unknown
00NR | NRIS | Thermal | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 26SP | T1 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | B | 211 | 68.5078 | 106.2632 |  |  |  | Rebuild line 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1
00NR | NRIS | Thermal | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 26SP | T1 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | B | 211 | 68.5594 | 106.2948 |  |  |  | Rebuild line 511494 COMMTAP4 138 529304 OMDUNCN4 138 1
00NR | NRIS | Thermal | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 26SP | T1 | Single 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | B | 444 | 77.6573 | 106.9994 |  |  |  | Rebuild line 514894 CZECHAL4 138 514898 CIMARON4 138 1
00NR | NRIS | Thermal | 653312 MORRILL 7 115 659814 SNAKECK-TS7 115 1 | 26SP | T1 | P12:230.0:UMZ:# N-1 #:: LINE WAYSIDE 4-STEGALL-LNX3-1 :HV: | B | 109 | 84.5124 | 118.1767 |  |  |  | Rebuild line 653312 MORRILL 7 115 659814 SNAKECK-TS7 115 1
00NR | NRIS | Thermal | 653570 ALIANCE 7 115 659814 SNAKECK-TS7 115 1 | 26SP | T1 | P12:230.0:UMZ:# N-1 #:: LINE WAYSIDE 4-STEGALL-LNX3-1 :HV: | B | 109 | 76.3485 | 117.1431 |  |  |  | Rebuild line 653570 ALIANCE 7 115 659814 SNAKECK-TS7 115 1
00NR | NRIS | Thermal | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | 29SP | T0 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | B | 829 | 72.8624 | 103.7671 |  |  |  | Rebuild line 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1
00NR | NRIS | Thermal | 505488 CARTHAG5 161 3WXFMR 300:CRG X1 161 1 | 29SP | T0 | Single 505490 CARTHG2 69 505488 CARTHAG5 161 505489 'CRG X2 1 ' 13 1 | B | 84 | 109.8355 | 108.6433 |  |  |  | Carthage_Add_transformer_fixed.idv :
00NR | NRIS | Thermal | 505488 CARTHAG5 161 3WXFMR 537:CRG X2 161 1 | 29SP | T0 | Single 505490 CARTHG2 69 505488 CARTHAG5 161 505487 'CRG X1 1 ' 13 1 | B | 84 | 109.1884 | 108.0024 |  |  |  | Carthage_Add_transformer_fixed.idv :
00NR | NRIS | Thermal | 505490 CARTHG 2 69 3WXFMR 300:CRG X1 161 1 | 29SP | T0 | Single 505490 CARTHG2 69 505488 CARTHAG5 161 505489 'CRG X2 1 ' 13 1 | B | 84 | 105.5528 | 103.8455 |  |  |  | Carthage_Add_transformer_fixed.idv :
00NR | NRIS | Thermal | 505490 CARTHG 2 69 3WXFMR 537:CRG X2 161 1 | 29SP | T0 | Single 505490 CARTHG2 69 505488 CARTHAG5 161 505487 'CRG X1 1 ' 13 1 | B | 84 | 104.8574 | 103.1531 |  |  |  | Carthage_Add_transformer_fixed.idv :
00NR | NRIS | Thermal | 509690 4PINELND 138 509691 4BROADUS 138 1 | 29SP | T0 | P23:345:EES::7ROCKYCRK%:1:EHV: | B | 135 | 67.728 | 101.13 |  |  |  | Rebuild line 509690 4PINELND 138 509691 4BROADUS 138 1
00NR | NRIS | Thermal | 509691 4BROADUS 138 509692 4ETOIL 138 1 | 29SP | T0 | P23:345:EES::7ROCKYCRK%:1:EHV: | B | 135 | 72.551 | 105.9999 |  |  |  | Rebuild line 509691 4BROADUS 138 509692 4ETOIL 138 1
00NR | NRIS | Thermal | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 29SP | T0 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | B | 106 | 88.2534 | 132.2092 |  |  |  | Rebuild line 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1
00NR | NRIS | Thermal | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 29SP | T0 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | B | 171 | 76.4805 | 111.9445 |  |  |  | Rebuild line 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1
00NR | NRIS | Thermal | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 29SP | T0 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | B | 106 | 81.1803 | 125.1801 |  |  |  | Line - Duncan - Duncan Tap - Duncan Eastside - Rush Springs Tap - Marlow 138 kV Rebuild.idv : 2025 ITP, PID: 900298, NTC, ISD: Unknown
00NR | NRIS | Thermal | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 29SP | T0 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | B | 106 | 72.0235 | 116.0225 |  |  |  | Line - Duncan - Duncan Tap - Duncan Eastside - Rush Springs Tap - Marlow 138 kV Rebuild.idv : 2025 ITP, PID: 900298, NTC, ISD: Unknown
00NR | NRIS | Thermal | 511467 L.E.S.-4 138 3WXFMR 520:LES 5 345 2 | 29SP | T0 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | B | 515 | 57.4274 | 115.4941 |  |  |  | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2
00NR | NRIS | Thermal | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | 29SP | T0 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | B | 173 | 50.2827 | 102.1634 |  |  |  | Rebuild line 511467 L.E.S.-4 138 511494 COMMTAP4 138 1
00NR | NRIS | Thermal | 511468 L.E.S.-7 345 3WXFMR 520:LES 5 345 2 | 29SP | T0 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | B | 515 | 58.3688 | 115.3782 |  |  |  | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2
00NR | NRIS | Thermal | 511468 L.E.S.-7 345 764550 G20-087-TAP 345 1 | 29SP | T0 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | B | 1176 | 57.3117 | 114.9872 |  |  |  | Rebuild line 511468 L.E.S.-7 345 764550 G20-087-TAP 345 1
00NR | NRIS | Thermal | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 29SP | T0 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | B | 171 | 76.6419 | 112.1038 |  |  |  | Rebuild line 511494 COMMTAP4 138 529304 OMDUNCN4 138 1
00NR | NRIS | Thermal | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | 29SP | T0 | Single 514894 CZECHAL4 138 514898 CIMARON4 138 1 | B | 308 | 84.0064 | 102.1233 |  |  |  | Rebuild line 514863 HAYMAKR4 138 514898 CIMARON4 138 1
00NR | NRIS | Thermal | 514901 CIMARON7 345 3WXFMR 524:524:CIMARON2 345 2 | 29SP | T0 | P13:138:OKGE:BKRBKR_3W020:::HV: | B | 478 | 76.3307 | 101.8584 |  |  |  | Add 3-winding transformer 514898 CIMARON4 138 514901 CIMARON7 345 515715 CIMARO21 13 M2
00NR | NRIS | Thermal | 515227 5TRIBES2 69 516093 OKTAHA 2 69 1 | 29SP | T0 | P22:345:EES:MUSKOGE7!:::EHV: | B | 111 | 61.8451 | 107.0862 |  |  |  | Rebuild line 515227 5TRIBES2 69 516093 OKTAHA 2 69 1
00NR | NRIS | Thermal | 516092 OKTAHA 5 161 3WXFMR OKTAHA 5 69 7 | 29SP | T0 | P22:345:EES:MUSKOGE7!:::EHV: | B | 112 | 105.868 | 165.8816 |  |  |  | Rebuild 3-winding transformer 516092 OKTAHA 5 161 516093 OKTAHA 2 69 516095 OKTAHA71 13 7
00NR | NRIS | Thermal | 516093 OKTAHA 2 69 3WXFMR OKTAHA 5 69 7 | 29SP | T0 | P22:345:EES:MUSKOGE7!:::EHV: | B | 112 | 104.0941 | 163.0673 |  |  |  | Rebuild 3-winding transformer 516092 OKTAHA 5 161 516093 OKTAHA 2 69 516095 OKTAHA71 13 7
00NR | NRIS | Thermal | 530565 SEWARD 2 69 3WXFMR 531:SEWARD T1 69 1 | 29SP | T0 | Single 539666 GBENDTP3 115 539692 SEWARD3 115 1 | B | 44.79 | -21.0827 | 117.8065 |  |  |  | Rebuild 3-winding transformer 530565 SEWARD 2 69 530631 SWRD1 1 12 530679 SEWRDMW3 115 1
00NR | NRIS | Thermal | 530679 SEWRDMW3 115 3WXFMR 531:SEWARD T1 69 1 | 29SP | T0 | Single 539666 GBENDTP3 115 539692 SEWARD3 115 1 | B | 44.79 | -21.296 | 117.8065 |  |  |  | Rebuild 3-winding transformer 530565 SEWARD 2 69 530631 SWRD1 1 12 530679 SEWRDMW3 115 1
00NR | NRIS | Thermal | 530679 SEWRDMW3 115 539692 SEWARD 3 115 1 | 29SP | T0 | Single 539666 GBENDTP3 115 539692 SEWARD3 115 1 | B | 40 | -24.204 | 128.1998 |  |  |  | Rebuild line 530679 SEWRDMW3 115 539692 SEWARD 3 115 1
00NR | NRIS | Thermal | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | 29SP | T0 | P23:345:SUNC:HLC_BRK188:::EHV: | B | 165.1 | 30.7069 | 118.9406 |  |  |  | Rebuild line 531405 WALKMYR3 115 539654 CIM-PLT3 115 1
00NR | NRIS | Thermal | 531481 HUGOTON3 115 531483 GRANTTP3 115 1 | 29SP | T0 | P23:345:SUNC:HLC_BRK188:::EHV: | B | 230.3 | 13.7221 | 100.7245 |  |  |  | Rebuild line 531481 HUGOTON3 115 531483 GRANTTP3 115 1
00NR | NRIS | Thermal | 532777 NRSS7 345 532793 NEOSHO 7 345 1 | 29SP | T0 | P12:345:WERE:LATH-ROSE-345:EHV: | B | 1159 | 11.7273 | 115.8195 |  |  |  | Rebuild line 532777 NRSS7 345 532793 NEOSHO 7 345 1
00NR | NRIS | Thermal | 532777 NRSS7 345 780840 G24-129-TAP 345 1 | 29SP | T0 | P12:345:WERE:LATH-ROSE-345:EHV: | B | 1159 | 7.6736 | 111.4772 |  |  |  | Rebuild line 532777 NRSS7 345 780840 G24-129-TAP 345 1
00NR | NRIS | Thermal | 532780 CANEYRV7 345 780720 G24-125-TAP 345 1 | 29SP | T0 | P23:345:WERE:N345-345-20:EHV: | B | 1159 | 8.7635 | 118.4554 |  |  |  | Rebuild line 532780 CANEYRV7 345 780720 G24-125-TAP 345 1
00NR | NRIS | Thermal | 532793 NEOSHO 7 345 3WXFMR 536:N345 TX-2 161 2 | 29SP | T0 | Single 533021 NEOSHO4 138 533023 N34534 138 1 | B | 550 | 64.8506 | 103.5308 |  |  |  | Add 3-winding transformer 532793 NEOSHO 7 345 532825 N345 2 1 13 532939 N345 4 5 161 M2
00NR | NRIS | Thermal | 532937 NEOSHO 5 161 3WXFMR 536:NEOSHO TX-5 138 1 | 29SP | T0 | Single 532793 NEOSHO7 345 532939 N34545 161 532825 'N345 2 1 ' 13 2 | B | 165 | 43.6087 | 114.2181 |  |  |  | Add 3-winding transformer 532937 NEOSHO 5 161 532959 NEOSH5 1 13 533020 NEOSHOS4 138 M2
00NR | NRIS | Thermal | 532939 N345 4 5 161 3WXFMR 536:N345 TX-2 161 2 | 29SP | T0 | Single 533021 NEOSHO4 138 533023 N34534 138 1 | B | 550 | 64.8507 | 103.5308 |  |  |  | Add 3-winding transformer 532793 NEOSHO 7 345 532825 N345 2 1 13 532939 N345 4 5 161 M2
00NR | NRIS | Thermal | 533020 NEOSHOS4 138 3WXFMR 536:NEOSHO TX-5 138 1 | 29SP | T0 | Single 532793 NEOSHO7 345 532939 N34545 161 532825 'N345 2 1 ' 13 2 | B | 165 | 43.6087 | 113.4225 |  |  |  | Add 3-winding transformer 532937 NEOSHO 5 161 532959 NEOSH5 1 13 533020 NEOSHOS4 138 M2
00NR | NRIS | Thermal | 539656 CLIFTON3 115 539657 CONCORD3 115 1 | 29SP | T0 | Single 539805 ELMCREEK7 345 640600 DAYKIN3 345 1 | B | 113.9 | 36.6387 | 102.7717 |  |  |  | Rebuild line 539656 CLIFTON3 115 539657 CONCORD3 115 1
00NR | NRIS | Thermal | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | 29SP | T0 | P12:115:SUNC:SAINTJOHN-SAINTJOHN(MIDWEST):::HV: | B | 101 | 4.5269 | 121.4881 |  |  |  | Rebuild line 539692 SEWARD 3 115 539696 ST-JOHN3 115 1
00NR | NRIS | Thermal | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | 29SP | T0 | P23:345:MEC:OBRIEN:906::EHV: | B | 981 | 57.0325 | 104.0624 |  |  |  | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
00NR | NRIS | Thermal | 640080 BELDEN 7 115 640212 HARTGTN7 115 1 | 29SP | T0 | Single 640149 CREITON7 115 640521 ANTELOPE7 115 1 | B | 123 | 44.3496 | 129.7178 |  |  |  | Rebuild line 640080 BELDEN 7 115 640212 HARTGTN7 115 1
00NR | NRIS | Thermal | 640125 COLMB.E3 345 3WXFMR 640:COL.EAST T4 345 1 | 29SP | T0 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | B | 336 | 31.674 | 111.4413 |  |  |  | Add 3-winding transformer 640125 COLMB.E3 345 640127 COLMB.E7 115 640129 COLMB.T9 13 M2
00NR | NRIS | Thermal | 640127 COLMB.E7 115 3WXFMR 640:COL.EAST T4 345 1 | 29SP | T0 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | B | 336 | 31.4781 | 111.4413 |  |  |  | Add 3-winding transformer 640125 COLMB.E3 345 640127 COLMB.E7 115 640129 COLMB.T9 13 M2
00NR | NRIS | Thermal | 640149 CREITON7 115 640521 ANTELOPE 7 115 1 | 29SP | T0 | P42:345:NPPD:BKR-HOS-3308:::: | B | 143 | 71.8733 | 114.0717 |  |  |  | Rebuild line 640149 CREITON7 115 640521 ANTELOPE 7 115 1
00NR | NRIS | Thermal | 640178 GENEVA 7 115 640272 MCCOOL 7 115 1 | 29SP | T0 | P42:345:NPPD:L3502A.MOORE.MCCOOL.CB3310:::: | B | 160 | -13.879 | 112.3173 |  |  |  | Rebuild line 640178 GENEVA 7 115 640272 MCCOOL 7 115 1
00NR | NRIS | Thermal | 640272 MCCOOL 7 115 640413 YORK SW7 115 1 | 29SP | T0 | P23:345:UMZW:# 2427 #:: GI IN NE. GI 1392 BKR FAULT:EHV: | B | 160 | 50.031 | 108.3007 |  |  |  | Rebuild line 640272 MCCOOL 7 115 640413 YORK SW7 115 1
00NR | NRIS | Thermal | 645454 S3454 3 345 650185 WAGENER 3 345 1 | 29SP | T0 | P55:345:OPPD:S3458 3::FN13:EHV: | B | 982 | 69.1087 | 124.4523 |  |  |  | Rebuild line 645454 S3454 3 345 650185 WAGENER 3 345 1
00NR | NRIS | Thermal | 645456 S3456 3 345 645458 S3458 3 345 1 | 29SP | T0 | P55:345:OPPD:S3740 3::FN13:EHV: | B | 982 | 85.3554 | 109.8564 |  |  |  | Rebuild line 645456 S3456 3 345 645458 S3458 3 345 1
00NR | NRIS | Thermal | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | 29SP | T0 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | B | 116 | 91.5151 | 163.2816 |  |  |  | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
00NR | NRIS | Thermal | 646221 S1221 5 161 646255 S1255 5 161 1 | 29SP | T0 | P23:345:OPPD:FUTURE 56-55&56-58:::EHV: | B | 352 | 83.122 | 105.1616 |  |  |  | Rebuild line 646221 S1221 5 161 646255 S1255 5 161 1
00NR | NRIS | Thermal | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | 29SP | T0 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | B | 120 | 90.3484 | 159.9633 |  |  |  | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
00NR | NRIS | Thermal | 650185 WAGENER 3 345 650189 103&ROKEBY3 345 1 | 29SP | T0 | P42:345:NPPD:L3502A.MOORE.MCCOOL.CB3310:::: | B | 1158 | 51.4072 | 105.9892 |  |  |  | Rebuild line 650185 WAGENER 3 345 650189 103&ROKEBY3 345 1
00NR | NRIS | Thermal | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | 29SP | T0 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | B | 120 | 90.3484 | 159.9633 |  |  |  | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
00NR | NRIS | Thermal | 652425 BELFELD4 230 659124 DICKINSN-BE4 230 1 | 29SP | T0 | P12:230.0:UMZ:# N-1 #:: LINE BOWMAN__-BE4-HETINGR4-1 :HV: | B | 321 | 51.787 | 100.0003 |  |  |  | Rebuild line 652425 BELFELD4 230 659124 DICKINSN-BE4 230 1
00NR | NRIS | Thermal | 652512 GROTON 7 115 660001 ABR SIEBRCHT 115 1 | 29SP | T0 | P12:230:MDU:ELLENDALE:ELLENDALE345:Z: | B | 180.3 | 113.8684 | 133.08 |  |  |  | Rebuild line 652512 GROTON 7 115 660001 ABR SIEBRCHT 115 1
00NR | NRIS | Thermal | 652552 SIOUXCY2 230 3WXFMR 652:652: SC2 KU1B 230 1 | 29SP | T0 | P23:345:XEL:396 BKR SPK:::EHV: | B | 750 | 54.9 | 100.7724 |  |  |  | Add 3-winding transformer 652305 SIOUXC29 13 652552 SIOUXCY2 230 652564 SIOUXCY3 345 M2
00NR | NRIS | Thermal | 652552 SIOUXCY2 230 659900 EAGLE___-NI4 230 1 | 29SP | T0 | P23:345:XEL:396 BKR SPK:::EHV: | B | 370 | 49.0753 | 101.858 |  |  |  | Rebuild line 652552 SIOUXCY2 230 659900 EAGLE___-NI4 230 1
00NR | NRIS | Thermal | 652564 SIOUXCY3 345 3WXFMR 652:652: SC2 KU1B 230 1 | 29SP | T0 | P23:345:XEL:396 BKR SPK:::EHV: | B | 750 | 54.87 | 100.7724 |  |  |  | Add 3-winding transformer 652305 SIOUXC29 13 652552 SIOUXCY2 230 652564 SIOUXCY3 345 M2
00NR | NRIS | Thermal | 653312 MORRILL 7 115 653313 GERING TAP 115 1 | 29SP | T0 | P12:230.0:UMZ:# N-1 #:: LINE WAYSIDE 4-STEGALL-LNX3-1 :HV: | B | 109 | 89.1153 | 121.822 |  |  |  | 640_NPPD_Rebuild_Morill_Gering_115.idv : 2024 ITP, PID: TBD, ISD: Unknown
00NR | NRIS | Thermal | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 29SP | T1 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | B | 211 | 69.7192 | 104.436 |  |  |  | Rebuild line 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1
00NR | NRIS | Thermal | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 29SP | T1 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | B | 211 | 69.7638 | 104.4644 |  |  |  | Rebuild line 511494 COMMTAP4 138 529304 OMDUNCN4 138 1
00NR | NRIS | Thermal | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 29SP | T1 | Single 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | B | 444 | 77.1689 | 103.6301 |  |  |  | Rebuild line 514894 CZECHAL4 138 514898 CIMARON4 138 1
00NR | NRIS | Thermal | 530565 SEWARD 2 69 3WXFMR 531:SEWARD T1 69 1 | 29SP | T1 | Single 539666 GBENDTP3 115 539692 SEWARD3 115 1 | B | 53 | -18.0804 | 101.4947 |  |  |  | Rebuild 3-winding transformer 530565 SEWARD 2 69 530631 SWRD1 1 12 530679 SEWRDMW3 115 1
00NR | NRIS | Thermal | 530679 SEWRDMW3 115 3WXFMR 531:SEWARD T1 69 1 | 29SP | T1 | Single 539666 GBENDTP3 115 539692 SEWARD3 115 1 | B | 53 | -18.2598 | 101.4947 |  |  |  | Rebuild 3-winding transformer 530565 SEWARD 2 69 530631 SWRD1 1 12 530679 SEWRDMW3 115 1
00NR | NRIS | Thermal | 532911 MUSTNG5 161 532937 NEOSHO 5 161 1 | 29SP | T1 | Single 547469 RIV4525 161 764310 G20-079-TAP 161 1 | B | 148 | 86.196 | 113.9313 |  |  |  | Rebuild line 532911 MUSTNG5 161 532937 NEOSHO 5 161 1
00NR | NRIS | Thermal | 652552 SIOUXCY2 230 659900 EAGLE___-NI4 230 1 | 29SP | T1 | P23:345:XEL:396 BKR SPK:::EHV: | B | 386 | 48.3131 | 100.2184 |  |  |  | Rebuild line 652552 SIOUXCY2 230 659900 EAGLE___-NI4 230 1
00NR | NRIS | Thermal | 653570 ALIANCE 7 115 659815 BOXBUTE-TS7 115 1 | 29SP | T1 | P12:230.0:UMZ:# N-1 #:: LINE STEGALL 4-STEGALL-LNX3-Z :HV: | B | 91 | 53.1117 | 105.6156 |  |  |  | Rebuild line 653570 ALIANCE 7 115 659815 BOXBUTE-TS7 115 1
00NR | NRIS | Thermal | 505492 SPRGFLD5 161 549970 CLAY 5 161 1 | 29WP | T0 | P23:345:AECI:7HUBEN:1312::: | B | 223 | 89.694 | 102.2853 |  |  |  | Rebuild line 505492 SPRGFLD5 161 549970 CLAY 5 161 1
00NR | NRIS | Thermal | 509690 4PINELND 138 509691 4BROADUS 138 1 | 29WP | T0 | P23:345:EES::7ROCKYCRK%:1:EHV: | B | 143 | 65.4958 | 108.9938 |  |  |  | Rebuild line 509690 4PINELND 138 509691 4BROADUS 138 1
00NR | NRIS | Thermal | 509691 4BROADUS 138 509692 4ETOIL 138 1 | 29WP | T0 | P23:345:EES::7ROCKYCRK%:1:EHV: | B | 143 | 72.1605 | 115.8519 |  |  |  | Rebuild line 509691 4BROADUS 138 509692 4ETOIL 138 1
00NR | NRIS | Thermal | 511468 L.E.S.-7 345 764550 G20-087-TAP 345 1 | 29WP | T0 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | B | 1324 | 50.8054 | 102.0233 |  |  |  | Rebuild line 511468 L.E.S.-7 345 764550 G20-087-TAP 345 1
00NR | NRIS | Thermal | 516092 OKTAHA 5 161 3WXFMR OKTAHA 5 69 7 | 29WP | T0 | P22:345:EES:MUSKOGE7!:::EHV: | B | 112 | 73.3141 | 128.9125 |  |  |  | Rebuild 3-winding transformer 516092 OKTAHA 5 161 516093 OKTAHA 2 69 516095 OKTAHA71 13 7
00NR | NRIS | Thermal | 516093 OKTAHA 2 69 3WXFMR OKTAHA 5 69 7 | 29WP | T0 | P22:345:EES:MUSKOGE7!:::EHV: | B | 112 | 72.1086 | 127.8893 |  |  |  | Rebuild 3-winding transformer 516092 OKTAHA 5 161 516093 OKTAHA 2 69 516095 OKTAHA71 13 7
00NR | NRIS | Thermal | 528618 LE-LOVINTON2 69 528334 LE-NRTH_INT3 115 1 | 29WP | T0 | Single 528626 LE-PLNSINT2 69 528709 LE-PLNSGOAB2 69 1 | B | 100 | 95.5738 | 126.5657 |  |  |  | Rebuild 2-winding transformer 528334 LE-NRTH_INT3 115 528618 LE-LOVINTON2 69 1
00NR | NRIS | Thermal | 530565 SEWARD 2 69 3WXFMR 531:SEWARD T1 69 1 | 29WP | T0 | Single 539666 GBENDTP3 115 539692 SEWARD3 115 1 | B | 44.79 | -24.3707 | 106.4389 |  |  |  | Rebuild 3-winding transformer 530565 SEWARD 2 69 530631 SWRD1 1 12 530679 SEWRDMW3 115 1
00NR | NRIS | Thermal | 530679 SEWRDMW3 115 3WXFMR 531:SEWARD T1 69 1 | 29WP | T0 | Single 539666 GBENDTP3 115 539692 SEWARD3 115 1 | B | 44.79 | -24.3661 | 106.4389 |  |  |  | Rebuild 3-winding transformer 530565 SEWARD 2 69 530631 SWRD1 1 12 530679 SEWRDMW3 115 1
00NR | NRIS | Thermal | 530679 SEWRDMW3 115 539692 SEWARD 3 115 1 | 29WP | T0 | Single 539666 GBENDTP3 115 539692 SEWARD3 115 1 | B | 40 | -26.2057 | 112.2153 |  |  |  | Rebuild line 530679 SEWRDMW3 115 539692 SEWARD 3 115 1
00NR | NRIS | Thermal | 532777 NRSS7 345 532793 NEOSHO 7 345 1 | 29WP | T0 | P12:345:WERE:LATH-ROSE-345:EHV: | B | 1159 | 14.6499 | 122.1748 |  |  |  | Rebuild line 532777 NRSS7 345 532793 NEOSHO 7 345 1
00NR | NRIS | Thermal | 532777 NRSS7 345 780840 G24-129-TAP 345 1 | 29WP | T0 | P12:345:WERE:LATH-ROSE-345:EHV: | B | 1159 | 7.8624 | 114.3329 |  |  |  | Rebuild line 532777 NRSS7 345 780840 G24-129-TAP 345 1
00NR | NRIS | Thermal | 532780 CANEYRV7 345 780720 G24-125-TAP 345 1 | 29WP | T0 | P23:345:WERE:N345-345-20:EHV: | B | 1159 | 10.3455 | 122.9304 |  |  |  | Rebuild line 532780 CANEYRV7 345 780720 G24-125-TAP 345 1
00NR | NRIS | Thermal | 532793 NEOSHO 7 345 3WXFMR 536:N345 TX-2 161 2 | 29WP | T0 | Single 533021 NEOSHO4 138 533023 N34534 138 1 | B | 550 | 62.4755 | 101.4582 |  |  |  | Add 3-winding transformer 532793 NEOSHO 7 345 532825 N345 2 1 13 532939 N345 4 5 161 M2
00NR | NRIS | Thermal | 532937 NEOSHO 5 161 3WXFMR 536:NEOSHO TX-5 138 1 | 29WP | T0 | Single 532937 NEOSHO5 161 532939 N34545 161 1 | B | 165 | 59.9595 | 130.1983 |  |  |  | Add 3-winding transformer 532937 NEOSHO 5 161 532959 NEOSH5 1 13 533020 NEOSHOS4 138 M2
00NR | NRIS | Thermal | 532939 N345 4 5 161 3WXFMR 536:N345 TX-2 161 2 | 29WP | T0 | Single 533021 NEOSHO4 138 533023 N34534 138 1 | B | 550 | 62.3936 | 100.4793 |  |  |  | Add 3-winding transformer 532793 NEOSHO 7 345 532825 N345 2 1 13 532939 N345 4 5 161 M2
00NR | NRIS | Thermal | 533020 NEOSHOS4 138 3WXFMR 536:NEOSHO TX-5 138 1 | 29WP | T0 | Single 532937 NEOSHO5 161 532939 N34545 161 1 | B | 165 | 59.6029 | 129.6104 |  |  |  | Add 3-winding transformer 532937 NEOSHO 5 161 532959 NEOSH5 1 13 533020 NEOSHOS4 138 M2
00NR | NRIS | Thermal | 640080 BELDEN 7 115 640212 HARTGTN7 115 1 | 29WP | T0 | Single 640149 CREITON7 115 640521 ANTELOPE7 115 1 | B | 132 | 28.94 | 109.87 |  |  |  | Rebuild line 640080 BELDEN 7 115 640212 HARTGTN7 115 1
00NR | NRIS | Thermal | 640125 COLMB.E3 345 3WXFMR 640:COL.EAST T4 345 1 | 29WP | T0 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | B | 336 | 36.8128 | 108.1049 |  |  |  | Add 3-winding transformer 640125 COLMB.E3 345 640127 COLMB.E7 115 640129 COLMB.T9 13 M2
00NR | NRIS | Thermal | 640127 COLMB.E7 115 3WXFMR 640:COL.EAST T4 345 1 | 29WP | T0 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | B | 336 | 36.6101 | 108.1031 |  |  |  | Add 3-winding transformer 640125 COLMB.E3 345 640127 COLMB.E7 115 640129 COLMB.T9 13 M2
00NR | NRIS | Thermal | 640178 GENEVA 7 115 640272 MCCOOL 7 115 1 | 29WP | T0 | P42:345:NPPD:L3502A.MOORE.MCCOOL.CB3310:::: | B | 160 | 6.9064 | 113.2969 |  |  |  | Rebuild line 640178 GENEVA 7 115 640272 MCCOOL 7 115 1
00NR | NRIS | Thermal | 640272 MCCOOL 7 115 640413 YORK SW7 115 1 | 29WP | T0 | P23:345:UMZW:# 2427 #:: GI IN NE. GI 1392 BKR FAULT:EHV: | B | 160 | 49.9545 | 103.0964 |  |  |  | Rebuild line 640272 MCCOOL 7 115 640413 YORK SW7 115 1
00NR | NRIS | Thermal | 640404 WAYSIDE 4 230 652484 NUNDRWD4 230 1 | 29WP | T0 | Single 659131 LARAMIE_-MB3 345 800120 UNDERWOOD2 345 1 | B | 352 | 71.0457 | 111.9467 |  |  |  | Rebuild line 640404 WAYSIDE 4 230 652484 NUNDRWD4 230 1
00NR | NRIS | Thermal | 640404 WAYSIDE 4 230 652873 STEGALL-LNX3 230 1 | 29WP | T0 | Single 659131 LARAMIE_-MB3 345 800120 UNDERWOOD2 345 1 | B | 320 | 72.1236 | 106.7867 |  |  |  | Rebuild line 640404 WAYSIDE 4 230 652873 STEGALL-LNX3 230 1
00NR | NRIS | Thermal | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | 29WP | T0 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | B | 120 | 59.3319 | 118.0094 |  |  |  | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
00NR | NRIS | Thermal | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | 29WP | T0 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | B | 120 | 59.3319 | 118.0094 |  |  |  | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
00NR | NRIS | Thermal | 652484 NUNDRWD4 230 652884 NUNDRWD-LNX3 230 Z | 29WP | T0 | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 | B | 398 | 82.3136 | 115.6175 |  |  |  | Rebuild line 652484 NUNDRWD4 230 652884 NUNDRWD-LNX3 230 Z
00NR | NRIS | Thermal | 652497 MAURINE4 230 652884 NUNDRWD-LNX3 230 1 | 29WP | T0 | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 | B | 398 | 82.014 | 114.6315 |  |  |  | Rebuild line 652497 MAURINE4 230 652884 NUNDRWD-LNX3 230 1
00NR | NRIS | Thermal | 652512 GROTON 7 115 660001 ABR SIEBRCHT 115 1 | 29WP | T0 | P12:230:MDU:ELLENDALE:ELLENDALE345:Z: | B | 180.3 | 111.9168 | 134.04 |  |  |  | Rebuild line 652512 GROTON 7 115 660001 ABR SIEBRCHT 115 1
00NR | NRIS | Thermal | 652573 STEGALL 4 230 652873 STEGALL-LNX3 230 Z | 29WP | T0 | Single 659131 LARAMIE_-MB3 345 800120 UNDERWOOD2 345 1 | B | 320 | 73.4794 | 108.7838 |  |  |  | Rebuild line 652573 STEGALL 4 230 652873 STEGALL-LNX3 230 Z
00NR | NRIS | Thermal | 659339 BOWMAN__-BE4 230 661047 HETINGR4 230 1 | 29WP | T0 | Single 652424 BELFELD3 345 800121 MAURINE2 345 1 | B | 351 | 93.4437 | 124.0351 |  |  |  | Rebuild line 659339 BOWMAN__-BE4 230 661047 HETINGR4 230 1
00NR | NRIS | Thermal | 532937 NEOSHO 5 161 764310 G20-079-TAP 161 1 | 29WP | T1 | P23:345:AECI:7BLACKBERRY:653::: | B | 533 | 53.5586 | 101.6771 |  |  |  | Rebuild line 532937 NEOSHO 5 161 764310 G20-079-TAP 161 1
00NR | NRIS | Thermal | 652497 MAURINE4 230 659351 BISON___-GE4 230 1 | 29WP | T1 | Single 652424 BELFELD3 345 800121 MAURINE2 345 1 | B | 398 | 69.7507 | 100.8995 |  |  |  | Rebuild line 652497 MAURINE4 230 659351 BISON___-GE4 230 1
00NR | NRIS | Thermal | 652573 STEGALL 4 230 652873 STEGALL-LNX3 230 Z | 29WP | T1 | Single 659131 LARAMIE_-MB3 345 800120 UNDERWOOD2 345 1 | B | 349 | 68.4067 | 101.6614 |  |  |  | Rebuild line 652573 STEGALL 4 230 652873 STEGALL-LNX3 230 Z
00NR | NRIS | Voltage | DH_CS_EA-TS4 | 26SP | V | P13:345-230.0:UMZ:# N-1 #:: 3WND STEGALL_-MB3-STEGALL_-MB4-STEGALL_-MB9-1 SGQ KV3A:EHV: |  |  |  |  | 0.89411 | 0.9 | 1.05 | Add 78 MVAR switched shunt at DH_CS_EA-TS4 230 kV
00NR | NRIS | Voltage | G17-140-BUS | 26SP | V | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: |  |  |  |  | 1.2088 | 0.92 | 1.05 | None
00NR | NRIS | Voltage | NP-GLAZIR_G2 | 26SP | V | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: |  |  |  |  | 0.68414 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | NP-LIPSCOMB2 | 26SP | V | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: |  |  |  |  | 0.64646 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | NP-LIPS_SHA2 | 26SP | V | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: |  |  |  |  | 0.64646 | 0.9 | 1.05 | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
00NR | NRIS | Voltage | NP-LUCKY_CR2 | 26SP | V | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: |  |  |  |  | 0.77192 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | NP-VALERO_P2 | 26SP | V | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: |  |  |  |  | 0.65438 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | STEGALL 4 | 26SP | V | P13:345-230.0:UMZ:# N-1 #:: 3WND STEGALL_-MB3-STEGALL_-MB4-STEGALL_-MB9-1 SGQ KV3A:EHV: |  |  |  |  | 0.89411 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | STEGALL-LNX3 | 26SP | V | P13:345-230.0:UMZ:# N-1 #:: 3WND STEGALL_-MB3-STEGALL_-MB4-STEGALL_-MB9-1 SGQ KV3A:EHV: |  |  |  |  | 0.89411 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | STEGALL_-MB4 | 26SP | V | P13:345-230.0:UMZ:# N-1 #:: 3WND STEGALL_-MB3-STEGALL_-MB4-STEGALL_-MB9-1 SGQ KV3A:EHV: |  |  |  |  | 0.89412 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | DEAFSMITH 6 | 29SP | V | P12:230:SPS:K11_K21::1_BUSHL_DFSMTH_PLANTX:HV: |  |  |  |  | 0.84862 | 0.9 | 1.05 | Add 10 MVAR switched shunt at DEAFSMITH 6 230 kV
00NR | NRIS | Voltage | DH_CS_EA-TS4 | 29SP | V | P12:230.0:UMZ:# N-1 #:: LINE STEGALL 4-STEGALL_-MB4-1 :HV: |  |  |  |  | 0.7872 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | DH_CS_EA-TS4 | 29SP | V | P12:230.0:UMZ:# N-1 #:: LINE STEGALL 4-STEGALL_-MB4-1 :HV: |  |  |  |  | 0.7872 | 0.9 | 1.05 | Add 78 MVAR switched shunt at DH_CS_EA-TS4 230 kV
00NR | NRIS | Voltage | DRYCREEK-BE4 | 29SP | V | P12:230.0:UMZ:# N-1 #:: LINE NUNDRWD4-PHILIP_T 4-1 :HV: |  |  |  |  | 0.88709 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | DRYCREEK-BE7 | 29SP | V | P12:230.0:UMZ:# N-1 #:: LINE NUNDRWD4-PHILIP_T 4-1 :HV: |  |  |  |  | 0.89092 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | ELKCRK 7 | 29SP | V | P12:230.0:UMZ:# N-1 #:: LINE NUNDRWD4-PHILIP_T 4-1 :HV: |  |  |  |  | 0.89793 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | ELSWRTH7 | 29SP | V | P12:230.0:UMZ:# N-1 #:: LINE NUNDRWD4-PHILIP_T 4-1 :HV: |  |  |  |  | 0.88579 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | FAITH 7 | 29SP | V | P12:230.0:UMZ:# N-1 #:: LINE WAYSIDE 4-NUNDRWD4-1 :HV: |  |  |  |  | 1.0511 | 0.9 | 1.05 | None
00NR | NRIS | Voltage | FREEDOM7 | 29SP | V | P12:230.0:UMZ:# N-1 #:: LINE NUNDRWD4-PHILIP_T 4-1 :HV: |  |  |  |  | 0.88597 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | G17-140-BUS | 29SP | V | P22:345:EES:MUSKOGE7!:::EHV: |  |  |  |  | 1.1829 | 0.92 | 1.05 | None
00NR | NRIS | Voltage | GEN-2017-097 | 29SP | V | P12:230.0:UMZ:# N-1 #:: LINE NUNDRWD4-PHILIP_T 4-1 :HV: |  |  |  |  | 0.88964 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | HASTING4 | 29SP | V | System Intact |  |  |  |  | 0.94645 | 0.95 | 1.05 | Add 14 MVAR switched shunt at HASTING4 230 kV
00NR | NRIS | Voltage | JHNCRSOL | 29SP | V | P12:115:SUNC:JOHNSONCORNER-ULYSSESPLANT:::HV: |  |  |  |  | 1.0662 | 0.9 | 1.05 | Add 8 MVAR switched shunt at JHNCRSOL 115 kV
00NR | NRIS | Voltage | MANTER 3 | 29SP | V | P12:115:SUNC:JOHNSONCORNER-ULYSSESPLANT:::HV: |  |  |  |  | 1.0655 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | MANTERT3 | 29SP | V | P12:115:SUNC:JOHNSONCORNER-ULYSSESPLANT:::HV: |  |  |  |  | 1.0657 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | MAURINE8 | 29SP | V | P12:230.0:UMZ:# N-1 #:: LINE WAYSIDE 4-NUNDRWD4-1 :HV: |  |  |  |  | 1.0564 | 0.9 | 1.05 | None
00NR | NRIS | Voltage | NP-GLAZIR_G2 | 29SP | V | P12:115:SPS:T87.1.SPRMN.HANSFRD:::HV: |  |  |  |  | 0.62694 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | NP-LIPSCOMB2 | 29SP | V | P12:115:SPS:T87.1.SPRMN.HANSFRD:::HV: |  |  |  |  | 0.58465 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | NP-LIPS_SHA2 | 29SP | V | P12:115:SPS:T87.1.SPRMN.HANSFRD:::HV: |  |  |  |  | 0.58465 | 0.9 | 1.05 | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
00NR | NRIS | Voltage | NP-LUCKY_CR2 | 29SP | V | P12:115:SPS:T87.1.SPRMN.HANSFRD:::HV: |  |  |  |  | 0.72674 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | NP-VALERO_P2 | 29SP | V | P12:115:SPS:T87.1.SPRMN.HANSFRD:::HV: |  |  |  |  | 0.5935 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | NUNDRWD-LNX3 | 29SP | V | P12:230.0:UMZ:# N-1 #:: LINE NUNDRWD4-PHILIP_T 4-1 :HV: |  |  |  |  | 0.88176 | 0.9 | 1.05 | Add 60 MVAR switched shunt at NUNDRWD-LNX3 230 kV
00NR | NRIS | Voltage | NUNDRWD4 | 29SP | V | P12:230.0:UMZ:# N-1 #:: LINE NUNDRWD4-PHILIP_T 4-1 :HV: |  |  |  |  | 0.88189 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | PR BRZ 4 | 29SP | V | Single 640342 SHELCRK3 345 763982 G19-069TAP 345 1 |  |  |  |  | 1.059 | 0.95 | 1.05 | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
00NR | NRIS | Voltage | RAPIDCTY-RM8 | 29SP | V | P12:230.0:UMZ:# N-1 #:: LINE NUNDRWD4-PHILIP_T 4-1 :HV: |  |  |  |  | 0.89008 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | RICHFLD3 | 29SP | V | P12:115:SUNC:JOHNSONCORNER-ULYSSESPLANT:::HV: |  |  |  |  | 1.0637 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | RUSHMORE-RM7 | 29SP | V | P12:230.0:UMZ:# N-1 #:: LINE NUNDRWD4-PHILIP_T 4-1 :HV: |  |  |  |  | 0.8922 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | STEGALL 4 | 29SP | V | P12:230.0:UMZ:# N-1 #:: LINE STEGALL 4-STEGALL_-MB4-1 :HV: |  |  |  |  | 0.7872 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | STEGALL-LNX3 | 29SP | V | P12:230.0:UMZ:# N-1 #:: LINE STEGALL 4-STEGALL_-MB4-1 :HV: |  |  |  |  | 0.7872 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | STEGALL-LNX3 | 29SP | V | P12:230.0:UMZ:# N-1 #:: LINE STEGALL 4-STEGALL_-MB4-1 :HV: |  |  |  |  | 0.7872 | 0.9 | 1.05 | Add 23 MVAR switched shunt at STEGALL-LNX3 230 kV
00NR | NRIS | Voltage | STEGALL_-MB4 | 29SP | V | P13:345-230.0:UMZ:# N-1 #:: 3WND STEGALL_-MB3-STEGALL_-MB4-STEGALL_-MB9-1 SGQ KV3A:EHV: |  |  |  |  | 0.78819 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | SULPHUR | 29SP | V | P12:230.0:UMZ:# N-1 #:: LINE WAYSIDE 4-NUNDRWD4-1 :HV: |  |  |  |  | 1.0576 | 0.9 | 1.05 | None
00NR | NRIS | Voltage | VICTRYH4 | 29SP | V | P12:230.0:UMZ:# N-1 #:: LINE STEGALL 4-STEGALL_-MB4-1 :HV: |  |  |  |  | 0.80685 | 0.9 | 1.05 | Add 0.04 MVAR switched shunt at VICTRYH4 230 kV
00NR | NRIS | Voltage | VICTRYH4 | 29SP | V | P12:230.0:UMZ:# N-1 #:: LINE STEGALL 4-STEGALL_-MB4-1 :HV: |  |  |  |  | 0.80685 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | WAYSIDE 4 | 29SP | V | P12:230.0:UMZ:# N-1 #:: LINE STEGALL 4-STEGALL_-MB4-1 :HV: |  |  |  |  | 0.83916 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | WAYSIDE 4 | 29SP | V | P12:230.0:UMZ:# N-1 #:: LINE STEGALL 4-STEGALL_-MB4-1 :HV: |  |  |  |  | 0.83916 | 0.9 | 1.05 | Add 154 MVAR SVC at WAYSIDE 4 230 kV
00NR | NRIS | Voltage | WILCRKXFRP 3 | 29SP | V | P12:230.0:UMZ:# N-1 #:: LINE WAYSIDE 4-NUNDRWD4-1 :HV: |  |  |  |  | 1.0576 | 0.9 | 1.05 | None
00NR | NRIS | Voltage | BBCMPRSS-MK7 | 29WP | V | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: |  |  |  |  | 0.89956 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | BERG -MK7 | 29WP | V | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: |  |  |  |  | 0.89039 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | BIGGULCH-MK7 | 29WP | V | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: |  |  |  |  | 0.86546 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | BISON___-GE4 | 29WP | V | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: |  |  |  |  | 0.89949 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | CHADRON 7 | 29WP | V | Single 659131 LARAMIE_-MB3 345 800120 UNDERWOOD2 345 1 |  |  |  |  | 0.89842 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | CHARLSON-MK7 | 29WP | V | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: |  |  |  |  | 0.88347 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | DH_CS_EA-TS4 | 29WP | V | P12:230.0:UMZ:# N-1 #:: LINE STEGALL 4-STEGALL_-MB4-1 :HV: |  |  |  |  | 0.84404 | 0.9 | 1.05 | Add 78 MVAR switched shunt at DH_CS_EA-TS4 230 kV
00NR | NRIS | Voltage | DRYCREEK-BE4 | 29WP | V | Single 659131 LARAMIE_-MB3 345 800120 UNDERWOOD2 345 1 |  |  |  |  | 0.88469 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | DRYCREEK-BE7 | 29WP | V | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: |  |  |  |  | 0.88789 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | EHALLTP3 | 29WP | V | P12:115:MIDW-MKEC:ELLSWORTH-BUSHTON:::HV: |  |  |  |  | 1.0569 | 0.9 | 1.05 | Add 7 MVAR switched shunt at EHALLTP3 115 kV
00NR | NRIS | Voltage | ELKCRK 7 | 29WP | V | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: |  |  |  |  | 0.88723 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | ELSWRTH7 | 29WP | V | Single 659131 LARAMIE_-MB3 345 800120 UNDERWOOD2 345 1 |  |  |  |  | 0.8811 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | FREEDOM7 | 29WP | V | Single 659131 LARAMIE_-MB3 345 800120 UNDERWOOD2 345 1 |  |  |  |  | 0.88123 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | GEN-2017-097 | 29WP | V | Single 659131 LARAMIE_-MB3 345 800120 UNDERWOOD2 345 1 |  |  |  |  | 0.88449 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | GORDON 7 | 29WP | V | Single 659131 LARAMIE_-MB3 345 800120 UNDERWOOD2 345 1 |  |  |  |  | 0.89124 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | HETINGR4 | 29WP | V | Single 652424 BELFELD3 345 800121 MAURINE2 345 1 |  |  |  |  | 0.89961 | 0.9 | 1.05 | None
00NR | NRIS | Voltage | J12_____-MK7 | 29WP | V | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: |  |  |  |  | 0.85469 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | KEENE -MK7 | 29WP | V | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: |  |  |  |  | 0.88688 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | KEENECRN-MK7 | 29WP | V | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: |  |  |  |  | 0.88295 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | L11_____-MK7 | 29WP | V | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: |  |  |  |  | 0.86836 | 0.9 | 1.05 | Add 12 MVAR switched shunt at L11_____-MK7 115 kV
00NR | NRIS | Voltage | L11_____-MK7 | 29WP | V | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: |  |  |  |  | 0.86836 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | MAURINE4 | 29WP | V | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: |  |  |  |  | 0.87592 | 0.9 | 1.05 | Add 108 MVAR switched shunt at MAURINE4 230 kV
00NR | NRIS | Voltage | MAURINE8 | 29WP | V | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 |  |  |  |  | 0.88716 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | MOCCASIN-MK7 | 29WP | V | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: |  |  |  |  | 0.84211 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | MOCCASIN-MK7 | 29WP | V | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: |  |  |  |  | 0.84211 | 0.9 | 1.05 | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV
00NR | NRIS | Voltage | MOUNTAIN-MK7 | 29WP | V | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: |  |  |  |  | 0.878 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | NEWELL 7 | 29WP | V | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 |  |  |  |  | 0.87836 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | NRTHFORK-MK7 | 29WP | V | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: |  |  |  |  | 0.88454 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | NUNDRWD-LNX3 | 29WP | V | Single 659131 LARAMIE_-MB3 345 800120 UNDERWOOD2 345 1 |  |  |  |  | 0.87933 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | NUNDRWD4 | 29WP | V | Single 659131 LARAMIE_-MB3 345 800120 UNDERWOOD2 345 1 |  |  |  |  | 0.87942 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | OAKDALE -MK7 | 29WP | V | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: |  |  |  |  | 0.89482 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | PR BRZ 4 | 29WP | V | P12:345.0:UMZ:# N-1 #:: LINE FTTHOM2-LNX3-GRPRAR2-LNX3-1 :EHV: |  |  |  |  | 1.0566 | 0.95 | 1.05 | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
00NR | NRIS | Voltage | RAPIDCTY-RM8 | 29WP | V | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: |  |  |  |  | 0.885 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | RUSHMORE-RM7 | 29WP | V | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: |  |  |  |  | 0.88865 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | RUSHVIL7 | 29WP | V | Single 659131 LARAMIE_-MB3 345 800120 UNDERWOOD2 345 1 |  |  |  |  | 0.88492 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | SANDCREK-MK7 | 29WP | V | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: |  |  |  |  | 0.88234 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | SNDCRKTP-MK7 | 29WP | V | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: |  |  |  |  | 0.88335 | 0.9 | 1.05 | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV
00NR | NRIS | Voltage | STEGALL 4 | 29WP | V | P12:230.0:UMZ:# N-1 #:: LINE STEGALL 4-STEGALL_-MB4-1 :HV: |  |  |  |  | 0.84404 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | STEGALL-LNX3 | 29WP | V | P12:230.0:UMZ:# N-1 #:: LINE STEGALL 4-STEGALL_-MB4-1 :HV: |  |  |  |  | 0.84404 | 0.9 | 1.05 | Add 23 MVAR switched shunt at STEGALL-LNX3 230 kV
00NR | NRIS | Voltage | STEGALL-LNX3 | 29WP | V | P12:230.0:UMZ:# N-1 #:: LINE STEGALL 4-STEGALL_-MB4-1 :HV: |  |  |  |  | 0.84404 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | STEGALL_-MB4 | 29WP | V | P13:345-230.0:UMZ:# N-1 #:: 3WND STEGALL_-MB3-STEGALL_-MB4-STEGALL_-MB9-1 SGQ KV3A:EHV: |  |  |  |  | 0.84492 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | SULPHUR | 29WP | V | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 |  |  |  |  | 0.8832 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | SWENSON -MK7 | 29WP | V | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: |  |  |  |  | 0.88391 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | TABLEBUT-MK7 | 29WP | V | P41:345:UMZB:# 2511 #:: LO IN ND. BREAKER FAULT (2596):EHV: |  |  |  |  | 0.88798 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | VICTRYH4 | 29WP | V | P12:230.0:UMZ:# N-1 #:: LINE STEGALL 4-STEGALL_-MB4-1 :HV: |  |  |  |  | 0.86188 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | WAYSIDE 4 | 29WP | V | Single 659131 LARAMIE_-MB3 345 800120 UNDERWOOD2 345 1 |  |  |  |  | 0.77451 | 0.9 | 1.05 | Add 154 MVAR SVC at WAYSIDE 4 230 kV
00NR | NRIS | Voltage | WAYSIDE 4 | 29WP | V | Single 659131 LARAMIE_-MB3 345 800120 UNDERWOOD2 345 1 |  |  |  |  | 0.77451 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | WAYSIDE 7 | 29WP | V | Single 659131 LARAMIE_-MB3 345 800120 UNDERWOOD2 345 1 |  |  |  |  | 0.87597 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | WEBSTER CITY | 29WP | V | P12:115.0:UMZ:# N-1 #:: LINE GROTON 7-GROTONSOUTH7-Z :HV: |  |  |  |  | 0.8947 | 0.9 | 1.05 | Add 2.8 MVAR switched shunt at WEBSTER CITY 69 kV
00NR | NRIS | Voltage | WEBSTER NW | 29WP | V | P12:115.0:UMZ:# N-1 #:: LINE GROTON 7-GROTONSOUTH7-Z :HV: |  |  |  |  | 0.89542 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | WICKSVL7 | 29WP | V | Single 659131 LARAMIE_-MB3 345 800120 UNDERWOOD2 345 1 |  |  |  |  | 0.89969 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | WILCRKXFRP 3 | 29WP | V | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 |  |  |  |  | 0.88322 | 0.9 | 1.05 | Mitigated at another bus
00NR | NRIS | Voltage | WWRDEHV4 | 29WP | V | P42:345:OKGE:SB_DGSE7385:::EHV: |  |  |  |  | 1.0538 | 0.92 | 1.05 | Add 11 MVAR switched shunt at WWRDEHV4 138 kV
01ALL | ERIS | Thermal | 603022 SOURIS 7 115 603023 MALLARD7 115 1 | 26S | JTIQ Expanded Scope Analysis | P11:22:GRE:GRE-COAL42G:2 | B | 112.6 | <90% | 110.78 |  |  |  | Rebuild the SOURIS 7 to MALLARD7 115kV Line 1
01ALL | ERIS | Thermal | 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1 | 26SP | T0 | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-CROCKER_-BE3-1 :EHV: | B | 119 | 91.4877 | 123.7796 |  |  |  | Rebuild line 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1
01ALL | ERIS | Thermal | 652522 SUMMIT-7 115 655457 BRISTOL-ER7 115 1 | 26SP | T0 | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-CROCKER_-BE3-1 :EHV: | B | 119 | 84.7691 | 116.9606 |  |  |  | Rebuild line 652522 SUMMIT-7 115 655457 BRISTOL-ER7 115 1
01ALL | ERIS | Thermal | 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1 | 29SP | T0 | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-CROCKER_-BE3-1 :EHV: | B | 119 | 80.1862 | 111.8115 |  |  |  | Rebuild line 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1
01ALL | ERIS | Thermal | 652522 SUMMIT-7 115 655457 BRISTOL-ER7 115 1 | 29SP | T0 | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-CROCKER_-BE3-1 :EHV: | B | 119 | 74.0326 | 104.9568 |  |  |  | Rebuild line 652522 SUMMIT-7 115 655457 BRISTOL-ER7 115 1
02ALL | ERIS | Thermal | 635201 RAUN 5 161 646300 S1300 5 161 1 | 26SP | T0 | P12:161:OPPD:S1300-TEKAMAH:::HV: | B | 217 | 33.6236 | 123.8066 |  |  |  | Rebuild line 635201 RAUN 5 161 646300 S1300 5 161 1
02ALL | ERIS | Thermal | 640054 ALBION 7 115 640318 PETRSBG7 115 1 | 26SP | T0 | P42:345:NPPD:BKR-HOS-3308:::: | B | 137 | 95.488 | 124.7531 |  |  |  | 640_NPPD_NewBranch_Holt-Antilope3_345.idv : 2024 ITP, PID: 94842, NTC, ISD: 12/31/2029
02ALL | ERIS | Thermal | 640072 BATTLCR7 115 640115 CO.LINE7 115 1 | 26SP | T0 | Single 640226 HOSKINS3 345 763443 G18-131-TAP 345 1 | B | 193 | 77.434 | 118.2169 |  |  |  | 640_NPPD_NewBranch_Holt-Antilope3_345.idv : 2024 ITP, PID: 94842, NTC, ISD: 12/31/2029
02ALL | ERIS | Thermal | 640072 BATTLCR7 115 640296 NORFK.N7 115 1 | 26SP | T0 | Single 640226 HOSKINS3 345 763443 G18-131-TAP 345 1 | B | 193 | 61.9609 | 102.5395 |  |  |  | 640_NPPD_NewBranch_Holt-Antilope3_345.idv : 2024 ITP, PID: 94842, NTC, ISD: 12/31/2029
02ALL | ERIS | Thermal | 640113 CLRWATR7 115 640293 NELIGH 7 115 1 | 26SP | T0 | P42:345:NPPD:BKR-HOS-3308:::: | B | 120 | 72.1578 | 107.9844 |  |  |  | 640_NPPD_NewBranch_Holt-Antilope3_345.idv : 2024 ITP, PID: 94842, NTC, ISD: 12/31/2029
02ALL | ERIS | Thermal | 640113 CLRWATR7 115 640305 ONEILL 7 115 1 | 26SP | T0 | P42:345:NPPD:BKR-HOS-3308:::: | B | 120 | 65.5575 | 101.1484 |  |  |  | 640_NPPD_NewBranch_Holt-Antilope3_345.idv : 2024 ITP, PID: 94842, NTC, ISD: 12/31/2029
02ALL | ERIS | Thermal | 640115 CO.LINE7 115 640521 ANTELOPE 7 115 1 | 26SP | T0 | Single 640226 HOSKINS3 345 763443 G18-131-TAP 345 1 | B | 193 | 80.641 | 121.4834 |  |  |  | 640_NPPD_NewBranch_Holt-Antilope3_345.idv : 2024 ITP, PID: 94842, NTC, ISD: 12/31/2029
02ALL | ERIS | Thermal | 640149 CREITON7 115 640521 ANTELOPE 7 115 1 | 26SP | T0 | Single 640226 HOSKINS3 345 763443 G18-131-TAP 345 1 | B | 143 | 74.2092 | 113.1478 |  |  |  | 640_NPPD_NewBranch_Holt-Antilope3_345.idv : 2024 ITP, PID: 94842, NTC, ISD: 12/31/2029
02ALL | ERIS | Thermal | 640173 FREMONT7 115 3WXFMR 640:FREMONT T1 115 1 | 26SP | T0 | P13:069-115:NPPD:FREMONT T4:::HV: | B | 63 | 34.1318 | 126.4086 |  |  |  | Fremont_Add_transformer_fixed.idv :
02ALL | ERIS | Thermal | 640173 FREMONT7 115 3WXFMR 640:FREMONT T4 115 1 | 26SP | T0 | Single 647976 S9768 69 640173 FREMONT7 115 643058 'FREMONT T1 9' 13 1 | B | 56 | 31.9963 | 133.698 |  |  |  | Fremont_Add_transformer_fixed.idv :
02ALL | ERIS | Thermal | 640316 PAWNEEL7 115 640340 SEWARD 7 115 1 | 26SP | T0 | P12:115:NPPD:L1156B::NW68&HOLDREGE.PAWNEELAKE.CKT1:: | B | 140 | -8.8964 | 130.8993 |  |  |  | Rebuild line 640316 PAWNEEL7 115 640340 SEWARD 7 115 1
02ALL | ERIS | Thermal | 640316 PAWNEEL7 115 650214 NW68HOLDRG7 115 1 | 26SP | T0 | Single 640316 PAWNEEL7 115 640340 SEWARD7 115 1 | B | 154 | -8.0384 | 119.0273 |  |  |  | Rebuild line 640316 PAWNEEL7 115 650214 NW68HOLDRG7 115 1
02ALL | ERIS | Thermal | 640318 PETRSBG7 115 640444 PETERSBRG.N7 115 Z1 | 26SP | T0 | P42:345:NPPD:BKR-HOS-3308:::: | B | 137 | 99.4562 | 128.8228 |  |  |  | 640_NPPD_NewBranch_Holt-Antilope3_345.idv : 2024 ITP, PID: 94842, NTC, ISD: 12/31/2029
02ALL | ERIS | Thermal | 640377 TEKAMAH5 161 646300 S1300 5 161 1 | 26SP | T0 | P12:161:OPPD:S1300-RAUN:::HV: | B | 217 | 33.7791 | 123.6499 |  |  |  | Rebuild line 640377 TEKAMAH5 161 646300 S1300 5 161 1
02ALL | ERIS | Thermal | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | 26SP | T0 | P12:345.0:UMZ:# N-1 #:: LINE RAUN 3-SIOUXCY3-1 :EHV: | B | 320 | 70.7972 | 109.5852 |  |  |  | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
02ALL | ERIS | Thermal | 646226 S1226 5 161 646247 S1247 5 161 1 | 26SP | T0 | P12:161:OPPD:S1247-S1252:::HV: | B | 217 | -4.6856 | 107.8107 |  |  |  | Rebuild line 646226 S1226 5 161 646247 S1247 5 161 1
02ALL | ERIS | Thermal | 647424 FREM D 8 69 647976 S976 8 69 1 | 26SP | T0 | GEN647418 8 | B | 96 | 46.2614 | 115.287 |  |  |  | Rebuild line 647424 FREM D 8 69 647976 S976 8 69 1
02ALL | ERIS | Thermal | 647976 S976 8 69 3WXFMR 640:FREMONT T1 115 1 | 26SP | T0 | P13:069-115:NPPD:FREMONT T4:::HV: | B | 63 | 33.4973 | 123.0184 |  |  |  | Fremont_Add_transformer_fixed.idv :
02ALL | ERIS | Thermal | 647976 S976 8 69 3WXFMR 640:FREMONT T4 115 1 | 26SP | T0 | Single 647976 S9768 69 640173 FREMONT7 115 643058 'FREMONT T1 9' 13 1 | B | 56 | 31.5305 | 131.2891 |  |  |  | Fremont_Add_transformer_fixed.idv :
02ALL | ERIS | Thermal | 635201 RAUN 5 161 646300 S1300 5 161 1 | 29SP | T0 | P12:161:OPPD:S1300-TEKAMAH:::HV: | B | 217 | 33.6363 | 123.8554 |  |  |  | Rebuild line 635201 RAUN 5 161 646300 S1300 5 161 1
02ALL | ERIS | Thermal | 640173 FREMONT7 115 3WXFMR 640:FREMONT T1 115 1 | 29SP | T0 | P13:069-115:NPPD:FREMONT T4:::HV: | B | 63 | 36.2348 | 129.3815 |  |  |  | Fremont_Add_transformer_fixed.idv :
02ALL | ERIS | Thermal | 640173 FREMONT7 115 3WXFMR 640:FREMONT T4 115 1 | 29SP | T0 | Single 647976 S9768 69 640173 FREMONT7 115 643058 'FREMONT T1 9' 13 1 | B | 56 | 34.8189 | 136.8298 |  |  |  | Fremont_Add_transformer_fixed.idv :
02ALL | ERIS | Thermal | 640316 PAWNEEL7 115 640340 SEWARD 7 115 1 | 29SP | T0 | P12:115:NPPD:L1156B::NW68&HOLDREGE.PAWNEELAKE.CKT1:: | B | 140 | -9.4263 | 130.7053 |  |  |  | Rebuild line 640316 PAWNEEL7 115 640340 SEWARD 7 115 1
02ALL | ERIS | Thermal | 640316 PAWNEEL7 115 650214 NW68HOLDRG7 115 1 | 29SP | T0 | Single 640316 PAWNEEL7 115 640340 SEWARD7 115 1 | B | 154 | -8.453 | 118.7703 |  |  |  | Rebuild line 640316 PAWNEEL7 115 650214 NW68HOLDRG7 115 1
02ALL | ERIS | Thermal | 640377 TEKAMAH5 161 646300 S1300 5 161 1 | 29SP | T0 | P12:161:OPPD:S1300-RAUN:::HV: | B | 217 | 33.8486 | 123.8434 |  |  |  | Rebuild line 640377 TEKAMAH5 161 646300 S1300 5 161 1
02ALL | ERIS | Thermal | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | 29SP | T0 | P12:345.0:UMZ:# N-1 #:: LINE RAUN 3-SIOUXCY3-1 :EHV: | B | 320 | 81.7503 | 116.7129 |  |  |  | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
02ALL | ERIS | Thermal | 646226 S1226 5 161 646247 S1247 5 161 1 | 29SP | T0 | P12:161:OPPD:S1247-S1252:::HV: | B | 217 | -5.0435 | 107.6487 |  |  |  | Rebuild line 646226 S1226 5 161 646247 S1247 5 161 1
02ALL | ERIS | Thermal | 647424 FREM D 8 69 647976 S976 8 69 1 | 29SP | T0 | GEN647418 8 | B | 96 | 48.8258 | 117.3606 |  |  |  | Rebuild line 647424 FREM D 8 69 647976 S976 8 69 1
02ALL | ERIS | Thermal | 647976 S976 8 69 3WXFMR 640:FREMONT T1 115 1 | 29SP | T0 | P13:069-115:NPPD:FREMONT T4:::HV: | B | 63 | 35.5882 | 125.7439 |  |  |  | Fremont_Add_transformer_fixed.idv :
02ALL | ERIS | Thermal | 647976 S976 8 69 3WXFMR 640:FREMONT T4 115 1 | 29SP | T0 | Single 647976 S9768 69 640173 FREMONT7 115 643058 'FREMONT T1 9' 13 1 | B | 56 | 34.3433 | 134.187 |  |  |  | Fremont_Add_transformer_fixed.idv :
02ALL | ERIS | Thermal | 635201 RAUN 5 161 646300 S1300 5 161 1 | 29WP | T0 | P12:161:OPPD:S1300-TEKAMAH:::HV: | B | 217 | 33.6331 | 123.9016 |  |  |  | Rebuild line 635201 RAUN 5 161 646300 S1300 5 161 1
02ALL | ERIS | Thermal | 640173 FREMONT7 115 3WXFMR 640:FREMONT T1 115 1 | 29WP | T0 | P13:069-115:NPPD:FREMONT T4:::HV: | B | 63 | 40.1733 | 132.5504 |  |  |  | Fremont_Add_transformer_fixed.idv :
02ALL | ERIS | Thermal | 640173 FREMONT7 115 3WXFMR 640:FREMONT T4 115 1 | 29WP | T0 | Single 647976 S9768 69 640173 FREMONT7 115 643058 'FREMONT T1 9' 13 1 | B | 56 | 40.5704 | 140.8163 |  |  |  | Fremont_Add_transformer_fixed.idv :
02ALL | ERIS | Thermal | 640316 PAWNEEL7 115 640340 SEWARD 7 115 1 | 29WP | T0 | P12:115:NPPD:L1156B::NW68&HOLDREGE.PAWNEELAKE.CKT1:: | B | 140 | -12.9921 | 127.5755 |  |  |  | Rebuild line 640316 PAWNEEL7 115 640340 SEWARD 7 115 1
02ALL | ERIS | Thermal | 640316 PAWNEEL7 115 650214 NW68HOLDRG7 115 1 | 29WP | T0 | Single 640316 PAWNEEL7 115 640340 SEWARD7 115 1 | B | 174 | -10.1619 | 102.4601 |  |  |  | Rebuild line 640316 PAWNEEL7 115 650214 NW68HOLDRG7 115 1
02ALL | ERIS | Thermal | 640377 TEKAMAH5 161 646300 S1300 5 161 1 | 29WP | T0 | P12:161:OPPD:S1300-RAUN:::HV: | B | 217 | 34.0057 | 124.0466 |  |  |  | Rebuild line 640377 TEKAMAH5 161 646300 S1300 5 161 1
02ALL | ERIS | Thermal | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | 29WP | T0 | Single 635200 RAUN3 345 640226 HOSKINS3 345 1 | B | 320 | 97.4724 | 136.3055 |  |  |  | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
02ALL | ERIS | Thermal | 646226 S1226 5 161 646247 S1247 5 161 1 | 29WP | T0 | P12:161:OPPD:S1247-S1252:::HV: | B | 217 | -2.7451 | 109.762 |  |  |  | Rebuild line 646226 S1226 5 161 646247 S1247 5 161 1
02ALL | ERIS | Thermal | 647424 FREM D 8 69 647976 S976 8 69 1 | 29WP | T0 | GEN647418 8 | B | 96 | 56.1068 | 122.214 |  |  |  | Rebuild line 647424 FREM D 8 69 647976 S976 8 69 1
02ALL | ERIS | Thermal | 647976 S976 8 69 3WXFMR 640:FREMONT T1 115 1 | 29WP | T0 | P13:069-115:NPPD:FREMONT T4:::HV: | B | 63 | 39.6058 | 129.1259 |  |  |  | Fremont_Add_transformer_fixed.idv :
02ALL | ERIS | Thermal | 647976 S976 8 69 3WXFMR 640:FREMONT T4 115 1 | 29WP | T0 | Single 647976 S9768 69 640173 FREMONT7 115 643058 'FREMONT T1 9' 13 1 | B | 56 | 40.1746 | 138.3493 |  |  |  | Fremont_Add_transformer_fixed.idv :
03ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | [7 empty] | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
03ALL | ERIS | Thermal | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 26SP | T0 | System Intact | A | 311 | 101.7231 | 121.8886 |  |  |  | Rebuild line 300071 5CLINTN 161 761278 G17-108-TAP 161 1
03ALL | ERIS | Thermal | 505488 CARTHAG5 161 547485 CAR395 5 161 1 | 26SP | T0 | Single 547476 ASB3495 161 547477 CJ3665 161 1 | B | 215 | 76.6675 | 143.9699 |  |  |  | Rebuild line 505488 CARTHAG5 161 547485 CAR395 5 161 1
03ALL | ERIS | Thermal | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | 26SP | T0 | P23:345:AECI:7BLACKBERRY:653::: | B | 829 | 77.4717 | 114.8446 |  |  |  | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
03ALL | ERIS | Thermal | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | 26SP | T0 | P23:345:AECI:7BLACKBERRY:653::: | B | 829 | 77.4717 | 114.8446 |  |  |  | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
03ALL | ERIS | Thermal | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | 26SP | T0 | P23:345:AECI:7BLACKBERRY:653::: | B | 829 | 77.4717 | 114.8446 |  |  |  | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
03ALL | ERIS | Thermal | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | 26SP | T0 | P23:345:AECI:7BLACKBERRY:653::: | B | 829 | 77.5731 | 111.8275 |  |  |  | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
03ALL | ERIS | Thermal | 532857 TECHILL6 230 3WXFMR 536:TECHILL TX-3 115 1 | 26SP | T0 | Single 532851 AUBURN6 230 533151 AUBURN3 115 532880 'AUBURN 1 ' 14 1 | B | 308 | 76.0057 | 111.133 |  |  |  | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2
03ALL | ERIS | Thermal | 532857 TECHILL6 230 785250 G24-276-TAP 230 1 | 26SP | T0 | Single 532851 AUBURN6 230 533151 AUBURN3 115 532880 'AUBURN 1 ' 14 1 | B | 318 | 75.0546 | 108.8422 |  |  |  | Rebuild line 532857 TECHILL6 230 785250 G24-276-TAP 230 1
03ALL | ERIS | Thermal | 532987 BUTLER 4 138 532990 MIDIAN 4 138 1 | 26SP | T0 | Single 532990 MIDIAN4 138 533597 MIDIAN2 69 533082 'MIDIAN TX3 1' 13 3 | B | 121 | 36.3909 | 111.2267 |  |  |  | Rebuild line 532987 BUTLER 4 138 532990 MIDIAN 4 138 1
03ALL | ERIS | Thermal | 532995 OTTRCRK4 138 533001 ALTOONA4 138 1 | 26SP | T0 | Single 533005 NEPARSN4 138 533022 NEOSHON4 138 1 | B | 98 | 83.2902 | 116.2498 |  |  |  | Rebuild line 532995 OTTRCRK4 138 533001 ALTOONA4 138 1
03ALL | ERIS | Thermal | 533182 TECHILE3 115 3WXFMR 536:TECHILL TX-3 115 1 | 26SP | T0 | Single 532851 AUBURN6 230 533151 AUBURN3 115 532880 'AUBURN 1 ' 14 1 | B | 308 | 75.1649 | 109.6861 |  |  |  | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2
03ALL | ERIS | Thermal | 533243 JAGGARD3 115 533261 PENTAGN3 115 1 | 26SP | T0 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | B | 201 | 48.0281 | 112.035 |  |  |  | Rebuild line 533243 JAGGARD3 115 533261 PENTAGN3 115 1
03ALL | ERIS | Thermal | 533583 BUTLERN2 69 533597 MIDIAN 2 69 1 | 26SP | T0 | P12:138:WERE:BUTL-MIDI-138:HV: | B | 45 | 99.583 | 177.1968 |  |  |  | Rebuild line 533583 BUTLERN2 69 533597 MIDIAN 2 69 1
03ALL | ERIS | Thermal | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 26SP | T0 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | B | 756 | 82.2612 | 101.463 |  |  |  | Rebuild line 541200 PHILL 7 345 541201 SIBLEY 7 345 1
03ALL | ERIS | Thermal | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | 26SP | T0 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | B | 261 | 75.2618 | 182.0098 |  |  |  | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
03ALL | ERIS | Thermal | 541204 SMTHVL 5 161 541221 PLTCTY 5 161 1 | 26SP | T0 | Single 541203 NASHUA5 161 541204 SMTHVL5 161 1 | B | 261 | -8.0279 | 123.916 |  |  |  | Rebuild line 541204 SMTHVL 5 161 541221 PLTCTY 5 161 1
03ALL | ERIS | Thermal | 541214 TWA 5 161 541318 NCONGRS5 161 1 | 26SP | T0 | Single 541203 NASHUA5 161 541204 SMTHVL5 161 1 | B | 193 | 27.2949 | 109.9324 |  |  |  | Rebuild line 541214 TWA 5 161 541318 NCONGRS5 161 1
03ALL | ERIS | Thermal | 547467 ORO110 5 161 547490 FIR417 5 161 1 | 26SP | T0 | Single 547476 ASB3495 161 547491 PUR4215 161 1 | B | 290 | 52.0429 | 107.1853 |  |  |  | Rebuild line 547467 ORO110 5 161 547490 FIR417 5 161 1
03ALL | ERIS | Thermal | 547476 ASB349 5 161 547477 CJ 366 5 161 1 | 26SP | T0 | Single 547476 ASB3495 161 547491 PUR4215 161 1 | B | 290 | 61.67 | 116.976 |  |  |  | Rebuild line 547476 ASB349 5 161 547477 CJ 366 5 161 1
03ALL | ERIS | Thermal | 547476 ASB349 5 161 547491 PUR421 5 161 1 | 26SP | T0 | Single 547476 ASB3495 161 547477 CJ3665 161 1 | B | 290 | 63.9258 | 113.9097 |  |  |  | Rebuild line 547476 ASB349 5 161 547491 PUR421 5 161 1
03ALL | ERIS | Thermal | 547477 CJ 366 5 161 547490 FIR417 5 161 1 | 26SP | T0 | Single 547476 ASB3495 161 547491 PUR4215 161 1 | B | 290 | 57.7785 | 113.0237 |  |  |  | Rebuild line 547477 CJ 366 5 161 547490 FIR417 5 161 1
03ALL | ERIS | Thermal | 547485 CAR395 5 161 547491 PUR421 5 161 1 | 26SP | T0 | Single 547476 ASB3495 161 547477 CJ3665 161 1 | B | 290 | 61.6641 | 111.6106 |  |  |  | Rebuild line 547485 CAR395 5 161 547491 PUR421 5 161 1
03ALL | ERIS | Thermal | 640277 MOORE 3 345 640525 TOBIAS 3 345 1 | 26SP | T0 | P55:345:OPPD:S3458 3::FN13:EHV: | B | 956 | 81.6378 | 109.5154 |  |  |  | Rebuild line 640277 MOORE 3 345 640525 TOBIAS 3 345 1
03ALL | ERIS | Thermal | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | 26SP | T1 | P23:345:AECI:7BLACKBERRY:653::: | B | 829 | 69.4471 | 105.0133 |  |  |  | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
03ALL | ERIS | Thermal | 532857 TECHILL6 230 785250 G24-276-TAP 230 1 | 26SP | T1 | Single 532851 AUBURN6 230 533151 AUBURN3 115 532880 'AUBURN 1 ' 14 1 | B | 386 | 72.5672 | 105.4121 |  |  |  | Rebuild line 532857 TECHILL6 230 785250 G24-276-TAP 230 1
03ALL | ERIS | Thermal | 541369 MIDWAY_5 161 541394 AVENUECTY 5 161 1 | 26SP | T1 | System Intact | A | 161 | 67.9585 | 104.1401 |  |  |  | Rebuild line 541369 MIDWAY_5 161 541394 AVENUECTY 5 161 1
03ALL | ERIS | Thermal | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 29SP | T0 | System Intact | A | 311 | 91.5413 | 111.039 |  |  |  | Rebuild line 300071 5CLINTN 161 761278 G17-108-TAP 161 1
03ALL | ERIS | Thermal | 505488 CARTHAG5 161 547485 CAR395 5 161 1 | 29SP | T0 | Single 547476 ASB3495 161 547477 CJ3665 161 1 | B | 215 | 71.665 | 137.1198 |  |  |  | Rebuild line 505488 CARTHAG5 161 547485 CAR395 5 161 1
03ALL | ERIS | Thermal | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | 29SP | T0 | P23:345:AECI:7BLACKBERRY:653::: | B | 829 | 65.1987 | 101.6955 |  |  |  | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
03ALL | ERIS | Thermal | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | 29SP | T0 | P23:345:AECI:7BLACKBERRY:653::: | B | 829 | 65.1987 | 101.6955 |  |  |  | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
03ALL | ERIS | Thermal | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | 29SP | T0 | P23:345:AECI:7BLACKBERRY:653::: | B | 829 | 65.1987 | 101.6955 |  |  |  | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
03ALL | ERIS | Thermal | 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | 29SP | T0 | P23:345:AECI:7BLACKBERRY:6_3::: | B | 956 | 64.6267 | 101.9438 |  |  |  | Rebuild line 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1
03ALL | ERIS | Thermal | 532857 TECHILL6 230 3WXFMR 536:TECHILL TX-3 115 1 | 29SP | T0 | Single 532851 AUBURN6 230 533151 AUBURN3 115 532880 'AUBURN 1 ' 14 1 | B | 308 | 83.1698 | 119.1646 |  |  |  | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2
03ALL | ERIS | Thermal | 532857 TECHILL6 230 785250 G24-276-TAP 230 1 | 29SP | T0 | Single 532851 AUBURN6 230 533151 AUBURN3 115 532880 'AUBURN 1 ' 14 1 | B | 318 | 82.492 | 117.2217 |  |  |  | Rebuild line 532857 TECHILL6 230 785250 G24-276-TAP 230 1
03ALL | ERIS | Thermal | 533182 TECHILE3 115 3WXFMR 536:TECHILL TX-3 115 1 | 29SP | T0 | Single 532851 AUBURN6 230 533151 AUBURN3 115 532880 'AUBURN 1 ' 14 1 | B | 308 | 82.1945 | 117.3469 |  |  |  | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2
03ALL | ERIS | Thermal | 533238 EDWARVL3 115 533282 MUND 3 115 1 | 29SP | T0 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | B | 201 | 96.4322 | 109.2108 |  |  |  | Rebuild line 533238 EDWARVL3 115 533282 MUND 3 115 1
03ALL | ERIS | Thermal | 533583 BUTLERN2 69 533597 MIDIAN 2 69 1 | 29SP | T0 | P12:138:WERE:BUTL-MIDI-138:HV: | B | 45 | 79.5024 | 160.6574 |  |  |  | Rebuild line 533583 BUTLERN2 69 533597 MIDIAN 2 69 1
03ALL | ERIS | Thermal | 539657 CONCORD3 115 3WXFMR 534:CONCORD6 230 1 | 29SP | T0 | Single 539805 ELMCREEK7 345 640600 DAYKIN3 345 1 | B | 225.5 | 70.8328 | 106.7468 |  |  |  | Add 3-winding transformer 539657 CONCORD3 115 539658 CONCRD6 230 539904 CONCOD-1 13 M2
03ALL | ERIS | Thermal | 539658 CONCRD6 230 3WXFMR 534:CONCORD6 230 1 | 29SP | T0 | Single 539805 ELMCREEK7 345 640600 DAYKIN3 345 1 | B | 225.5 | 70.9257 | 107.4002 |  |  |  | Add 3-winding transformer 539657 CONCORD3 115 539658 CONCRD6 230 539904 CONCOD-1 13 M2
03ALL | ERIS | Thermal | 541199 ST JOE 7 345 541400 EASTOWN7 345 1 | 29SP | T0 | Single 541199 STJOE7 345 761383 G17-183-TAP 345 1 | B | 1185 | 69.6006 | 100.396 |  |  |  | Rebuild line 541199 ST JOE 7 345 541400 EASTOWN7 345 1
03ALL | ERIS | Thermal | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 29SP | T0 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | B | 756 | 95.48 | 117.5821 |  |  |  | Rebuild line 541200 PHILL 7 345 541201 SIBLEY 7 345 1
03ALL | ERIS | Thermal | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | 29SP | T0 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | B | 261 | 83.3265 | 196.2546 |  |  |  | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
03ALL | ERIS | Thermal | 541204 SMTHVL 5 161 541221 PLTCTY 5 161 1 | 29SP | T0 | Single 541203 NASHUA5 161 541204 SMTHVL5 161 1 | B | 261 | -8.1148 | 124.0382 |  |  |  | Rebuild line 541204 SMTHVL 5 161 541221 PLTCTY 5 161 1
03ALL | ERIS | Thermal | 541251 MARYVLE5 161 635038 BRADDYVILLE5 161 1 | 29SP | T0 | System Intact | A | 161 | 69.1784 | 100.2848 |  |  |  | Rebuild line 541251 MARYVLE5 161 635038 BRADDYVILLE5 161 1
03ALL | ERIS | Thermal | 541253 ST JOE 5 161 541394 AVENUECTY 5 161 1 | 29SP | T0 | System Intact | A | 161 | 70.5374 | 100.5556 |  |  |  | Rebuild line 541253 ST JOE 5 161 541394 AVENUECTY 5 161 1
03ALL | ERIS | Thermal | 541254 EAST 5 161 541401 EASTOWN5 161 1 | 29SP | T0 | Single 541199 STJOE7 345 541400 EASTOWN7 345 1 | B | 334 | 73.7744 | 117.1628 |  |  |  | Rebuild line 541254 EAST 5 161 541401 EASTOWN5 161 1
03ALL | ERIS | Thermal | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | 29SP | T0 | Single 541199 STJOE7 345 761383 G17-183-TAP 345 1 | B | 1195 | 84.9052 | 107.005 |  |  |  | Rebuild line 541400 EASTOWN7 345 542982 IATAN 7 345 1
03ALL | ERIS | Thermal | 547467 ORO110 5 161 547490 FIR417 5 161 1 | 29SP | T0 | Single 547476 ASB3495 161 547491 PUR4215 161 1 | B | 290 | 47.78 | 101.3552 |  |  |  | Rebuild line 547467 ORO110 5 161 547490 FIR417 5 161 1
03ALL | ERIS | Thermal | 547476 ASB349 5 161 547477 CJ 366 5 161 1 | 29SP | T0 | Single 547476 ASB3495 161 547491 PUR4215 161 1 | B | 290 | 57.58 | 111.3193 |  |  |  | Rebuild line 547476 ASB349 5 161 547477 CJ 366 5 161 1
03ALL | ERIS | Thermal | 547476 ASB349 5 161 547491 PUR421 5 161 1 | 29SP | T0 | Single 547476 ASB3495 161 547477 CJ3665 161 1 | B | 290 | 60.3433 | 108.9532 |  |  |  | Rebuild line 547476 ASB349 5 161 547491 PUR421 5 161 1
03ALL | ERIS | Thermal | 547477 CJ 366 5 161 547490 FIR417 5 161 1 | 29SP | T0 | Single 547476 ASB3495 161 547491 PUR4215 161 1 | B | 290 | 53.6201 | 107.2979 |  |  |  | Rebuild line 547477 CJ 366 5 161 547490 FIR417 5 161 1
03ALL | ERIS | Thermal | 547485 CAR395 5 161 547491 PUR421 5 161 1 | 29SP | T0 | Single 547476 ASB3495 161 547477 CJ3665 161 1 | B | 290 | 58.0423 | 106.6168 |  |  |  | Rebuild line 547485 CAR395 5 161 547491 PUR421 5 161 1
03ALL | ERIS | Thermal | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | 29SP | T0 | P55:345:OPPD:S3458 3::FN13:EHV: | B | 956 | 82.8311 | 117.7598 |  |  |  | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
03ALL | ERIS | Thermal | 532857 TECHILL6 230 785250 G24-276-TAP 230 1 | 29SP | T1 | Single 532851 AUBURN6 230 533151 AUBURN3 115 532880 'AUBURN 1 ' 14 1 | B | 386 | 80.6643 | 114.6785 |  |  |  | Rebuild line 532857 TECHILL6 230 785250 G24-276-TAP 230 1
03ALL | ERIS | Thermal | 541251 MARYVLE5 161 541369 MIDWAY_5 161 1 | 29SP | T1 | System Intact | A | 161 | 80.2908 | 118.7915 |  |  |  | Rebuild line 541251 MARYVLE5 161 541369 MIDWAY_5 161 1
03ALL | ERIS | Thermal | 541369 MIDWAY_5 161 541394 AVENUECTY 5 161 1 | 29SP | T1 | System Intact | A | 161 | 89.1272 | 127.6857 |  |  |  | Rebuild line 541369 MIDWAY_5 161 541394 AVENUECTY 5 161 1
03ALL | ERIS | Thermal | 345072 5MCBAINE 161 345411 5OVERTON 2 161 1 | 29W | JTIQ Expanded Scope Analysis | P23:345:AECI:7MCCRED:352::: | B | 355 | <90% | 100.48 |  |  |  | Rebuild the 5MCBAINE to 5OVERTON 2 115kV Line 1
03ALL | ERIS | Thermal | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | 29WP | T0 | System Intact | A | 334 | 119.7792 | 145.0684 |  |  |  | Rebuild line 300071 5CLINTN 161 761278 G17-108-TAP 161 1
03ALL | ERIS | Thermal | 505488 CARTHAG5 161 547485 CAR395 5 161 1 | 29WP | T0 | Single 547476 ASB3495 161 547477 CJ3665 161 1 | B | 293 | 75.364 | 126.3605 |  |  |  | Rebuild line 505488 CARTHAG5 161 547485 CAR395 5 161 1
03ALL | ERIS | Thermal | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | 29WP | T0 | P23:345:AECI:7BLACKBERRY:653::: | B | 956 | 64.1049 | 106.5956 |  |  |  | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
03ALL | ERIS | Thermal | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | 29WP | T0 | P23:345:AECI:7BLACKBERRY:653::: | B | 956 | 64.1049 | 106.5956 |  |  |  | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
03ALL | ERIS | Thermal | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | 29WP | T0 | P23:345:AECI:7BLACKBERRY:653::: | B | 956 | 64.1049 | 106.5956 |  |  |  | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
03ALL | ERIS | Thermal | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | 29WP | T0 | P23:345:AECI:7BLACKBERRY:653::: | B | 956 | 64.4068 | 104.394 |  |  |  | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
03ALL | ERIS | Thermal | 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | 29WP | T0 | P23:345:AECI:7BLACKBERRY:6_3::: | B | 956 | 69.2507 | 105.9589 |  |  |  | Rebuild line 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1
03ALL | ERIS | Thermal | 532995 OTTRCRK4 138 533001 ALTOONA4 138 1 | 29WP | T0 | P12:345:WERE:NRSS-N345-345:EHV: | B | 111 | 77.5136 | 116.6599 |  |  |  | Rebuild line 532995 OTTRCRK4 138 533001 ALTOONA4 138 1
03ALL | ERIS | Thermal | 533238 EDWARVL3 115 533282 MUND 3 115 1 | 29WP | T0 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | B | 230 | 93.1526 | 102.2074 |  |  |  | Rebuild line 533238 EDWARVL3 115 533282 MUND 3 115 1
03ALL | ERIS | Thermal | 533583 BUTLERN2 69 533597 MIDIAN 2 69 1 | 29WP | T0 | P12:138:WERE:BUTL-MIDI-138:HV: | B | 57 | 72.1722 | 133.8619 |  |  |  | Rebuild line 533583 BUTLERN2 69 533597 MIDIAN 2 69 1
03ALL | ERIS | Thermal | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | 29WP | T0 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | B | 297 | 76.6176 | 175.5841 |  |  |  | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
03ALL | ERIS | Thermal | 541204 SMTHVL 5 161 541221 PLTCTY 5 161 1 | 29WP | T0 | Single 541203 NASHUA5 161 541204 SMTHVL5 161 1 | B | 297 | -5.6916 | 109.8349 |  |  |  | Rebuild line 541204 SMTHVL 5 161 541221 PLTCTY 5 161 1
03ALL | ERIS | Thermal | 547467 ORO110 5 161 547490 FIR417 5 161 1 | 29WP | T0 | Single 547476 ASB3495 161 547491 PUR4215 161 1 | B | 335 | 62.2904 | 111.6996 |  |  |  | Rebuild line 547467 ORO110 5 161 547490 FIR417 5 161 1
03ALL | ERIS | Thermal | 547476 ASB349 5 161 547477 CJ 366 5 161 1 | 29WP | T0 | Single 547476 ASB3495 161 547491 PUR4215 161 1 | B | 322 | 73.9867 | 125.5385 |  |  |  | Rebuild line 547476 ASB349 5 161 547477 CJ 366 5 161 1
03ALL | ERIS | Thermal | 547476 ASB349 5 161 547491 PUR421 5 161 1 | 29WP | T0 | Single 547476 ASB3495 161 547477 CJ3665 161 1 | B | 322 | 75.2881 | 121.7911 |  |  |  | Rebuild line 547476 ASB349 5 161 547491 PUR421 5 161 1
03ALL | ERIS | Thermal | 547477 CJ 366 5 161 547490 FIR417 5 161 1 | 29WP | T0 | Single 547476 ASB3495 161 547491 PUR4215 161 1 | B | 335 | 67.5513 | 117.0461 |  |  |  | Rebuild line 547477 CJ 366 5 161 547490 FIR417 5 161 1
03ALL | ERIS | Thermal | 547485 CAR395 5 161 547491 PUR421 5 161 1 | 29WP | T0 | Single 547476 ASB3495 161 547477 CJ3665 161 1 | B | 335 | 70.3053 | 114.965 |  |  |  | Rebuild line 547485 CAR395 5 161 547491 PUR421 5 161 1
03ALL | ERIS | Thermal | 301402 5LOSTVALY 161 505502 TRUMAN 5 161 1 | 29WP | T1 | System Intact | A | 278 | 87.8144 | 103.0727 |  |  |  | Rebuild line 301402 5LOSTVALY 161 505502 TRUMAN 5 161 1
03ALL | ERIS | Thermal | 505488 CARTHAG5 161 547485 CAR395 5 161 1 | 29WP | T1 | Single 547476 ASB3495 161 547477 CJ3665 161 1 | B | 364 | 62.5467 | 104.8704 |  |  |  | Rebuild line 505488 CARTHAG5 161 547485 CAR395 5 161 1
03ALL | ERIS | Thermal | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | 29WP | T1 | P23:345:AECI:7BLACKBERRY:653::: | B | 956 | 64.0883 | 106.2154 |  |  |  | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
03ALL | ERIS | Thermal | 533243 JAGGARD3 115 533261 PENTAGN3 115 1 | 29WP | T1 | P23:345:WERE:STRA-345-643:::EHV: | B | 260 | 64.7663 | 109.1652 |  |  |  | Rebuild line 533243 JAGGARD3 115 533261 PENTAGN3 115 1
03ALL | ERIS | Thermal | 547467 ORO110 5 161 547494 OAK432 5 161 1 | 29WP | T1 | Single 547476 ASB3495 161 547491 PUR4215 161 1 | B | 335 | 90.7536 | 101.6854 |  |  |  | Rebuild line 547467 ORO110 5 161 547494 OAK432 5 161 1
03ALL | ERIS | Voltage | DVRSION-WIND | 26SP | V | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 |  |  |  |  | 1.0725 | 0.92 | 1.05 | None
03ALL | ERIS | Voltage | BURLNGTNJCT2 | 29SP | V | P55:345:OPPD:S3458 3::FN13:EHV: |  |  |  |  | 0.91126 | 0.93 | 1.05 | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
03ALL | ERIS | Voltage | BURLNGTNJCT2 | 29SP | V | P55:345:OPPD:S3458 3::FN13:EHV: |  |  |  |  | 0.91126 | 0.93 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | DVRSION-WIND | 29SP | V | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 |  |  |  |  | 1.0705 | 0.92 | 1.05 | None
03ALL | ERIS | Voltage | FAIRFAX2 | 29SP | V | P55:345:OPPD:S3458 3::FN13:EHV: |  |  |  |  | 0.90024 | 0.93 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | FILLMORE_TP2 | 29SP | V | P55:345:OPPD:S3458 3::FN13:EHV: |  |  |  |  | 0.92111 | 0.93 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | FILMORE2 | 29SP | V | P55:345:OPPD:S3458 3::FN13:EHV: |  |  |  |  | 0.91988 | 0.93 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | G20-094-TAP | 29SP | V | P55:345:OPPD:S3458 3::FN13:EHV: |  |  |  |  | 0.94764 | 0.95 | 1.05 | None
03ALL | ERIS | Voltage | GEN-2020-094 | 29SP | V | P55:345:OPPD:S3458 3::FN13:EHV: |  |  |  |  | 0.94764 | 0.95 | 1.05 | None
03ALL | ERIS | Voltage | HUMBOLT5 | 29SP | V | P55:345:OPPD:S3458 3::FN13:EHV: |  |  |  |  | 0.93682 | 0.95 | 1.05 | Add 16 MVAR switched shunt at HUMBOLT5 161 kV
03ALL | ERIS | Voltage | HUMBOLT5 | 29SP | V | P55:345:OPPD:S3458 3::FN13:EHV: |  |  |  |  | 0.93682 | 0.95 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | MRVL#2 | 29SP | V | P55:345:OPPD:S3458 3::FN13:EHV: |  |  |  |  | 0.92174 | 0.93 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | NC1HS 5 | 29SP | V | P55:345:OPPD:S3458 3::FN13:EHV: |  |  |  |  | 0.94039 | 0.95 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | NC2HS 5 | 29SP | V | P55:345:OPPD:S3458 3::FN13:EHV: |  |  |  |  | 0.94039 | 0.95 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | NP-GLAZIR_G2 | 29SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.67076 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | NP-LIPSCOMB2 | 29SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.62964 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | NP-LIPS_SHA2 | 29SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.62964 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | NP-LUCKY_CR2 | 29SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.76718 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | NP-LUCKY_G 2 | 29SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.76734 | 0.9 | 1.05 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
03ALL | ERIS | Voltage | NP-SHATTUCK2 | 29SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.60679 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | NP-SUB_A 2 | 29SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.83786 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | NP-VALERO_P2 | 29SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 0.63826 | 0.9 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | NTHWARD2 | 29SP | V | P55:345:OPPD:S3458 3::FN13:EHV: |  |  |  |  | 0.90006 | 0.93 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | NTHWARD2 | 29SP | V | P55:345:OPPD:S3458 3::FN13:EHV: |  |  |  |  | 0.90006 | 0.93 | 1.05 | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
03ALL | ERIS | Voltage | PICKRG_2 | 29SP | V | P55:345:OPPD:S3458 3::FN13:EHV: |  |  |  |  | 0.9173 | 0.93 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | PICKRG_TP_2 | 29SP | V | P55:345:OPPD:S3458 3::FN13:EHV: |  |  |  |  | 0.92124 | 0.93 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | S1258 5 | 29SP | V | P55:345:OPPD:S3458 3::FN13:EHV: |  |  |  |  | 0.94039 | 0.95 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | S1263 5 | 29SP | V | P55:345:OPPD:S3458 3::FN13:EHV: |  |  |  |  | 0.93681 | 0.95 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | S1263 5 | 29SP | V | P55:345:OPPD:S3458 3::FN13:EHV: |  |  |  |  | 0.93681 | 0.95 | 1.05 | Add 21 MVAR switched shunt at S1263 5 161 kV
03ALL | ERIS | Voltage | S1280 5 | 29SP | V | P55:345:OPPD:S3458 3::FN13:EHV: |  |  |  |  | 0.94289 | 0.95 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | S1398 5 | 29SP | V | P55:345:OPPD:S3458 3::FN13:EHV: |  |  |  |  | 0.9402 | 0.95 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | TARKIO_2 | 29SP | V | P55:345:OPPD:S3458 3::FN13:EHV: |  |  |  |  | 0.90105 | 0.93 | 1.05 | Mitigated at another bus
03ALL | ERIS | Voltage | DVRSION-WIND | 29WP | V | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 |  |  |  |  | 1.0697 | 0.92 | 1.05 | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 515012 RVRVALY7 345 780360 G24-113-TAP 345 1 | [7 empty] | Add line 515012 RVRVALY7 345 780360 G24-113-TAP 345 P2
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | [7 empty] | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | [7 empty] | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | [7 empty] | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | [7 empty] | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | [7 empty] | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | [7 empty] | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | [7 empty] | DIS2301-1_G03_ERIS_TurnOffReactors_Carpenter_Finney.idv : Switch out Carpenter 25 MVAR line reactor on the Carpenter to Hitchland 345 kV line
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | [7 empty] | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | [7 empty] | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | [7 empty] | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | [7 empty] | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | [7 empty] | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | [7 empty] | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P42:345:NPPD:BKR-AXT-3306:::: | [7 empty] | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P42:345:NPPD:BKR-AXT-3306:::: | [7 empty] | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P42:345:NPPD:BKR-AXT-3306:::: | [7 empty] | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P42:345:NPPD:BKR-MAC-3304:::: | [7 empty] | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P42:345:NPPD:BKR-MAC-3304:::: | [7 empty] | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P42:345:NPPD:BKR-MAC-3304:::: | [7 empty] | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 530583 POSTROCK7 345 640527 MACON3 345 1 | [7 empty] | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 530583 POSTROCK7 345 640527 MACON3 345 1 | [7 empty] | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 530583 POSTROCK7 345 640527 MACON3 345 1 | [7 empty] | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | [7 empty] | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | [7 empty] | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | [7 empty] | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | [7 empty] | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | [7 empty] | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | [7 empty] | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 640065 AXTELL3 345 640527 MACON3 345 1 | [7 empty] | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P23:345:ITCGP:SV_BRK388:::EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 515012 RVRVALY7 345 515302 FTSMITH7 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P42:345:OKGE:SB_FTTH7386:::EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P23:345:WERE:WICH-345-50:EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P23:345:SUNC:HLC_BRK282:::EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P23:345:SUNC:HLC_BRK188:::EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P12:345:WERE:RENO-WICH-345:EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P23:115-345:SUNC:MO_BRK188:::HV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P42:345:SPS:CARPENTER-OR335:::EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P42:345:OKGE:SB_DGSE7313:::EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P23:345:SUNC:SB_BRK482:::EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 26SP | N1 | P42:345:OKGE:SB_DGSE7313:::EHV: | [7 empty] | None
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | [7 empty] | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | [7 empty] | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | [7 empty] | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | [7 empty] | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | [7 empty] | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | [7 empty] | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P42:345:NPPD:BKR-AXT-3306:::: | [7 empty] | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P42:345:NPPD:BKR-AXT-3306:::: | [7 empty] | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P42:345:NPPD:BKR-AXT-3306:::: | [7 empty] | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P23:345:SUNC:SB_BRK482:::EHV: | [7 empty] | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P23:345:SUNC:SB_BRK482:::EHV: | [7 empty] | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P23:345:SUNC:SB_BRK482:::EHV: | [7 empty] | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P51:13:WERE:EMPEC 7:EHV: | [7 empty] | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P51:13:WERE:EMPEC 7:EHV: | [7 empty] | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P51:13:WERE:EMPEC 7:EHV: | [7 empty] | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P51:13:WERE:EMPEC 7:EHV: | [7 empty] | DIS2301-1_G03_ERIS_TurnOffReactors_Carpenter_Finney.idv : Switch out Carpenter 25 MVAR line reactor on the Carpenter to Hitchland 345 kV line
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | [7 empty] | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | [7 empty] | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | [7 empty] | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | [7 empty] | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | [7 empty] | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | [7 empty] | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 539805 ELMCREEK7 345 640600 DAYKIN3 345 1 | [7 empty] | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | [7 empty] | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | [7 empty] | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | [7 empty] | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | [7 empty] | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
04ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P23:115-345:SUNC:MO_BRK188:::HV: | [7 empty] | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
04ALL | ERIS | Thermal | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | 26SP | T0 | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | B | 157 | 102.2765 | 177.0636 |  |  |  | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
04ALL | ERIS | Thermal | 505600 TUPELO 4 138 505602 S BROWN4 138 1 | 26SP | T0 | Single 520918 FROGVIL4 138 773820 G23-092-TAP 138 1 | B | 147 | 51.4263 | 106.4089 |  |  |  | Rebuild line 505600 TUPELO 4 138 505602 S BROWN4 138 1
04ALL | ERIS | Thermal | 505602 S BROWN4 138 769060 G22-104-TAP 138 1 | 26SP | T0 | Single 520918 FROGVIL4 138 773820 G23-092-TAP 138 1 | B | 287 | 65.2766 | 103.4164 |  |  |  | Rebuild line 505602 S BROWN4 138 769060 G22-104-TAP 138 1
04ALL | ERIS | Thermal | 507454 TURK 4 138 3WXFMR 520:TURK 2 138 1 | 26SP | T0 | Single 338875 3PATMOS.W# 115 503912 FULTON3 115 1 | B | 177 | 38.5199 | 105.2371 |  |  |  | 2023ITP PORTFOLIO - REPLACE TURK 138_115 KV CKT 1 XFMR.idv : 2023 ITP upgrade, PID : 92976, NTC, ISD : 4/25/2027
04ALL | ERIS | Thermal | 507456 TURK 3 115 3WXFMR 520:TURK 2 138 1 | 26SP | T0 | Single 338875 3PATMOS.W# 115 503912 FULTON3 115 1 | B | 177 | 38.6389 | 105.2371 |  |  |  | 2023ITP PORTFOLIO - REPLACE TURK 138_115 KV CKT 1 XFMR.idv : 2023 ITP upgrade, PID : 92976, NTC, ISD : 4/25/2027
04ALL | ERIS | Thermal | 508055 BLOOMBG2 69 783570 G24-220-TAP 69 1 | 26SP | T0 | Single 508814 RODESSA2 69 783570 G24-220-TAP 69 1 | B | 53 | -1.1812 | 101.6598 |  |  |  | Rebuild line 508055 BLOOMBG2 69 783570 G24-220-TAP 69 1
04ALL | ERIS | Thermal | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 26SP | T0 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | B | 1000 | 95.2447 | 116.8554 |  |  |  | Rebuild line 508359 WELSH 7 345 508841 WILKES 7 345 1
04ALL | ERIS | Thermal | 508804 HOSSTON2 69 508846 GODFREYRDTP2 69 1 | 26SP | T0 | P12:69:AEPW:WATLANT2:LINDEN 2::: | B | 53 | 11.4987 | 110.5579 |  |  |  | Rebuild line 508804 HOSSTON2 69 508846 GODFREYRDTP2 69 1
04ALL | ERIS | Thermal | 508806 LIEBERM4 138 780630 G24-122-TAP 138 1 | 26SP | T0 | P23:345:AEPW:LONGWOOD CB 1N60 NBTB:::: | B | 162 | 59.7388 | 142.1541 |  |  |  | Rebuild line 508806 LIEBERM4 138 780630 G24-122-TAP 138 1
04ALL | ERIS | Thermal | 508814 RODESSA2 69 508846 GODFREYRDTP2 69 1 | 26SP | T0 | P12:69:AEPW:WATLANT2:LINDEN 2::: | B | 53 | 12.6471 | 113.2563 |  |  |  | Rebuild line 508814 RODESSA2 69 508846 GODFREYRDTP2 69 1
04ALL | ERIS | Thermal | 508814 RODESSA2 69 783570 G24-220-TAP 69 1 | 26SP | T0 | P12:69:AEPW:WATLANT2:LINDEN 2::: | B | 53 | 23.0503 | 124.1415 |  |  |  | Rebuild line 508814 RODESSA2 69 783570 G24-220-TAP 69 1
04ALL | ERIS | Thermal | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | 26SP | T0 | Single 515012 RVRVALY7 345 515302 FTSMITH7 345 1 | B | 1059 | 74.2687 | 105.0075 |  |  |  | Rebuild line 509745 CLARKSV7 345 515224 MUSKOGE7 345 1
04ALL | ERIS | Thermal | 509770 LLAN WT4 138 509803 DAWSONT4 138 1 | 26SP | T0 | Single 509790 CATOOSA4 138 509804 E11THST4 138 1 | B | 187 | 80.4568 | 129.7618 |  |  |  | Rebuild line 509770 LLAN WT4 138 509803 DAWSONT4 138 1
04ALL | ERIS | Thermal | 509770 LLAN WT4 138 509804 E 11TH ST 4 138 1 | 26SP | T0 | Single 509790 CATOOSA4 138 509804 E11THST4 138 1 | B | 187 | 86.4595 | 135.7637 |  |  |  | Rebuild line 509770 LLAN WT4 138 509804 E 11TH ST 4 138 1
04ALL | ERIS | Thermal | 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1 | 26SP | T0 | P12:345:EES:CHAMSPR7!:CLARKSV7!:1:EHV: | B | 235 | 96.4809 | 174.4925 |  |  |  | Rebuild line 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1
04ALL | ERIS | Thermal | 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | 26SP | T0 | Single 509790 CATOOSA4 138 512636 CATSAGR4 138 Z1 | B | 188 | 59.9482 | 115.0684 |  |  |  | Rebuild line 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1
04ALL | ERIS | Thermal | 509792 DAWSON-4 138 509803 DAWSONT4 138 1 | 26SP | T0 | Single 509790 CATOOSA4 138 509804 E11THST4 138 1 | B | 187 | 69.8219 | 119.0915 |  |  |  | Rebuild line 509792 DAWSON-4 138 509803 DAWSONT4 138 1
04ALL | ERIS | Thermal | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | 26SP | T0 | System Intact | A | 1011 | 80.2566 | 107.7039 |  |  |  | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
04ALL | ERIS | Thermal | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | 26SP | T0 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | B | 829 | 111.9819 | 157.3662 |  |  |  | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
04ALL | ERIS | Thermal | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | 26SP | T0 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | B | 829 | 111.9819 | 157.3662 |  |  |  | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
04ALL | ERIS | Thermal | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | 26SP | T0 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | B | 829 | 111.9819 | 157.3662 |  |  |  | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
04ALL | ERIS | Thermal | 510422 COFFEYT4 138 533002 DEARING4 138 1 | 26SP | T0 | P23:345:WERE:N345-345-20:EHV: | B | 478 | 68.7316 | 114.9546 |  |  |  | Rebuild line 510422 COFFEYT4 138 533002 DEARING4 138 1
04ALL | ERIS | Thermal | 512623 CATSAGD4 138 3WXFMR 523:CATAUTO1 138 1 | 26SP | T0 | Single 509790 CATOOSA4 138 512636 CATSAGR4 138 Z1 | B | 188 | 59.884 | 114.3439 |  |  |  | Add 3-winding transformer 512623 CATSAGD4 138 512638 CATSAGR5 161 512833 CATTER1 1 13 M2
04ALL | ERIS | Thermal | 512636 CATSAGR4 138 3WXFMR 523:CATAUTO2 138 2 | 26SP | T0 | Single 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | B | 188 | 60.0679 | 114.6833 |  |  |  | Add 3-winding transformer 512636 CATSAGR4 138 512638 CATSAGR5 161 512834 CATTER2 1 13 M2
04ALL | ERIS | Thermal | 512638 CATSAGR5 161 3WXFMR 523:CATAUTO1 138 1 | 26SP | T0 | Single 509790 CATOOSA4 138 512636 CATSAGR4 138 Z1 | B | 188 | 59.9811 | 114.3095 |  |  |  | Add 3-winding transformer 512623 CATSAGD4 138 512638 CATSAGR5 161 512833 CATTER1 1 13 M2
04ALL | ERIS | Thermal | 512638 CATSAGR5 161 3WXFMR 523:CATAUTO2 138 2 | 26SP | T0 | Single 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | B | 188 | 60.1602 | 114.6349 |  |  |  | Add 3-winding transformer 512636 CATSAGR4 138 512638 CATSAGR5 161 512834 CATTER2 1 13 M2
04ALL | ERIS | Thermal | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | 26SP | T0 | P23:345:WERE:N345-345-20:EHV: | B | 1195 | 68.2307 | 115.6656 |  |  |  | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
04ALL | ERIS | Thermal | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | 26SP | T0 | P23:345:WERE:N345-345-20:EHV: | B | 1055 | 55.4379 | 108.8315 |  |  |  | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
04ALL | ERIS | Thermal | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 | 26SP | T0 | P42:345:OKGE:SB_DGSE7313:::EHV: | B | 1015 | 61.3384 | 102.04 |  |  |  | Rebuild line 514715 WOODRNG7 345 515875 REDNGTN7 345 1
04ALL | ERIS | Thermal | 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 | 26SP | T0 | System Intact | A | 194 | 86.5388 | 127.5435 |  |  |  | Rebuild line 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1
04ALL | ERIS | Thermal | 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 | 26SP | T0 | System Intact | A | 194 | 83.6195 | 124.6163 |  |  |  | Rebuild line 514759 NEWKIRK4 138 515381 PECKHMT4 138 1
04ALL | ERIS | Thermal | 514760 KILDARE4 138 514764 NWKRKAT4 138 1 | 26SP | T0 | System Intact | A | 194 | 90.3929 | 131.4149 |  |  |  | Rebuild line 514760 KILDARE4 138 514764 NWKRKAT4 138 1
04ALL | ERIS | Thermal | 514804 MIDLTNT4 138 515381 PECKHMT4 138 1 | 26SP | T0 | System Intact | A | 194 | 81.5269 | 122.5161 |  |  |  | Rebuild line 514804 MIDLTNT4 138 515381 PECKHMT4 138 1
04ALL | ERIS | Thermal | 514804 MIDLTNT4 138 532981 CRESWLN4 138 1 | 26SP | T0 | System Intact | A | 194 | 92.1039 | 132.8517 |  |  |  | Rebuild line 514804 MIDLTNT4 138 532981 CRESWLN4 138 1
04ALL | ERIS | Thermal | 515055 MAUD 4 138 787770 G24-360-TAP 138 1 | 26SP | T0 | P12:138:OKGE:BKRBKR2170:::HV: | B | 287 | 86.1345 | 114.0688 |  |  |  | Rebuild line 515055 MAUD 4 138 787770 G24-360-TAP 138 1
04ALL | ERIS | Thermal | 515301 FTSMTHW5 161 3WXFMR 524:524:FTSMITH5 345 5 | 26SP | T0 | P12:345:EES:FTSMITH7%:FTSMITH8%:FTSMTH111:EHV: | B | 493 | 73.4923 | 126.769 |  |  |  | Add 3-winding transformer 515301 FTSMTHW5 161 515302 FTSMITH7 345 515728 FTSMTH51 13 M2
04ALL | ERIS | Thermal | 515302 FTSMITH7 345 3WXFMR 524:524:FTSMITH1 500 1 | 26SP | T0 | P12:161:EES:FTSMTHW5%:FTSMITH7%:FTSMTH511:HV: | B | 693 | 59.5113 | 107.4747 |  |  |  | Add 3-winding transformer 515302 FTSMITH7 345 515305 FTSMITH8 500 515726 FTSMTH11 13 M2
04ALL | ERIS | Thermal | 515302 FTSMITH7 345 3WXFMR 524:524:FTSMITH5 345 5 | 26SP | T0 | P12:345:EES:FTSMITH7%:FTSMITH8%:FTSMTH111:EHV: | B | 493 | 73.4923 | 126.769 |  |  |  | Add 3-winding transformer 515301 FTSMTHW5 161 515302 FTSMITH7 345 515728 FTSMTH51 13 M2
04ALL | ERIS | Thermal | 515305 FTSMITH8 500 3WXFMR 524:524:FTSMITH1 500 1 | 26SP | T0 | P12:161:EES:FTSMTHW5%:FTSMITH7%:FTSMTH511:HV: | B | 693 | 59.7548 | 108.5609 |  |  |  | Add 3-winding transformer 515302 FTSMITH7 345 515305 FTSMITH8 500 515726 FTSMTH11 13 M2
04ALL | ERIS | Thermal | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 26SP | T0 | System Intact | A | 1075 | 79.5184 | 114.6214 |  |  |  | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1
04ALL | ERIS | Thermal | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | 26SP | T0 | System Intact | A | 827 | 78.9507 | 107.8643 |  |  |  | Rebuild line 532791 BENTON 7 345 532794 ROSEHIL7 345 1
04ALL | ERIS | Thermal | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | 26SP | T0 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | B | 829 | 111.8845 | 177.0235 |  |  |  | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
04ALL | ERIS | Thermal | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 26SP | T0 | System Intact | A | 1806 | 83.3625 | 104.7272 |  |  |  | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1
04ALL | ERIS | Thermal | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 26SP | T0 | System Intact | A | 1075 | 79.5099 | 114.6025 |  |  |  | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
04ALL | ERIS | Thermal | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | 26SP | T1 | System Intact | A | 829 | 76.7557 | 103.0993 |  |  |  | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
04ALL | ERIS | Thermal | 334197 7ROCKYCRK% 345 783930 G24-232-TAP 345 1 | 29SP | T0 | P11:18:EES:1J472MCPS G2:1::EHV: | B | 1193 | 90.7127 | 101.2 |  |  |  | Rebuild line 334197 7ROCKYCRK% 345 783930 G24-232-TAP 345 1
04ALL | ERIS | Thermal | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | 29SP | T0 | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | B | 157 | 117.1986 | 185.7511 |  |  |  | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
04ALL | ERIS | Thermal | 505600 TUPELO 4 138 505602 S BROWN4 138 1 | 29SP | T0 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | B | 147 | 66.7246 | 105.0878 |  |  |  | Rebuild line 505600 TUPELO 4 138 505602 S BROWN4 138 1
04ALL | ERIS | Thermal | 508055 BLOOMBG2 69 783570 G24-220-TAP 69 1 | 29SP | T0 | Single 508814 RODESSA2 69 783570 G24-220-TAP 69 1 | B | 53 | -1.1858 | 101.9287 |  |  |  | Rebuild line 508055 BLOOMBG2 69 783570 G24-220-TAP 69 1
04ALL | ERIS | Thermal | 508806 LIEBERM4 138 780630 G24-122-TAP 138 1 | 29SP | T0 | P42:345:AEPW:WILKES CB 1W10 NBTB+FAULT:::: | B | 162 | 91.0839 | 160.6045 |  |  |  | Rebuild line 508806 LIEBERM4 138 780630 G24-122-TAP 138 1
04ALL | ERIS | Thermal | 508814 RODESSA2 69 508846 GODFREYRDTP2 69 1 | 29SP | T0 | P12:69:AEPW:WATLANT2:LINDEN 2::: | B | 53 | 3.7572 | 101.8575 |  |  |  | Rebuild line 508814 RODESSA2 69 508846 GODFREYRDTP2 69 1
04ALL | ERIS | Thermal | 508814 RODESSA2 69 783570 G24-220-TAP 69 1 | 29SP | T0 | P12:69:AEPW:WATLANT2:LINDEN 2::: | B | 53 | 13.963 | 112.112 |  |  |  | Rebuild line 508814 RODESSA2 69 783570 G24-220-TAP 69 1
04ALL | ERIS | Thermal | 509770 LLAN WT4 138 509803 DAWSONT4 138 1 | 29SP | T0 | Single 509790 CATOOSA4 138 509804 E11THST4 138 1 | B | 187 | 79.9897 | 127.2777 |  |  |  | Rebuild line 509770 LLAN WT4 138 509803 DAWSONT4 138 1
04ALL | ERIS | Thermal | 509770 LLAN WT4 138 509804 E 11TH ST 4 138 1 | 29SP | T0 | Single 509790 CATOOSA4 138 509804 E11THST4 138 1 | B | 187 | 85.8872 | 133.1826 |  |  |  | Rebuild line 509770 LLAN WT4 138 509804 E 11TH ST 4 138 1
04ALL | ERIS | Thermal | 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1 | 29SP | T0 | P12:345:EES:CHAMSPR7!:CLARKSV7!:1:EHV: | B | 235 | 101.4854 | 175.9265 |  |  |  | Rebuild line 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1
04ALL | ERIS | Thermal | 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | 29SP | T0 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | B | 188 | 108.4559 | 190.5992 |  |  |  | Rebuild line 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1
04ALL | ERIS | Thermal | 509790 CATOOSA4 138 512636 CATSAGR4 138 Z1 | 29SP | T0 | Single 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | B | 218 | 65.5018 | 110.4083 |  |  |  | Rebuild line 509790 CATOOSA4 138 512636 CATSAGR4 138 Z1
04ALL | ERIS | Thermal | 509792 DAWSON-4 138 509803 DAWSONT4 138 1 | 29SP | T0 | Single 509790 CATOOSA4 138 509804 E11THST4 138 1 | B | 187 | 69.5257 | 116.7873 |  |  |  | Rebuild line 509792 DAWSON-4 138 509803 DAWSONT4 138 1
04ALL | ERIS | Thermal | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | 29SP | T0 | System Intact | A | 1011 | 84.5944 | 106.9293 |  |  |  | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
04ALL | ERIS | Thermal | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | 29SP | T0 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | B | 829 | 121.9178 | 155.6146 |  |  |  | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
04ALL | ERIS | Thermal | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | 29SP | T0 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | B | 829 | 121.9178 | 155.6146 |  |  |  | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
04ALL | ERIS | Thermal | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | 29SP | T0 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | B | 829 | 121.9178 | 155.6146 |  |  |  | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
04ALL | ERIS | Thermal | 510422 COFFEYT4 138 533002 DEARING4 138 1 | 29SP | T0 | P23:345:WERE:N345-345-20:EHV: | B | 478 | 78.2632 | 115.247 |  |  |  | Rebuild line 510422 COFFEYT4 138 533002 DEARING4 138 1
04ALL | ERIS | Thermal | 512636 CATSAGR4 138 3WXFMR 523:CATAUTO2 138 2 | 29SP | T0 | Single 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | B | 188 | 76.0564 | 127.8636 |  |  |  | Add 3-winding transformer 512636 CATSAGR4 138 512638 CATSAGR5 161 512834 CATTER2 1 13 M2
04ALL | ERIS | Thermal | 512638 CATSAGR5 161 3WXFMR 523:CATAUTO2 138 2 | 29SP | T0 | Single 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | B | 188 | 76.0603 | 127.7708 |  |  |  | Add 3-winding transformer 512636 CATSAGR4 138 512638 CATSAGR5 161 512834 CATTER2 1 13 M2
04ALL | ERIS | Thermal | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | 29SP | T0 | P23:345:WERE:N345-345-20:EHV: | B | 1195 | 62.2818 | 106.3738 |  |  |  | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
04ALL | ERIS | Thermal | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | 29SP | T0 | P23:345:WERE:N345-345-20:EHV: | B | 1055 | 57.8302 | 108.4042 |  |  |  | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
04ALL | ERIS | Thermal | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 | 29SP | T0 | P42:345:OKGE:SB_DGSE7313:::EHV: | B | 1015 | 68.9336 | 102.2256 |  |  |  | Rebuild line 514715 WOODRNG7 345 515875 REDNGTN7 345 1
04ALL | ERIS | Thermal | 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 | 29SP | T0 | System Intact | A | 194 | 94.4278 | 127.5714 |  |  |  | Rebuild line 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1
04ALL | ERIS | Thermal | 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 | 29SP | T0 | System Intact | A | 194 | 91.6389 | 124.7711 |  |  |  | Rebuild line 514759 NEWKIRK4 138 515381 PECKHMT4 138 1
04ALL | ERIS | Thermal | 514760 KILDARE4 138 514764 NWKRKAT4 138 1 | 29SP | T0 | System Intact | A | 194 | 98.3959 | 131.5644 |  |  |  | Rebuild line 514760 KILDARE4 138 514764 NWKRKAT4 138 1
04ALL | ERIS | Thermal | 514804 MIDLTNT4 138 515381 PECKHMT4 138 1 | 29SP | T0 | System Intact | A | 194 | 89.4863 | 122.6094 |  |  |  | Rebuild line 514804 MIDLTNT4 138 515381 PECKHMT4 138 1
04ALL | ERIS | Thermal | 514804 MIDLTNT4 138 532981 CRESWLN4 138 1 | 29SP | T0 | System Intact | A | 194 | 99.7283 | 132.7096 |  |  |  | Rebuild line 514804 MIDLTNT4 138 532981 CRESWLN4 138 1
04ALL | ERIS | Thermal | 515055 MAUD 4 138 787770 G24-360-TAP 138 1 | 29SP | T0 | P12:138:OKGE:BKRBKR2170:::HV: | B | 287 | 90.2982 | 115.6328 |  |  |  | Rebuild line 515055 MAUD 4 138 787770 G24-360-TAP 138 1
04ALL | ERIS | Thermal | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | 29SP | T0 | System Intact | A | 1075 | 87.2875 | 114.5102 |  |  |  | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1
04ALL | ERIS | Thermal | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | 29SP | T0 | System Intact | A | 827 | 88.1872 | 113.506 |  |  |  | Rebuild line 532791 BENTON 7 345 532794 ROSEHIL7 345 1
04ALL | ERIS | Thermal | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | 29SP | T0 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | B | 829 | 121.8412 | 175.0352 |  |  |  | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
04ALL | ERIS | Thermal | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 29SP | T0 | System Intact | A | 1806 | 87.8242 | 104.7927 |  |  |  | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1
04ALL | ERIS | Thermal | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | 29SP | T0 | System Intact | A | 1075 | 87.25 | 114.4362 |  |  |  | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
04ALL | ERIS | Thermal | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 29SP | T0 | System Intact | A | 717 | 83.1459 | 102.1682 |  |  |  | Rebuild line 541198 PECULR 7 345 541200 PHILL 7 345 1
04ALL | ERIS | Thermal | 509790 CATOOSA4 138 512636 CATSAGR4 138 Z1 | 29SP | T1 | Single 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | B | 272 | 59.0479 | 100.1562 |  |  |  | Rebuild line 509790 CATOOSA4 138 512636 CATSAGR4 138 Z1
04ALL | ERIS | Thermal | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | 29SP | T1 | System Intact | A | 829 | 84.1866 | 103.3038 |  |  |  | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
04ALL | ERIS | Thermal | 532768 EMPEC 7 345 776400 G23-221-TAP 345 1 | 29SP | T1 | System Intact | A | 1076 | 82.347 | 100.907 |  |  |  | Rebuild line 532768 EMPEC 7 345 776400 G23-221-TAP 345 1
04ALL | ERIS | Thermal | 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | 29SP | T1 | System Intact | A | 1076 | 82.3874 | 100.9112 |  |  |  | Rebuild line 532774 SWISVAL7 345 776380 G23-220-TAP 345 1
04ALL | ERIS | Thermal | 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | 29SP | T1 | System Intact | A | 1076 | 82.3521 | 100.9112 |  |  |  | Rebuild line 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1
04ALL | ERIS | Thermal | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | 29WP | T0 | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | B | 159 | 110.2281 | 184.4152 |  |  |  | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
04ALL | ERIS | Thermal | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 29WP | T0 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | B | 1220 | 90.8675 | 105.5159 |  |  |  | Rebuild line 508359 WELSH 7 345 508841 WILKES 7 345 1
04ALL | ERIS | Thermal | 508804 HOSSTON2 69 508846 GODFREYRDTP2 69 1 | 29WP | T0 | P12:69:AEPW:WATLANT2:LINDEN 2::: | B | 53 | 24.5246 | 120.2355 |  |  |  | Rebuild line 508804 HOSSTON2 69 508846 GODFREYRDTP2 69 1
04ALL | ERIS | Thermal | 508806 LIEBERM4 138 780630 G24-122-TAP 138 1 | 29WP | T0 | P23:345:AEPW:LONGWOOD CB 1N60 NBTB:::: | B | 183 | 69.7444 | 141.0502 |  |  |  | Rebuild line 508806 LIEBERM4 138 780630 G24-122-TAP 138 1
04ALL | ERIS | Thermal | 508814 RODESSA2 69 508846 GODFREYRDTP2 69 1 | 29WP | T0 | P12:69:AEPW:WATLANT2:LINDEN 2::: | B | 65 | 22.0863 | 100.3955 |  |  |  | Rebuild line 508814 RODESSA2 69 508846 GODFREYRDTP2 69 1
04ALL | ERIS | Thermal | 508814 RODESSA2 69 783570 G24-220-TAP 69 1 | 29WP | T0 | P12:69:AEPW:WATLANT2:LINDEN 2::: | B | 65 | 29.3121 | 107.6918 |  |  |  | Rebuild line 508814 RODESSA2 69 783570 G24-220-TAP 69 1
04ALL | ERIS | Thermal | 509770 LLAN WT4 138 509804 E 11TH ST 4 138 1 | 29WP | T0 | Single 509790 CATOOSA4 138 509804 E11THST4 138 1 | B | 211 | 57.8079 | 103.0073 |  |  |  | Rebuild line 509770 LLAN WT4 138 509804 E 11TH ST 4 138 1
04ALL | ERIS | Thermal | 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1 | 29WP | T0 | P12:345:EES:CHAMSPR7!:CLARKSV7!:1:EHV: | B | 293 | 72.7725 | 134.4196 |  |  |  | Rebuild line 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1
04ALL | ERIS | Thermal | 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | 29WP | T0 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | B | 188 | 123.5996 | 203.1414 |  |  |  | Rebuild line 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1
04ALL | ERIS | Thermal | 509790 CATOOSA4 138 512636 CATSAGR4 138 Z1 | 29WP | T0 | Single 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | B | 218 | 79.4889 | 124.6315 |  |  |  | Rebuild line 509790 CATOOSA4 138 512636 CATSAGR4 138 Z1
04ALL | ERIS | Thermal | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | 29WP | T0 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | B | 1324 | 87.5805 | 124.3274 |  |  |  | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
04ALL | ERIS | Thermal | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | 29WP | T0 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | B | 1324 | 80.4288 | 116.5975 |  |  |  | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
04ALL | ERIS | Thermal | 512636 CATSAGR4 138 3WXFMR 523:CATAUTO2 138 2 | 29WP | T0 | Single 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | B | 188 | 91.8754 | 143.4156 |  |  |  | Add 3-winding transformer 512636 CATSAGR4 138 512638 CATSAGR5 161 512834 CATTER2 1 13 M2
04ALL | ERIS | Thermal | 512638 CATSAGR5 161 3WXFMR 523:CATAUTO2 138 2 | 29WP | T0 | Single 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | B | 188 | 92.1069 | 143.3437 |  |  |  | Add 3-winding transformer 512636 CATSAGR4 138 512638 CATSAGR5 161 512834 CATTER2 1 13 M2
04ALL | ERIS | Thermal | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | 29WP | T0 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | B | 1195 | 66.2281 | 109.0559 |  |  |  | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
04ALL | ERIS | Thermal | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | 29WP | T0 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | B | 1182 | 57.0065 | 100.7917 |  |  |  | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
04ALL | ERIS | Thermal | 515055 MAUD 4 138 787770 G24-360-TAP 138 1 | 29WP | T0 | P12:138:OKGE:BKRBKR2170:::HV: | B | 287 | 79.4611 | 107.4306 |  |  |  | Rebuild line 515055 MAUD 4 138 787770 G24-360-TAP 138 1
04ALL | ERIS | Thermal | 515302 FTSMITH7 345 3WXFMR 524:524:FTSMITH1 500 1 | 29WP | T0 | Single 515302 FTSMITH7 345 515305 FTSMITH8 500 519010 'FTSMITH71 ' 13 2 | B | 693 | 77.1271 | 114.2948 |  |  |  | Add 3-winding transformer 515302 FTSMITH7 345 515305 FTSMITH8 500 515726 FTSMTH11 13 M2
04ALL | ERIS | Thermal | 515305 FTSMITH8 500 3WXFMR 524:524:FTSMITH1 500 1 | 29WP | T0 | Single 515302 FTSMITH7 345 515305 FTSMITH8 500 519010 'FTSMITH71 ' 13 2 | B | 693 | 77.5119 | 115.3188 |  |  |  | Add 3-winding transformer 515302 FTSMITH7 345 515305 FTSMITH8 500 515726 FTSMTH11 13 M2
04ALL | ERIS | Thermal | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | 29WP | T0 | Single 510380 DELWARE7 345 580555 MONETT345 345 1 | B | 956 | 62.7601 | 103.1002 |  |  |  | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
04ALL | ERIS | Thermal | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | 29WP | T1 | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | B | 297 | 63.8572 | 102.9874 |  |  |  | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
04ALL | ERIS | Thermal | 509790 CATOOSA4 138 512636 CATSAGR4 138 Z1 | 29WP | T1 | Single 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | B | 272 | 70.5338 | 112.6598 |  |  |  | Rebuild line 509790 CATOOSA4 138 512636 CATSAGR4 138 Z1
04ALL | ERIS | Voltage | 12MILE 4 | 26SP | V | P42:345:OKGE:SB_GRIN7382:::EHV: |  |  |  |  | 0.54335 | 0.92 | 1.05 | None
04ALL | ERIS | Voltage | 15THSTRT | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92083 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | 4CORNER3 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91849 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | 87TH 7 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.93521 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ADRIAN 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92823 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | ALTAMNS2 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.87826 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ALTAMNS2 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.87826 | 0.93 | 1.05 | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV
04ALL | ERIS | Voltage | ALTAMNT2 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.87114 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ALTOONA4 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.9052 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ANTIOCH5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90546 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | ASG-2018-011 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91815 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | ATLNTIC3 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91679 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | ATLNTIC7 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90497 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | AUBURN 6 | 26SP | V | P23:345:KCPL:LACYGNE-R2-5:::EHV: |  |  |  |  | 0.92997 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | AUR124 5 | 26SP | V | P23:345:AECI:7JASPER:1182::: |  |  |  |  | 0.91697 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | AUR124 5 | 26SP | V | P23:345:AECI:7JASPER:1182::: |  |  |  |  | 0.91697 | 0.925 | 1.05 | Add 0.04 MVAR switched shunt at AUR124 5 161 kV
04ALL | ERIS | Voltage | AVOCA 5 | 26SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.91867 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BEECRK4 | 26SP | V | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 |  |  |  |  | 0.92157 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BELTONS5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.9231 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | BENTLEY4 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90537 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BENTVJ_5 | 26SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.91906 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BENT_SL5 | 26SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.91928 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BIRDHOL4 | 26SP | V | Single 509752 INOLATP4 138 509790 CATOOSA4 138 1 |  |  |  |  | 0.91553 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BNSF 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.9263 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | BONITA 3 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91637 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | BRKRIDG5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91231 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | BUCYRUS5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90827 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | BUFFALO4 | 26SP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.92083 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | BUFFALO7 | 26SP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.91802 | 0.95 | 1.05 | Add 0.02 MVAR switched shunt at BUFFALO7 345 kV
04ALL | ERIS | Voltage | BUFFALO7 | 26SP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.91802 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BUNKRDG5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92915 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | BURNS 7 | 26SP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.91787 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | CANEYRV7 | 26SP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.92897 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | CANEYWF7 | 26SP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.92908 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | CARB-KW 3 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92628 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | CEDRCRK5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92248 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | CENTENL5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90426 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | CHAMSPR7 | 26SP | V | P23:345:GRDA:TONNECE CB9580:::EHV: |  |  |  |  | 0.91701 | 0.92 | 1.05 | Add 0.11 MVAR switched shunt at CHAMSPR7 345 kV
04ALL | ERIS | Voltage | CHAMSPR7 | 26SP | V | P23:345:GRDA:TONNECE CB9580:::EHV: |  |  |  |  | 0.91701 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | CHOUTEA4 | 26SP | V | Single 509752 INOLATP4 138 509790 CATOOSA4 138 1 |  |  |  |  | 0.86218 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | CLEARVW3 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92296 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | CLINTON5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91278 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | CNTRVIL5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.89462 | 0.93 | 1.05 | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
04ALL | ERIS | Voltage | COLLEGE5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91639 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | COOYYAH4 | 26SP | V | Single 509752 INOLATP4 138 509790 CATOOSA4 138 1 |  |  |  |  | 0.87785 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | COWSKIN 4 | 26SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.89765 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | COWSKIN2 | 26SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.89063 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | CPK446 5 | 26SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.91772 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | CPK446 5 | 26SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.91772 | 0.925 | 1.05 | Add 16 MVAR switched shunt at CPK446 5 161 kV
04ALL | ERIS | Voltage | CRAIG 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.9231 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | CRAIG 7 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92502 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | CRAIG_CAP 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92411 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | CRAWFOR2 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91899 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | DAD368 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91516 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | DAKOTA_5 | 26SP | V | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: |  |  |  |  | 0.91859 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | EAST ST3 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.86149 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | EDWRDVL5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92632 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | EEUREKA3 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90795 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | ELKRVR17 | 26SP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.92068 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | EUDORA 3 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92671 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | EXPCLAR4 | 26SP | V | Single 509752 INOLATP4 138 509790 CATOOSA4 138 1 |  |  |  |  | 0.87729 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | EXPED WF7 | 26SP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.92088 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | FINNEY 7 | 26SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 1.0551 | 0.9 | 1.05 | Add 23 MVAR switched shunt at FINNEY 7 345 kV
04ALL | ERIS | Voltage | FLORENC3 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.89521 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | FOREST 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92684 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | FR4 XMF1 345 | 26SP | V | P42:345:OKGE:SB_DGSE7313:::EHV: |  |  |  |  | 0.91417 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | FR4345KV-TAP | 26SP | V | P42:345:OKGE:SB_DGSE7313:::EHV: |  |  |  |  | 0.9141 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G15052_1 | 26SP | V | P42:345:OKGE:SB_DGSE7313:::EHV: |  |  |  |  | 0.87593 | 0.95 | 1.05 | Add 280 MVAR SVC at G15052_1 345 kV
04ALL | ERIS | Voltage | G15052_T | 26SP | V | P42:345:OKGE:SB_DGSE7313:::EHV: |  |  |  |  | 0.87593 | 0.95 | 1.05 | Add 45 MVAR SVC at G15052_T 345 kV
04ALL | ERIS | Voltage | G15052_T | 26SP | V | P42:345:OKGE:SB_DGSE7313:::EHV: |  |  |  |  | 0.87593 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G16-111-TAP | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.87098 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G16-111-TAP | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.87098 | 0.95 | 1.05 | Add 150 MVAR SVC at G16-111-TAP 345 kV
04ALL | ERIS | Voltage | G17-108-TAP | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91474 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | G18-128-TAP | 26SP | V | P42:345:OKGE:SB_DGSE7313:::EHV: |  |  |  |  | 0.88757 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G18-128-TAP | 26SP | V | P42:345:OKGE:SB_DGSE7313:::EHV: |  |  |  |  | 0.88757 | 0.95 | 1.05 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
04ALL | ERIS | Voltage | G20-007-TAP | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.8826 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G20-072-TAP | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92593 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | G20-073-TAP | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91747 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | G20-092-TAP | 26SP | V | Single 509752 INOLATP4 138 509790 CATOOSA4 138 1 |  |  |  |  | 0.91176 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G21-029-TAP | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.88054 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G21-096-TAP | 26SP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.92248 | 0.95 | 1.05 | None
04ALL | ERIS | Voltage | G22-007-TAP | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.86895 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | G22-013-TAP | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.88966 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G22-013-TAP | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.88966 | 0.95 | 1.05 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
04ALL | ERIS | Voltage | G23-220-TAP | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91876 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G23-220-TAP | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91876 | 0.95 | 1.05 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
04ALL | ERIS | Voltage | G23-221-TAP | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91876 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G24-076-TAP | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.89079 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G24-125-TAP | 26SP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.94281 | 0.95 | 1.05 | None
04ALL | ERIS | Voltage | G24-129-TAP | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.93555 | 0.95 | 1.05 | None
04ALL | ERIS | Voltage | G24-276-TAP | 26SP | V | P23:345:KCPL:LACYGNE-R2-5:::EHV: |  |  |  |  | 0.92971 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GARDNER5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91947 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | GATZ 2 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92721 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | GEARY 7 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.9323 | 0.95 | 1.05 | None
04ALL | ERIS | Voltage | GEN-2016-073 | 26SP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.92242 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2016-111 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.87179 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2017-022 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.9052 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2017-074 | 26SP | V | Single 509752 INOLATP4 138 509790 CATOOSA4 138 1 |  |  |  |  | 0.91545 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2017-077 | 26SP | V | Single 509752 INOLATP4 138 509790 CATOOSA4 138 1 |  |  |  |  | 0.87785 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2017-086 | 26SP | V | P42:345:OKGE:SB_DGSE7313:::EHV: |  |  |  |  | 0.9141 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2017-108 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91474 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | GEN-2017-195 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.89179 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2017-220 | 26SP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.91802 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2018-032 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91963 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2018-128 | 26SP | V | P42:345:OKGE:SB_DGSE7313:::EHV: |  |  |  |  | 0.88759 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2019-016 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91525 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2020-007 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.8826 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2020-057 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90497 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2020-058 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90497 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2020-072 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92593 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | GEN-2020-073 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91747 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | GEN-2020-092 | 26SP | V | Single 509752 INOLATP4 138 509790 CATOOSA4 138 1 |  |  |  |  | 0.91176 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2021-006 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91944 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2021-029 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.88054 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2021-030 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.88054 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2021-096 | 26SP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.92248 | 0.95 | 1.05 | None
04ALL | ERIS | Voltage | GEN-2021-103 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91679 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | GEN-2022-006 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92254 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | GEN-2022-007 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.86895 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | GEN-2022-013 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.88966 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2023-220 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91876 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2023-221 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91876 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2024-076 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.89328 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2024-125 | 26SP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.94306 | 0.95 | 1.05 | None
04ALL | ERIS | Voltage | GEN-2024-129 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.93575 | 0.95 | 1.05 | None
04ALL | ERIS | Voltage | GEN-2024-170 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91187 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2024-276 | 26SP | V | P23:345:KCPL:LACYGNE-R2-5:::EHV: |  |  |  |  | 0.92981 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2024-352 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.94146 | 0.95 | 1.05 | None
04ALL | ERIS | Voltage | GRDVWE 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92385 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | GROVE 4 | 26SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.89843 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GROVE 4 | 26SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.89843 | 0.92 | 1.05 | Add 24 MVAR switched shunt at GROVE 4 138 kV
04ALL | ERIS | Voltage | GROVE 5 | 26SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.90541 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GROVE 5 | 26SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.90541 | 0.92 | 1.05 | Add 0.2 MVAR switched shunt at GROVE 5 161 kV
04ALL | ERIS | Voltage | GUAVA 4 | 26SP | V | Single 509752 INOLATP4 138 509790 CATOOSA4 138 1 |  |  |  |  | 0.79862 | 0.92 | 1.05 | Add 57 MVAR switched shunt at GUAVA 4 138 kV
04ALL | ERIS | Voltage | HALSTD 4 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.88581 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | HALSTED2 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92877 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | HAWTH 7 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.94933 | 0.95 | 1.05 | None
04ALL | ERIS | Voltage | HESSTON2 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92223 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | HICKMAN5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91537 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | HONEYWL5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91664 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | HOOVER 4 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92568 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | HOYT 7 | 26SP | V | P23:345:KCPL:LACYGNE-R2-5:::EHV: |  |  |  |  | 0.9466 | 0.95 | 1.05 | None
04ALL | ERIS | Voltage | INDEPCO5 | 26SP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.91914 | 0.92 | 1.05 | Add 40 MVAR switched shunt at INDEPCO5 161 kV
04ALL | ERIS | Voltage | INDIAN_CK_5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91456 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | INOLA 4 | 26SP | V | Single 509752 INOLATP4 138 509790 CATOOSA4 138 1 |  |  |  |  | 0.79802 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | INOLATP4 | 26SP | V | Single 509752 INOLATP4 138 509790 CATOOSA4 138 1 |  |  |  |  | 0.79838 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | JADE 3 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.89206 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | JAY 4 | 26SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.90661 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | JAY 4 | 26SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.90661 | 0.92 | 1.05 | Add 0.02 MVAR switched shunt at JAY 4 138 kV
04ALL | ERIS | Voltage | JOP391 5 | 26SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.92395 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | KNLWRTH5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91368 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | LABETTE2 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.891 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LABETTS2 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.89308 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LABETTS2 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.89308 | 0.93 | 1.05 | Add 0.25 MVAR switched shunt at LABETTS2 69 kV
04ALL | ERIS | Voltage | LACKMAN5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90938 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | LACYGNE11_7 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.88286 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LACYGNE11_7 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.88286 | 0.95 | 1.05 | Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
04ALL | ERIS | Voltage | LACYGNE2 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.87052 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LACYGNE22_7 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.88286 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LACYGNE_LK2 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.86921 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LANG 3 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.86847 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | LANG 7 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.7895 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LENEXA 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92236 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | LIBERTY4 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91024 | 0.93 | 1.05 | Add 20 MVAR switched shunt at LIBERTY4 138 kV
04ALL | ERIS | Voltage | LIBERTY4 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91024 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | MARMTNE5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92251 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | MARMTNW5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92243 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | MARTCIT5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.9138 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | MARTCTY5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91671 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | MCARBDE4 | 26SP | V | Single 509752 INOLATP4 138 509790 CATOOSA4 138 1 |  |  |  |  | 0.89994 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | MERRIAM5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92228 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | MERRIAM_CAP5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92329 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | MIDLAND6 | 26SP | V | P23:345:KCPL:LACYGNE-R2-5:::EHV: |  |  |  |  | 0.94979 | 0.95 | 1.05 | None
04ALL | ERIS | Voltage | MISNJCT5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91382 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | MON383 5 | 26SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.92227 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | MONTGOM4 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91392 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | MOONLIT3 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92134 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | MOONLT 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91947 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | MORRIS 7 | 26SP | V | P23:345:KCPL:LACYGNE-R2-5:::EHV: |  |  |  |  | 0.94653 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | MOUND 2 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91881 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | MOUND 4 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.87335 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | MOUND 4 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.87335 | 0.93 | 1.05 | Add 0.02 MVAR switched shunt at MOUND 4 138 kV
04ALL | ERIS | Voltage | MURLEN 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90747 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | NEASTOTTW5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91571 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | NEO SPA5 | 26SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.9185 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NEO184 5 | 26SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.9161 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NEO184 5 | 26SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.9161 | 0.925 | 1.05 | Add 15 MVAR switched shunt at NEO184 5 161 kV
04ALL | ERIS | Voltage | NEOSHO 4 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.88168 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NEOSHO 4 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.88168 | 0.93 | 1.05 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
04ALL | ERIS | Voltage | NEOSHO 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92254 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | NEOSHO 7 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91944 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NEOSHON2 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.89389 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NEOSHON2 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.89389 | 0.93 | 1.05 | Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
04ALL | ERIS | Voltage | NEOSHON4 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.88175 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NEOSHOS2 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.8939 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NEOSHOS4 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.88185 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NEVADA 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.89381 | 0.93 | 1.05 | Add 45 MVAR switched shunt at NEVADA 5 161 kV
04ALL | ERIS | Voltage | NINN1WF7 | 26SP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.94656 | 0.95 | 1.05 | None
04ALL | ERIS | Voltage | NLOUISB5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90779 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | NOL435 5 | 26SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.90711 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NP-GLAZIR_G2 | 26SP | V | P42:345:OKGE:SB_DGSE7313:::EHV: |  |  |  |  | 0.67252 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NP-LIPSCOMB2 | 26SP | V | P42:345:OKGE:SB_DGSE7313:::EHV: |  |  |  |  | 0.63439 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NP-LIPS_SHA2 | 26SP | V | P42:345:OKGE:SB_DGSE7313:::EHV: |  |  |  |  | 0.63439 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NP-LUCKY_CR2 | 26SP | V | P42:345:OKGE:SB_DGSE7313:::EHV: |  |  |  |  | 0.76151 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NP-LUCKY_G 2 | 26SP | V | P42:345:OKGE:SB_DGSE7313:::EHV: |  |  |  |  | 0.76165 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NP-SHATTUCK2 | 26SP | V | P42:345:OKGE:SB_DGSE7313:::EHV: |  |  |  |  | 0.61312 | 0.9 | 1.05 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
04ALL | ERIS | Voltage | NP-SUB_A 2 | 26SP | V | P42:345:OKGE:SB_DGSE7313:::EHV: |  |  |  |  | 0.82664 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NP-VALERO_P2 | 26SP | V | P42:345:OKGE:SB_DGSE7313:::EHV: |  |  |  |  | 0.6424 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NRSS7 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.9291 | 0.95 | 1.05 | None
04ALL | ERIS | Voltage | OLATHE 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90779 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | OPENSKY7 | 26SP | V | P42:345:OKGE:SB_DGSE7313:::EHV: |  |  |  |  | 0.91124 | 0.92 | 1.05 | None
04ALL | ERIS | Voltage | ORDNCE 2 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.88864 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ORDNJCT2 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.88919 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | OSAGE 3 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.89401 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | OSAGE J3 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.89503 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | OSAWAT 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90502 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | OSAWTM_CAP5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90606 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | OTTRCRK3 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91657 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | OTTRCRK4 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91846 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | OVERLPK5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91621 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | OXFORD 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90445 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | PAOLA 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90483 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | PECULR 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92764 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | PECULR 7 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.8964 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | PFLUMM 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91886 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | PHILL 7 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91187 | 0.95 | 1.05 | Add 0.02 MVAR switched shunt at PHILL 7 345 kV
04ALL | ERIS | Voltage | PHILL 7 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91187 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | PLSTVAL5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92692 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | PRAIRIE3 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.86865 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | PRY-JCT4 | 26SP | V | Single 509752 INOLATP4 138 509790 CATOOSA4 138 1 |  |  |  |  | 0.9154 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | PRY_CRK4 | 26SP | V | Single 509752 INOLATP4 138 509790 CATOOSA4 138 1 |  |  |  |  | 0.88577 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | QUARRY 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91288 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | READING3 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.88176 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | REDEL 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91137 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | REEDER 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91616 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | RENFROW7 | 26SP | V | P42:345:OKGE:SB_DGSE7313:::EHV: |  |  |  |  | 0.90409 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | RILEY 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90942 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | RNM393 5 | 26SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.92256 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ROCKPT-4 | 26SP | V | Single 509752 INOLATP4 138 509790 CATOOSA4 138 1 |  |  |  |  | 0.80373 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ROEPARK5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92728 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | S.OTTWA5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91406 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | SCRANTN3 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90812 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | SE1GREE2 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92963 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | SEOTTWA5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.9159 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | SHAWNEE5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92933 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | SHWNMSN5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.9251 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | SIBLEYRD2 | 26SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.90914 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SIBLEYRD2 | 26SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.90914 | 0.925 | 1.05 | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV
04ALL | ERIS | Voltage | SIBLEYRD5 | 26SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.90994 | 0.925 | 1.05 | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV
04ALL | ERIS | Voltage | SIBLEYRD5 | 26SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.90994 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SOUTHTN3 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91995 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | SPRGHL 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90929 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | SPRINT15 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91045 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | SPRINT25 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91041 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | STHTOWN5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92293 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | STHTOWN_CAP5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92399 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | STILWEL5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91036 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | STILWEL7 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.88333 | 0.95 | 1.05 | Add 213 MVAR switched shunt at STILWEL7 345 kV
04ALL | ERIS | Voltage | STK324 2 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90598 | 0.925 | 1.05 | None
04ALL | ERIS | Voltage | STK324J2 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90598 | 0.925 | 1.05 | None
04ALL | ERIS | Voltage | STK418 2 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90166 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SUMMIT 6 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.94577 | 0.95 | 1.05 | None
04ALL | ERIS | Voltage | SUMMIT 7 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92053 | 0.95 | 1.05 | None
04ALL | ERIS | Voltage | SUNSHINE5 | 26SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.91885 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SWISVAL6 | 26SP | V | P23:345:KCPL:LACYGNE-R2-5:::EHV: |  |  |  |  | 0.92862 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SWISVAL7 | 26SP | V | P23:345:KCPL:LACYGNE-R2-5:::EHV: |  |  |  |  | 0.91571 | 0.95 | 1.05 | Add 177 MVAR switched shunt at SWISVAL7 345 kV
04ALL | ERIS | Voltage | SWISVAL7 | 26SP | V | P23:345:KCPL:LACYGNE-R2-5:::EHV: |  |  |  |  | 0.91571 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SWITZER5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90724 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | TAYLOR 4 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91257 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | TECHILL6 | 26SP | V | P23:345:KCPL:LACYGNE-R2-5:::EHV: |  |  |  |  | 0.92969 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | TIOGA 4 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91207 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | TIP292 5 | 26SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.92434 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | TOMHAWK5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91659 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | TONTITN7 | 26SP | V | P23:345:GRDA:TONNECE CB9580:::EHV: |  |  |  |  | 0.91823 | 0.92 | 1.05 | Add 0.4 MVAR switched shunt at TONTITN7 345 kV
04ALL | ERIS | Voltage | TURNER_RD5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91955 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | TV1MNDV4 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90237 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | W.GRDNR7 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.89179 | 0.95 | 1.05 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
04ALL | ERIS | Voltage | WAGSTAF5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90674 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | WAVERLY3 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92593 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | WHARV4 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.87787 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | WHARV4 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.87787 | 0.93 | 1.05 | Add 56 MVAR switched shunt at WHARV4 138 kV
04ALL | ERIS | Voltage | WICHITA7 | 26SP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.90901 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | WICHITA7 | 26SP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.90901 | 0.95 | 1.05 | Add 160 MVAR switched shunt at WICHITA7 345 kV
04ALL | ERIS | Voltage | WINDSR 5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92552 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | WMBROS 3 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.87096 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | WMBROSJ3 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.87096 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | WOODLND5 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92303 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | WROGERS 5 | 26SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.91883 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | WWUPLNT4 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90514 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | YOST 2 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92043 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | ZOO 4 | 26SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92873 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | RSS T1 4 | 29L | V | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: |  |  |  |  | 1.0524 | 0.92 | 1.05 | Add 13 MVAR switched shunt at RSS T1 4 138 kV
04ALL | ERIS | Voltage | RSS T1 4 | 29L | V | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: |  |  |  |  | 1.0524 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | RSS T2 4 | 29L | V | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: |  |  |  |  | 1.0522 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | T.P.S.-2 | 29L | V | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: |  |  |  |  | 1.0647 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | T.P.S.-2 | 29L | V | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: |  |  |  |  | 1.0647 | 0.92 | 1.05 | Add 14 MVAR switched shunt at T.P.S.-2 69 kV
04ALL | ERIS | Voltage | 15THSTRT | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91275 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | 19THST 3 | 29SP | V | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: |  |  |  |  | 0.92433 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | 2WEIRGAT | 29SP | V | P23:345:EES::7ROCKYCRK%:1:EHV: |  |  |  |  | 0.90335 | 0.92 | 1.05 | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV
04ALL | ERIS | Voltage | 4CORNER3 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90384 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | 6TH ST 3 | 29SP | V | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: |  |  |  |  | 0.92843 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | 87TH 3 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.9195 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | 87TH 7 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92264 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ADRIAN 5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92134 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | ALTAMNS2 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.88165 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ALTAMNT2 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.8745 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ALTOONA4 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90502 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ANGELUS | 29SP | V | P42:345:NPPD:BKR-AXT-3306:::: |  |  |  |  | 0.89863 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ANTIOCH5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.89852 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | ARC250 2 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92339 | 0.925 | 1.05 | None
04ALL | ERIS | Voltage | ARCHIE 5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92366 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | ARNOLD3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.87437 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ASG-2018-010 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92915 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | ASG-2018-011 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92439 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | ATLNTIC3 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90459 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ATLNTIC7 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.89447 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ATWODSW3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.89042 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ATWOOD 3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.89047 | 0.9 | 1.05 | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
04ALL | ERIS | Voltage | ATWOOD 3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.89047 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | AUBURN 6 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.916 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | AUR124 5 | 29SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.916 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | AVOCA 5 | 29SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.91749 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | AXTELL 3 | 29SP | V | System Intact |  |  |  |  | 0.94674 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BALDCRK3 | 29SP | V | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: |  |  |  |  | 0.92783 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | BEECRK4 | 29SP | V | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 |  |  |  |  | 0.92516 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BEELER 3 | 29SP | V | P23:345:SUNC:SB_BRK482:::EHV: |  |  |  |  | 0.88839 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BELTONS5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91521 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | BENTLEY4 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92917 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | BENTVJ_5 | 29SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.91845 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BENT_SL5 | 29SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.91861 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BIRDCTY3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.87439 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BIRDCTY3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.87439 | 0.9 | 1.05 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV
04ALL | ERIS | Voltage | BISMARK3 | 29SP | V | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: |  |  |  |  | 0.9276 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | BLSPW 5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92939 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | BNSF 5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91905 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | BONITA 3 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90468 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | BREWSTR3 | 29SP | V | P42:345:NPPD:BKR-AXT-3306:::: |  |  |  |  | 0.89495 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BRKRIDG5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90459 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | BUCYRUS5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90554 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | BUFFALO7 | 29SP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.93804 | 0.95 | 1.05 | Add 0.02 MVAR switched shunt at BUFFALO7 345 kV
04ALL | ERIS | Voltage | BUFFALO7 | 29SP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.93804 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BUNKRDG5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92273 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | BURNS 7 | 29SP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.93339 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BVRVLY 3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.88195 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BVRVLYT3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.88217 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | CANEYRV7 | 29SP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.94027 | 0.95 | 1.05 | None
04ALL | ERIS | Voltage | CANEYWF7 | 29SP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.94039 | 0.95 | 1.05 | None
04ALL | ERIS | Voltage | CARB-KW 3 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91123 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | CEDARNL5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92459 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | CEDRCRK5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91434 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | CENTENL5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.9179 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | CHAMSPR7 | 29SP | V | P23:345:GRDA:TONNECE CB9580:::EHV: |  |  |  |  | 0.91437 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | CHASE 3 | 29SP | V | P23:345:SUNC:SB_BRK482:::EHV: |  |  |  |  | 0.85906 | 0.9 | 1.05 | Add 3.3 MVAR switched shunt at CHASE 3 115 kV
04ALL | ERIS | Voltage | CHASE 3 | 29SP | V | P23:345:SUNC:SB_BRK482:::EHV: |  |  |  |  | 0.85906 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | CLEARVW3 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90998 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | CLIFTON3 | 29SP | V | Single 539805 ELMCREEK7 345 640600 DAYKIN3 345 1 |  |  |  |  | 0.8909 | 0.9 | 1.05 | Add 2 MVAR switched shunt at CLIFTON3 115 kV
04ALL | ERIS | Voltage | CLINTON5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90685 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | CNTRVIL5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91073 | 0.93 | 1.05 | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
04ALL | ERIS | Voltage | COLBY_PUMP3 | 29SP | V | P42:345:NPPD:BKR-AXT-3306:::: |  |  |  |  | 0.89191 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | COLLEGE5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90789 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | COWSKIN 4 | 29SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.89984 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | COWSKIN2 | 29SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.8909 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | CPK446 5 | 29SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.91431 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | CPK446 5 | 29SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.91431 | 0.925 | 1.05 | Add 16 MVAR switched shunt at CPK446 5 161 kV
04ALL | ERIS | Voltage | CRAIG 5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91439 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | CRAIG 7 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91373 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | CRAIG_CAP 5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91539 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | CRAWFOR2 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92098 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | CSTFRAN3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.8671 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | DAD368 5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91586 | 0.925 | 1.05 | None
04ALL | ERIS | Voltage | DAKOTA_5 | 29SP | V | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: |  |  |  |  | 0.92889 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | DIGHTON3 | 29SP | V | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: |  |  |  |  | 0.89591 | 0.9 | 1.05 | Add 1 MVAR switched shunt at DIGHTON3 115 kV
04ALL | ERIS | Voltage | EAST ST3 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.85205 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | ECNTRTN5 | 29SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.91969 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | EDWRDVL5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92134 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | EEUREKA3 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.905 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | ELKRVR17 | 29SP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.93304 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ELLIS 2 | 29SP | V | P23:345:SUNC:SB_BRK482:::EHV: |  |  |  |  | 0.86605 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | EUDORA 3 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91275 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | EXPED WF7 | 29SP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.93645 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | FAIRGDS3 | 29SP | V | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: |  |  |  |  | 0.92366 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | FINNEY 7 | 29SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 1.0611 | 0.9 | 1.05 | Add 23 MVAR switched shunt at FINNEY 7 345 kV
04ALL | ERIS | Voltage | FLORENC3 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.89997 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | FMC 3 | 29SP | V | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: |  |  |  |  | 0.92771 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | FOREST 5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92166 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | FR4 XMF1 345 | 29SP | V | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 |  |  |  |  | 0.9423 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | FR4345KV-TAP | 29SP | V | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 |  |  |  |  | 0.94223 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | FREESTATE3 | 29SP | V | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: |  |  |  |  | 0.92523 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | G15052_1 | 29SP | V | P42:345:OKGE:SB_DGSE7313:::EHV: |  |  |  |  | 0.89198 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G15052_1 | 29SP | V | P42:345:OKGE:SB_DGSE7313:::EHV: |  |  |  |  | 0.89198 | 0.95 | 1.05 | Add 280 MVAR SVC at G15052_1 345 kV
04ALL | ERIS | Voltage | G15052_T | 29SP | V | P42:345:OKGE:SB_DGSE7313:::EHV: |  |  |  |  | 0.89198 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G15052_T | 29SP | V | P42:345:OKGE:SB_DGSE7313:::EHV: |  |  |  |  | 0.89198 | 0.95 | 1.05 | Add 45 MVAR SVC at G15052_T 345 kV
04ALL | ERIS | Voltage | G16-111-TAP | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.87875 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G16-111-TAP | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.87875 | 0.95 | 1.05 | Add 150 MVAR SVC at G16-111-TAP 345 kV
04ALL | ERIS | Voltage | G17-108-TAP | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90853 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | G18-128-TAP | 29SP | V | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 |  |  |  |  | 0.91175 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G18-128-TAP | 29SP | V | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 |  |  |  |  | 0.91175 | 0.95 | 1.05 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
04ALL | ERIS | Voltage | G20-007-TAP | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.87964 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G20-072-TAP | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91948 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | G20-073-TAP | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92151 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | G21-029-TAP | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.8771 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G21-096-TAP | 29SP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.93353 | 0.95 | 1.05 | None
04ALL | ERIS | Voltage | G22-007-TAP | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.85886 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | G22-013-TAP | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.89132 | 0.95 | 1.05 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
04ALL | ERIS | Voltage | G22-075-TAP | 29SP | V | System Intact |  |  |  |  | 0.93407 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G23-015-TAP | 29SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 1.0602 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G23-220-TAP | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90641 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G23-220-TAP | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90641 | 0.95 | 1.05 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
04ALL | ERIS | Voltage | G23-221-TAP | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90641 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G24-076-TAP | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.89261 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G24-129-TAP | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.94304 | 0.95 | 1.05 | None
04ALL | ERIS | Voltage | G24-253-TAP | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.9446 | 0.95 | 1.05 | None
04ALL | ERIS | Voltage | G24-276-TAP | 29SP | V | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: |  |  |  |  | 0.91711 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GARDNER5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91199 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | GEARY 7 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91805 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEM_SW 3 | 29SP | V | P42:345:NPPD:BKR-AXT-3306:::: |  |  |  |  | 0.89289 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2016-073 | 29SP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.94254 | 0.95 | 1.05 | None
04ALL | ERIS | Voltage | GEN-2016-111 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.87957 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2017-022 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90502 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2017-086 | 29SP | V | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 |  |  |  |  | 0.94223 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2017-108 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90853 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | GEN-2017-195 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.88276 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2017-220 | 29SP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.93804 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2018-032 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92478 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2018-128 | 29SP | V | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 |  |  |  |  | 0.91176 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2019-016 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91595 | 0.925 | 1.05 | None
04ALL | ERIS | Voltage | GEN-2020-007 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.87964 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2020-057 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.89447 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2020-058 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.89447 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2020-072 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91948 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | GEN-2020-073 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92151 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | GEN-2021-006 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92459 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2021-029 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.8771 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2021-030 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.8771 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2021-096 | 29SP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.93353 | 0.95 | 1.05 | None
04ALL | ERIS | Voltage | GEN-2021-103 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90459 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2021-107 | 29SP | V | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: |  |  |  |  | 0.93769 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2022-006 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92559 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | GEN-2022-007 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.85886 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | GEN-2022-013 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.89132 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2022-075 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.8851 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2023-015 | 29SP | V | P23:345:SUNC:HLC_BRK282:::EHV: |  |  |  |  | 1.0602 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2023-220 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90641 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2023-221 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90641 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2024-076 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.89509 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2024-129 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.94324 | 0.95 | 1.05 | None
04ALL | ERIS | Voltage | GEN-2024-170 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90184 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2024-249 | 29SP | V | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: |  |  |  |  | 0.93769 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2024-253 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.9446 | 0.95 | 1.05 | None
04ALL | ERIS | Voltage | GEN-2024-276 | 29SP | V | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: |  |  |  |  | 0.91721 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2024-352 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.93034 | 0.95 | 1.05 | None
04ALL | ERIS | Voltage | GODLNDT3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.87288 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GOODCTY3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.86869 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GOODCTY3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.86869 | 0.9 | 1.05 | Add 12 MVAR switched shunt at GOODCTY3 115 kV
04ALL | ERIS | Voltage | GOODLND3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.87425 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GOVE 3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.87194 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GRDVWE 5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91549 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | GREENHOUSE 5 | 29SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.91978 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GRINNEL3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.89269 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GROVE 4 | 29SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.90076 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GROVE 4 | 29SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.90076 | 0.92 | 1.05 | Add 24 MVAR switched shunt at GROVE 4 138 kV
04ALL | ERIS | Voltage | GROVE 5 | 29SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.90693 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | HALSTD 4 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.907 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | HAWTH 7 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.93837 | 0.95 | 1.05 | None
04ALL | ERIS | Voltage | HERNDON3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.89131 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | HICKMAN5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90926 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | HIGHPT 3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.85298 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | HONEYWL5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90886 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | HOYT 7 | 29SP | V | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: |  |  |  |  | 0.92935 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | HSNVL 5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92685 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | INDIAN_CK_5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90733 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | JADE 3 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90122 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | JAGGER 3 | 29SP | V | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: |  |  |  |  | 0.89662 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | JAY 4 | 29SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.91033 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | JEC 6 | 29SP | V | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: |  |  |  |  | 0.94089 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | JEC N 7 | 29SP | V | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: |  |  |  |  | 0.93769 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | JOHNSON3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.89247 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | JOP391 5 | 29SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.92324 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | KANARAD3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.85097 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | KNLWRTH5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90609 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | KNOLL N 6 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.89975 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | KNOLL S 6 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.89975 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LABETTE2 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.89412 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LABETTS2 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.89619 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LABETTS2 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.89619 | 0.93 | 1.05 | Add 0.25 MVAR switched shunt at LABETTS2 69 kV
04ALL | ERIS | Voltage | LACKMAN5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90168 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | LACYGNE11_7 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.87974 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LACYGNE11_7 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.87974 | 0.95 | 1.05 | Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
04ALL | ERIS | Voltage | LACYGNE2 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.86718 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LACYGNE22_7 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.87975 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LACYGNE_LK2 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.86585 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LANG 3 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.85844 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | LANG 7 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.78038 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LAWHILL6 | 29SP | V | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: |  |  |  |  | 0.93781 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LAWNRID3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.86176 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LEC U5 6 | 29SP | V | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: |  |  |  |  | 0.93843 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LENEXA 5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91419 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | LEX161 5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92961 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | LIBERTY4 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91494 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LITTLEBLUEW3 | 29SP | V | Single 539805 ELMCREEK7 345 640600 DAYKIN3 345 1 |  |  |  |  | 0.89748 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LKWOOD 5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92868 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | LNGVW 5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92783 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | LUDELL 3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.89046 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LUDELLT3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.89047 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LVISTA 5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92575 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | MACON 3 | 29SP | V | System Intact |  |  |  |  | 0.93254 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | MACON 3 | 29SP | V | System Intact |  |  |  |  | 0.93254 | 0.95 | 1.05 | Add 48 MVAR switched shunt at MACON 3 345 kV
04ALL | ERIS | Voltage | MANNING3 | 29SP | V | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: |  |  |  |  | 0.89937 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | MARTCIT5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90631 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | MARTCTY5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90907 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | MCDONLD3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.87996 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | MERRIAM5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.9156 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | MERRIAM_CAP5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.9166 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | MIDLAND6 | 29SP | V | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: |  |  |  |  | 0.93651 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | MIDTOWN5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.9253 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | MISNJCT5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90647 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | MNTCLLO3 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92317 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | MOCKBRD3 | 29SP | V | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: |  |  |  |  | 0.92867 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | MON383 5 | 29SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.91886 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | MON383 5 | 29SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.91886 | 0.925 | 1.05 | Add 21 MVAR switched shunt at MON383 5 161 kV
04ALL | ERIS | Voltage | MONTGOM4 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91847 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | MOONLIT3 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90793 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | MOONLT 5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91199 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | MORRIS 3 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92692 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | MORRIS 6 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.93875 | 0.95 | 1.05 | None
04ALL | ERIS | Voltage | MORRIS 7 | 29SP | V | P23:345:KCPL:LACYGNE-R2-5:::EHV: |  |  |  |  | 0.94033 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | MOUND 4 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.89164 | 0.93 | 1.05 | Add 0.02 MVAR switched shunt at MOUND 4 138 kV
04ALL | ERIS | Voltage | MOUND 4 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.89164 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | MURLEN 5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.89955 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | MUSTNG5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91876 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | NATWOOD3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.89036 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NEASTOTTW5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92071 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | NEO SPA5 | 29SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.91793 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NEO184 5 | 29SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.9157 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NEO184 5 | 29SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.9157 | 0.925 | 1.05 | Add 15 MVAR switched shunt at NEO184 5 161 kV
04ALL | ERIS | Voltage | NEOSHO 4 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.88501 | 0.93 | 1.05 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
04ALL | ERIS | Voltage | NEOSHO 4 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.88501 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NEOSHO 5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92559 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | NEOSHO 7 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92459 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NEOSHON2 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.89687 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NEOSHON4 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.88507 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NEOSHOS2 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.89688 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NEOSHOS2 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.89688 | 0.93 | 1.05 | Add 3 MVAR switched shunt at NEOSHOS2 69 kV
04ALL | ERIS | Voltage | NEOSHOS4 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.88517 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NESCTY 3 | 29SP | V | P23:345:SUNC:SB_BRK482:::EHV: |  |  |  |  | 0.88679 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NESSCTY3 | 29SP | V | P23:345:SUNC:SB_BRK482:::EHV: |  |  |  |  | 0.88672 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NEVADA 5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.8875 | 0.93 | 1.05 | Add 45 MVAR switched shunt at NEVADA 5 161 kV
04ALL | ERIS | Voltage | NLOUISB5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90506 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | NOL435 5 | 29SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.90793 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NOL435 5 | 29SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.90793 | 0.925 | 1.05 | Add 0.09 MVAR switched shunt at NOL435 5 161 kV
04ALL | ERIS | Voltage | NORCATR3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.89965 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NP-GLAZIR_G2 | 29SP | V | P42:345:OKGE:SB_DGSE7313:::EHV: |  |  |  |  | 0.63691 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NP-LIPSCOMB2 | 29SP | V | P42:345:OKGE:SB_DGSE7313:::EHV: |  |  |  |  | 0.59473 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NP-LIPS_SHA2 | 29SP | V | P42:345:OKGE:SB_DGSE7313:::EHV: |  |  |  |  | 0.59473 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NP-LUCKY_CR2 | 29SP | V | P42:345:OKGE:SB_DGSE7313:::EHV: |  |  |  |  | 0.73628 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | NP-LUCKY_G 2 | 29SP | V | P42:345:OKGE:SB_DGSE7313:::EHV: |  |  |  |  | 0.73644 | 0.9 | 1.05 | None
04ALL | ERIS | Voltage | NP-SHATTUCK2 | 29SP | V | P42:345:OKGE:SB_DGSE7313:::EHV: |  |  |  |  | 0.57137 | 0.9 | 1.05 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
04ALL | ERIS | Voltage | NP-VALERO_P2 | 29SP | V | P42:345:OKGE:SB_DGSE7313:::EHV: |  |  |  |  | 0.60356 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NRAYMORE | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92453 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | NRAYMORETP 5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92477 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | NRSS7 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.9356 | 0.95 | 1.05 | None
04ALL | ERIS | Voltage | NSI 3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.85279 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NSI TAP3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.85404 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NSI TAP3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.85404 | 0.9 | 1.05 | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV
04ALL | ERIS | Voltage | OAKGRV 5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92981 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | OBER T 3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.89309 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | OBERLIN3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.89287 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | OLATHE 5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.89982 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ORDNCE 2 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.89167 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ORDNJCT2 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.8922 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | OSAGE 3 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.88092 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | OSAGE J3 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.88199 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | OSAWTM_CAP5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92319 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | OTTRCRK3 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91535 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | OTTRCRK4 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91783 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | OVERLPK5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90858 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | OXFORD 5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.89698 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | PALMER3 | 29SP | V | P23:345:SUNC:SB_BRK482:::EHV: |  |  |  |  | 0.88658 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | PAOLA 5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92174 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | PECULR 5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91957 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | PECULR 7 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.88757 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | PECULR 7 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.88757 | 0.95 | 1.05 | Add 0.13 MVAR switched shunt at PECULR 7 345 kV
04ALL | ERIS | Voltage | PECULRS5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92286 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | PFLUMM 5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91074 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | PH RUN 3 | 29SP | V | P42:345:NPPD:BKR-AXT-3306:::: |  |  |  |  | 0.89783 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | PHILL 7 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90184 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | PLSTVAL5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92501 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | POSTROCK6 | 29SP | V | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.89952 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | POSTROCK7 | 29SP | V | System Intact |  |  |  |  | 0.9277 | 0.95 | 1.05 | Add 86 MVAR switched shunt at POSTROCK7 345 kV
04ALL | ERIS | Voltage | POSTROCK7 | 29SP | V | System Intact |  |  |  |  | 0.9277 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | PRAIRIE3 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.85933 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | QUARRY 5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90515 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | RANSOM 2 | 29SP | V | P23:345:SUNC:SB_BRK482:::EHV: |  |  |  |  | 0.8733 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | RANSOM 3 | 29SP | V | P23:345:SUNC:SB_BRK482:::EHV: |  |  |  |  | 0.87621 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | RANSOM 3 | 29SP | V | P23:345:SUNC:SB_BRK482:::EHV: |  |  |  |  | 0.87621 | 0.9 | 1.05 | Add 20 MVAR switched shunt at RANSOM 3 115 kV
04ALL | ERIS | Voltage | RAYTOWN5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92937 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | RCKFALLPV7 | 29SP | V | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 |  |  |  |  | 0.91801 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | READING3 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.87 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | REDEL 5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90438 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | REEDER 5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90826 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | RENFROW7 | 29SP | V | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 |  |  |  |  | 0.91775 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | RILEY 5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90176 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | RNM393 5 | 29SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.92184 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ROEPARK5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92194 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | S.OTTWA5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92027 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | SCRANTN3 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.89414 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | SEGUIN 3 | 29SP | V | P42:345:NPPD:BKR-AXT-3306:::: |  |  |  |  | 0.89933 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SEOTTWA5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.9209 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | SHALE 7 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.94337 | 0.95 | 1.05 | None
04ALL | ERIS | Voltage | SHARNSP3 | 29SP | V | P23:345:SUNC:SB_BRK482:::EHV: |  |  |  |  | 0.85918 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SHAWNEE5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92268 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | SHWNMSN5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91809 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | SIBLEYRD2 | 29SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.9097 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SIBLEYRD5 | 29SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.91062 | 0.925 | 1.05 | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV
04ALL | ERIS | Voltage | SIBLEYRD5 | 29SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.91062 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SOUTHTN3 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90719 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | SPRGHL 5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90104 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | SPRINT15 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90287 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | SPRINT25 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90282 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | STFRAN 3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.86863 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | STFRANT3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.86726 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | STHTOWN5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91669 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | STHTOWN_CAP5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91774 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | STILWEL5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90395 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | STILWEL7 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.87557 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | STILWEL7 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.87557 | 0.95 | 1.05 | Add 213 MVAR switched shunt at STILWEL7 345 kV
04ALL | ERIS | Voltage | STK324 2 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90297 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | STK324J2 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90298 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | STK418 2 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.89867 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SUMMIT 6 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.94098 | 0.95 | 1.05 | None
04ALL | ERIS | Voltage | SUMMIT 7 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91208 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SUMMIT 7 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91208 | 0.95 | 1.05 | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV
04ALL | ERIS | Voltage | SUNSHINE5 | 29SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.9183 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SWISVAL6 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91673 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SWISVAL7 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90507 | 0.95 | 1.05 | Add 177 MVAR switched shunt at SWISVAL7 345 kV
04ALL | ERIS | Voltage | SWISVAL7 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90507 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SWITZER5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.89938 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SWLWRNC3 | 29SP | V | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: |  |  |  |  | 0.92591 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | SWOPE S5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92931 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | TAYLOR 4 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.9167 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | TECHILL6 | 29SP | V | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: |  |  |  |  | 0.91708 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | TIOGA 4 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90821 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | TIP292 5 | 29SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.92354 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | TOMHAWK5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90968 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | TONTITN7 | 29SP | V | P23:345:GRDA:TONNECE CB9580:::EHV: |  |  |  |  | 0.91525 | 0.92 | 1.05 | Add 0.4 MVAR switched shunt at TONTITN7 345 kV
04ALL | ERIS | Voltage | TRIB SW3 | 29SP | V | P23:345:SUNC:SB_BRK482:::EHV: |  |  |  |  | 0.89889 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | TURNER_RD5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91166 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | TV1MNDV4 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90665 | 0.93 | 1.05 | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
04ALL | ERIS | Voltage | TV1MNDV4 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90665 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | W.GRDNR7 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.88276 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | W.GRDNR7 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.88276 | 0.95 | 1.05 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
04ALL | ERIS | Voltage | WAGSTAF5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.90857 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | WASHBURN5 | 29SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.91862 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | WAVERLY3 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91264 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | WGARDNR5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92479 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | WHARV4 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.89782 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | WHARV4 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.89782 | 0.93 | 1.05 | Add 56 MVAR switched shunt at WHARV4 138 kV
04ALL | ERIS | Voltage | WICHITA7 | 29SP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.92969 | 0.95 | 1.05 | Add 160 MVAR switched shunt at WICHITA7 345 kV
04ALL | ERIS | Voltage | WICHITA7 | 29SP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.92969 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | WINDSR 5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91908 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | WINJT S5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92934 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | WMBROS 3 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.86333 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | WMBROSJ3 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.86333 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | WOODLND5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.91439 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | WREN 3 | 29SP | V | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: |  |  |  |  | 0.92566 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | WROGERS 5 | 29SP | V | P23:345:AECI:7BLACKBERRY:6_3::: |  |  |  |  | 0.91844 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | WSTELEC5 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92966 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | WTCLF 3 | 29SP | V | Single 531451 MINGO7 345 531465 SETAB7 345 1 |  |  |  |  | 0.85292 | 0.9 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | WWUPLNT4 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.92893 | 0.93 | 1.05 | None
04ALL | ERIS | Voltage | 2WEIRGAT | 29WP | V | P21:138:EES:HEMPHIL4!:SIXMILE4:1:HV: |  |  |  |  | 0.91648 | 0.92 | 1.05 | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV
04ALL | ERIS | Voltage | ALTAMNS2 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.91884 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ALTAMNT2 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.91582 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ATLNTIC7 | 29WP | V | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: |  |  |  |  | 0.9475 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | AUR124 5 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.9219 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BIRDHOL4 | 29WP | V | Single 509752 INOLATP4 138 509790 CATOOSA4 138 1 |  |  |  |  | 0.89578 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | BURNS 7 | 29WP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.9483 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | CHOUTEA4 | 29WP | V | Single 509752 INOLATP4 138 509790 CATOOSA4 138 1 |  |  |  |  | 0.82089 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | COOYYAH4 | 29WP | V | Single 509752 INOLATP4 138 509790 CATOOSA4 138 1 |  |  |  |  | 0.83731 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | CPK446 5 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.91633 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | CPK446 5 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.91633 | 0.925 | 1.05 | Add 16 MVAR switched shunt at CPK446 5 161 kV
04ALL | ERIS | Voltage | DAD368 5 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.91738 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | DAD368 5 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.91738 | 0.925 | 1.05 | Add 11 MVAR switched shunt at DAD368 5 161 kV
04ALL | ERIS | Voltage | EXPCLAR4 | 29WP | V | Single 509752 INOLATP4 138 509790 CATOOSA4 138 1 |  |  |  |  | 0.83672 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G15052_1 | 29WP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.92871 | 0.95 | 1.05 | Add 280 MVAR SVC at G15052_1 345 kV
04ALL | ERIS | Voltage | G15052_1 | 29WP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.92871 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G15052_T | 29WP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.92871 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G16-111-TAP | 29WP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.94359 | 0.95 | 1.05 | Add 150 MVAR SVC at G16-111-TAP 345 kV
04ALL | ERIS | Voltage | G20-092-TAP | 29WP | V | Single 509752 INOLATP4 138 509790 CATOOSA4 138 1 |  |  |  |  | 0.87956 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G21-096-TAP | 29WP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.93893 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G21-096-TAP | 29WP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.93893 | 0.95 | 1.05 | Add 28 MVAR switched shunt at G21-096-TAP 345 kV
04ALL | ERIS | Voltage | G23-220-TAP | 29WP | V | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: |  |  |  |  | 0.9374 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | G23-220-TAP | 29WP | V | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: |  |  |  |  | 0.9374 | 0.95 | 1.05 | Add 30 MVAR switched shunt at G23-220-TAP 345 kV
04ALL | ERIS | Voltage | G23-221-TAP | 29WP | V | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: |  |  |  |  | 0.93797 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2016-111 | 29WP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.94447 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2017-074 | 29WP | V | Single 509752 INOLATP4 138 509790 CATOOSA4 138 1 |  |  |  |  | 0.88492 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2017-077 | 29WP | V | Single 509752 INOLATP4 138 509790 CATOOSA4 138 1 |  |  |  |  | 0.83731 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2017-195 | 29WP | V | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: |  |  |  |  | 0.93704 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2019-016 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.91747 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2020-057 | 29WP | V | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: |  |  |  |  | 0.9475 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2020-058 | 29WP | V | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: |  |  |  |  | 0.9475 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2020-092 | 29WP | V | Single 509752 INOLATP4 138 509790 CATOOSA4 138 1 |  |  |  |  | 0.87956 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2021-096 | 29WP | V | P51:25:WERE:WOLFCRK7:EHV: |  |  |  |  | 0.93893 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2021-107 | 29WP | V | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: |  |  |  |  | 0.94853 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2023-220 | 29WP | V | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: |  |  |  |  | 0.9374 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2023-221 | 29WP | V | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: |  |  |  |  | 0.93797 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GEN-2024-249 | 29WP | V | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: |  |  |  |  | 0.94853 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GROVE 4 | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.90388 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GROVE 4 | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.90388 | 0.92 | 1.05 | Add 24 MVAR switched shunt at GROVE 4 138 kV
04ALL | ERIS | Voltage | GROVE 5 | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.91078 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | GROVE 5 | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.91078 | 0.92 | 1.05 | Add 0.2 MVAR switched shunt at GROVE 5 161 kV
04ALL | ERIS | Voltage | GUAVA 4 | 29WP | V | Single 509752 INOLATP4 138 509790 CATOOSA4 138 1 |  |  |  |  | 0.75428 | 0.92 | 1.05 | Add 57 MVAR switched shunt at GUAVA 4 138 kV
04ALL | ERIS | Voltage | HOYT 7 | 29WP | V | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: |  |  |  |  | 0.94558 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | INDEPCO5 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.88787 | 0.92 | 1.05 | Add 40 MVAR switched shunt at INDEPCO5 161 kV
04ALL | ERIS | Voltage | INOLA 4 | 29WP | V | Single 509752 INOLATP4 138 509790 CATOOSA4 138 1 |  |  |  |  | 0.75389 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | INOLATP4 | 29WP | V | Single 509752 INOLATP4 138 509790 CATOOSA4 138 1 |  |  |  |  | 0.75412 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | JAY 4 | 29WP | V | Single 509752 INOLATP4 138 509790 CATOOSA4 138 1 |  |  |  |  | 0.90629 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | JEC N 7 | 29WP | V | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: |  |  |  |  | 0.94853 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | JOP391 5 | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.9239 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LABETTE2 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.92359 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LABETTS2 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.92437 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LANG 7 | 29WP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 0.84891 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LAWHILL6 | 29WP | V | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: |  |  |  |  | 0.94454 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LEC U5 6 | 29WP | V | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: |  |  |  |  | 0.94454 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | LIBERTY4 | 29WP | V | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 |  |  |  |  | 0.92941 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | MCARBDE4 | 29WP | V | Single 509752 INOLATP4 138 509790 CATOOSA4 138 1 |  |  |  |  | 0.8646 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | MIDLAND6 | 29WP | V | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: |  |  |  |  | 0.94528 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NEO184 5 | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.91888 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NEOSHO 4 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.9113 | 0.93 | 1.05 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
04ALL | ERIS | Voltage | NEOSHON2 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.92259 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NEOSHON4 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.91137 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NEOSHOS2 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.92261 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NEOSHOS4 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.91144 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NOL435 5 | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.9124 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | NOL435 5 | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.9124 | 0.925 | 1.05 | Add 0.09 MVAR switched shunt at NOL435 5 161 kV
04ALL | ERIS | Voltage | ORDNCE 2 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.92179 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ORDNJCT2 | 29WP | V | P23:500:EES-EAI:KEO:B4941::EHV: |  |  |  |  | 0.92211 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | PRY-JCT2 | 29WP | V | Single 509752 INOLATP4 138 509790 CATOOSA4 138 1 |  |  |  |  | 0.91433 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | PRY-JCT3 | 29WP | V | Single 509752 INOLATP4 138 509790 CATOOSA4 138 1 |  |  |  |  | 0.89874 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | PRY-JCT4 | 29WP | V | Single 509752 INOLATP4 138 509790 CATOOSA4 138 1 |  |  |  |  | 0.8849 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | PRY_CRK4 | 29WP | V | Single 509752 INOLATP4 138 509790 CATOOSA4 138 1 |  |  |  |  | 0.84685 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | RNM393 5 | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.92279 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | ROCKPT-4 | 29WP | V | Single 509752 INOLATP4 138 509790 CATOOSA4 138 1 |  |  |  |  | 0.75959 | 0.92 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SIBLEYRD2 | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.91428 | 0.925 | 1.05 | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV
04ALL | ERIS | Voltage | SIBLEYRD2 | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.91428 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SIBLEYRD5 | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.91536 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | STILWEL7 | 29WP | V | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: |  |  |  |  | 0.93667 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | STILWEL7 | 29WP | V | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: |  |  |  |  | 0.93667 | 0.95 | 1.05 | Add 213 MVAR switched shunt at STILWEL7 345 kV
04ALL | ERIS | Voltage | SWISVAL6 | 29WP | V | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: |  |  |  |  | 0.93974 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | SWISVAL6 | 29WP | V | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: |  |  |  |  | 0.93974 | 0.95 | 1.05 | Add 0.09 MVAR switched shunt at SWISVAL6 230 kV
04ALL | ERIS | Voltage | SWISVAL7 | 29WP | V | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: |  |  |  |  | 0.93503 | 0.95 | 1.05 | Add 177 MVAR switched shunt at SWISVAL7 345 kV
04ALL | ERIS | Voltage | SWISVAL7 | 29WP | V | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: |  |  |  |  | 0.93503 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | TIP292 5 | 29WP | V | P23:345:AECI:7BLACKBERRY:6_2::: |  |  |  |  | 0.92487 | 0.925 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | TV1MNDV4 | 29WP | V | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: |  |  |  |  | 0.92485 | 0.93 | 1.05 | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV
04ALL | ERIS | Voltage | TV1MNDV4 | 29WP | V | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: |  |  |  |  | 0.92485 | 0.93 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | W.GRDNR7 | 29WP | V | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: |  |  |  |  | 0.93704 | 0.95 | 1.05 | Mitigated at another bus
04ALL | ERIS | Voltage | W.GRDNR7 | 29WP | V | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: |  |  |  |  | 0.93704 | 0.95 | 1.05 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | [7 empty] | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P52:345:AEPW:NR5O.K.U.-7:::: | [7 empty] | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P52:138:AEPW:NR5O.K.U:::: | [7 empty] | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | [7 empty] | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P42:345:SPS:HITCHLAND-1R15:::EHV: | [7 empty] | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | [7 empty] | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | [7 empty] | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | [7 empty] | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | [7 empty] | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 523097 HITCHLAND7 345 523961 POTTER_CO7 345 1 | [7 empty] | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | [7 empty] | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | P12:230:SPS:K97:1:CHAN+TASCOS_POTTERCO___:HV: | [7 empty] | 526_SPS_New_Branch_MooreCo_XIT_230kv.idv : 2024 ITP upgrade, PID : 220945, NTC, ISD : 12/15/2028
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 523221 XIT_INTG6 230 523869 CHAN+TASCOS6 230 1 | [7 empty] | 526_SPS_New_Branch_MooreCo_XIT_230kv.idv : 2024 ITP upgrade, PID : 220945, NTC, ISD : 12/15/2028
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 523869 CHAN+TASCOS6 230 523959 POTTER_CO6 230 1 | [7 empty] | 526_SPS_New_Branch_MooreCo_XIT_230kv.idv : 2024 ITP upgrade, PID : 220945, NTC, ISD : 12/15/2028
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | N0 | Single 525839 G17-151TAP 345 762467 G18-015-TAP 345 1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | SI-NC | System Intact | [7 empty] | Apply contingent IDV 01_NewLine_Phantom_Crossroads_Potter_765_26SP.idv
05ALL | ERIS | Non-Converged | Non-Converged | 26SP | SI-NC | System Intact | [7 empty] | Apply contingent IDV 02_765_Phantom_Craw_1_DIS24_TC05ALL-26SP.idv
05ALL | ERIS | Non-Converged | Non-Converged | 29L | N0 | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | [7 empty] | Add line 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 P2
05ALL | ERIS | Non-Converged | Non-Converged | 29L | N0 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29L | N0 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29L | N0 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29L | N0 | Single 525839 G17-151TAP 345 762467 G18-015-TAP 345 1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29L | N0 | P42:345:SPS:CARPENTER-OR335:::EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29L | N0 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29L | N0 | P52:345:AEPW:NR5O.K.U.-7:::: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29L | N0 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29L | N0 | P52:138:AEPW:NR5O.K.U:::: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29L | N0 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P52:345:AEPW:NR5O.K.U.-7:::: | [7 empty] | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P52:138:AEPW:NR5O.K.U:::: | [7 empty] | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | [7 empty] | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | [7 empty] | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | N0 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | [7 empty] | None
05ALL | ERIS | Non-Converged | Non-Converged | 29SP | SI-NC | System Intact | [7 empty] | Apply contingent IDV 02_765_Phantom_Craw_1_DIS24_TC05ALL-29SP.idv
05ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | [7 empty] | Add line 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 P2
05ALL | ERIS | Non-Converged | Non-Converged | 29WP | N0 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | [7 empty] | None
05ALL | ERIS | Thermal | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | 26SP | T0 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | B | 330 | 85.7764 | 119.313 |  |  |  | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
05ALL | ERIS | Thermal | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | 26SP | T0 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | B | 330 | 86.0444 | 119.313 |  |  |  | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
05ALL | ERIS | Thermal | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 26SP | T0 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | B | 353 | 78.8184 | 111.8755 |  |  |  | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
05ALL | ERIS | Thermal | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | 26SP | T0 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | B | 997 | 56.4169 | 101.1047 |  |  |  | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1
05ALL | ERIS | Thermal | 523221 XIT_INTG 6 230 3WXFMR 526:SIEM_T126401 115 1 | 26SP | T0 | Single 523309 MOORE_CNTY6 230 523308 MOORE_E3 115 523302 'MOORE_TR1 1' 13 1 | B | 284 | 71.1082 | 101.4148 |  |  |  | Add 3-winding transformer 523219 XIT_INTG TR1 13 523220 XIT_INTG 3 115 523221 XIT_INTG 6 230 M2
05ALL | ERIS | Thermal | 523308 MOORE_E 3 115 3WXFMR 526:ENRCO 136402 115 1 | 26SP | T0 | P12:230:SPS:K98:1:XITINTG_CHAN+TASCOS___:HV: | B | 239 | 87.5547 | 120.7667 |  |  |  | 526_New_MooreCounty_2ndTransformer_230_115.idv : PID: 220817, 2024 ITP, NTC, ISD: 5/15/2029
05ALL | ERIS | Thermal | 523309 MOORE_CNTY 6 230 3WXFMR 526:ENRCO 136402 115 1 | 26SP | T0 | P12:230:SPS:K98:1:XITINTG_CHAN+TASCOS___:HV: | B | 239 | 93.8824 | 126.5251 |  |  |  | 526_New_MooreCounty_2ndTransformer_230_115.idv : PID: 220817, 2024 ITP, NTC, ISD: 5/15/2029
05ALL | ERIS | Thermal | 523959 POTTER_CO 6 230 3WXFMR 526:WAUK 90343-A 230 1 | 26SP | T0 | Single 523097 HITCHLAND7 345 523961 POTTER_CO7 345 1 | B | 559 | 73.1276 | 107.3953 |  |  |  | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028
05ALL | ERIS | Thermal | 523961 POTTER_CO 7 345 3WXFMR 526:WAUK 90343-A 230 1 | 26SP | T0 | Single 523097 HITCHLAND7 345 523961 POTTER_CO7 345 1 | B | 559 | 79.3123 | 108.9122 |  |  |  | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028
05ALL | ERIS | Thermal | 524875 OASIS 6 230 781740 G24-159-TAP 230 1 | 26SP | T0 | Single 527799 EDDY_NORTH6 230 786270 G24-310-TAP 230 1 | B | 319 | -21.4214 | 125.4479 |  |  |  | Rebuild line 524875 OASIS 6 230 781740 G24-159-TAP 230 1
05ALL | ERIS | Thermal | 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | 26SP | T0 | Single 525832 TUCO_INT7 345 526000 CRAWFISH_DR 345 2 | B | 997 | 79.4418 | 109.7018 |  |  |  | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1
05ALL | ERIS | Thermal | 527891 HOBBS_INT 3 115 784800 G24-261-TAP 115 1 | 26SP | T0 | Single 528333 LE-WEST_SUB3 115 528334 LE-NRTH_INT3 115 1 | B | 199 | 33.4545 | 101.7442 |  |  |  | Rebuild line 527891 HOBBS_INT 3 115 784800 G24-261-TAP 115 1
05ALL | ERIS | Thermal | 528333 LE-WEST_SUB3 115 528334 LE-NRTH_INT3 115 1 | 26SP | T0 | Single 527891 HOBBS_INT3 115 784800 G24-261-TAP 115 1 | B | 199.4 | 35.7014 | 103.3987 |  |  |  | Rebuild line 528333 LE-WEST_SUB3 115 528334 LE-NRTH_INT3 115 1
05ALL | ERIS | Thermal | 528526 TEAGUE 3 115 528596 CARDINAL 3 115 1 | 26SP | T0 | Single 528540 WHITTEN3 115 528547 S_JAL3 115 1 | B | 175 | -6.4833 | 138.672 |  |  |  | Multi - Battle Axe - Wolfcamp Tap 115 kV DblCkt_Battle Axe - Ponderosa - Dollarhide 115 kV New Line.idv : PID : 900119, NTC, 2025 ITP, ISD: 6/1/2029
05ALL | ERIS | Thermal | 528526 TEAGUE 3 115 785400 G24-281-TAP 115 1 | 26SP | T0 | Single 528540 WHITTEN3 115 528547 S_JAL3 115 1 | B | 154 | 8.9529 | 162.1558 |  |  |  | Multi - Battle Axe - Wolfcamp Tap 115 kV DblCkt_Battle Axe - Ponderosa - Dollarhide 115 kV New Line.idv : PID : 900119, NTC, 2025 ITP, ISD: 6/1/2029
05ALL | ERIS | Thermal | 528540 WHITTEN 3 115 528547 S_JAL 3 115 1 | 26SP | T0 | Single 528526 TEAGUE3 115 785400 G24-281-TAP 115 1 | B | 154 | 9.4782 | 160.627 |  |  |  | Multi - Battle Axe - Wolfcamp Tap 115 kV DblCkt_Battle Axe - Ponderosa - Dollarhide 115 kV New Line.idv : PID : 900119, NTC, 2025 ITP, ISD: 6/1/2029
05ALL | ERIS | Thermal | 528547 S_JAL 3 115 785400 G24-281-TAP 115 1 | 26SP | T0 | Single 528526 TEAGUE3 115 785400 G24-281-TAP 115 1 | B | 154 | -6.0648 | 157.9814 |  |  |  | Rebuild line 528547 S_JAL 3 115 785400 G24-281-TAP 115 1
05ALL | ERIS | Thermal | 523216 RB-HOGUE 3 115 523246 DALHART 3 115 1 | 26SP | T1 | Single 523228 DALLAM3 115 523235 HILMRCHZ_TP3 115 1 | B | 82 | 64.6336 | 106.1269 |  |  |  | Rebuild line 523216 RB-HOGUE 3 115 523246 DALHART 3 115 1
05ALL | ERIS | Thermal | 528526 TEAGUE 3 115 528596 CARDINAL 3 115 1 | 26SP | T1 | Single 528547 S_JAL3 115 785400 G24-281-TAP 115 1 | B | 175 | -5.5175 | 136.0524 |  |  |  | Rebuild line 528526 TEAGUE 3 115 528596 CARDINAL 3 115 1
05ALL | ERIS | Thermal | 528526 TEAGUE 3 115 785400 G24-281-TAP 115 1 | 26SP | T1 | Single 528547 S_JAL3 115 785400 G24-281-TAP 115 1 | B | 154 | -5.4648 | 159.172 |  |  |  | Rebuild line 528526 TEAGUE 3 115 785400 G24-281-TAP 115 1
05ALL | ERIS | Thermal | 528547 S_JAL 3 115 528561 DOLLARHIDE 3 115 1 | 26SP | T1 | Single 528526 TEAGUE3 115 785400 G24-281-TAP 115 1 | B | 106 | 18.0853 | 108.5231 |  |  |  | Rebuild line 528547 S_JAL 3 115 528561 DOLLARHIDE 3 115 1
05ALL | ERIS | Thermal | 511541 DEMPSEYR POI 230 511557 CHISHOLM6 230 1 | 29L | T0 | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | B | 439 | 76.2332 | 100.3116 |  |  |  | Rebuild line 511541 DEMPSEYR POI 230 511557 CHISHOLM6 230 1
05ALL | ERIS | Thermal | 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | 29L | T0 | Single 525832 TUCO_INT7 345 526000 CRAWFISH_DR 345 2 | B | 997 | 60.1673 | 116.6859 |  |  |  | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1
05ALL | ERIS | Thermal | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | 29SP | T0 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | B | 330 | 75.2429 | 104.888 |  |  |  | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
05ALL | ERIS | Thermal | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | 29SP | T0 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | B | 330 | 75.376 | 104.888 |  |  |  | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
05ALL | ERIS | Thermal | 523220 XIT_INTG 3 115 3WXFMR 526:SIEM_T126401 115 1 | 29SP | T0 | Single 523221 XIT_INTG6 230 523309 MOORE_CNTY6 230 1 | B | 284 | 47.6707 | 110.6438 |  |  |  | Add 3-winding transformer 523219 XIT_INTG TR1 13 523220 XIT_INTG 3 115 523221 XIT_INTG 6 230 M2
05ALL | ERIS | Thermal | 523220 XIT_INTG 3 115 523228 DALLAM 3 115 1 | 29SP | T0 | Single 523221 XIT_INTG6 230 523309 MOORE_CNTY6 230 1 | B | 271 | 42.2242 | 107.7522 |  |  |  | Rebuild line 523220 XIT_INTG 3 115 523228 DALLAM 3 115 1
05ALL | ERIS | Thermal | 523221 XIT_INTG 6 230 3WXFMR 526:SIEM_T126401 115 1 | 29SP | T0 | Single 523221 XIT_INTG6 230 523309 MOORE_CNTY6 230 1 | B | 284 | 49.0503 | 113.4078 |  |  |  | Add 3-winding transformer 523219 XIT_INTG TR1 13 523220 XIT_INTG 3 115 523221 XIT_INTG 6 230 M2
05ALL | ERIS | Thermal | 523959 POTTER_CO 6 230 524010 ROLLHILLS 6 230 1 | 29SP | T0 | MULTIGEN523978 | B | 548 | 44.0027 | 114.0984 |  |  |  | Rebuild line 523959 POTTER_CO 6 230 524010 ROLLHILLS 6 230 1
05ALL | ERIS | Thermal | 524875 OASIS 6 230 781740 G24-159-TAP 230 1 | 29SP | T0 | Single 527799 EDDY_NORTH6 230 786270 G24-310-TAP 230 1 | B | 319 | -23.7319 | 120.7292 |  |  |  | Rebuild line 524875 OASIS 6 230 781740 G24-159-TAP 230 1
05ALL | ERIS | Thermal | 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | 29SP | T0 | Single 525832 TUCO_INT7 345 526000 CRAWFISH_DR 345 2 | B | 997 | 86.6474 | 111.09 |  |  |  | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1
05ALL | ERIS | Thermal | 527891 HOBBS_INT 3 115 784800 G24-261-TAP 115 1 | 29SP | T0 | Single 528333 LE-WEST_SUB3 115 528334 LE-NRTH_INT3 115 1 | B | 199 | 33.6926 | 101.8764 |  |  |  | Rebuild line 527891 HOBBS_INT 3 115 784800 G24-261-TAP 115 1
05ALL | ERIS | Thermal | 528333 LE-WEST_SUB3 115 528334 LE-NRTH_INT3 115 1 | 29SP | T0 | Single 527891 HOBBS_INT3 115 784800 G24-261-TAP 115 1 | B | 199.4 | 34.9072 | 102.4732 |  |  |  | Rebuild line 528333 LE-WEST_SUB3 115 528334 LE-NRTH_INT3 115 1
05ALL | ERIS | Thermal | 528526 TEAGUE 3 115 528596 CARDINAL 3 115 1 | 29SP | T0 | Single 528540 WHITTEN3 115 528547 S_JAL3 115 1 | B | 175 | -6.7979 | 138.2602 |  |  |  | Multi - Battle Axe - Wolfcamp Tap 115 kV DblCkt_Battle Axe - Ponderosa - Dollarhide 115 kV New Line.idv : PID : 900119, NTC, 2025 ITP, ISD: 6/1/2029
05ALL | ERIS | Thermal | 528526 TEAGUE 3 115 785400 G24-281-TAP 115 1 | 29SP | T0 | Single 528540 WHITTEN3 115 528547 S_JAL3 115 1 | B | 154 | 9.1753 | 160.9054 |  |  |  | Multi - Battle Axe - Wolfcamp Tap 115 kV DblCkt_Battle Axe - Ponderosa - Dollarhide 115 kV New Line.idv : PID : 900119, NTC, 2025 ITP, ISD: 6/1/2029
05ALL | ERIS | Thermal | 528540 WHITTEN 3 115 528547 S_JAL 3 115 1 | 29SP | T0 | Single 528526 TEAGUE3 115 785400 G24-281-TAP 115 1 | B | 239 | 6.1466 | 103.9331 |  |  |  | Multi - Battle Axe - Wolfcamp Tap 115 kV DblCkt_Battle Axe - Ponderosa - Dollarhide 115 kV New Line.idv : PID : 900119, NTC, 2025 ITP, ISD: 6/1/2029
05ALL | ERIS | Thermal | 528547 S_JAL 3 115 785400 G24-281-TAP 115 1 | 29SP | T0 | Single 528526 TEAGUE3 115 785400 G24-281-TAP 115 1 | B | 154 | -6.063 | 158.4648 |  |  |  | Rebuild line 528547 S_JAL 3 115 785400 G24-281-TAP 115 1
05ALL | ERIS | Thermal | 531405 WALKMYR3 115 531510 HARBNGR3 115 1 | 29SP | T0 | P23:345:SUNC:HLC_BRK188:::EHV: | B | 331.39 | 77.9663 | 122.4803 |  |  |  | Rebuild line 531405 WALKMYR3 115 531510 HARBNGR3 115 1
05ALL | ERIS | Thermal | 531510 HARBNGR3 115 3WXFMR 534:HARBGR345 345 1 | 29SP | T0 | P23:345:SUNC:HLC_BRK188:::EHV: | B | 385 | 67.7801 | 105.7318 |  |  |  | Add 3-winding transformer 531510 HARBNGR3 115 531511 HARBNGR-1 13 531512 HARBNGR7 345 M2
05ALL | ERIS | Thermal | 531512 HARBNGR7 345 3WXFMR 534:HARBGR345 345 1 | 29SP | T0 | P23:345:SUNC:HLC_BRK188:::EHV: | B | 385 | 67.9598 | 107.8261 |  |  |  | Add 3-winding transformer 531510 HARBNGR3 115 531511 HARBNGR-1 13 531512 HARBNGR7 345 M2
05ALL | ERIS | Thermal | 523216 RB-HOGUE 3 115 523246 DALHART 3 115 1 | 29SP | T1 | Single 523228 DALLAM3 115 523235 HILMRCHZ_TP3 115 1 | B | 82 | 63.9733 | 108.5963 |  |  |  | Rebuild line 523216 RB-HOGUE 3 115 523246 DALHART 3 115 1
05ALL | ERIS | Thermal | 523220 XIT_INTG 3 115 523228 DALLAM 3 115 1 | 29SP | T1 | Single 523221 XIT_INTG6 230 523309 MOORE_CNTY6 230 1 | B | 297 | 42.493 | 107.6799 |  |  |  | Rebuild line 523220 XIT_INTG 3 115 523228 DALLAM 3 115 1
05ALL | ERIS | Thermal | 528526 TEAGUE 3 115 528596 CARDINAL 3 115 1 | 29SP | T1 | Single 528547 S_JAL3 115 785400 G24-281-TAP 115 1 | B | 175 | -5.2999 | 135.7216 |  |  |  | Rebuild line 528526 TEAGUE 3 115 528596 CARDINAL 3 115 1
05ALL | ERIS | Thermal | 528526 TEAGUE 3 115 785400 G24-281-TAP 115 1 | 29SP | T1 | Single 528547 S_JAL3 115 785400 G24-281-TAP 115 1 | B | 154 | -5.5491 | 158.0142 |  |  |  | Rebuild line 528526 TEAGUE 3 115 785400 G24-281-TAP 115 1
05ALL | ERIS | Thermal | 528547 S_JAL 3 115 528561 DOLLARHIDE 3 115 1 | 29SP | T1 | P12:115:SPS:W81.1.CUSMTN.PONDEROSA:::HV: | B | 106 | 79.4908 | 123.9245 |  |  |  | Rebuild line 528547 S_JAL 3 115 528561 DOLLARHIDE 3 115 1
05ALL | ERIS | Thermal | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | 29WP | T0 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | B | 373 | 46.8464 | 107.2951 |  |  |  | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
05ALL | ERIS | Thermal | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | 29WP | T0 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | B | 373 | 47.3063 | 107.2951 |  |  |  | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
05ALL | ERIS | Thermal | 524875 OASIS 6 230 781740 G24-159-TAP 230 1 | 29WP | T0 | Single 527799 EDDY_NORTH6 230 786270 G24-310-TAP 230 1 | B | 319 | -31.1392 | 117.1851 |  |  |  | Rebuild line 524875 OASIS 6 230 781740 G24-159-TAP 230 1
05ALL | ERIS | Thermal | 527020 SIDEWINDER 7 345 527896 HOBBS_INT 7 345 1 | 29WP | T0 | Single 528027 RDRUNNER7 345 528604 ANDREWS6 345 1 | B | 797 | 84.0111 | 104.3766 |  |  |  | 22.DIS2001_ERIS_G00_Line_Uprate_Hobbs_to_Sidewinder_345kV_Line.idv : DISIS-2020-001 Upgrade
05ALL | ERIS | Thermal | 527891 HOBBS_INT 3 115 784800 G24-261-TAP 115 1 | 29WP | T0 | Single 528333 LE-WEST_SUB3 115 528334 LE-NRTH_INT3 115 1 | B | 199 | 33.7121 | 102.1468 |  |  |  | Rebuild line 527891 HOBBS_INT 3 115 784800 G24-261-TAP 115 1
05ALL | ERIS | Thermal | 528333 LE-WEST_SUB3 115 528334 LE-NRTH_INT3 115 1 | 29WP | T0 | Single 527891 HOBBS_INT3 115 784800 G24-261-TAP 115 1 | B | 199.4 | 34.7355 | 102.7319 |  |  |  | Rebuild line 528333 LE-WEST_SUB3 115 528334 LE-NRTH_INT3 115 1
05ALL | ERIS | Thermal | 528526 TEAGUE 3 115 528596 CARDINAL 3 115 1 | 29WP | T0 | Single 528540 WHITTEN3 115 528547 S_JAL3 115 1 | B | 194 | -6.202 | 124.999 |  |  |  | Multi - Battle Axe - Wolfcamp Tap 115 kV DblCkt_Battle Axe - Ponderosa - Dollarhide 115 kV New Line.idv : PID : 900119, NTC, 2025 ITP, ISD: 6/1/2029
05ALL | ERIS | Thermal | 528526 TEAGUE 3 115 785400 G24-281-TAP 115 1 | 29WP | T0 | Single 528540 WHITTEN3 115 528547 S_JAL3 115 1 | B | 154 | 9.3815 | 161.1693 |  |  |  | Multi - Battle Axe - Wolfcamp Tap 115 kV DblCkt_Battle Axe - Ponderosa - Dollarhide 115 kV New Line.idv : PID : 900119, NTC, 2025 ITP, ISD: 6/1/2029
05ALL | ERIS | Thermal | 528540 WHITTEN 3 115 528547 S_JAL 3 115 1 | 29WP | T0 | Single 528526 TEAGUE3 115 785400 G24-281-TAP 115 1 | B | 239 | 6.3078 | 104.0301 |  |  |  | Multi - Battle Axe - Wolfcamp Tap 115 kV DblCkt_Battle Axe - Ponderosa - Dollarhide 115 kV New Line.idv : PID : 900119, NTC, 2025 ITP, ISD: 6/1/2029
05ALL | ERIS | Thermal | 528547 S_JAL 3 115 785400 G24-281-TAP 115 1 | 29WP | T0 | Single 528526 TEAGUE3 115 785400 G24-281-TAP 115 1 | B | 154 | -6.0788 | 158.331 |  |  |  | Rebuild line 528547 S_JAL 3 115 785400 G24-281-TAP 115 1
05ALL | ERIS | Thermal | 528526 TEAGUE 3 115 528596 CARDINAL 3 115 1 | 29WP | T1 | Single 528547 S_JAL3 115 785400 G24-281-TAP 115 1 | B | 194 | -4.7639 | 122.347 |  |  |  | Rebuild line 528526 TEAGUE 3 115 528596 CARDINAL 3 115 1
05ALL | ERIS | Thermal | 528526 TEAGUE 3 115 785400 G24-281-TAP 115 1 | 29WP | T1 | Single 528547 S_JAL3 115 785400 G24-281-TAP 115 1 | B | 154 | -5.5636 | 157.8172 |  |  |  | Rebuild line 528526 TEAGUE 3 115 785400 G24-281-TAP 115 1
05ALL | ERIS | Thermal | 528547 S_JAL 3 115 528561 DOLLARHIDE 3 115 1 | 29WP | T1 | Single 528540 WHITTEN3 115 528547 S_JAL3 115 1 | B | 117 | 27.927 | 109.4992 |  |  |  | Rebuild line 528547 S_JAL 3 115 528561 DOLLARHIDE 3 115 1
05ALL | ERIS | Voltage | CLARREC2 | 26SP | V | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 |  |  |  |  | 0.91286 | 0.92 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | G23-015-TAP | 26SP | V | P42:345:SPS:FINNEY_OR70:::EHV: |  |  |  |  | 1.0552 | 0.9 | 1.05 | None
05ALL | ERIS | Voltage | GB-SHAMROCK | 26SP | V | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 |  |  |  |  | 0.86644 | 0.92 | 1.05 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
05ALL | ERIS | Voltage | GEN-2023-015 | 26SP | V | P42:345:SPS:FINNEY_OR70:::EHV: |  |  |  |  | 1.0552 | 0.9 | 1.05 | None
05ALL | ERIS | Voltage | HEDLEY 2 | 26SP | V | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 |  |  |  |  | 0.91964 | 0.92 | 1.05 | Add 3.6 MVAR switched shunt at HEDLEY 2 69 kV
05ALL | ERIS | Voltage | HI_BNKS1_WF7 | 26SP | V | P42:345:OKGE:SB_DGSE7313:::EHV: |  |  |  |  | 1.0712 | 0.95 | 1.05 | None
05ALL | ERIS | Voltage | HI_BNKS2_WF7 | 26SP | V | P42:345:OKGE:SB_DGSE7313:::EHV: |  |  |  |  | 1.076 | 0.95 | 1.05 | None
05ALL | ERIS | Voltage | HOLLIS 4 | 26SP | V | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 |  |  |  |  | 0.91629 | 0.92 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | HOLTP4WT | 26SP | V | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 |  |  |  |  | 0.9172 | 0.92 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | NP-GLAZIR_G2 | 26SP | V | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 |  |  |  |  | 0.66169 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | NP-LIPSCOMB2 | 26SP | V | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 |  |  |  |  | 0.62318 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | NP-LIPS_SHA2 | 26SP | V | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 |  |  |  |  | 0.62318 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | NP-LUCKY_CR2 | 26SP | V | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 |  |  |  |  | 0.7517 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | NP-LUCKY_G 2 | 26SP | V | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 |  |  |  |  | 0.75184 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | NP-SHATTUCK2 | 26SP | V | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 |  |  |  |  | 0.60173 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | NP-SHATTUCK2 | 26SP | V | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 |  |  |  |  | 0.60173 | 0.9 | 1.05 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
05ALL | ERIS | Voltage | NP-SUB_A 2 | 26SP | V | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 |  |  |  |  | 0.81767 | 0.9 | 1.05 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
05ALL | ERIS | Voltage | NP-SUB_A 2 | 26SP | V | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 |  |  |  |  | 0.81767 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | NP-VALERO_P2 | 26SP | V | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 |  |  |  |  | 0.63127 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | RB-477_TP 2 | 26SP | V | P12:115:SPS:W80.1.XIT.DALM:::HV: |  |  |  |  | 0.89029 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | RB-DALHART 2 | 26SP | V | P12:115:SPS:W80.1.XIT.DALM:::HV: |  |  |  |  | 0.89264 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | RB-DALLAM 2 | 26SP | V | P12:115:SPS:W80.1.XIT.DALM:::HV: |  |  |  |  | 0.89491 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | RB-NMO1_SW 2 | 26SP | V | P12:115:SPS:W80.1.XIT.DALM:::HV: |  |  |  |  | 0.80331 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | RB-N_SEDAN 2 | 26SP | V | P12:115:SPS:W80.1.XIT.DALM:::HV: |  |  |  |  | 0.8153 | 0.9 | 1.05 | Add 8 MVAR switched shunt at RB-N_SEDAN 2 69 kV
05ALL | ERIS | Voltage | RB-TEXLINE 2 | 26SP | V | P12:115:SPS:W80.1.XIT.DALM:::HV: |  |  |  |  | 0.80331 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | RB-TEXLN_SW2 | 26SP | V | P12:115:SPS:W80.1.XIT.DALM:::HV: |  |  |  |  | 0.80628 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | RB-TEXRURAL2 | 26SP | V | P12:115:SPS:W80.1.XIT.DALM:::HV: |  |  |  |  | 0.8051 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | SHAM 3WT | 26SP | V | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 |  |  |  |  | 0.89172 | 0.92 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | SHAM 4WT | 26SP | V | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 |  |  |  |  | 0.90581 | 0.92 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | WELL 4WT | 26SP | V | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 |  |  |  |  | 0.90958 | 0.92 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | WELLGS4 | 26SP | V | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 |  |  |  |  | 0.90938 | 0.92 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | BLACKRIVER 3 | 29SP | V | Single 528182 NORTH_LOVNG3 115 528193 BLACKRIVER3 115 1 |  |  |  |  | 0.84688 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | G23-015-TAP | 29SP | V | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 |  |  |  |  | 1.0527 | 0.9 | 1.05 | None
05ALL | ERIS | Voltage | GB-SHAMROCK | 29SP | V | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 |  |  |  |  | 0.89741 | 0.92 | 1.05 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
05ALL | ERIS | Voltage | GEN-2023-015 | 29SP | V | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 |  |  |  |  | 1.0527 | 0.9 | 1.05 | None
05ALL | ERIS | Voltage | HI_BNKS1_WF7 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 1.07 | 0.95 | 1.05 | None
05ALL | ERIS | Voltage | HI_BNKS2_WF7 | 29SP | V | P51:13:WERE:EMPEC 7:EHV: |  |  |  |  | 1.0748 | 0.95 | 1.05 | None
05ALL | ERIS | Voltage | NP-BOOKER 2 | 29SP | V | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 |  |  |  |  | 0.89759 | 0.9 | 1.05 | Add 1.6 MVAR switched shunt at NP-BOOKER 2 69 kV
05ALL | ERIS | Voltage | NP-GLAZIR_G2 | 29SP | V | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 |  |  |  |  | 0.65842 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | NP-LIPSCOMB2 | 29SP | V | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 |  |  |  |  | 0.61687 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | NP-LIPS_SHA2 | 29SP | V | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 |  |  |  |  | 0.61687 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | NP-LUCKY_CR2 | 29SP | V | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 |  |  |  |  | 0.75603 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | NP-LUCKY_G 2 | 29SP | V | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 |  |  |  |  | 0.75618 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | NP-LUCKY_G 2 | 29SP | V | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 |  |  |  |  | 0.75618 | 0.9 | 1.05 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
05ALL | ERIS | Voltage | NP-SHATTUCK2 | 29SP | V | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 |  |  |  |  | 0.59381 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | NP-SUB_A 2 | 29SP | V | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 |  |  |  |  | 0.82771 | 0.9 | 1.05 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
05ALL | ERIS | Voltage | NP-SUB_A 2 | 29SP | V | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 |  |  |  |  | 0.82771 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | NP-VALERO_P2 | 29SP | V | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 |  |  |  |  | 0.62558 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | SENDERO +3 | 29SP | V | Single 528182 NORTH_LOVNG3 115 528193 BLACKRIVER3 115 1 |  |  |  |  | 0.84743 | 0.9 | 1.05 | Add 69 MVAR switched shunt at SENDERO +3 115 kV
05ALL | ERIS | Voltage | BLACKRIVER 3 | 29WP | V | Single 528182 NORTH_LOVNG3 115 528193 BLACKRIVER3 115 1 |  |  |  |  | 0.851 | 0.9 | 1.05 | None
05ALL | ERIS | Voltage | RB-NMO1_SW 2 | 29WP | V | P12:115:SPS:W80.1.XIT.DALM:::HV: |  |  |  |  | 0.8666 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | RB-N_SEDAN 2 | 29WP | V | P12:115:SPS:W80.1.XIT.DALM:::HV: |  |  |  |  | 0.89033 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | RB-TEXLINE 2 | 29WP | V | P12:115:SPS:W80.1.XIT.DALM:::HV: |  |  |  |  | 0.8666 | 0.9 | 1.05 | Add 2.1 MVAR switched shunt at RB-TEXLINE 2 69 kV
05ALL | ERIS | Voltage | RB-TEXLN_SW2 | 29WP | V | P12:115:SPS:W80.1.XIT.DALM:::HV: |  |  |  |  | 0.87231 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | RB-TEXRURAL2 | 29WP | V | P12:115:SPS:W80.1.XIT.DALM:::HV: |  |  |  |  | 0.87003 | 0.9 | 1.05 | Mitigated at another bus
05ALL | ERIS | Voltage | SENDERO +3 | 29WP | V | Single 528182 NORTH_LOVNG3 115 528193 BLACKRIVER3 115 1 |  |  |  |  | 0.8516 | 0.9 | 1.05 | None
WECC | ERIS | Non-Converged | None | 26SP, 31WP, 31SP | WECC | None | [7 empty] | None
WECC | ERIS | Thermal | None | 26SP, 31WP, 31SP | WECC | None | [7 empty] | None
WECC | ERIS | Voltage | None | 26SP, 31WP, 31SP | WECC | None | [7 empty] | None
WECC | NRIS | Non-Converged | None | 26SP, 31WP, 31SP | WECC | None | [7 empty] | None
WECC | NRIS | Thermal | None | 26SP, 31WP, 31SP | WECC | None | [7 empty] | None
WECC | NRIS | Voltage | None | 26SP, 31WP, 31SP | WECC | None | [7 empty] | None

## Assigned Upgrade Costs
Gen Number | Group | Upgrade ID | Service Type | Upgrade Name | Upgrade Type | Upgrade length (miles) | Upgrade Rating (MVA) | Allocated Cost | %Allocated | Total Upgrade Cost | PTDF
ASGI-2024-001 | 01 NORTH | 900426 | ERIS | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030 | Contingent |  |  | 0 | 0 | 2372127948.71 | N/A
ASGI-2024-001 | 01 NORTH | TBD | ERIS | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV | Current Study |  |  | 459.6289 | 0.033306 | 1380000 | 0.01904
ASGI-2024-001 | 01 NORTH | TBD | ERIS | Add 2 MVAR switched shunt at GEN-2017-140 345 kV | Current Study |  |  | 4947.775 | 0.093354 | 5300000 | 0.062456
ASGI-2024-001 | 01 NORTH | TBD | ERIS | Add 23 MVAR switched shunt at FINNEY 7 345 kV | Current Study |  |  | 9088.4002 | 0.17148 | 5300000 | 0.033254
ASGI-2024-001 | 01 NORTH | TBD | ERIS | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | Current Study | 45.48 | (1793.00, 1793.00) | 46674.7891 | 0.046649 | 100056000 | 0.0071862
ASGI-2024-002 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 5158.7638 | 0.37382 | 1380000 | 0.087099
ASGI-2024-002 | 05 SOUTHWEST | TBD | ERIS | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV | Current Study |  |  | 6645.4918 | 0.48156 | 1380000 | 0.15692
ASGI-2024-002 | 05 SOUTHWEST | TBD | ERIS | Add 1.6 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 4069.6198 | 0.2949 | 1380000 | 0.073563
ASGI-2024-002 | 05 SOUTHWEST | TBD | ERIS | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 3482.3154 | 0.25234 | 1380000 | 0.073563
ASGI-2024-002 | 05 SOUTHWEST | TBD | ERIS | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV | Current Study |  |  | 3482.3154 | 0.25234 | 1380000 | 0.073563
ASGI-2024-002 | 05 SOUTHWEST | TBD | ERIS | Add 3.6 MVAR switched shunt at HEDLEY 2 69 kV | Current Study |  |  | 6933.5959 | 0.50243 | 1380000 | 0.0030837
ASGI-2024-002 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2 | Current Study |  | (339.00, 330.00) | 57966.3768 | 0.41405 | 14000000 | 0.019639
ASGI-2024-002 | 05 SOUTHWEST | TBD | ERIS | Add line 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 P2 | Current Study | 66.8 | (1011.00, 1176.00) | 550130.1846 | 0.25342 | 217080000 | 0.0371
ASGI-2024-002 | 05 SOUTHWEST | TBD | ERIS | Apply contingent IDV 01_NewLine_Phantom_Crossroads_Potter_765_26SP.idv | Contingent |  |  | 0 | 0 | 3275253469 | N/A
ASGI-2024-002 | 05 SOUTHWEST | TBD | ERIS | Apply contingent IDV 02_765_Phantom_Craw_1_DIS24_TC05ALL-26SP.idv | Contingent |  |  | 0 | 0 | 1366342009.82 | N/A
ASGI-2024-002 | 05 SOUTHWEST | TBD | ERIS | Apply contingent IDV 02_765_Phantom_Craw_1_DIS24_TC05ALL-29SP.idv | Contingent |  |  | 0 | 0 | 1366342009.82 | N/A
ASGI-2024-002 | 05 SOUTHWEST | 900427 | ERIS | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032 | Contingent |  |  | 0 | 0 | 1790026304.1702 | N/A
ASGI-2024-002 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | Current Study | 18.75 | (519.00, 519.00) | 147503.7266 | 0.41405 | 35625000 | 0.039277
ASGI-2024-002 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Current Study | 57.98 | (1793.00, 1793.00) | 321864.5821 | 0.25233 | 127556000 | 0.073556
ASGI-2024-002 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | Current Study | 3.02 | (1793.00, 1793.00) | 7152.0915 | 0.10765 | 6644000 | 0.033089
ASGI-2024-003 | 03 CENTRAL | TBD | ERIS | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV | Current Study |  |  | 48692.0819 | 3.5284 | 1380000 | 0.43224
ASGI-2024-003 | 03 CENTRAL | TBD | NRIS | Add 11 MVAR switched shunt at WWRDEHV4 138 kV | Current Study |  |  | 29404.0922 | 1.2088 | 2432500 | 0.05677
ASGI-2024-003 | 03 CENTRAL | TBD | NRIS | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV | Current Study |  |  | 8051.8204 | 0.35008 | 2300000 | 0.045918
ASGI-2024-003 | 03 CENTRAL | TBD | NRIS | Add 45 MVAR switched shunt at PR BRZ 4 230 kV | Current Study |  |  | 30913.8828 | 0.80821 | 3825000 | 0.034775
ASGI-2024-003 | 03 CENTRAL | TBD | NRIS | Add 8 MVAR switched shunt at JHNCRSOL 115 kV | Current Study |  |  | 2212500 | 100 | 2212500 | 0.04997
ASGI-2024-003 | 03 CENTRAL | TBD | NRIS | Rebuild line 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Current Study | 27.23 | (217.00, 217.00) | 27230000 | 100 | 27230000 | 0.085843
ASGI-2024-003 | 03 CENTRAL | TBD | NRIS | Rebuild line 531481 HUGOTON3 115 531483 GRANTTP3 115 1 | Current Study | 18.19 | (260.00, 260.00) | 16718532.5164 | 91.9106 | 18190000 | 0.25628
ASGI-2024-003 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640525 TOBIAS 3 345 1 | Current Study | 26.47 | (1793.00, 1793.00) | 998020.6579 | 1.7138 | 58234000 | 0.035278
ASGI-2024-006 | 03 CENTRAL | TBD | ERIS | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV | Current Study |  |  | 21533.2984 | 1.5604 | 1380000 | 0.15254
ASGI-2024-006 | 03 CENTRAL | TBD | NRIS | Add 11 MVAR switched shunt at WWRDEHV4 138 kV | Current Study |  |  | 79159.7532 | 3.2543 | 2432500 | 0.12196
ASGI-2024-006 | 03 CENTRAL | TBD | NRIS | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV | Current Study |  |  | 16865.3599 | 0.73328 | 2300000 | 0.076752
ASGI-2024-006 | 03 CENTRAL | TBD | NRIS | Rebuild line 531481 HUGOTON3 115 531483 GRANTTP3 115 1 | Current Study | 18.19 | (260.00, 260.00) | 1471467.4836 | 8.0894 | 18190000 | 0.018
ASGI-2024-007 | 03 CENTRAL | 900426 | ERIS | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030 | Contingent |  |  | 0 | 0 | 2372127948.71 | N/A
ASGI-2024-007 | 03 CENTRAL | TBD | ERIS | Add 2 MVAR switched shunt at GEN-2017-140 345 kV | Current Study |  |  | 10763.8457 | 0.20309 | 5300000 | 0.048414
ASGI-2024-007 | 03 CENTRAL | TBD | ERIS | Add 7 MVAR switched shunt at SWAVRLY5 161 kV | Current Study |  |  | 1164023.4346 | 35.8161 | 3250000 | 0.058802
ASGI-2024-007 | 03 CENTRAL | TBD | ERIS | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2 | Current Study | 0.75 | (2390.00, 2390.00) | 14241.7104 | 0.080122 | 17775000 | 0.0091571
ASGI-2024-008 | 03 CENTRAL | 900426 | ERIS | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030 | Contingent |  |  | 0 | 0 | 2372127948.71 | N/A
ASGI-2024-008 | 03 CENTRAL | TBD | ERIS | Add 2 MVAR switched shunt at GEN-2017-140 345 kV | Current Study |  |  | 19289.2421 | 0.36395 | 5300000 | 0.048414
ASGI-2024-008 | 03 CENTRAL | TBD | ERIS | Add 7 MVAR switched shunt at SWAVRLY5 161 kV | Current Study |  |  | 2085976.5654 | 64.1839 | 3250000 | 0.058802
ASGI-2024-008 | 03 CENTRAL | TBD | ERIS | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2 | Current Study | 0.75 | (2390.00, 2390.00) | 25521.7147 | 0.14358 | 17775000 | 0.0091571
ASGI-2024-020 | 03 CENTRAL | TBD | ERIS | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV | Current Study |  |  | 9627.8242 | 0.69767 | 1380000 | 0.051833
ASGI-2024-020 | 03 CENTRAL | TBD | ERIS | Add 23 MVAR switched shunt at FINNEY 7 345 kV | Current Study |  |  | 109003.3944 | 2.0567 | 5300000 | 0.051833
ASGI-2024-020 | 03 CENTRAL | TBD | NRIS | Add 7 MVAR switched shunt at EHALLTP3 115 kV | Current Study |  |  | 2212500 | 100 | 2212500 | 0.033284
ASGI-2024-020 | 03 CENTRAL | TBD | ERIS | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2 | Current Study | 0.75 | (2390.00, 2390.00) | 22524.9455 | 0.12672 | 17775000 | 0.0052823
ASGI-2024-020 | 03 CENTRAL | TBD | ERIS | Rebuild line 533417 EMCPHER3 115 533426 MANVILE3 115 1 | Current Study | 5.7 | (176.00, 176.00) | 5700000 | 100 | 5700000 | 0.56039
ASGI-2024-020 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 | Current Study | 19.87 | (1793.00, 1793.00) | 758998.2562 | 1.7363 | 43714000 | 0.031066
ASGI-2024-020 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 | Current Study | 16.71 | (1793.00, 1793.00) | 635049.7124 | 1.7275 | 36762000 | 0.047539
ASGI-2024-023 | 04 SOUTHEAST | 92976 | ERIS | 2023ITP PORTFOLIO - REPLACE TURK 138_115 KV CKT 1 XFMR.idv : 2023 ITP upgrade, PID : 92976, NTC, ISD : 4/25/2027 | Contingent |  |  | 0 | 0 | 5250000 | N/A
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 63624.038 | 4.6104 | 1380000 | 0.085204
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at PHILL 7 345 kV | Current Study |  |  | 335360.0647 | 6.3275 | 5300000 | 0.03435
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 66388.803 | 1.2526 | 5300000 | 0.031974
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV | Current Study |  |  | 63624.038 | 4.6104 | 1380000 | 0.085204
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add 0.2 MVAR switched shunt at GROVE 5 161 kV | Current Study |  |  | 78279.6438 | 2.4086 | 3250000 | 0.065476
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add 0.25 MVAR switched shunt at LABETTS2 69 kV | Current Study |  |  | 36051.1106 | 2.6124 | 1380000 | 0.065476
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add 11 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 146434.7835 | 4.5057 | 3250000 | 0.085204
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 144807.7893 | 1.2067 | 12000000 | 0.031974
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR switched shunt at NEOSHO 4 138 kV | Current Study |  |  | 52089.4921 | 2.1414 | 2432500 | 0.085204
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at CPK446 5 161 kV | Current Study |  |  | 111152.8204 | 3.4201 | 3250000 | 0.085204
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add 24 MVAR switched shunt at GROVE 4 138 kV | Current Study |  |  | 70409.3509 | 2.8945 | 2432500 | 0.085204
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV | Current Study |  |  | 26305.6214 | 1.9062 | 1380000 | 0.040401
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at INDEPCO5 161 kV | Current Study |  |  | 146434.7835 | 4.5057 | 3250000 | 0.085204
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 40710.115 | 1.2526 | 3250000 | 0.031974
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Add 45 MVAR switched shunt at NEVADA 5 161 kV | Current Study |  |  | 57310.2677 | 1.7634 | 3250000 | 0.031974
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | Current Study | 14.95 | (329.00, 329.00) | 7923951.2405 | 53.003 | 14950000 | 0.23064
ASGI-2024-023 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508359 WELSH 7 345 508841 WILKES 7 345 1 | Current Study | 30.63 | (1793.00, 1793.00) | 5214016.0145 | 7.7375 | 67386000 | 0.085032
ASGI-2024-024 | 03 CENTRAL | 94615 | ERIS | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029 | Contingent |  |  | 0 | 0 | 543515503 | N/A
ASGI-2024-024 | 03 CENTRAL | TBD | ERIS | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV | Current Study |  |  | 72542.0438 | 5.2567 | 1380000 | 0.18384
ASGI-2024-024 | 03 CENTRAL | TBD | ERIS | Add 16 MVAR switched shunt at HUMBOLT5 161 kV | Current Study |  |  | 138442.4206 | 4.2598 | 3250000 | 0.13097
ASGI-2024-024 | 03 CENTRAL | TBD | ERIS | Add 21 MVAR switched shunt at S1263 5 161 kV | Current Study |  |  | 138442.4206 | 4.2598 | 3250000 | 0.13097
ASGI-2024-024 | 03 CENTRAL | TBD | ERIS | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV | Current Study |  |  | 58784.7817 | 4.2598 | 1380000 | 0.13097
ASGI-2024-024 | 03 CENTRAL | TBD | ERIS | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2 | Current Study | 0.75 | (2390.00, 2390.00) | 79243.5881 | 0.44581 | 17775000 | 0.030952
ASGI-2024-024 | 03 CENTRAL | 94721 | ERIS | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 213682884 | N/A
ASGI-2024-024 | 03 CENTRAL | 94929 | ERIS | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 413934522 | N/A
ASGI-2024-024 | 03 CENTRAL | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 79549.962 | 0.68225 | 11660000 | 0.047623
ASGI-2024-024 | 03 CENTRAL | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 553005.1777 | 0.5884 | 93984000 | 0.047623
ASGI-2024-024 | 03 CENTRAL | TBD | ERIS | Rebuild line 541251 MARYVLE5 161 541369 MIDWAY_5 161 1 | Current Study | 19.5 | (246.00, 246.00) | 9203983.8994 | 31.4666 | 29250000 | 0.078403
ASGI-2024-024 | 03 CENTRAL | TBD | ERIS | Rebuild line 541251 MARYVLE5 161 635038 BRADDYVILLE5 161 1 | Current Study | 16.92 | (246.00, 246.00) | 25380000 | 100 | 25380000 | 0.036794
ASGI-2024-024 | 03 CENTRAL | TBD | ERIS | Rebuild line 541253 ST JOE 5 161 541394 AVENUECTY 5 161 1 | Current Study | 3.32 | (246.00, 246.00) | 1567037.2588 | 31.4666 | 4980000 | 0.078403
ASGI-2024-024 | 03 CENTRAL | TBD | ERIS | Rebuild line 541254 EAST 5 161 541401 EASTOWN5 161 1 | Current Study | 4.02 | (446.00, 446.00) | 640500.9109 | 10.6219 | 6030000 | 0.091088
ASGI-2024-024 | 03 CENTRAL | TBD | ERIS | Rebuild line 541369 MIDWAY_5 161 541394 AVENUECTY 5 161 1 | Current Study | 20.54 | (246.00, 246.00) | 9694863.0407 | 31.4666 | 30810000 | 0.078403
GEN-2024-003 | 04 SOUTHEAST | 900426 | ERIS | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030 | Contingent |  |  | 0 | 0 | 2372127948.71 | N/A
GEN-2024-003 | 04 SOUTHEAST | TBD | ERIS | Add 2 MVAR switched shunt at GEN-2017-140 345 kV | Current Study |  |  | 63938.9139 | 1.2064 | 5300000 | 0.13504
GEN-2024-003 | 04 SOUTHEAST | 171474 | ERIS | Fitzhugh 161kV GEN-2024-003 Interconnection (Non-Shared NU) (AECC) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-003 | 04 SOUTHEAST | 171473 | ERIS | Fitzhugh 161kV GEN-2024-003 Interconnection (TOIF) (AECC) | Interconnection |  |  | 1750000 | 100 | 1750000 | 1
GEN-2024-003 | 04 SOUTHEAST | TBD | ERIS | Rebuild 3-winding transformer 515336 VBI 2 69 515339 VBI 5 161 515769 VBI 1 13 2 | Current Study |  | (90.00, 90.00) | 6075000 | 100 | 6075000 | 0.034492
GEN-2024-003 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 505522 VAN BUR5 161 505524 LIBERTY5 161 1 | Current Study | 12.1 | (309.00, 309.00) | 4320664.5898 | 23.8053 | 18150000 | 0.11174
GEN-2024-003 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 505552 GORE 5 161 505558 MUSKTAP5 161 1 | Current Study | 16 | (246.00, 246.00) | 5051949.4844 | 21.0498 | 24000000 | 0.077126
GEN-2024-003 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514934 DRAPER 7 345 515045 SEMINOL7 345 2 | Current Study | 44.14 | (1793.00, 1793.00) | 813983.2037 | 0.83822 | 97108000 | 0.033628
GEN-2024-013 | 04 SOUTHEAST | 92996 | NRIS | 524_SW134TP4-WESTMOR4_extendLine.idv : 2023 ITP, PID: 92996, NTC, ISD: 12/15/2025 (marked as in service) | Contingent |  |  | 0 | 0 | 9666986 | N/A
GEN-2024-013 | 04 SOUTHEAST | TBD | ERIS | Add 2 MVAR switched shunt at GEN-2017-140 345 kV | Current Study |  |  | 122154.1187 | 2.3048 | 5300000 | 0.05316
GEN-2024-013 | 04 SOUTHEAST | TBD | ERIS | Add 23 MVAR switched shunt at FINNEY 7 345 kV | Current Study |  |  | 230070.1906 | 4.3409 | 5300000 | 0.029022
GEN-2024-013 | 04 SOUTHEAST | TBD | NRIS | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV | Current Study |  |  | 41543.4222 | 1.8062 | 2300000 | 0.038117
GEN-2024-013 | 04 SOUTHEAST | 171478 | ERIS | Norman Hills 345 kV GEN-2024-013 Interconnection (Non-Shared NU) (OGE) | Interconnection |  |  | 2000000 | 100 | 2000000 | 1
GEN-2024-013 | 04 SOUTHEAST | 171477 | ERIS | Norman Hills 345 kV GEN-2024-013 Interconnection (TOIF) (OGE) | Interconnection |  |  | 3500000 | 100 | 3500000 | 1
GEN-2024-015 | 05 SOUTHWEST | 94067 | ERIS | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028 | Contingent |  |  | 0 | 0 | 38846321 | N/A
GEN-2024-015 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 59366.992 | 4.302 | 1380000 | 0.10739
GEN-2024-015 | 05 SOUTHWEST | TBD | ERIS | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV | Current Study |  |  | 38275.0947 | 2.7736 | 1380000 | 0.096833
GEN-2024-015 | 05 SOUTHWEST | TBD | ERIS | Add 1.6 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 77513.4948 | 5.6169 | 1380000 | 0.15012
GEN-2024-015 | 05 SOUTHWEST | TBD | NRIS | Add 10 MVAR switched shunt at DEAFSMITH 6 230 kV | Current Study |  |  | 732572.1316 | 19.1522 | 3825000 | 0.036473
GEN-2024-015 | 05 SOUTHWEST | TBD | NRIS | Add 11 MVAR switched shunt at WWRDEHV4 138 kV | Current Study |  |  | 114010.3601 | 4.687 | 2432500 | 0.062733
GEN-2024-015 | 05 SOUTHWEST | TBD | ERIS | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 66327.1877 | 4.8063 | 1380000 | 0.15012
GEN-2024-015 | 05 SOUTHWEST | TBD | ERIS | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV | Current Study |  |  | 66327.1877 | 4.8063 | 1380000 | 0.15012
GEN-2024-015 | 05 SOUTHWEST | TBD | NRIS | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV | Current Study |  |  | 74437.4644 | 3.2364 | 2300000 | 0.12098
GEN-2024-015 | 05 SOUTHWEST | TBD | ERIS | Add 3.6 MVAR switched shunt at HEDLEY 2 69 kV | Current Study |  |  | 68737.9161 | 4.981 | 1380000 | 0.0032755
GEN-2024-015 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2 | Current Study |  | (339.00, 330.00) | 702185.7762 | 5.0156 | 14000000 | 0.025489
GEN-2024-015 | 05 SOUTHWEST | TBD | ERIS | Add line 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 P2 | Current Study | 66.8 | (1011.00, 1176.00) | 10437527.2792 | 4.8081 | 217080000 | 0.075416
GEN-2024-015 | 05 SOUTHWEST | TBD | ERIS | Apply contingent IDV 01_NewLine_Phantom_Crossroads_Potter_765_26SP.idv | Contingent |  |  | 0 | 0 | 3275253469 | N/A
GEN-2024-015 | 05 SOUTHWEST | TBD | ERIS | Apply contingent IDV 02_765_Phantom_Craw_1_DIS24_TC05ALL-26SP.idv | Contingent |  |  | 0 | 0 | 1366342009.82 | N/A
GEN-2024-015 | 05 SOUTHWEST | TBD | ERIS | Apply contingent IDV 02_765_Phantom_Craw_1_DIS24_TC05ALL-29SP.idv | Contingent |  |  | 0 | 0 | 1366342009.82 | N/A
GEN-2024-015 | 05 SOUTHWEST | 900427 | ERIS | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032 | Contingent |  |  | 0 | 0 | 1790026304.1702 | N/A
GEN-2024-015 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | Current Study | 18.75 | (519.00, 519.00) | 1786812.0198 | 5.0156 | 35625000 | 0.050978
GEN-2024-015 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Current Study | 57.98 | (1793.00, 1793.00) | 6130749.4194 | 4.8063 | 127556000 | 0.15012
GEN-2024-015 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | Current Study | 3.02 | (1793.00, 1793.00) | 347068.7552 | 5.2238 | 6644000 | 0.17204
GEN-2024-015 | 05 SOUTHWEST | 171480 | ERIS | Sundown-Amaco-Yoakum 230 kV Substation GEN-2024-015 Interconnection (Non-Shared NU) (SPS) | Interconnection |  |  | 24794114 | 100 | 24794114 | 1
GEN-2024-015 | 05 SOUTHWEST | 171479 | ERIS | Sundown-Amaco-Yoakum 230 kV Substation GEN-2024-015 Interconnection (TOIF) (SPS) | Interconnection |  |  | 3766557 | 100 | 3766557 | 1
GEN-2024-017 | 02 NEBRASKA | TBD | ERIS | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV | Current Study |  |  | 3996.4376 | 0.2896 | 1380000 | 0.045661
GEN-2024-017 | 02 NEBRASKA | TBD | NRIS | Add 108 MVAR switched shunt at MAURINE4 230 kV | Current Study |  |  | 63569.5819 | 1.6619 | 3825000 | 0.037073
GEN-2024-017 | 02 NEBRASKA | TBD | NRIS | Add 12 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 41079.9185 | 1.8567 | 2212500 | 0.037073
GEN-2024-017 | 02 NEBRASKA | TBD | NRIS | Add 154 MVAR SVC at WAYSIDE 4 230 kV | Current Study |  |  | 121615.3427 | 1.4141 | 8600000 | 0.04207
GEN-2024-017 | 02 NEBRASKA | TBD | ERIS | Add 2 MVAR switched shunt at GEN-2017-140 345 kV | Current Study |  |  | 9175.2303 | 0.17312 | 5300000 | 0.031944
GEN-2024-017 | 02 NEBRASKA | TBD | ERIS | Add 23 MVAR switched shunt at FINNEY 7 345 kV | Current Study |  |  | 45246.4909 | 0.85371 | 5300000 | 0.045661
GEN-2024-017 | 02 NEBRASKA | TBD | NRIS | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 15705.8451 | 0.70987 | 2212500 | 0.037073
GEN-2024-017 | 02 NEBRASKA | TBD | ERIS | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2 | Current Study |  | (417.00, 417.00) | 72032.027 | 0.42876 | 16800000 | 0.0039686
GEN-2024-017 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 640125 COLMB.E3 345 640127 COLMB.E7 115 640129 COLMB.T9 13 M2 | Current Study |  | (336.00, 336.00) | 632092.6767 | 3.7625 | 16800000 | 0.009093
GEN-2024-017 | 02 NEBRASKA | TBD | ERIS | Add 3-winding transformer 640277 MOORE 3 345 640278 SHELDON7 115 640280 MOORE 9 13 M2 | Current Study |  | (336.00, 400.00) | 736921.0664 | 4.3864 | 16800000 | 0.011046
GEN-2024-017 | 02 NEBRASKA | TBD | ERIS | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2 | Current Study |  | (417.00, 417.00) | 929521.3174 | 5.5329 | 16800000 | 0.015937
GEN-2024-017 | 02 NEBRASKA | TBD | ERIS | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2 | Current Study |  | (417.00, 417.00) | 929521.3174 | 5.5329 | 16800000 | 0.015937
GEN-2024-017 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2 | Current Study |  | (110.00, 120.00) | 226448.1338 | 1.8871 | 12000000 | 0.012885
GEN-2024-017 | 02 NEBRASKA | TBD | NRIS | Add 45 MVAR switched shunt at PR BRZ 4 230 kV | Current Study |  |  | 47760.8322 | 1.2486 | 3825000 | 0.069151
GEN-2024-017 | 02 NEBRASKA | TBD | ERIS | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2 | Current Study | 0.75 | (2390.00, 2390.00) | 657828.1448 | 3.7009 | 17775000 | 0.32739
GEN-2024-017 | 02 NEBRASKA | 171484 | ERIS | Olive Creek 345 kV Substation GEN-2024-017 Interconnection (Non-Shared NU) (NPPD) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-017 | 02 NEBRASKA | 171483 | ERIS | Olive Creek 345 kV Substation GEN-2024-017 Interconnection (TOIF) (NPPD) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-017 | 02 NEBRASKA | TBD | NRIS | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | Current Study | 23.48 | (1793.00, 1793.00) | 824230.0812 | 1.5956 | 51656000 | 0.042048
GEN-2024-017 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640139 COOPER 3 345 640590 OLIVECREEK 3 345 1 | Current Study | 62.88 | (1793.00, 1793.00) | 5166050.7689 | 3.7344 | 138336000 | 0.17566
GEN-2024-017 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | Current Study | 45.48 | (1793.00, 1793.00) | 2582697.2975 | 2.5813 | 100056000 | 0.10967
GEN-2024-017 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 | Current Study | 19.87 | (1793.00, 1793.00) | 1618000.7762 | 3.7013 | 43714000 | 0.14055
GEN-2024-017 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 | Current Study | 16.71 | (1793.00, 1793.00) | 1348901.3897 | 3.6693 | 36762000 | 0.2143
GEN-2024-017 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640278 SHELDON7 115 640591 OLIVECREEK 7 115 1 | Current Study | 1 | (598.00, 598.00) | 31376.4528 | 3.1376 | 1000000 | 0.016398
GEN-2024-017 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640278 SHELDON7 115 640591 OLIVECREEK 7 115 2 | Current Study | 1 | (598.00, 598.00) | 31376.4528 | 3.1376 | 1000000 | 0.016398
GEN-2024-017 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640278 SHELDON7 115 650242 FOLSM&PHIL7 115 1 | Current Study | 15.49 | (329.00, 329.00) | 502172.3377 | 3.2419 | 15490000 | 0.017418
GEN-2024-017 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1 | Current Study | 10.55 | (598.00, 598.00) | 363391.6908 | 3.4445 | 10550000 | 0.022226
GEN-2024-017 | 02 NEBRASKA | TBD | ERIS | Rebuild line 645454 S3454 3 345 645455 S3455 3 345 1 | Current Study | 6.67 | (1793.00, 1793.00) | 538724.2602 | 3.6713 | 14674000 | 0.079217
GEN-2024-017 | 02 NEBRASKA | TBD | NRIS | Rebuild line 645454 S3454 3 345 650185 WAGENER 3 345 1 | Current Study | 33.67 | (1793.00, 1793.00) | 1720512.3084 | 2.3227 | 74074000 | 0.16704
GEN-2024-017 | 02 NEBRASKA | TBD | NRIS | Rebuild line 645456 S3456 3 345 645458 S3458 3 345 1 | Current Study | 44.95 | (1793.00, 1793.00) | 3567860.3398 | 3.6079 | 98890000 | 0.027446
GEN-2024-017 | 02 NEBRASKA | TBD | NRIS | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | Current Study | 17.69 | (246.00, 246.00) | 500733.4359 | 1.8871 | 26535000 | 0.025769
GEN-2024-017 | 02 NEBRASKA | TBD | NRIS | Rebuild line 650185 WAGENER 3 345 650189 103&ROKEBY3 345 1 | Current Study | 9.45 | (1793.00, 1793.00) | 666237.5947 | 3.2046 | 20790000 | 0.10846
GEN-2024-018 | 02 NEBRASKA | TBD | ERIS | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV | Current Study |  |  | 2003.6995 | 0.1452 | 1380000 | 0.045786
GEN-2024-018 | 02 NEBRASKA | TBD | NRIS | Add 108 MVAR switched shunt at MAURINE4 230 kV | Current Study |  |  | 31712.545 | 0.82909 | 3825000 | 0.036989
GEN-2024-018 | 02 NEBRASKA | TBD | NRIS | Add 12 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 20493.2725 | 0.92625 | 2212500 | 0.036989
GEN-2024-018 | 02 NEBRASKA | TBD | NRIS | Add 154 MVAR SVC at WAYSIDE 4 230 kV | Current Study |  |  | 61016.3469 | 0.70949 | 8600000 | 0.042215
GEN-2024-018 | 02 NEBRASKA | TBD | ERIS | Add 2 MVAR switched shunt at GEN-2017-140 345 kV | Current Study |  |  | 4286.5997 | 0.080879 | 5300000 | 0.029848
GEN-2024-018 | 02 NEBRASKA | TBD | ERIS | Add 23 MVAR switched shunt at FINNEY 7 345 kV | Current Study |  |  | 22685.296 | 0.42802 | 5300000 | 0.045786
GEN-2024-018 | 02 NEBRASKA | TBD | NRIS | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 7835.0731 | 0.35413 | 2212500 | 0.036989
GEN-2024-018 | 02 NEBRASKA | TBD | ERIS | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2 | Current Study |  | (417.00, 417.00) | 644186.0752 | 3.8344 | 16800000 | 0.070983
GEN-2024-018 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 640125 COLMB.E3 345 640127 COLMB.E7 115 640129 COLMB.T9 13 M2 | Current Study |  | (336.00, 336.00) | 271226.0512 | 1.6144 | 16800000 | 0.0078035
GEN-2024-018 | 02 NEBRASKA | TBD | ERIS | Add 3-winding transformer 640234 HUMBOLT5 161 640235 HUMBOLT7 115 643087 HUMBOLDT T29 13 M2 | Current Study |  | (126.00, 126.00) | 494023.9044 | 4.1169 | 12000000 | 0.01256
GEN-2024-018 | 02 NEBRASKA | TBD | ERIS | Add 3-winding transformer 640277 MOORE 3 345 640278 SHELDON7 115 640280 MOORE 9 13 M2 | Current Study |  | (336.00, 400.00) | 206224.6362 | 1.2275 | 16800000 | 0.0061826
GEN-2024-018 | 02 NEBRASKA | TBD | ERIS | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2 | Current Study |  | (417.00, 417.00) | 79359.1322 | 0.47238 | 16800000 | 0.0027213
GEN-2024-018 | 02 NEBRASKA | TBD | ERIS | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2 | Current Study |  | (417.00, 417.00) | 79359.1322 | 0.47238 | 16800000 | 0.0027212
GEN-2024-018 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2 | Current Study |  | (110.00, 120.00) | 108523.3695 | 0.90436 | 12000000 | 0.01235
GEN-2024-018 | 02 NEBRASKA | TBD | NRIS | Add 45 MVAR switched shunt at PR BRZ 4 230 kV | Current Study |  |  | 22255.1148 | 0.58183 | 3825000 | 0.064444
GEN-2024-018 | 02 NEBRASKA | TBD | ERIS | Add line 640088 BPS SUB7 115 640278 SHELDON7 115 M2 | Current Study | 16.85 | (598.00, 598.00) | 1144077.0252 | 4.1169 | 27790000 | 0.032771
GEN-2024-018 | 02 NEBRASKA | TBD | ERIS | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2 | Current Study | 0.75 | (2390.00, 2390.00) | 173647.9368 | 0.97692 | 17775000 | 0.17284
GEN-2024-018 | 02 NEBRASKA | TBD | ERIS | DIS2301_P2_G00_ERIS_2_640_NPPD_TO_1000_DAYKIN_345KV_SUB.idv : DISIS_2023 Identified Upgrade | Contingent |  |  | 0 | 0 | 23000000 | 0.094245
GEN-2024-018 | 02 NEBRASKA | TBD | ERIS | DIS2301_P2_G00_ERIS_3_640_NPPD_TO_2000_add_BPS_345_Lines_Rev34.idv : DISIS_2023 Identified Upgrade | Contingent |  |  | 0 | 0 | 53000000 | 0.36735
GEN-2024-018 | 02 NEBRASKA | 171485 | ERIS | New Beatrice Power Station 345 kV GEN-2024-018 Interconnection (TOIF) (NPPD) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-018 | 02 NEBRASKA | 171492 | ERIS | New Beatrice Power Station 345 kV GEN-2024-018/019/022/023 Interconnection (Shared NU) (NPPD) | Interconnection |  |  | 1090909.09 | 16 | 7000000 | 1
GEN-2024-018 | 02 NEBRASKA | 171492 | ERIS | New Beatrice Power Station 345 kV GEN-2024-018/019/022/023 Interconnection (TOIF) (NPPD) | Interconnection |  |  | 750000 | 25 | 3000000 | 1
GEN-2024-018 | 02 NEBRASKA | TBD | NRIS | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | Current Study | 23.48 | (1793.00, 1793.00) | 397611.2148 | 0.76973 | 51656000 | 0.040568
GEN-2024-018 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640076 BEATRCE7 115 640361 STEINER7 115 1 | Current Study | 30.1 | (217.00, 217.00) | 1239176.6268 | 4.1169 | 30100000 | 0.02512
GEN-2024-018 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640088 BPS SUB7 115 640111 CLATONA7 115 1 | Current Study | 8.96 | (598.00, 598.00) | 368871.1819 | 4.1169 | 8960000 | 0.025353
GEN-2024-018 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640111 CLATONA7 115 640278 SHELDON7 115 1 | Current Study | 12.41 | (598.00, 598.00) | 510903.0544 | 4.1169 | 12410000 | 0.025353
GEN-2024-018 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640139 COOPER 3 345 640590 OLIVECREEK 3 345 1 | Current Study | 62.88 | (1793.00, 1793.00) | 2292237.4749 | 1.657 | 138336000 | 0.15588
GEN-2024-018 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640169 FAIRBRY7 115 640208 HARBINE7 115 1 | Current Study | 9.82 | (217.00, 217.00) | 404276.2284 | 4.1169 | 9820000 | 0.0097069
GEN-2024-018 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640169 FAIRBRY7 115 640218 HEBRN N7 115 1 | Current Study | 22.1 | (176.00, 176.00) | 909827.3572 | 4.1169 | 22100000 | 0.0097069
GEN-2024-018 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640235 HUMBOLT7 115 640361 STEINER7 115 1 | Current Study | 17.7 | (217.00, 217.00) | 728685.259 | 4.1169 | 17700000 | 0.02512
GEN-2024-018 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | Current Study | 45.48 | (1793.00, 1793.00) | 1037361.3563 | 1.0368 | 100056000 | 0.088101
GEN-2024-018 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 | Current Study | 19.87 | (1793.00, 1793.00) | 702625.0585 | 1.6073 | 43714000 | 0.12207
GEN-2024-018 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 | Current Study | 16.71 | (1793.00, 1793.00) | 598778.7113 | 1.6288 | 36762000 | 0.19025
GEN-2024-018 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640278 SHELDON7 115 640591 OLIVECREEK 7 115 1 | Current Study | 1 | (598.00, 598.00) | 20501.0351 | 2.0501 | 1000000 | 0.021428
GEN-2024-018 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640278 SHELDON7 115 640591 OLIVECREEK 7 115 2 | Current Study | 1 | (598.00, 598.00) | 20501.0351 | 2.0501 | 1000000 | 0.021428
GEN-2024-018 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640278 SHELDON7 115 650242 FOLSM&PHIL7 115 1 | Current Study | 15.49 | (329.00, 329.00) | 306922.338 | 1.9814 | 15490000 | 0.021291
GEN-2024-018 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1 | Current Study | 10.55 | (598.00, 598.00) | 194963.7734 | 1.848 | 10550000 | 0.023849
GEN-2024-018 | 02 NEBRASKA | TBD | ERIS | Rebuild line 645454 S3454 3 345 645455 S3455 3 345 1 | Current Study | 6.67 | (1793.00, 1793.00) | 245512.7603 | 1.6731 | 14674000 | 0.072203
GEN-2024-018 | 02 NEBRASKA | TBD | NRIS | Rebuild line 645454 S3454 3 345 650185 WAGENER 3 345 1 | Current Study | 33.67 | (1793.00, 1793.00) | 795874.5708 | 1.0744 | 74074000 | 0.15453
GEN-2024-018 | 02 NEBRASKA | TBD | NRIS | Rebuild line 645456 S3456 3 345 645458 S3458 3 345 1 | Current Study | 44.95 | (1793.00, 1793.00) | 1721024.2649 | 1.7403 | 98890000 | 0.026478
GEN-2024-018 | 02 NEBRASKA | TBD | NRIS | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | Current Study | 17.69 | (246.00, 246.00) | 239972.3009 | 0.90436 | 26535000 | 0.0247
GEN-2024-018 | 02 NEBRASKA | TBD | NRIS | Rebuild line 650185 WAGENER 3 345 650189 103&ROKEBY3 345 1 | Current Study | 9.45 | (1793.00, 1793.00) | 297820.2925 | 1.4325 | 20790000 | 0.096969
GEN-2024-019 | 02 NEBRASKA | TBD | ERIS | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV | Current Study |  |  | 4007.3989 | 0.29039 | 1380000 | 0.045786
GEN-2024-019 | 02 NEBRASKA | TBD | NRIS | Add 108 MVAR switched shunt at MAURINE4 230 kV | Current Study |  |  | 63425.09 | 1.6582 | 3825000 | 0.036989
GEN-2024-019 | 02 NEBRASKA | TBD | NRIS | Add 12 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 40986.5449 | 1.8525 | 2212500 | 0.036989
GEN-2024-019 | 02 NEBRASKA | TBD | NRIS | Add 154 MVAR SVC at WAYSIDE 4 230 kV | Current Study |  |  | 122032.6937 | 1.419 | 8600000 | 0.042215
GEN-2024-019 | 02 NEBRASKA | TBD | ERIS | Add 2 MVAR switched shunt at GEN-2017-140 345 kV | Current Study |  |  | 8573.1993 | 0.16176 | 5300000 | 0.029848
GEN-2024-019 | 02 NEBRASKA | TBD | ERIS | Add 23 MVAR switched shunt at FINNEY 7 345 kV | Current Study |  |  | 45370.592 | 0.85605 | 5300000 | 0.045786
GEN-2024-019 | 02 NEBRASKA | TBD | NRIS | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 15670.1462 | 0.70826 | 2212500 | 0.036989
GEN-2024-019 | 02 NEBRASKA | TBD | ERIS | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2 | Current Study |  | (417.00, 417.00) | 1288372.1504 | 7.6689 | 16800000 | 0.070983
GEN-2024-019 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 640125 COLMB.E3 345 640127 COLMB.E7 115 640129 COLMB.T9 13 M2 | Current Study |  | (336.00, 336.00) | 542452.1024 | 3.2289 | 16800000 | 0.0078035
GEN-2024-019 | 02 NEBRASKA | TBD | ERIS | Add 3-winding transformer 640234 HUMBOLT5 161 640235 HUMBOLT7 115 643087 HUMBOLDT T29 13 M2 | Current Study |  | (126.00, 126.00) | 988047.8088 | 8.2337 | 12000000 | 0.01256
GEN-2024-019 | 02 NEBRASKA | TBD | ERIS | Add 3-winding transformer 640277 MOORE 3 345 640278 SHELDON7 115 640280 MOORE 9 13 M2 | Current Study |  | (336.00, 400.00) | 412449.2724 | 2.4551 | 16800000 | 0.0061826
GEN-2024-019 | 02 NEBRASKA | TBD | ERIS | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2 | Current Study |  | (417.00, 417.00) | 158718.2645 | 0.94475 | 16800000 | 0.0027213
GEN-2024-019 | 02 NEBRASKA | TBD | ERIS | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2 | Current Study |  | (417.00, 417.00) | 158718.2645 | 0.94475 | 16800000 | 0.0027212
GEN-2024-019 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2 | Current Study |  | (110.00, 120.00) | 217046.7391 | 1.8087 | 12000000 | 0.01235
GEN-2024-019 | 02 NEBRASKA | TBD | NRIS | Add 45 MVAR switched shunt at PR BRZ 4 230 kV | Current Study |  |  | 44510.2295 | 1.1637 | 3825000 | 0.064444
GEN-2024-019 | 02 NEBRASKA | TBD | ERIS | Add line 640088 BPS SUB7 115 640278 SHELDON7 115 M2 | Current Study | 16.85 | (598.00, 598.00) | 2288154.0505 | 8.2337 | 27790000 | 0.032771
GEN-2024-019 | 02 NEBRASKA | TBD | ERIS | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2 | Current Study | 0.75 | (2390.00, 2390.00) | 347295.8737 | 1.9538 | 17775000 | 0.17284
GEN-2024-019 | 02 NEBRASKA | TBD | ERIS | DIS2301_P2_G00_ERIS_2_640_NPPD_TO_1000_DAYKIN_345KV_SUB.idv : DISIS_2023 Identified Upgrade | Contingent |  |  | 0 | 0 | 23000000 | 0.094245
GEN-2024-019 | 02 NEBRASKA | TBD | ERIS | DIS2301_P2_G00_ERIS_3_640_NPPD_TO_2000_add_BPS_345_Lines_Rev34.idv : DISIS_2023 Identified Upgrade | Contingent |  |  | 0 | 0 | 53000000 | 0.36735
GEN-2024-019 | 02 NEBRASKA | 171492 | ERIS | New Beatrice Power Station 345 kV GEN-2024-018/019/022/023 Interconnection (Shared NU) (NPPD) | Interconnection |  |  | 1818181.82 | 26 | 7000000 | 1
GEN-2024-019 | 02 NEBRASKA | 171492 | ERIS | New Beatrice Power Station 345 kV GEN-2024-018/019/022/023 Interconnection (TOIF) (NPPD) | Interconnection |  |  | 750000 | 25 | 3000000 | 1
GEN-2024-019 | 02 NEBRASKA | 171486 | ERIS | New Beatrice Power Station 345 kV Substation GEN-2024-019 Interconnection (TOIF) (NPPD) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-019 | 02 NEBRASKA | TBD | NRIS | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | Current Study | 23.48 | (1793.00, 1793.00) | 795222.4295 | 1.5395 | 51656000 | 0.040568
GEN-2024-019 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640076 BEATRCE7 115 640361 STEINER7 115 1 | Current Study | 30.1 | (217.00, 217.00) | 2478353.2537 | 8.2337 | 30100000 | 0.02512
GEN-2024-019 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640088 BPS SUB7 115 640111 CLATONA7 115 1 | Current Study | 8.96 | (598.00, 598.00) | 737742.3639 | 8.2337 | 8960000 | 0.025353
GEN-2024-019 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640111 CLATONA7 115 640278 SHELDON7 115 1 | Current Study | 12.41 | (598.00, 598.00) | 1021806.1089 | 8.2337 | 12410000 | 0.025353
GEN-2024-019 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640139 COOPER 3 345 640590 OLIVECREEK 3 345 1 | Current Study | 62.88 | (1793.00, 1793.00) | 4584474.9499 | 3.314 | 138336000 | 0.15588
GEN-2024-019 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640169 FAIRBRY7 115 640208 HARBINE7 115 1 | Current Study | 9.82 | (217.00, 217.00) | 808552.4568 | 8.2337 | 9820000 | 0.0097069
GEN-2024-019 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640169 FAIRBRY7 115 640218 HEBRN N7 115 1 | Current Study | 22.1 | (176.00, 176.00) | 1819654.7145 | 8.2337 | 22100000 | 0.0097069
GEN-2024-019 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640235 HUMBOLT7 115 640361 STEINER7 115 1 | Current Study | 17.7 | (217.00, 217.00) | 1457370.5179 | 8.2337 | 17700000 | 0.02512
GEN-2024-019 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | Current Study | 45.48 | (1793.00, 1793.00) | 2074722.7127 | 2.0736 | 100056000 | 0.088101
GEN-2024-019 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 | Current Study | 19.87 | (1793.00, 1793.00) | 1405250.1171 | 3.2146 | 43714000 | 0.12207
GEN-2024-019 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 | Current Study | 16.71 | (1793.00, 1793.00) | 1197557.4227 | 3.2576 | 36762000 | 0.19025
GEN-2024-019 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640278 SHELDON7 115 640591 OLIVECREEK 7 115 1 | Current Study | 1 | (598.00, 598.00) | 41002.0702 | 4.1002 | 1000000 | 0.021428
GEN-2024-019 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640278 SHELDON7 115 640591 OLIVECREEK 7 115 2 | Current Study | 1 | (598.00, 598.00) | 41002.0702 | 4.1002 | 1000000 | 0.021428
GEN-2024-019 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640278 SHELDON7 115 650242 FOLSM&PHIL7 115 1 | Current Study | 15.49 | (329.00, 329.00) | 613844.6759 | 3.9628 | 15490000 | 0.021291
GEN-2024-019 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1 | Current Study | 10.55 | (598.00, 598.00) | 389927.5468 | 3.696 | 10550000 | 0.023849
GEN-2024-019 | 02 NEBRASKA | TBD | ERIS | Rebuild line 645454 S3454 3 345 645455 S3455 3 345 1 | Current Study | 6.67 | (1793.00, 1793.00) | 491025.5207 | 3.3462 | 14674000 | 0.072203
GEN-2024-019 | 02 NEBRASKA | TBD | NRIS | Rebuild line 645454 S3454 3 345 650185 WAGENER 3 345 1 | Current Study | 33.67 | (1793.00, 1793.00) | 1591749.1416 | 2.1489 | 74074000 | 0.15453
GEN-2024-019 | 02 NEBRASKA | TBD | NRIS | Rebuild line 645456 S3456 3 345 645458 S3458 3 345 1 | Current Study | 44.95 | (1793.00, 1793.00) | 3442048.5297 | 3.4807 | 98890000 | 0.026478
GEN-2024-019 | 02 NEBRASKA | TBD | NRIS | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | Current Study | 17.69 | (246.00, 246.00) | 479944.6018 | 1.8087 | 26535000 | 0.0247
GEN-2024-019 | 02 NEBRASKA | TBD | NRIS | Rebuild line 650185 WAGENER 3 345 650189 103&ROKEBY3 345 1 | Current Study | 9.45 | (1793.00, 1793.00) | 595640.5851 | 2.865 | 20790000 | 0.096969
GEN-2024-020 | 02 NEBRASKA | TBD | ERIS | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV | Current Study |  |  | 25138.8814 | 1.8217 | 1380000 | 0.045661
GEN-2024-020 | 02 NEBRASKA | TBD | NRIS | Add 108 MVAR switched shunt at MAURINE4 230 kV | Current Study |  |  | 399873.1767 | 10.4542 | 3825000 | 0.037073
GEN-2024-020 | 02 NEBRASKA | TBD | NRIS | Add 12 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 258405.9389 | 11.6794 | 2212500 | 0.037073
GEN-2024-020 | 02 NEBRASKA | TBD | NRIS | Add 154 MVAR SVC at WAYSIDE 4 230 kV | Current Study |  |  | 764999.7364 | 8.8953 | 8600000 | 0.04207
GEN-2024-020 | 02 NEBRASKA | TBD | ERIS | Add 2 MVAR switched shunt at GEN-2017-140 345 kV | Current Study |  |  | 57715.1582 | 1.089 | 5300000 | 0.031944
GEN-2024-020 | 02 NEBRASKA | TBD | ERIS | Add 23 MVAR switched shunt at FINNEY 7 345 kV | Current Study |  |  | 284615.0233 | 5.3701 | 5300000 | 0.045661
GEN-2024-020 | 02 NEBRASKA | TBD | NRIS | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 98794.8322 | 4.4653 | 2212500 | 0.037073
GEN-2024-020 | 02 NEBRASKA | TBD | ERIS | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2 | Current Study |  | (417.00, 417.00) | 453104.6859 | 2.6971 | 16800000 | 0.0039686
GEN-2024-020 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 640125 COLMB.E3 345 640127 COLMB.E7 115 640129 COLMB.T9 13 M2 | Current Study |  | (336.00, 336.00) | 3976066.8375 | 23.6671 | 16800000 | 0.009093
GEN-2024-020 | 02 NEBRASKA | TBD | ERIS | Add 3-winding transformer 640277 MOORE 3 345 640278 SHELDON7 115 640280 MOORE 9 13 M2 | Current Study |  | (336.00, 400.00) | 4635471.2243 | 27.5921 | 16800000 | 0.011046
GEN-2024-020 | 02 NEBRASKA | TBD | ERIS | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2 | Current Study |  | (417.00, 417.00) | 5846988.932 | 34.8035 | 16800000 | 0.015937
GEN-2024-020 | 02 NEBRASKA | TBD | ERIS | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2 | Current Study |  | (417.00, 417.00) | 5846988.932 | 34.8035 | 16800000 | 0.015937
GEN-2024-020 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2 | Current Study |  | (110.00, 120.00) | 1424431.8096 | 11.8703 | 12000000 | 0.012885
GEN-2024-020 | 02 NEBRASKA | TBD | NRIS | Add 45 MVAR switched shunt at PR BRZ 4 230 kV | Current Study |  |  | 300431.0412 | 7.8544 | 3825000 | 0.069151
GEN-2024-020 | 02 NEBRASKA | TBD | ERIS | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2 | Current Study | 0.75 | (2390.00, 2390.00) | 4137951.2335 | 23.2796 | 17775000 | 0.32739
GEN-2024-020 | 02 NEBRASKA | 171488 | ERIS | Olive Creek 345 kV Substation GEN-2024-020 Interconnection (Non-Shared NU) (NPPD) | Interconnection |  |  | 5000000 | 100 | 5000000 | 1
GEN-2024-020 | 02 NEBRASKA | 171487 | ERIS | Olive Creek 345 kV Substation GEN-2024-020 Interconnection (TOIF) (NPPD) | Interconnection |  |  | 1000000 | 100 | 1000000 | 1
GEN-2024-020 | 02 NEBRASKA | TBD | NRIS | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | Current Study | 23.48 | (1793.00, 1793.00) | 5184673.0915 | 10.0369 | 51656000 | 0.042048
GEN-2024-020 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640139 COOPER 3 345 640590 OLIVECREEK 3 345 1 | Current Study | 62.88 | (1793.00, 1793.00) | 32496125.8044 | 23.4907 | 138336000 | 0.17566
GEN-2024-020 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | Current Study | 45.48 | (1793.00, 1793.00) | 16245999.1295 | 16.2369 | 100056000 | 0.10967
GEN-2024-020 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 | Current Study | 19.87 | (1793.00, 1793.00) | 10177746.8179 | 23.2826 | 43714000 | 0.14055
GEN-2024-020 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 | Current Study | 16.71 | (1793.00, 1793.00) | 8485024.8705 | 23.081 | 36762000 | 0.2143
GEN-2024-020 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640278 SHELDON7 115 640591 OLIVECREEK 7 115 1 | Current Study | 1 | (598.00, 598.00) | 197368.0095 | 19.7368 | 1000000 | 0.016398
GEN-2024-020 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640278 SHELDON7 115 640591 OLIVECREEK 7 115 2 | Current Study | 1 | (598.00, 598.00) | 197368.0095 | 19.7368 | 1000000 | 0.016398
GEN-2024-020 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640278 SHELDON7 115 650242 FOLSM&PHIL7 115 1 | Current Study | 15.49 | (329.00, 329.00) | 3158825.9955 | 20.3927 | 15490000 | 0.017418
GEN-2024-020 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1 | Current Study | 10.55 | (598.00, 598.00) | 2285850.9583 | 21.6668 | 10550000 | 0.022226
GEN-2024-020 | 02 NEBRASKA | TBD | ERIS | Rebuild line 645454 S3454 3 345 645455 S3455 3 345 1 | Current Study | 6.67 | (1793.00, 1793.00) | 3388749.3789 | 23.0936 | 14674000 | 0.079217
GEN-2024-020 | 02 NEBRASKA | TBD | NRIS | Rebuild line 645454 S3454 3 345 650185 WAGENER 3 345 1 | Current Study | 33.67 | (1793.00, 1793.00) | 10822577.4236 | 14.6105 | 74074000 | 0.16704
GEN-2024-020 | 02 NEBRASKA | TBD | NRIS | Rebuild line 645456 S3456 3 345 645458 S3458 3 345 1 | Current Study | 44.95 | (1793.00, 1793.00) | 22442992.4603 | 22.6949 | 98890000 | 0.027446
GEN-2024-020 | 02 NEBRASKA | TBD | NRIS | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | Current Study | 17.69 | (246.00, 246.00) | 3149774.8389 | 11.8703 | 26535000 | 0.025769
GEN-2024-020 | 02 NEBRASKA | TBD | NRIS | Rebuild line 650185 WAGENER 3 345 650189 103&ROKEBY3 345 1 | Current Study | 9.45 | (1793.00, 1793.00) | 4190849.3862 | 20.158 | 20790000 | 0.10846
GEN-2024-021 | 02 NEBRASKA | TBD | ERIS | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV | Current Study |  |  | 34807.6819 | 2.5223 | 1380000 | 0.045661
GEN-2024-021 | 02 NEBRASKA | TBD | NRIS | Add 108 MVAR switched shunt at MAURINE4 230 kV | Current Study |  |  | 553670.5523 | 14.475 | 3825000 | 0.037073
GEN-2024-021 | 02 NEBRASKA | TBD | NRIS | Add 12 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 357792.8385 | 16.1714 | 2212500 | 0.037073
GEN-2024-021 | 02 NEBRASKA | TBD | NRIS | Add 154 MVAR SVC at WAYSIDE 4 230 kV | Current Study |  |  | 1059230.4042 | 12.3166 | 8600000 | 0.04207
GEN-2024-021 | 02 NEBRASKA | TBD | ERIS | Add 2 MVAR switched shunt at GEN-2017-140 345 kV | Current Study |  |  | 79913.2959 | 1.5078 | 5300000 | 0.031944
GEN-2024-021 | 02 NEBRASKA | TBD | ERIS | Add 23 MVAR switched shunt at FINNEY 7 345 kV | Current Study |  |  | 394082.3399 | 7.4355 | 5300000 | 0.045661
GEN-2024-021 | 02 NEBRASKA | TBD | NRIS | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 136792.8446 | 6.1827 | 2212500 | 0.037073
GEN-2024-021 | 02 NEBRASKA | TBD | ERIS | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2 | Current Study |  | (417.00, 417.00) | 627375.719 | 3.7344 | 16800000 | 0.0039686
GEN-2024-021 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 640125 COLMB.E3 345 640127 COLMB.E7 115 640129 COLMB.T9 13 M2 | Current Study |  | (336.00, 336.00) | 5505323.3134 | 32.7698 | 16800000 | 0.009093
GEN-2024-021 | 02 NEBRASKA | TBD | ERIS | Add 3-winding transformer 640277 MOORE 3 345 640278 SHELDON7 115 640280 MOORE 9 13 M2 | Current Study |  | (336.00, 400.00) | 6418344.7721 | 38.2044 | 16800000 | 0.011046
GEN-2024-021 | 02 NEBRASKA | TBD | ERIS | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2 | Current Study |  | (417.00, 417.00) | 8095830.8289 | 48.1895 | 16800000 | 0.015937
GEN-2024-021 | 02 NEBRASKA | TBD | ERIS | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2 | Current Study |  | (417.00, 417.00) | 8095830.8289 | 48.1895 | 16800000 | 0.015937
GEN-2024-021 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2 | Current Study |  | (110.00, 120.00) | 1972290.1978 | 16.4358 | 12000000 | 0.012885
GEN-2024-021 | 02 NEBRASKA | TBD | NRIS | Add 45 MVAR switched shunt at PR BRZ 4 230 kV | Current Study |  |  | 415981.4417 | 10.8753 | 3825000 | 0.069151
GEN-2024-021 | 02 NEBRASKA | TBD | ERIS | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2 | Current Study | 0.75 | (2390.00, 2390.00) | 5729470.9387 | 32.2333 | 17775000 | 0.32739
GEN-2024-021 | 02 NEBRASKA | 171490 | ERIS | Olive Creek 345 kV Substation GEN-2024-021 Interconnection (Non-Shared NU) (NPPD) | Interconnection |  |  | 5000000 | 100 | 5000000 | 1
GEN-2024-021 | 02 NEBRASKA | 171489 | ERIS | Olive Creek 345 kV Substation GEN-2024-021 Interconnection (TOIF) (NPPD) | Interconnection |  |  | 1000000 | 100 | 1000000 | 1
GEN-2024-021 | 02 NEBRASKA | TBD | NRIS | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | Current Study | 23.48 | (1793.00, 1793.00) | 7178778.1267 | 13.8973 | 51656000 | 0.042048
GEN-2024-021 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640139 COOPER 3 345 640590 OLIVECREEK 3 345 1 | Current Study | 62.88 | (1793.00, 1793.00) | 44994635.7292 | 32.5256 | 138336000 | 0.17566
GEN-2024-021 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | Current Study | 45.48 | (1793.00, 1793.00) | 22494460.3331 | 22.4819 | 100056000 | 0.10967
GEN-2024-021 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 | Current Study | 19.87 | (1793.00, 1793.00) | 14092264.8248 | 32.2374 | 43714000 | 0.14055
GEN-2024-021 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 | Current Study | 16.71 | (1793.00, 1793.00) | 11748495.9745 | 31.9583 | 36762000 | 0.2143
GEN-2024-021 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640278 SHELDON7 115 640591 OLIVECREEK 7 115 1 | Current Study | 1 | (598.00, 598.00) | 273278.7824 | 27.3279 | 1000000 | 0.016398
GEN-2024-021 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640278 SHELDON7 115 640591 OLIVECREEK 7 115 2 | Current Study | 1 | (598.00, 598.00) | 273278.7824 | 27.3279 | 1000000 | 0.016398
GEN-2024-021 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640278 SHELDON7 115 650242 FOLSM&PHIL7 115 1 | Current Study | 15.49 | (329.00, 329.00) | 4373759.0707 | 28.236 | 15490000 | 0.017418
GEN-2024-021 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1 | Current Study | 10.55 | (598.00, 598.00) | 3165024.4038 | 30.0002 | 10550000 | 0.022226
GEN-2024-021 | 02 NEBRASKA | TBD | ERIS | Rebuild line 645454 S3454 3 345 645455 S3455 3 345 1 | Current Study | 6.67 | (1793.00, 1793.00) | 4692114.5247 | 31.9757 | 14674000 | 0.079217
GEN-2024-021 | 02 NEBRASKA | TBD | NRIS | Rebuild line 645454 S3454 3 345 650185 WAGENER 3 345 1 | Current Study | 33.67 | (1793.00, 1793.00) | 14985107.202 | 20.2299 | 74074000 | 0.16704
GEN-2024-021 | 02 NEBRASKA | TBD | NRIS | Rebuild line 645456 S3456 3 345 645458 S3458 3 345 1 | Current Study | 44.95 | (1793.00, 1793.00) | 31074912.6374 | 31.4237 | 98890000 | 0.027446
GEN-2024-021 | 02 NEBRASKA | TBD | NRIS | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | Current Study | 17.69 | (246.00, 246.00) | 4361226.7 | 16.4358 | 26535000 | 0.025769
GEN-2024-021 | 02 NEBRASKA | TBD | NRIS | Rebuild line 650185 WAGENER 3 345 650189 103&ROKEBY3 345 1 | Current Study | 9.45 | (1793.00, 1793.00) | 5802714.5347 | 27.9111 | 20790000 | 0.10846
GEN-2024-022 | 02 NEBRASKA | TBD | ERIS | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV | Current Study |  |  | 25207.8318 | 1.8267 | 1380000 | 0.045786
GEN-2024-022 | 02 NEBRASKA | TBD | NRIS | Add 108 MVAR switched shunt at MAURINE4 230 kV | Current Study |  |  | 398964.2756 | 10.4304 | 3825000 | 0.036989
GEN-2024-022 | 02 NEBRASKA | TBD | NRIS | Add 12 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 257818.5891 | 11.6528 | 2212500 | 0.036989
GEN-2024-022 | 02 NEBRASKA | TBD | NRIS | Add 154 MVAR SVC at WAYSIDE 4 230 kV | Current Study |  |  | 767625.009 | 8.9259 | 8600000 | 0.042215
GEN-2024-022 | 02 NEBRASKA | TBD | ERIS | Add 2 MVAR switched shunt at GEN-2017-140 345 kV | Current Study |  |  | 53928.1892 | 1.0175 | 5300000 | 0.029848
GEN-2024-022 | 02 NEBRASKA | TBD | ERIS | Add 23 MVAR switched shunt at FINNEY 7 345 kV | Current Study |  |  | 285395.6596 | 5.3848 | 5300000 | 0.045786
GEN-2024-022 | 02 NEBRASKA | TBD | NRIS | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 98570.2742 | 4.4552 | 2212500 | 0.036989
GEN-2024-022 | 02 NEBRASKA | TBD | ERIS | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2 | Current Study |  | (417.00, 417.00) | 8104276.4297 | 48.2397 | 16800000 | 0.070983
GEN-2024-022 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 640125 COLMB.E3 345 640127 COLMB.E7 115 640129 COLMB.T9 13 M2 | Current Study |  | (336.00, 336.00) | 3412198.7088 | 20.3107 | 16800000 | 0.0078035
GEN-2024-022 | 02 NEBRASKA | TBD | ERIS | Add 3-winding transformer 640234 HUMBOLT5 161 640235 HUMBOLT7 115 643087 HUMBOLDT T29 13 M2 | Current Study |  | (126.00, 126.00) | 6215139.4422 | 51.7928 | 12000000 | 0.01256
GEN-2024-022 | 02 NEBRASKA | TBD | ERIS | Add 3-winding transformer 640277 MOORE 3 345 640278 SHELDON7 115 640280 MOORE 9 13 M2 | Current Study |  | (336.00, 400.00) | 2594438.9714 | 15.4431 | 16800000 | 0.0061826
GEN-2024-022 | 02 NEBRASKA | TBD | ERIS | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2 | Current Study |  | (417.00, 417.00) | 998389.0829 | 5.9428 | 16800000 | 0.0027213
GEN-2024-022 | 02 NEBRASKA | TBD | ERIS | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2 | Current Study |  | (417.00, 417.00) | 998389.0829 | 5.9428 | 16800000 | 0.0027212
GEN-2024-022 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2 | Current Study |  | (110.00, 120.00) | 1365294.004 | 11.3775 | 12000000 | 0.01235
GEN-2024-022 | 02 NEBRASKA | TBD | NRIS | Add 45 MVAR switched shunt at PR BRZ 4 230 kV | Current Study |  |  | 279983.7017 | 7.3198 | 3825000 | 0.064444
GEN-2024-022 | 02 NEBRASKA | TBD | ERIS | Add line 640088 BPS SUB7 115 640278 SHELDON7 115 M2 | Current Study | 16.85 | (598.00, 598.00) | 14393227.0916 | 51.7928 | 27790000 | 0.032771
GEN-2024-022 | 02 NEBRASKA | TBD | ERIS | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2 | Current Study | 0.75 | (2390.00, 2390.00) | 2184603.0763 | 12.2903 | 17775000 | 0.17284
GEN-2024-022 | 02 NEBRASKA | TBD | ERIS | DIS2301_P2_G00_ERIS_2_640_NPPD_TO_1000_DAYKIN_345KV_SUB.idv : DISIS_2023 Identified Upgrade | Contingent |  |  | 0 | 0 | 23000000 | 0.094245
GEN-2024-022 | 02 NEBRASKA | TBD | ERIS | DIS2301_P2_G00_ERIS_3_640_NPPD_TO_2000_add_BPS_345_Lines_Rev34.idv : DISIS_2023 Identified Upgrade | Contingent |  |  | 0 | 0 | 53000000 | 0.36735
GEN-2024-022 | 02 NEBRASKA | 171492 | ERIS | New Beatrice Power Station 345 kV GEN-2024-018/019/022/023 Interconnection (Shared NU) (NPPD) | Interconnection |  |  | 2272727.27 | 32 | 7000000 | 1
GEN-2024-022 | 02 NEBRASKA | 171492 | ERIS | New Beatrice Power Station 345 kV GEN-2024-018/019/022/023 Interconnection (TOIF) (NPPD) | Interconnection |  |  | 750000 | 25 | 3000000 | 1
GEN-2024-022 | 02 NEBRASKA | 171491 | ERIS | New Beatrice Power Station 345 kV GEN-2024-022 Interconnection (TOIF) (NPPD) | Interconnection |  |  | 1000000 | 100 | 1000000 | 1
GEN-2024-022 | 02 NEBRASKA | TBD | NRIS | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | Current Study | 23.48 | (1793.00, 1793.00) | 5002205.605 | 9.6837 | 51656000 | 0.040568
GEN-2024-022 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640076 BEATRCE7 115 640361 STEINER7 115 1 | Current Study | 30.1 | (217.00, 217.00) | 15589641.4343 | 51.7928 | 30100000 | 0.02512
GEN-2024-022 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640088 BPS SUB7 115 640111 CLATONA7 115 1 | Current Study | 8.96 | (598.00, 598.00) | 4640637.4502 | 51.7928 | 8960000 | 0.025353
GEN-2024-022 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640111 CLATONA7 115 640278 SHELDON7 115 1 | Current Study | 12.41 | (598.00, 598.00) | 6427490.0398 | 51.7928 | 12410000 | 0.025353
GEN-2024-022 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640139 COOPER 3 345 640590 OLIVECREEK 3 345 1 | Current Study | 62.88 | (1793.00, 1793.00) | 28837826.2975 | 20.8462 | 138336000 | 0.15588
GEN-2024-022 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640169 FAIRBRY7 115 640208 HARBINE7 115 1 | Current Study | 9.82 | (217.00, 217.00) | 5086055.7769 | 51.7928 | 9820000 | 0.0097069
GEN-2024-022 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640169 FAIRBRY7 115 640218 HEBRN N7 115 1 | Current Study | 22.1 | (176.00, 176.00) | 11446215.1394 | 51.7928 | 22100000 | 0.0097069
GEN-2024-022 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640235 HUMBOLT7 115 640361 STEINER7 115 1 | Current Study | 17.7 | (217.00, 217.00) | 9167330.6773 | 51.7928 | 17700000 | 0.02512
GEN-2024-022 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | Current Study | 45.48 | (1793.00, 1793.00) | 13050675.1282 | 13.0434 | 100056000 | 0.088101
GEN-2024-022 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 | Current Study | 19.87 | (1793.00, 1793.00) | 8839476.5428 | 20.2212 | 43714000 | 0.12207
GEN-2024-022 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 | Current Study | 16.71 | (1793.00, 1793.00) | 7533022.4975 | 20.4913 | 36762000 | 0.19025
GEN-2024-022 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640278 SHELDON7 115 640591 OLIVECREEK 7 115 1 | Current Study | 1 | (598.00, 598.00) | 257916.2478 | 25.7916 | 1000000 | 0.021428
GEN-2024-022 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640278 SHELDON7 115 640591 OLIVECREEK 7 115 2 | Current Study | 1 | (598.00, 598.00) | 257916.2478 | 25.7916 | 1000000 | 0.021428
GEN-2024-022 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640278 SHELDON7 115 650242 FOLSM&PHIL7 115 1 | Current Study | 15.49 | (329.00, 329.00) | 3861281.0258 | 24.9276 | 15490000 | 0.021291
GEN-2024-022 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1 | Current Study | 10.55 | (598.00, 598.00) | 2452770.0523 | 23.249 | 10550000 | 0.023849
GEN-2024-022 | 02 NEBRASKA | TBD | ERIS | Rebuild line 645454 S3454 3 345 645455 S3455 3 345 1 | Current Study | 6.67 | (1793.00, 1793.00) | 3088708.9203 | 21.0489 | 14674000 | 0.072203
GEN-2024-022 | 02 NEBRASKA | TBD | NRIS | Rebuild line 645454 S3454 3 345 650185 WAGENER 3 345 1 | Current Study | 33.67 | (1793.00, 1793.00) | 10012615.5679 | 13.517 | 74074000 | 0.15453
GEN-2024-022 | 02 NEBRASKA | TBD | NRIS | Rebuild line 645456 S3456 3 345 645458 S3458 3 345 1 | Current Study | 44.95 | (1793.00, 1793.00) | 21651595.5901 | 21.8946 | 98890000 | 0.026478
GEN-2024-022 | 02 NEBRASKA | TBD | NRIS | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | Current Study | 17.69 | (246.00, 246.00) | 3019006.3663 | 11.3775 | 26535000 | 0.0247
GEN-2024-022 | 02 NEBRASKA | TBD | NRIS | Rebuild line 650185 WAGENER 3 345 650189 103&ROKEBY3 345 1 | Current Study | 9.45 | (1793.00, 1793.00) | 3746771.4224 | 18.022 | 20790000 | 0.096969
GEN-2024-023 | 02 NEBRASKA | TBD | ERIS | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV | Current Study |  |  | 17451.5759 | 1.2646 | 1380000 | 0.045786
GEN-2024-023 | 02 NEBRASKA | TBD | NRIS | Add 108 MVAR switched shunt at MAURINE4 230 kV | Current Study |  |  | 276206.037 | 7.2211 | 3825000 | 0.036989
GEN-2024-023 | 02 NEBRASKA | TBD | NRIS | Add 12 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 178489.7925 | 8.0673 | 2212500 | 0.036989
GEN-2024-023 | 02 NEBRASKA | TBD | NRIS | Add 154 MVAR SVC at WAYSIDE 4 230 kV | Current Study |  |  | 531432.6985 | 6.1794 | 8600000 | 0.042215
GEN-2024-023 | 02 NEBRASKA | TBD | ERIS | Add 2 MVAR switched shunt at GEN-2017-140 345 kV | Current Study |  |  | 37334.9002 | 0.70443 | 5300000 | 0.029848
GEN-2024-023 | 02 NEBRASKA | TBD | ERIS | Add 23 MVAR switched shunt at FINNEY 7 345 kV | Current Study |  |  | 197581.6105 | 3.728 | 5300000 | 0.045786
GEN-2024-023 | 02 NEBRASKA | TBD | NRIS | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 68240.9591 | 3.0843 | 2212500 | 0.036989
GEN-2024-023 | 02 NEBRASKA | TBD | ERIS | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2 | Current Study |  | (417.00, 417.00) | 5610652.9129 | 33.3967 | 16800000 | 0.070983
GEN-2024-023 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 640125 COLMB.E3 345 640127 COLMB.E7 115 640129 COLMB.T9 13 M2 | Current Study |  | (336.00, 336.00) | 2362291.4138 | 14.0613 | 16800000 | 0.0078035
GEN-2024-023 | 02 NEBRASKA | TBD | ERIS | Add 3-winding transformer 640234 HUMBOLT5 161 640235 HUMBOLT7 115 643087 HUMBOLDT T29 13 M2 | Current Study |  | (126.00, 126.00) | 4302788.8446 | 35.8566 | 12000000 | 0.01256
GEN-2024-023 | 02 NEBRASKA | TBD | ERIS | Add 3-winding transformer 640277 MOORE 3 345 640278 SHELDON7 115 640280 MOORE 9 13 M2 | Current Study |  | (336.00, 400.00) | 1796150.0571 | 10.6914 | 16800000 | 0.0061826
GEN-2024-023 | 02 NEBRASKA | TBD | ERIS | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2 | Current Study |  | (417.00, 417.00) | 691192.442 | 4.1142 | 16800000 | 0.0027213
GEN-2024-023 | 02 NEBRASKA | TBD | ERIS | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2 | Current Study |  | (417.00, 417.00) | 691192.442 | 4.1142 | 16800000 | 0.0027212
GEN-2024-023 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2 | Current Study |  | (110.00, 120.00) | 945203.5412 | 7.8767 | 12000000 | 0.01235
GEN-2024-023 | 02 NEBRASKA | TBD | NRIS | Add 45 MVAR switched shunt at PR BRZ 4 230 kV | Current Study |  |  | 193834.8704 | 5.0676 | 3825000 | 0.064444
GEN-2024-023 | 02 NEBRASKA | TBD | ERIS | Add line 640088 BPS SUB7 115 640278 SHELDON7 115 M2 | Current Study | 16.85 | (598.00, 598.00) | 9964541.8327 | 35.8566 | 27790000 | 0.032771
GEN-2024-023 | 02 NEBRASKA | TBD | ERIS | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2 | Current Study | 0.75 | (2390.00, 2390.00) | 1512417.5143 | 8.5087 | 17775000 | 0.17284
GEN-2024-023 | 02 NEBRASKA | TBD | ERIS | DIS2301_P2_G00_ERIS_2_640_NPPD_TO_1000_DAYKIN_345KV_SUB.idv : DISIS_2023 Identified Upgrade | Contingent |  |  | 0 | 0 | 23000000 | 0.094245
GEN-2024-023 | 02 NEBRASKA | TBD | ERIS | DIS2301_P2_G00_ERIS_3_640_NPPD_TO_2000_add_BPS_345_Lines_Rev34.idv : DISIS_2023 Identified Upgrade | Contingent |  |  | 0 | 0 | 53000000 | 0.36735
GEN-2024-023 | 02 NEBRASKA | 171492 | ERIS | New Beatrice Power Station 345 kV GEN-2024-018/019/022/023 Interconnection (Shared NU) (NPPD) | Interconnection |  |  | 1818181.82 | 26 | 7000000 | 1
GEN-2024-023 | 02 NEBRASKA | 171492 | ERIS | New Beatrice Power Station 345 kV GEN-2024-018/019/022/023 Interconnection (TOIF) (NPPD) | Interconnection |  |  | 750000 | 25 | 3000000 | 1
GEN-2024-023 | 02 NEBRASKA | 171493 | ERIS | New Beatrice Power Station 345 kV GEN-2024-023 Interconnection (TOIF) (NPPD) | Interconnection |  |  | 1000000 | 100 | 1000000 | 1
GEN-2024-023 | 02 NEBRASKA | TBD | NRIS | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | Current Study | 23.48 | (1793.00, 1793.00) | 3463065.4189 | 6.7041 | 51656000 | 0.040568
GEN-2024-023 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640076 BEATRCE7 115 640361 STEINER7 115 1 | Current Study | 30.1 | (217.00, 217.00) | 10792828.6853 | 35.8566 | 30100000 | 0.02512
GEN-2024-023 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640088 BPS SUB7 115 640111 CLATONA7 115 1 | Current Study | 8.96 | (598.00, 598.00) | 3212749.004 | 35.8566 | 8960000 | 0.025353
GEN-2024-023 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640111 CLATONA7 115 640278 SHELDON7 115 1 | Current Study | 12.41 | (598.00, 598.00) | 4449800.7968 | 35.8566 | 12410000 | 0.025353
GEN-2024-023 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640139 COOPER 3 345 640590 OLIVECREEK 3 345 1 | Current Study | 62.88 | (1793.00, 1793.00) | 19964648.9752 | 14.432 | 138336000 | 0.15588
GEN-2024-023 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640169 FAIRBRY7 115 640208 HARBINE7 115 1 | Current Study | 9.82 | (217.00, 217.00) | 3521115.5378 | 35.8566 | 9820000 | 0.0097069
GEN-2024-023 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640169 FAIRBRY7 115 640218 HEBRN N7 115 1 | Current Study | 22.1 | (176.00, 176.00) | 7924302.7888 | 35.8566 | 22100000 | 0.0097069
GEN-2024-023 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640235 HUMBOLT7 115 640361 STEINER7 115 1 | Current Study | 17.7 | (217.00, 217.00) | 6346613.5458 | 35.8566 | 17700000 | 0.02512
GEN-2024-023 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | Current Study | 45.48 | (1793.00, 1793.00) | 9035082.781 | 9.03 | 100056000 | 0.088101
GEN-2024-023 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 | Current Study | 19.87 | (1793.00, 1793.00) | 6119637.6065 | 13.9993 | 43714000 | 0.12207
GEN-2024-023 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 | Current Study | 16.71 | (1793.00, 1793.00) | 5215169.4214 | 14.1863 | 36762000 | 0.19025
GEN-2024-023 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640278 SHELDON7 115 640591 OLIVECREEK 7 115 1 | Current Study | 1 | (598.00, 598.00) | 178557.4023 | 17.8557 | 1000000 | 0.021428
GEN-2024-023 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640278 SHELDON7 115 640591 OLIVECREEK 7 115 2 | Current Study | 1 | (598.00, 598.00) | 178557.4023 | 17.8557 | 1000000 | 0.021428
GEN-2024-023 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640278 SHELDON7 115 650242 FOLSM&PHIL7 115 1 | Current Study | 15.49 | (329.00, 329.00) | 2673194.5564 | 17.2576 | 15490000 | 0.021291
GEN-2024-023 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1 | Current Study | 10.55 | (598.00, 598.00) | 1698071.5747 | 16.0955 | 10550000 | 0.023849
GEN-2024-023 | 02 NEBRASKA | TBD | ERIS | Rebuild line 645454 S3454 3 345 645455 S3455 3 345 1 | Current Study | 6.67 | (1793.00, 1793.00) | 2138336.9448 | 14.5723 | 14674000 | 0.072203
GEN-2024-023 | 02 NEBRASKA | TBD | NRIS | Rebuild line 645454 S3454 3 345 650185 WAGENER 3 345 1 | Current Study | 33.67 | (1793.00, 1793.00) | 6931810.7778 | 9.358 | 74074000 | 0.15453
GEN-2024-023 | 02 NEBRASKA | TBD | NRIS | Rebuild line 645456 S3456 3 345 645458 S3458 3 345 1 | Current Study | 44.95 | (1793.00, 1793.00) | 14989566.1778 | 15.1578 | 98890000 | 0.026478
GEN-2024-023 | 02 NEBRASKA | TBD | NRIS | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | Current Study | 17.69 | (246.00, 246.00) | 2090081.3305 | 7.8767 | 26535000 | 0.0247
GEN-2024-023 | 02 NEBRASKA | TBD | NRIS | Rebuild line 650185 WAGENER 3 345 650189 103&ROKEBY3 345 1 | Current Study | 9.45 | (1793.00, 1793.00) | 2593918.677 | 12.4768 | 20790000 | 0.096969
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 59469.7851 | 4.3094 | 1380000 | 0.063712
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at PHILL 7 345 kV | Current Study |  |  | 362611.7473 | 6.8417 | 5300000 | 0.029713
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 29182.8148 | 1.1997 | 2432500 | 0.029107
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 88701.7215 | 1.6736 | 5300000 | 0.034176
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV | Current Study |  |  | 59469.7851 | 4.3094 | 1380000 | 0.063712
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 0.2 MVAR switched shunt at GROVE 5 161 kV | Current Study |  |  | 78296.3507 | 2.4091 | 3250000 | 0.052392
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 0.25 MVAR switched shunt at LABETTS2 69 kV | Current Study |  |  | 36058.8049 | 2.613 | 1380000 | 0.052392
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 11 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 136873.5054 | 4.2115 | 3250000 | 0.063712
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 193476.9062 | 1.6123 | 12000000 | 0.034176
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR switched shunt at NEOSHO 4 138 kV | Current Study |  |  | 48688.3732 | 2.0016 | 2432500 | 0.063712
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at CPK446 5 161 kV | Current Study |  |  | 103895.2344 | 3.1968 | 3250000 | 0.063712
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR switched shunt at WICHITA7 345 kV | Current Study |  |  | 82404.3741 | 1.5548 | 5300000 | 0.034176
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 177 MVAR switched shunt at SWISVAL7 345 kV | Current Study |  |  | 70484.9114 | 1.3299 | 5300000 | 0.01726
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 24 MVAR switched shunt at GROVE 4 138 kV | Current Study |  |  | 22415.8971 | 0.92152 | 2432500 | 0.021701
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 280 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 200538.9661 | 1.6712 | 12000000 | 0.038615
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV | Current Study |  |  | 45959.6876 | 3.3304 | 1380000 | 0.056469
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at INDEPCO5 161 kV | Current Study |  |  | 136873.5054 | 4.2115 | 3250000 | 0.063712
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 54392.5651 | 1.6736 | 3250000 | 0.034176
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Add 45 MVAR switched shunt at NEVADA 5 161 kV | Current Study |  |  | 38672.4783 | 1.1899 | 3250000 | 0.01726
GEN-2024-025 | 04 SOUTHEAST | 171495 | ERIS | Lydia 345 kV Substation GEN-2024-025 Interconnection (Non-Shared NU) (AEP) | Interconnection |  |  | 3900000 | 100 | 3900000 | 1
GEN-2024-025 | 04 SOUTHEAST | 171494 | ERIS | Lydia 345 kV Substation GEN-2024-025 Interconnection (TOIF) (AEP) | Interconnection |  |  | 5225000 | 100 | 5225000 | 1
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | Current Study | 14.95 | (329.00, 329.00) | 1578021.9243 | 10.5553 | 14950000 | 0.036744
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508359 WELSH 7 345 508841 WILKES 7 345 1 | Current Study | 30.63 | (1793.00, 1793.00) | 12633240.5607 | 18.7476 | 67386000 | 0.16482
GEN-2024-025 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | Current Study | 21.38 | (1793.00, 1793.00) | 1698646.6402 | 3.6114 | 47036000 | 0.074992
GEN-2024-035 | 01 NORTH | TBD | NRIS | Add 2.8 MVAR switched shunt at WEBSTER CITY 69 kV | Current Study |  |  | 1380000 | 100 | 1380000 | 0.12256
GEN-2024-035 | 01 NORTH | 171505 | ERIS | Groton 345 kV Substation GEN-2024-035 Interconnection (Non-Shared NU) (BEPC) | Interconnection |  |  | 7125379 | 100 | 7125379 | 1
GEN-2024-035 | 01 NORTH | 171504 | ERIS | Groton 345 kV Substation GEN-2024-035 Interconnection (TOIF) (BEPC) | Interconnection |  |  | 2834775 | 100 | 2834775 | 1
GEN-2024-035 | 01 NORTH | TBD | ERIS | Rebuild line 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1 | Current Study | 21.31 | (176.00, 176.00) | 21310000 | 100 | 21310000 | 0.05207
GEN-2024-035 | 01 NORTH | TBD | NRIS | Rebuild line 652512 GROTON 7 115 660001 ABR SIEBRCHT 115 1 | Current Study | 25.8 | (260.00, 260.00) | 25800000 | 100 | 25800000 | 0.072635
GEN-2024-035 | 01 NORTH | TBD | ERIS | Rebuild line 652522 SUMMIT-7 115 655457 BRISTOL-ER7 115 1 | Current Study | 32.97 | (176.00, 176.00) | 32970000 | 100 | 32970000 | 0.05207
GEN-2024-041 | 05 SOUTHWEST | 94067 | ERIS | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028 | Contingent |  |  | 0 | 0 | 38846321 | N/A
GEN-2024-041 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 48307.0546 | 3.5005 | 1380000 | 0.097872
GEN-2024-041 | 05 SOUTHWEST | TBD | ERIS | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV | Current Study |  |  | 25398.0477 | 1.8404 | 1380000 | 0.071966
GEN-2024-041 | 05 SOUTHWEST | TBD | ERIS | Add 1.6 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 38361.379 | 2.7798 | 1380000 | 0.083211
GEN-2024-041 | 05 SOUTHWEST | TBD | NRIS | Add 11 MVAR switched shunt at WWRDEHV4 138 kV | Current Study |  |  | 103561.9786 | 4.2574 | 2432500 | 0.063822
GEN-2024-041 | 05 SOUTHWEST | TBD | ERIS | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 65650.5655 | 4.7573 | 1380000 | 0.16642
GEN-2024-041 | 05 SOUTHWEST | TBD | ERIS | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV | Current Study |  |  | 65650.5655 | 4.7573 | 1380000 | 0.16642
GEN-2024-041 | 05 SOUTHWEST | TBD | NRIS | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV | Current Study |  |  | 87930.0526 | 3.823 | 2300000 | 0.16006
GEN-2024-041 | 05 SOUTHWEST | TBD | ERIS | Add 3.6 MVAR switched shunt at HEDLEY 2 69 kV | Current Study |  |  | 34851.3983 | 2.5255 | 1380000 | 0.00186
GEN-2024-041 | 05 SOUTHWEST | TBD | NRIS | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2 | Current Study |  | (484.00, 515.00) | 1431981.0902 | 7.9115 | 18100000 | 0.012459
GEN-2024-041 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2 | Current Study |  | (339.00, 330.00) | 505480.8231 | 3.6106 | 14000000 | 0.020551
GEN-2024-041 | 05 SOUTHWEST | TBD | ERIS | Add line 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 P2 | Current Study | 66.8 | (1011.00, 1176.00) | 10311445.658 | 4.7501 | 217080000 | 0.083446
GEN-2024-041 | 05 SOUTHWEST | TBD | ERIS | Apply contingent IDV 01_NewLine_Phantom_Crossroads_Potter_765_26SP.idv | Contingent |  |  | 0 | 0 | 3275253469 | N/A
GEN-2024-041 | 05 SOUTHWEST | TBD | ERIS | Apply contingent IDV 02_765_Phantom_Craw_1_DIS24_TC05ALL-26SP.idv | Contingent |  |  | 0 | 0 | 1366342009.82 | N/A
GEN-2024-041 | 05 SOUTHWEST | TBD | ERIS | Apply contingent IDV 02_765_Phantom_Craw_1_DIS24_TC05ALL-29SP.idv | Contingent |  |  | 0 | 0 | 1366342009.82 | N/A
GEN-2024-041 | 05 SOUTHWEST | 900427 | ERIS | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032 | Contingent |  |  | 0 | 0 | 1790026304.1702 | N/A
GEN-2024-041 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | Current Study | 18.75 | (519.00, 519.00) | 1286268.1659 | 3.6106 | 35625000 | 0.041101
GEN-2024-041 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Current Study | 57.98 | (1793.00, 1793.00) | 6068220.7431 | 4.7573 | 127556000 | 0.16641
GEN-2024-041 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | Current Study | 3.02 | (1793.00, 1793.00) | 1494030.3524 | 22.4869 | 6644000 | 0.82946
GEN-2024-041 | 05 SOUTHWEST | 171512 | ERIS | Tuco - Whirlwind 345 kV line GEN-2024-041 Interconnection (TOIF) (SPS) | Interconnection |  |  | 5024078.97 | 100 | 5024078.97 | 1
GEN-2024-041 | 05 SOUTHWEST | 171514 | ERIS | Tuco - Whirlwind 345 kV line GEN-2024-041/042 Interconnection (Shared NU) (SPS) | Interconnection |  |  | 13860161.15 | 50 | 27720322.3 | 1
GEN-2024-042 | 05 SOUTHWEST | 94067 | ERIS | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028 | Contingent |  |  | 0 | 0 | 38846321 | N/A
GEN-2024-042 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 48307.0546 | 3.5005 | 1380000 | 0.097872
GEN-2024-042 | 05 SOUTHWEST | TBD | ERIS | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV | Current Study |  |  | 25398.0477 | 1.8404 | 1380000 | 0.071966
GEN-2024-042 | 05 SOUTHWEST | TBD | ERIS | Add 1.6 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 38361.379 | 2.7798 | 1380000 | 0.083211
GEN-2024-042 | 05 SOUTHWEST | TBD | NRIS | Add 11 MVAR switched shunt at WWRDEHV4 138 kV | Current Study |  |  | 103561.9786 | 4.2574 | 2432500 | 0.063822
GEN-2024-042 | 05 SOUTHWEST | TBD | ERIS | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 65650.5655 | 4.7573 | 1380000 | 0.16642
GEN-2024-042 | 05 SOUTHWEST | TBD | ERIS | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV | Current Study |  |  | 65650.5655 | 4.7573 | 1380000 | 0.16642
GEN-2024-042 | 05 SOUTHWEST | TBD | NRIS | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV | Current Study |  |  | 87930.0526 | 3.823 | 2300000 | 0.16006
GEN-2024-042 | 05 SOUTHWEST | TBD | ERIS | Add 3.6 MVAR switched shunt at HEDLEY 2 69 kV | Current Study |  |  | 34851.3983 | 2.5255 | 1380000 | 0.00186
GEN-2024-042 | 05 SOUTHWEST | TBD | NRIS | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2 | Current Study |  | (484.00, 515.00) | 1431981.0902 | 7.9115 | 18100000 | 0.012459
GEN-2024-042 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2 | Current Study |  | (339.00, 330.00) | 505480.8231 | 3.6106 | 14000000 | 0.020551
GEN-2024-042 | 05 SOUTHWEST | TBD | ERIS | Add line 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 P2 | Current Study | 66.8 | (1011.00, 1176.00) | 10311445.658 | 4.7501 | 217080000 | 0.083446
GEN-2024-042 | 05 SOUTHWEST | TBD | ERIS | Apply contingent IDV 01_NewLine_Phantom_Crossroads_Potter_765_26SP.idv | Contingent |  |  | 0 | 0 | 3275253469 | N/A
GEN-2024-042 | 05 SOUTHWEST | TBD | ERIS | Apply contingent IDV 02_765_Phantom_Craw_1_DIS24_TC05ALL-26SP.idv | Contingent |  |  | 0 | 0 | 1366342009.82 | N/A
GEN-2024-042 | 05 SOUTHWEST | TBD | ERIS | Apply contingent IDV 02_765_Phantom_Craw_1_DIS24_TC05ALL-29SP.idv | Contingent |  |  | 0 | 0 | 1366342009.82 | N/A
GEN-2024-042 | 05 SOUTHWEST | 900427 | ERIS | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032 | Contingent |  |  | 0 | 0 | 1790026304.1702 | N/A
GEN-2024-042 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | Current Study | 18.75 | (519.00, 519.00) | 1286268.1659 | 3.6106 | 35625000 | 0.041101
GEN-2024-042 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Current Study | 57.98 | (1793.00, 1793.00) | 6068220.7431 | 4.7573 | 127556000 | 0.16641
GEN-2024-042 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | Current Study | 3.02 | (1793.00, 1793.00) | 1494030.3524 | 22.4869 | 6644000 | 0.82946
GEN-2024-042 | 05 SOUTHWEST | 171514 | ERIS | Tuco - Whirlwind 345 kV line GEN-2024-041/042 Interconnection (Shared NU) (SPS) | Interconnection |  |  | 13860161.15 | 50 | 27720322.3 | 1
GEN-2024-042 | 05 SOUTHWEST | 171513 | ERIS | Tuco - Whirlwind 345 kV line GEN-2024-042 Interconnection (TOIF) (SPS) | Interconnection |  |  | 5024078.97 | 100 | 5024078.97 | 1
GEN-2024-043 | 05 SOUTHWEST | 94067 | ERIS | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028 | Contingent |  |  | 0 | 0 | 38846321 | N/A
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 46817.7147 | 3.3926 | 1380000 | 0.094855
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV | Current Study |  |  | 30874.9349 | 2.2373 | 1380000 | 0.087485
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Add 1.6 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 27812.1652 | 2.0154 | 1380000 | 0.060329
GEN-2024-043 | 05 SOUTHWEST | TBD | NRIS | Add 11 MVAR switched shunt at WWRDEHV4 138 kV | Current Study |  |  | 98670.3529 | 4.0563 | 2432500 | 0.060807
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 47596.9431 | 3.4491 | 1380000 | 0.12066
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV | Current Study |  |  | 47596.9431 | 3.4491 | 1380000 | 0.12066
GEN-2024-043 | 05 SOUTHWEST | TBD | NRIS | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV | Current Study |  |  | 62728.7396 | 2.7273 | 2300000 | 0.11419
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Add 3.6 MVAR switched shunt at HEDLEY 2 69 kV | Current Study |  |  | 56186.328 | 4.0715 | 1380000 | 0.0029987
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2 | Current Study |  | (339.00, 330.00) | 597501.1785 | 4.2679 | 14000000 | 0.024292
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 531510 HARBNGR3 115 531511 HARBNGR-1 13 531512 HARBNGR7 345 M2 | Current Study |  | (350.00, 385.00) | 1620891.9117 | 9.6482 | 16800000 | 0.0084191
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Add line 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 P2 | Current Study | 66.8 | (1011.00, 1176.00) | 7491375.7561 | 3.451 | 217080000 | 0.060624
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Apply contingent IDV 01_NewLine_Phantom_Crossroads_Potter_765_26SP.idv | Contingent |  |  | 0 | 0 | 3275253469 | N/A
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Apply contingent IDV 02_765_Phantom_Craw_1_DIS24_TC05ALL-26SP.idv | Contingent |  |  | 0 | 0 | 1366342009.82 | N/A
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Apply contingent IDV 02_765_Phantom_Craw_1_DIS24_TC05ALL-29SP.idv | Contingent |  |  | 0 | 0 | 1366342009.82 | N/A
GEN-2024-043 | 05 SOUTHWEST | 171516 | ERIS | Crossroads - Tolk 345 kV Line GEN-2024-043 Interconnection (Non-Shared NU) (SPS) | Interconnection |  |  | 29754372.46 | 100 | 29754372.46 | 1
GEN-2024-043 | 05 SOUTHWEST | 171515 | ERIS | Crossroads - Tolk 345 kV Line GEN-2024-043 Interconnection (TOIF) (SPS) | Interconnection |  |  | 4774296.21 | 100 | 4774296.21 | 1
GEN-2024-043 | 05 SOUTHWEST | 900427 | ERIS | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032 | Contingent |  |  | 0 | 0 | 1790026304.1702 | N/A
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | Current Study | 18.75 | (519.00, 519.00) | 1520427.106 | 4.2679 | 35625000 | 0.048583
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 511541 DEMPSEYR POI 230 511557 CHISHOLM6 230 1 | Current Study | 11.15 | (519.00, 519.00) | 2781515.4007 | 13.1296 | 21185000 | 0.042336
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Current Study | 57.98 | (1793.00, 1793.00) | 4399406.9753 | 3.449 | 127556000 | 0.12065
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523959 POTTER_CO 6 230 524010 ROLLHILLS 6 230 1 | Current Study | 6.23 | (637.00, 637.00) | 1399445.1993 | 11.8226 | 11837000 | 0.045898
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | Current Study | 3.02 | (1793.00, 1793.00) | 134958.9235 | 2.0313 | 6644000 | 0.074927
GEN-2024-043 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 531405 WALKMYR3 115 531510 HARBNGR3 115 1 | Current Study | 1.28 | (598.00, 598.00) | 123496.5266 | 9.6482 | 1280000 | 0.016838
GEN-2024-051 | 02 NEBRASKA | TBD | NRIS | Add 108 MVAR switched shunt at MAURINE4 230 kV | Current Study |  |  | 172176.7471 | 4.5014 | 3825000 | 0.03662
GEN-2024-051 | 02 NEBRASKA | TBD | NRIS | Add 12 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 111264.0121 | 5.0289 | 2212500 | 0.03662
GEN-2024-051 | 02 NEBRASKA | TBD | NRIS | Add 154 MVAR SVC at WAYSIDE 4 230 kV | Current Study |  |  | 306224.5963 | 3.5608 | 8600000 | 0.038634
GEN-2024-051 | 02 NEBRASKA | TBD | NRIS | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 42538.9194 | 1.9227 | 2212500 | 0.03662
GEN-2024-051 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 640125 COLMB.E3 345 640127 COLMB.E7 115 640129 COLMB.T9 13 M2 | Current Study |  | (336.00, 336.00) | 98348.8962 | 0.58541 | 16800000 | 0.00051599
GEN-2024-051 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2 | Current Study |  | (110.00, 120.00) | 3030053.1138 | 25.2504 | 12000000 | 0.062878
GEN-2024-051 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 652305 SIOUXC29 13 652552 SIOUXCY2 230 652564 SIOUXCY3 345 M2 | Current Study |  | (600.00, 750.00) | 5730021.5445 | 22.9201 | 25000000 | 0.0064319
GEN-2024-051 | 02 NEBRASKA | TBD | NRIS | Add 45 MVAR switched shunt at PR BRZ 4 230 kV | Current Study |  |  | 145311.4806 | 3.799 | 3825000 | 0.076731
GEN-2024-051 | 02 NEBRASKA | TBD | NRIS | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | Current Study | 23.48 | (1793.00, 1793.00) | 2519697.4632 | 4.8778 | 51656000 | 0.04688
GEN-2024-051 | 02 NEBRASKA | TBD | NRIS | Rebuild line 645454 S3454 3 345 650185 WAGENER 3 345 1 | Current Study | 33.67 | (1793.00, 1793.00) | 5648912.2247 | 7.626 | 74074000 | 0.20001
GEN-2024-051 | 02 NEBRASKA | TBD | NRIS | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | Current Study | 17.69 | (246.00, 246.00) | 6700204.948 | 25.2504 | 26535000 | 0.12576
GEN-2024-051 | 02 NEBRASKA | TBD | NRIS | Rebuild line 646221 S1221 5 161 646255 S1255 5 161 1 | Current Study | 4.09 | (446.00, 446.00) | 6135000 | 100 | 6135000 | 0.016416
GEN-2024-051 | 02 NEBRASKA | 171525 | ERIS | Waverly 115 kV Substation GEN-2024-051 Interconnection (Non-Shared NU) (LES) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-051 | 02 NEBRASKA | 171524 | ERIS | Waverly 115 kV Substation GEN-2024-051 Interconnection (TOIF) (LES) | Interconnection |  |  | 7533500 | 100 | 7533500 | 1
GEN-2024-054 | 03 CENTRAL | 94615 | ERIS | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029 | Contingent |  |  | 0 | 0 | 543515503 | N/A
GEN-2024-054 | 03 CENTRAL | TBD | ERIS | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV | Current Study |  |  | 19988.3545 | 1.4484 | 1380000 | 0.033349
GEN-2024-054 | 03 CENTRAL | TBD | ERIS | Add 16 MVAR switched shunt at HUMBOLT5 161 kV | Current Study |  |  | 65640.7294 | 2.0197 | 3250000 | 0.04088
GEN-2024-054 | 03 CENTRAL | TBD | ERIS | Add 21 MVAR switched shunt at S1263 5 161 kV | Current Study |  |  | 65640.7294 | 2.0197 | 3250000 | 0.04088
GEN-2024-054 | 03 CENTRAL | TBD | ERIS | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV | Current Study |  |  | 27872.0636 | 2.0197 | 1380000 | 0.04088
GEN-2024-054 | 03 CENTRAL | 94721 | ERIS | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 213682884 | N/A
GEN-2024-054 | 03 CENTRAL | 94929 | ERIS | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 413934522 | N/A
GEN-2024-054 | 03 CENTRAL | 171903 | ERIS | Overton - Sedalia East 161 kV line GEN-2024-054 Interconnection (Non-Shared NU) (WERE) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-054 | 03 CENTRAL | 171902 | ERIS | Overton - Sedalia East 161 kV line GEN-2024-054 Interconnection (TOIF) (WERE) | Interconnection |  |  | 112911 | 100 | 112911 | 1
GEN-2024-054 | 03 CENTRAL | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 118321.6767 | 1.0148 | 11660000 | 0.046632
GEN-2024-054 | 03 CENTRAL | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 822533.3892 | 0.87518 | 93984000 | 0.046632
GEN-2024-054 | 03 CENTRAL | TBD | ERIS | Rebuild the 5MCBAINE to 5OVERTON 2 115kV Line 1 | JTIQ Expanded Scope Analysis | 11.98 | (557, 557) | 16766010 | 100 | 16766010 | 0.09781
GEN-2024-055 | 03 CENTRAL | 94615 | ERIS | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029 | Contingent |  |  | 0 | 0 | 543515503 | N/A
GEN-2024-055 | 03 CENTRAL | TBD | ERIS | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV | Current Study |  |  | 45600.5435 | 3.3044 | 1380000 | 0.05217
GEN-2024-055 | 03 CENTRAL | TBD | ERIS | Add 16 MVAR switched shunt at HUMBOLT5 161 kV | Current Study |  |  | 107941.6047 | 3.3213 | 3250000 | 0.046097
GEN-2024-055 | 03 CENTRAL | TBD | ERIS | Add 21 MVAR switched shunt at S1263 5 161 kV | Current Study |  |  | 107941.6047 | 3.3213 | 3250000 | 0.046097
GEN-2024-055 | 03 CENTRAL | TBD | ERIS | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV | Current Study |  |  | 45833.666 | 3.3213 | 1380000 | 0.046097
GEN-2024-055 | 03 CENTRAL | TBD | ERIS | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2 | Current Study | 0.75 | (2390.00, 2390.00) | 74640.7118 | 0.41992 | 17775000 | 0.013161
GEN-2024-055 | 03 CENTRAL | 94721 | ERIS | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 213682884 | N/A
GEN-2024-055 | 03 CENTRAL | 94929 | ERIS | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 413934522 | N/A
GEN-2024-055 | 03 CENTRAL | 171905 | ERIS | Butler - Nevada 161 kV line GEN-2024-055 Interconnection (Non-Shared NU) (WERE) | Interconnection |  |  | 15550547 | 100 | 15550547 | 1
GEN-2024-055 | 03 CENTRAL | 171904 | ERIS | Butler - Nevada 161 kV line GEN-2024-055 Interconnection (TOIF) (WERE) | Interconnection |  |  | 1495123 | 100 | 1495123 | 1
GEN-2024-055 | 03 CENTRAL | TBD | ERIS | Rebuild line 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | Current Study | 3.02 | (551.00, 551.00) | 438369.8718 | 9.677 | 4530000 | 0.037094
GEN-2024-055 | 03 CENTRAL | TBD | ERIS | Rebuild line 301402 5LOSTVALY 161 505502 TRUMAN 5 161 1 | Current Study | 2.6 | (309.00, 309.00) | 3900000 | 100 | 3900000 | 0.028035
GEN-2024-055 | 03 CENTRAL | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 252949.2266 | 2.1694 | 11660000 | 0.068359
GEN-2024-055 | 03 CENTRAL | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 1758419.8477 | 1.871 | 93984000 | 0.068359
GEN-2024-055 | 03 CENTRAL | TBD | ERIS | Rebuild line 541199 ST JOE 7 345 541400 EASTOWN7 345 1 | Current Study | 8.12 | (1793.00, 1793.00) | 436676.4491 | 2.4444 | 17864000 | 0.02651
GEN-2024-055 | 03 CENTRAL | TBD | ERIS | Rebuild line 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | Current Study | 28.98 | (1793.00, 1793.00) | 6402204.0679 | 10.0417 | 63756000 | 0.090706
GEN-2024-055 | 03 CENTRAL | TBD | ERIS | Rebuild line 541400 EASTOWN7 345 542982 IATAN 7 345 1 | Current Study | 23.71 | (1793.00, 1793.00) | 1285857.2003 | 2.4651 | 52162000 | 0.031172
GEN-2024-056 | 04 SOUTHEAST | 94615 | ERIS | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029 | Contingent |  |  | 0 | 0 | 543515503 | N/A
GEN-2024-056 | 04 SOUTHEAST | 94811 | ERIS | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030 | Contingent |  |  | 0 | 0 | 1097029189 | N/A
GEN-2024-056 | 04 SOUTHEAST | 94911 | ERIS | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030 | Contingent |  |  | 0 | 0 | 143524375 | N/A
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 280731.9855 | 5.2968 | 5300000 | 0.038234
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at MOUND 4 138 kV | Current Study |  |  | 64125.8179 | 2.6362 | 2432500 | 0.053748
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV | Current Study |  |  | 182262.4192 | 3.4389 | 5300000 | 0.043205
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 34770.0047 | 1.4294 | 2432500 | 0.04335
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 0.04 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 171313.138 | 5.2712 | 3250000 | 0.02853
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 0.09 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 52872.0464 | 1.6268 | 3250000 | 0.02853
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 0.09 MVAR switched shunt at SWISVAL6 230 kV | Current Study |  |  | 239531.373 | 6.2623 | 3825000 | 0.038234
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 91897.1024 | 1.7339 | 5300000 | 0.044259
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 0.2 MVAR switched shunt at GROVE 5 161 kV | Current Study |  |  | 34108.9022 | 1.0495 | 3250000 | 0.02853
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at TONTITN7 345 kV | Current Study |  |  | 133228.4837 | 2.5137 | 5300000 | 0.027709
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 15 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 52872.0464 | 1.6268 | 3250000 | 0.02853
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 200446.6966 | 1.6704 | 12000000 | 0.044259
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR switched shunt at NEOSHO 4 138 kV | Current Study |  |  | 56144.2117 | 2.3081 | 2432500 | 0.091836
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV | Current Study |  |  | 48619.3106 | 1.496 | 3250000 | 0.0262
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR switched shunt at WICHITA7 345 kV | Current Study |  |  | 133816.0315 | 2.5248 | 5300000 | 0.069373
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 177 MVAR switched shunt at SWISVAL7 345 kV | Current Study |  |  | 115188.7647 | 2.1734 | 5300000 | 0.03526
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 2 MVAR switched shunt at CLIFTON3 115 kV | Current Study |  |  | 206228.6687 | 9.3211 | 2212500 | 0.030043
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 20 MVAR switched shunt at LIBERTY4 138 kV | Current Study |  |  | 39000.9769 | 1.6033 | 2432500 | 0.04335
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 48619.3106 | 1.496 | 3250000 | 0.0262
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR switched shunt at STILWEL7 345 kV | Current Study |  |  | 151660.0324 | 2.8615 | 5300000 | 0.03526
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 24 MVAR switched shunt at GROVE 4 138 kV | Current Study |  |  | 21651.0804 | 0.89008 | 2432500 | 0.0262
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at G21-096-TAP 345 kV | Current Study |  |  | 208871.6212 | 3.941 | 5300000 | 0.03985
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 280 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 354857.6105 | 2.9571 | 12000000 | 0.085413
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 295 MVAR switched shunt at G18-128-TAP 345 kV | Current Study |  |  | 201790.6144 | 3.8074 | 5300000 | 0.091836
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 3 MVAR switched shunt at NEOSHOS2 69 kV | Current Study |  |  | 66925.2973 | 4.8497 | 1380000 | 0.091836
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at G23-220-TAP 345 kV | Current Study |  |  | 180741.8787 | 3.4102 | 5300000 | 0.038234
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 316 MVAR switched shunt at W.GRDNR7 345 kV | Current Study |  |  | 151660.0324 | 2.8615 | 5300000 | 0.03526
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 56351.9968 | 1.7339 | 3250000 | 0.044259
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 45 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 488027.069 | 4.0669 | 12000000 | 0.091836
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 45 MVAR switched shunt at NEVADA 5 161 kV | Current Study |  |  | 63199.8383 | 1.9446 | 3250000 | 0.03526
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 387499.2291 | 7.3113 | 5300000 | 0.030043
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 56 MVAR switched shunt at WHARV4 138 kV | Current Study |  |  | 64125.8179 | 2.6362 | 2432500 | 0.053748
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV | Current Study |  |  | 24162.1052 | 1.7509 | 1380000 | 0.02853
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add 86 MVAR switched shunt at POSTROCK7 345 kV | Current Study |  |  | 241266.7676 | 4.5522 | 5300000 | 0.016777
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Add line 515012 RVRVALY7 345 780360 G24-113-TAP 345 P2 | Current Study | 23.28 | (1195.00, 1195.00) | 1128045.3833 | 1.3729 | 82168000 | 0.015693
GEN-2024-056 | 04 SOUTHEAST | 94721 | ERIS | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 213682884 | N/A
GEN-2024-056 | 04 SOUTHEAST | 94929 | ERIS | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 413934522 | N/A
GEN-2024-056 | 04 SOUTHEAST | 171528 | ERIS | Cow Creek - Morrison 138 kV line GEN-2024-056 Interconnection (Non-Shared NU) (OGE) | Interconnection |  |  | 7000000 | 100 | 7000000 | 1
GEN-2024-056 | 04 SOUTHEAST | 171527 | ERIS | Cow Creek - Morrison 138 kV line GEN-2024-056 Interconnection (TOIF) (OGE) | Interconnection |  |  | 2000000 | 100 | 2000000 | 1
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | DIS2301-1_G03_ERIS_TurnOffReactors_Carpenter_Finney.idv : Switch out Carpenter 25 MVAR line reactor on the Carpenter to Hitchland 345 kV line | Contingent |  |  | 0 | 0 | 1450000 | 0.019723
GEN-2024-056 | 04 SOUTHEAST | 900427 | ERIS | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032 | Contingent |  |  | 0 | 0 | 1790026304.1702 | N/A
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 565875.3616 | 1.6845 | 33594000 | 0.051183
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 109844.0489 | 0.94206 | 11660000 | 0.043291
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Current Study | 14.6 | (1793.00, 1793.00) | 541046.5147 | 1.6845 | 32120000 | 0.051183
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 34930.7997 | 1.5878 | 2200000 | 0.044951
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 | Current Study | 3.89 | (265.00, 265.00) | 4668000 | 100 | 4668000 | 0.043116
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 | Current Study | 1.46 | (265.00, 265.00) | 1752000 | 100 | 1752000 | 0.043116
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514760 KILDARE4 138 514764 NWKRKAT4 138 1 | Current Study | 0.58 | (265.00, 265.00) | 696000 | 100 | 696000 | 0.043116
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514804 MIDLTNT4 138 515381 PECKHMT4 138 1 | Current Study | 3.49 | (265.00, 265.00) | 4188000 | 100 | 4188000 | 0.043116
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514804 MIDLTNT4 138 532981 CRESWLN4 138 1 | Current Study | 9.08 | (265.00, 265.00) | 10896000 | 100 | 10896000 | 0.043116
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 2255221.2498 | 4.9118 | 45914000 | 0.085725
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532768 EMPEC 7 345 776400 G23-221-TAP 345 1 | Current Study | 12 | (1793.00, 1793.00) | 26400000 | 100 | 26400000 | 0.03558
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | Current Study | 25.07 | (1793.00, 1793.00) | 55154000 | 100 | 55154000 | 0.03558
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | Current Study | 15.48 | (1793.00, 1793.00) | 1786451.1671 | 5.2456 | 34056000 | 0.046587
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 763599.7088 | 0.81248 | 93984000 | 0.043291
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Current Study | 25.29 | (2390.00, 2390.00) | 2513449.3404 | 4.5175 | 55638000 | 0.092054
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 1230808.339 | 4.9118 | 25058000 | 0.085725
GEN-2024-056 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 2200000 | 100 | 2200000 | 0.03558
GEN-2024-065 | 02 NEBRASKA | TBD | NRIS | Add 108 MVAR switched shunt at MAURINE4 230 kV | Current Study |  |  | 155495.1489 | 4.0652 | 3825000 | 0.037482
GEN-2024-065 | 02 NEBRASKA | TBD | NRIS | Add 12 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 100484.0342 | 4.5417 | 2212500 | 0.037482
GEN-2024-065 | 02 NEBRASKA | TBD | NRIS | Add 154 MVAR SVC at WAYSIDE 4 230 kV | Current Study |  |  | 235250.8046 | 2.7355 | 8600000 | 0.033637
GEN-2024-065 | 02 NEBRASKA | TBD | NRIS | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 38417.4735 | 1.7364 | 2212500 | 0.037482
GEN-2024-065 | 02 NEBRASKA | TBD | NRIS | Add 45 MVAR switched shunt at PR BRZ 4 230 kV | Current Study |  |  | 66140.8404 | 1.7292 | 3825000 | 0.039582
GEN-2024-065 | 02 NEBRASKA | TBD | ERIS | Fremont_Add_transformer_fixed.idv : | Current Study |  |  | 8125000 | 100 | 8125000 | 0.14046
GEN-2024-065 | 02 NEBRASKA | 171536 | ERIS | FREMONT7 115 kV Substation GEN-2024-065 Interconnection (Non-Shared NU) (NPPD) | Interconnection |  |  | 9500000 | 100 | 9500000 | 1
GEN-2024-065 | 02 NEBRASKA | 171535 | ERIS | FREMONT7 115 kV Substation GEN-2024-065 Interconnection (TOIF) (NPPD) | Interconnection |  |  | 500000 | 100 | 500000 | 1
GEN-2024-065 | 02 NEBRASKA | TBD | NRIS | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | Current Study | 23.48 | (1793.00, 1793.00) | 1412077.4762 | 2.7336 | 51656000 | 0.029775
GEN-2024-065 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | Current Study | 23.61 | (519.00, 519.00) | 4676088.2762 | 10.424 | 44859000 | 0.065787
GEN-2024-065 | 02 NEBRASKA | TBD | ERIS | Rebuild line 647424 FREM D 8 69 647976 S976 8 69 1 | Current Study | 0.06 | (140.00, 140.00) | 47454.7269 | 93.0485 | 51000 | 0.40858
GEN-2024-067 | 03 CENTRAL | 94615 | ERIS | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029 | Contingent |  |  | 0 | 0 | 543515503 | N/A
GEN-2024-067 | 03 CENTRAL | 94911 | ERIS | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030 | Contingent |  |  | 0 | 0 | 143524375 | N/A
GEN-2024-067 | 03 CENTRAL | TBD | ERIS | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV | Current Study |  |  | 21742.6441 | 1.5756 | 1380000 | 0.040532
GEN-2024-067 | 03 CENTRAL | TBD | ERIS | Add 3-winding transformer 539657 CONCORD3 115 539658 CONCRD6 230 539904 CONCOD-1 13 M2 | Current Study |  | (205.00, 225.50) | 7385678.2932 | 53.5194 | 13800000 | 0.020999
GEN-2024-067 | 03 CENTRAL | TBD | ERIS | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2 | Current Study | 0.75 | (2390.00, 2390.00) | 165776.3262 | 0.93264 | 17775000 | 0.013461
GEN-2024-067 | 03 CENTRAL | 94721 | ERIS | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 213682884 | N/A
GEN-2024-067 | 03 CENTRAL | 94929 | ERIS | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 413934522 | N/A
GEN-2024-067 | 03 CENTRAL | 171538 | ERIS | Cirrus 345 kV Substation GEN-2024-067 Interconnection (Non-Shared NU) (ITCGP) | Interconnection |  |  | 4630435 | 100 | 4630435 | 1
GEN-2024-067 | 03 CENTRAL | 171537 | ERIS | Cirrus 345 kV Substation GEN-2024-067 Interconnection (TOIF) (ITCGP) | Interconnection |  |  | 1306438 | 100 | 1306438 | 1
GEN-2024-067 | 03 CENTRAL | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 1466469.5855 | 1.5603 | 93984000 | 0.026254
GEN-2024-067 | 03 CENTRAL | TBD | NRIS | Rebuild line 539656 CLIFTON3 115 539657 CONCORD3 115 1 | Current Study | 23.19 | (176.00, 176.00) | 12504256.471 | 53.9209 | 23190000 | 0.022832
GEN-2024-067 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640525 TOBIAS 3 345 1 | Current Study | 26.47 | (1793.00, 1793.00) | 27812460.4137 | 47.7598 | 58234000 | 0.20645
GEN-2024-067 | 03 CENTRAL | TBD | NRIS | Rebuild line 645454 S3454 3 345 650185 WAGENER 3 345 1 | Current Study | 33.67 | (1793.00, 1793.00) | 3862324.3967 | 5.2141 | 74074000 | 0.06118
GEN-2024-067 | 03 CENTRAL | TBD | NRIS | Rebuild line 650185 WAGENER 3 345 650189 103&ROKEBY3 345 1 | Current Study | 9.45 | (1793.00, 1793.00) | 946458.6434 | 4.5525 | 20790000 | 0.025139
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 122171.599 | 8.853 | 1380000 | 0.065444
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at PHILL 7 345 kV | Current Study |  |  | 739759.1134 | 13.9577 | 5300000 | 0.030308
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 175660.4503 | 3.3143 | 5300000 | 0.03384
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV | Current Study |  |  | 122171.599 | 8.853 | 1380000 | 0.065444
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 0.2 MVAR switched shunt at GROVE 5 161 kV | Current Study |  |  | 159335.1865 | 4.9026 | 3250000 | 0.05331
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 0.25 MVAR switched shunt at LABETTS2 69 kV | Current Study |  |  | 73380.6409 | 5.3174 | 1380000 | 0.05331
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 11 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 281185.7312 | 8.6519 | 3250000 | 0.065444
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 383151.9825 | 3.1929 | 12000000 | 0.03384
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR switched shunt at NEOSHO 4 138 kV | Current Study |  |  | 100022.8332 | 4.1119 | 2432500 | 0.065444
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at CPK446 5 161 kV | Current Study |  |  | 213436.9057 | 6.5673 | 3250000 | 0.065444
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 24 MVAR switched shunt at GROVE 4 138 kV | Current Study |  |  | 135200.8337 | 5.5581 | 2432500 | 0.065444
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 280 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 395883.9514 | 3.299 | 12000000 | 0.038115
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV | Current Study |  |  | 96659.0965 | 7.0043 | 1380000 | 0.059381
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at INDEPCO5 161 kV | Current Study |  |  | 281185.7312 | 8.6519 | 3250000 | 0.065444
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 107716.3138 | 3.3143 | 3250000 | 0.03384
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Add 45 MVAR switched shunt at NEVADA 5 161 kV | Current Study |  |  | 151639.237 | 4.6658 | 3250000 | 0.03384
GEN-2024-068 | 04 SOUTHEAST | 171540 | ERIS | Lydia - Welsh 345 kV Line GEN-2024-068 Interconnection (Non-Shared NU) (AEP) | Interconnection |  |  | 28225000 | 100 | 28225000 | 1
GEN-2024-068 | 04 SOUTHEAST | 171539 | ERIS | Lydia - Welsh 345 kV Line GEN-2024-068 Interconnection (TOIF) (AEP) | Interconnection |  |  | 5225000 | 100 | 5225000 | 1
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | Current Study | 14.95 | (329.00, 329.00) | 2960934.9225 | 19.8056 | 14950000 | 0.034473
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508359 WELSH 7 345 508841 WILKES 7 345 1 | Current Study | 30.63 | (1793.00, 1793.00) | 28032987.271 | 41.6006 | 67386000 | 0.18287
GEN-2024-068 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | Current Study | 21.38 | (1793.00, 1793.00) | 3368229.5988 | 7.161 | 47036000 | 0.07435
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 33831.6299 | 2.4516 | 1380000 | 0.07249
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at PHILL 7 345 kV | Current Study |  |  | 197581.8792 | 3.728 | 5300000 | 0.03238
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 42486.1673 | 0.80163 | 5300000 | 0.032739
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV | Current Study |  |  | 33831.6299 | 2.4516 | 1380000 | 0.07249
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 0.2 MVAR switched shunt at GROVE 5 161 kV | Current Study |  |  | 42832.7446 | 1.3179 | 3250000 | 0.057323
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 0.25 MVAR switched shunt at LABETTS2 69 kV | Current Study |  |  | 19726.3035 | 1.4294 | 1380000 | 0.057323
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 11 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 77865.655 | 2.3959 | 3250000 | 0.07249
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 92671.1687 | 0.77226 | 12000000 | 0.032739
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR switched shunt at NEOSHO 4 138 kV | Current Study |  |  | 27698.2171 | 1.1387 | 2432500 | 0.07249
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at CPK446 5 161 kV | Current Study |  |  | 59104.722 | 1.8186 | 3250000 | 0.07249
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 24 MVAR switched shunt at GROVE 4 138 kV | Current Study |  |  | 37439.6717 | 1.5391 | 2432500 | 0.07249
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV | Current Study |  |  | 24148.9346 | 1.7499 | 1380000 | 0.059342
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at INDEPCO5 161 kV | Current Study |  |  | 77865.655 | 2.3959 | 3250000 | 0.07249
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 26052.8384 | 0.80163 | 3250000 | 0.032739
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Add 45 MVAR switched shunt at NEVADA 5 161 kV | Current Study |  |  | 36676.2693 | 1.1285 | 3250000 | 0.032739
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | Current Study | 14.95 | (329.00, 329.00) | 817299.6909 | 5.4669 | 14950000 | 0.038062
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508804 HOSSTON2 69 508846 GODFREYRDTP2 69 1 | Current Study | 8.6 | (69.00, 69.00) | 2484549.9044 | 33.9884 | 7310000 | 0.11463
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508806 LIEBERM4 138 780630 G24-122-TAP 138 1 | Current Study | 7.6 | (265.00, 265.00) | 185757.6349 | 2.0368 | 9120000 | 0.031179
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508814 RODESSA2 69 508846 GODFREYRDTP2 69 1 | Current Study | 0.28 | (69.00, 69.00) | 80892.3225 | 33.9884 | 238000 | 0.11463
GEN-2024-071 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508814 RODESSA2 69 783570 G24-220-TAP 69 1 | Current Study | 10.34 | (69.00, 69.00) | 2987237.9083 | 33.9884 | 8789000 | 0.11463
GEN-2024-071 | 04 SOUTHEAST | 171542 | ERIS | West Atlanta - Atlanta 69 kV Line GEN-2024-071 Interconnection (Non-Shared NU) (AEP) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-071 | 04 SOUTHEAST | 171541 | ERIS | West Atlanta - Atlanta 69 kV Line GEN-2024-071 Interconnection (TOIF) (AEP) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-074 | 03 CENTRAL | 94615 | ERIS | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029 | Contingent |  |  | 0 | 0 | 543515503 | N/A
GEN-2024-074 | 03 CENTRAL | TBD | ERIS | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV | Current Study |  |  | 72544.538 | 5.2569 | 1380000 | 0.072621
GEN-2024-074 | 03 CENTRAL | TBD | ERIS | Add 16 MVAR switched shunt at HUMBOLT5 161 kV | Current Study |  |  | 178855.126 | 5.5032 | 3250000 | 0.066834
GEN-2024-074 | 03 CENTRAL | TBD | ERIS | Add 21 MVAR switched shunt at S1263 5 161 kV | Current Study |  |  | 178855.126 | 5.5032 | 3250000 | 0.066834
GEN-2024-074 | 03 CENTRAL | TBD | ERIS | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV | Current Study |  |  | 75944.6381 | 5.5032 | 1380000 | 0.066834
GEN-2024-074 | 03 CENTRAL | TBD | ERIS | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2 | Current Study | 0.75 | (2390.00, 2390.00) | 110273.0635 | 0.62038 | 17775000 | 0.017013
GEN-2024-074 | 03 CENTRAL | 94721 | ERIS | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 213682884 | N/A
GEN-2024-074 | 03 CENTRAL | 94929 | ERIS | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 413934522 | N/A
GEN-2024-074 | 03 CENTRAL | 171911 | ERIS | Duncan Road 161 kV Substation GEN-2024-074 Interconnection (Non-Shared NU) (WERE) | Interconnection |  |  | 1235193 | 100 | 1235193 | 1
GEN-2024-074 | 03 CENTRAL | 171910 | ERIS | Duncan Road 161 kV Substation GEN-2024-074 Interconnection (TOIF) (WERE) | Interconnection |  |  | 1061550 | 100 | 1061550 | 1
GEN-2024-074 | 03 CENTRAL | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 243971.0894 | 2.0924 | 11660000 | 0.057691
GEN-2024-074 | 03 CENTRAL | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 1696006.7896 | 1.8046 | 93984000 | 0.057691
GEN-2024-074 | 03 CENTRAL | TBD | ERIS | Rebuild line 541199 ST JOE 7 345 541400 EASTOWN7 345 1 | Current Study | 8.12 | (1793.00, 1793.00) | 428541.9049 | 2.3989 | 17864000 | 0.022764
GEN-2024-074 | 03 CENTRAL | TBD | ERIS | Rebuild line 541400 EASTOWN7 345 542982 IATAN 7 345 1 | Current Study | 23.71 | (1793.00, 1793.00) | 1315281.394 | 2.5215 | 52162000 | 0.0279
GEN-2024-076 | 03 CENTRAL | 94615 | ERIS | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029 | Contingent |  |  | 0 | 0 | 543515503 | N/A
GEN-2024-076 | 03 CENTRAL | TBD | ERIS | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV | Current Study |  |  | 26836.9755 | 1.9447 | 1380000 | 0.041331
GEN-2024-076 | 03 CENTRAL | TBD | ERIS | Add 16 MVAR switched shunt at HUMBOLT5 161 kV | Current Study |  |  | 60444.0991 | 1.8598 | 3250000 | 0.034748
GEN-2024-076 | 03 CENTRAL | TBD | ERIS | Add 21 MVAR switched shunt at S1263 5 161 kV | Current Study |  |  | 60444.0991 | 1.8598 | 3250000 | 0.034748
GEN-2024-076 | 03 CENTRAL | TBD | NRIS | Add 3-winding transformer 532793 NEOSHO 7 345 532825 N345 2 1 13 532939 N345 4 5 161 M2 | Current Study |  | (500.00, 550.00) | 1383226.9574 | 6.8139 | 20300000 | 0.030927
GEN-2024-076 | 03 CENTRAL | TBD | ERIS | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV | Current Study |  |  | 25665.4944 | 1.8598 | 1380000 | 0.034748
GEN-2024-076 | 03 CENTRAL | 94721 | ERIS | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 213682884 | N/A
GEN-2024-076 | 03 CENTRAL | 94929 | ERIS | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 413934522 | N/A
GEN-2024-076 | 03 CENTRAL | 171913 | ERIS | Neosho - LaCygne 345 kV Line GEN-2024-076 Interconnection (Non-Shared NU) (WERE) | Interconnection |  |  | 1958090 | 100 | 1958090 | 1
GEN-2024-076 | 03 CENTRAL | 171912 | ERIS | Neosho - LaCygne 345 kV Line GEN-2024-076 Interconnection (TOIF) (WERE) | Interconnection |  |  | 1958090 | 100 | 1958090 | 1
GEN-2024-076 | 03 CENTRAL | TBD | NRIS | Rebuild line 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | Current Study | 31.46 | (1793.00, 1793.00) | 3260894.5124 | 4.7115 | 69212000 | 0.1576
GEN-2024-076 | 03 CENTRAL | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 440042.6875 | 3.774 | 11660000 | 0.16009
GEN-2024-076 | 03 CENTRAL | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 3059032.0671 | 3.2548 | 93984000 | 0.16009
GEN-2024-076 | 03 CENTRAL | TBD | ERIS | Rebuild line 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | Current Study | 15.42 | (1793.00, 1793.00) | 1607482.0912 | 4.7385 | 33924000 | 0.085574
GEN-2024-076 | 03 CENTRAL | TBD | NRIS | Rebuild line 532937 NEOSHO 5 161 532939 N345 4 5 161 1 | Current Study | 0.3 | (837.00, 837.00) | 30662.6665 | 6.8139 | 450000 | 0.061853
GEN-2024-076 | 03 CENTRAL | TBD | NRIS | Rebuild line 532937 NEOSHO 5 161 764310 G20-079-TAP 161 1 | Current Study | 20.67 | (551.00, 551.00) | 2034521.8393 | 6.5619 | 31005000 | 0.044976
GEN-2024-076 | 03 CENTRAL | TBD | ERIS | Rebuild line 541199 ST JOE 7 345 541400 EASTOWN7 345 1 | Current Study | 8.12 | (1793.00, 1793.00) | 393745.7917 | 2.2041 | 17864000 | 0.032178
GEN-2024-076 | 03 CENTRAL | TBD | ERIS | Rebuild line 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | Current Study | 28.98 | (1793.00, 1793.00) | 3584187.6112 | 5.6217 | 63756000 | 0.068359
GEN-2024-076 | 03 CENTRAL | TBD | ERIS | Rebuild line 541400 EASTOWN7 345 542982 IATAN 7 345 1 | Current Study | 23.71 | (1793.00, 1793.00) | 1134703.0859 | 2.1753 | 52162000 | 0.03703
GEN-2024-081 | 01 NORTH | 92168 | ERIS | 21ITP_Multi - Tande - Finstad - Leland Olds 345 kV.idv : 2021 ITP, PID: 92168, NTC, ISD: 11/30/2026 | Contingent |  |  | 0 | 0 | 346873086 | N/A
GEN-2024-081 | 01 NORTH | 92168 | ERIS | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026 | Contingent |  |  | 0 | 0 | 358995074 | N/A
GEN-2024-081 | 01 NORTH | 92211 | ERIS | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024 | Contingent |  |  | 0 | 0 | 9200000 | N/A
GEN-2024-081 | 01 NORTH | 900426 | ERIS | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030 | Contingent |  |  | 0 | 0 | 2372127948.71 | N/A
GEN-2024-081 | 01 NORTH | TBD | ERIS | Add 0.02 MVAR switched shunt at GEN-2017-214 230 kV | Current Study |  |  | 1912500 | 50 | 3825000 | 0.053439
GEN-2024-081 | 01 NORTH | TBD | ERIS | Add 0.02 MVAR switched shunt at RUSHMORE-RM8 69 kV | Current Study |  |  | 690000 | 50 | 1380000 | 0.038948
GEN-2024-081 | 01 NORTH | TBD | ERIS | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV | Current Study |  |  | 45880.4682 | 3.3247 | 1380000 | 0.043625
GEN-2024-081 | 01 NORTH | TBD | ERIS | Add 2 MVAR switched shunt at GEN-2017-140 345 kV | Current Study |  |  | 193528.1722 | 3.6515 | 5300000 | 0.056072
GEN-2024-081 | 01 NORTH | TBD | ERIS | Add 23 MVAR switched shunt at FINNEY 7 345 kV | Current Study |  |  | 519445.1703 | 9.8009 | 5300000 | 0.043625
GEN-2024-081 | 01 NORTH | TBD | ERIS | Add 3-winding transformer 659336 TANDE___-BE3 345 659337 TANDE___-BE4 230 659338 TND.KU3A-BE9 13 M2 | Current Study |  | (600.00, 637.00) | 12500000 | 50 | 25000000 | 0.10117
GEN-2024-081 | 01 NORTH | 94673 | ERIS | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032 | Contingent |  |  | 0 | 0 | 79492390 | N/A
GEN-2024-081 | 01 NORTH | TBD | ERIS | Rebuild line 652391 WILLISTON27 115 652421 WILISTN7 115 Z1 | Current Study | 0.035484 | (260.00, 260.00) | 17741.9356 | 50 | 35483.8712 | 0.020952
GEN-2024-081 | 01 NORTH | TBD | ERIS | Rebuild line 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1 | Current Study | 1.04 | (772.00, 772.00) | 988000 | 50 | 1976000 | 0.1541
GEN-2024-081 | 01 NORTH | TBD | ERIS | Rebuild line 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z | Current Study | 1 | (580.00, 580.00) | 95000 | 50 | 190000 | 0.15021
GEN-2024-081 | 01 NORTH | TBD | ERIS | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | Current Study | 9 | (1793.00, 1793.00) | 9900000 | 50 | 19800000 | 0.70727
GEN-2024-081 | 01 NORTH | TBD | ERIS | Rebuild line 659336 TANDE___-BE3 345 659427 TN.LS-JD-BE3 345 Z | Current Study | 0 | (1501.00, 1501.00) | 110000 | 50 | 220000 | 0.29273
GEN-2024-081 | 01 NORTH | TBD | ERIS | Rebuild line 659427 TN.LS-JD-BE3 345 779400 G24-081-TAP 345 1 | Current Study | 33.88 | (1793.00, 1793.00) | 37268000 | 50 | 74536000 | 0.29273
GEN-2024-081 | 01 NORTH | 171554 | ERIS | Springbrook - Tande 345 kV Line GEN-2024-081 Interconnection (TOIF) (BEPC) | Interconnection |  |  | 3093490 | 100 | 3093490 | 1
GEN-2024-081 | 01 NORTH | 171555 | ERIS | Springbrook - Tande 345 kV Line GEN-2024-081/082 Interconnection (Shared NU) (BEPC) | Interconnection |  |  | 1546743 | 50 | 3093486 | 1
GEN-2024-082 | 01 NORTH | 92168 | ERIS | 21ITP_Multi - Tande - Finstad - Leland Olds 345 kV.idv : 2021 ITP, PID: 92168, NTC, ISD: 11/30/2026 | Contingent |  |  | 0 | 0 | 346873086 | N/A
GEN-2024-082 | 01 NORTH | 92168 | ERIS | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026 | Contingent |  |  | 0 | 0 | 358995074 | N/A
GEN-2024-082 | 01 NORTH | 92211 | ERIS | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024 | Contingent |  |  | 0 | 0 | 9200000 | N/A
GEN-2024-082 | 01 NORTH | 900426 | ERIS | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030 | Contingent |  |  | 0 | 0 | 2372127948.71 | N/A
GEN-2024-082 | 01 NORTH | TBD | ERIS | Add 0.02 MVAR switched shunt at GEN-2017-214 230 kV | Current Study |  |  | 1912500 | 50 | 3825000 | 0.053439
GEN-2024-082 | 01 NORTH | TBD | ERIS | Add 0.02 MVAR switched shunt at RUSHMORE-RM8 69 kV | Current Study |  |  | 690000 | 50 | 1380000 | 0.038948
GEN-2024-082 | 01 NORTH | TBD | ERIS | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV | Current Study |  |  | 45880.4682 | 3.3247 | 1380000 | 0.043625
GEN-2024-082 | 01 NORTH | TBD | ERIS | Add 2 MVAR switched shunt at GEN-2017-140 345 kV | Current Study |  |  | 193528.1722 | 3.6515 | 5300000 | 0.056072
GEN-2024-082 | 01 NORTH | TBD | ERIS | Add 23 MVAR switched shunt at FINNEY 7 345 kV | Current Study |  |  | 519445.1703 | 9.8009 | 5300000 | 0.043625
GEN-2024-082 | 01 NORTH | TBD | ERIS | Add 3-winding transformer 659336 TANDE___-BE3 345 659337 TANDE___-BE4 230 659338 TND.KU3A-BE9 13 M2 | Current Study |  | (600.00, 637.00) | 12500000 | 50 | 25000000 | 0.10117
GEN-2024-082 | 01 NORTH | 94673 | ERIS | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032 | Contingent |  |  | 0 | 0 | 79492390 | N/A
GEN-2024-082 | 01 NORTH | TBD | ERIS | Rebuild line 652391 WILLISTON27 115 652421 WILISTN7 115 Z1 | Current Study | 0.035484 | (260.00, 260.00) | 17741.9356 | 50 | 35483.8712 | 0.020952
GEN-2024-082 | 01 NORTH | TBD | ERIS | Rebuild line 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1 | Current Study | 1.04 | (772.00, 772.00) | 988000 | 50 | 1976000 | 0.1541
GEN-2024-082 | 01 NORTH | TBD | ERIS | Rebuild line 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z | Current Study | 1 | (580.00, 580.00) | 95000 | 50 | 190000 | 0.15021
GEN-2024-082 | 01 NORTH | TBD | ERIS | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | Current Study | 9 | (1793.00, 1793.00) | 9900000 | 50 | 19800000 | 0.70727
GEN-2024-082 | 01 NORTH | TBD | ERIS | Rebuild line 659336 TANDE___-BE3 345 659427 TN.LS-JD-BE3 345 Z | Current Study | 0 | (1501.00, 1501.00) | 110000 | 50 | 220000 | 0.29273
GEN-2024-082 | 01 NORTH | TBD | ERIS | Rebuild line 659427 TN.LS-JD-BE3 345 779400 G24-081-TAP 345 1 | Current Study | 33.88 | (1793.00, 1793.00) | 37268000 | 50 | 74536000 | 0.29273
GEN-2024-082 | 01 NORTH | 171555 | ERIS | Springbrook - Tande 345 kV Line GEN-2024-081/082 Interconnection (Shared NU) (BEPC) | Interconnection |  |  | 1546743 | 50 | 3093486 | 1
GEN-2024-082 | 01 NORTH | 171556 | ERIS | Springbrook - Tande 345 kV Line GEN-2024-082 Interconnection (TOIF) (BEPC) | Interconnection |  |  | 38027515 | 100 | 38027515 | 1
GEN-2024-088 | 03 CENTRAL | 171564 | ERIS | McCartney 161 kV Substation GEN-2024-088 Interconnection (Non-Shared NU) (CUS) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-088 | 03 CENTRAL | 171564 | ERIS | McCartney 161 kV Substation GEN-2024-088 Interconnection (Non-Shared NU) (CUS) | Interconnection |  |  | 2930000 | 100 | 2930000 | 1
GEN-2024-088 | 03 CENTRAL | 171563 | ERIS | McCartney 161 kV Substation GEN-2024-088 Interconnection (TOIF) (CUS) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-088 | 03 CENTRAL | 171563 | ERIS | McCartney 161 kV Substation GEN-2024-088 Interconnection (TOIF) (CUS) | Interconnection |  |  | 2700000 | 100 | 2700000 | 1
GEN-2024-090 | 03 CENTRAL | 94615 | ERIS | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029 | Contingent |  |  | 0 | 0 | 543515503 | N/A
GEN-2024-090 | 03 CENTRAL | TBD | ERIS | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV | Current Study |  |  | 52760.9705 | 3.8233 | 1380000 | 0.10563
GEN-2024-090 | 03 CENTRAL | TBD | ERIS | Add 16 MVAR switched shunt at HUMBOLT5 161 kV | Current Study |  |  | 97543.194 | 3.0013 | 3250000 | 0.072899
GEN-2024-090 | 03 CENTRAL | TBD | ERIS | Add 21 MVAR switched shunt at S1263 5 161 kV | Current Study |  |  | 97543.194 | 3.0013 | 3250000 | 0.072899
GEN-2024-090 | 03 CENTRAL | TBD | ERIS | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV | Current Study |  |  | 41418.3408 | 3.0013 | 1380000 | 0.072899
GEN-2024-090 | 03 CENTRAL | TBD | ERIS | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2 | Current Study | 0.75 | (2390.00, 2390.00) | 69818.7856 | 0.39279 | 17775000 | 0.021544
GEN-2024-090 | 03 CENTRAL | 94721 | ERIS | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 213682884 | N/A
GEN-2024-090 | 03 CENTRAL | 94929 | ERIS | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 413934522 | N/A
GEN-2024-090 | 03 CENTRAL | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 114437.4253 | 0.98145 | 11660000 | 0.054121
GEN-2024-090 | 03 CENTRAL | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 795531.3507 | 0.84645 | 93984000 | 0.054121
GEN-2024-090 | 03 CENTRAL | TBD | ERIS | Rebuild line 541199 ST JOE 7 345 541400 EASTOWN7 345 1 | Current Study | 8.12 | (1793.00, 1793.00) | 309011.5887 | 1.7298 | 17864000 | 0.03283
GEN-2024-090 | 03 CENTRAL | TBD | ERIS | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | Current Study | 2.29 | (551.00, 551.00) | 968131.3153 | 28.1843 | 3435000 | 0.81151
GEN-2024-090 | 03 CENTRAL | TBD | ERIS | Rebuild line 541204 SMTHVL 5 161 541221 PLTCTY 5 161 1 | Current Study | 7.49 | (364.00, 364.00) | 3210000 | 28.5714 | 11235000 | 0.18849
GEN-2024-090 | 03 CENTRAL | TBD | ERIS | Rebuild line 541214 TWA 5 161 541318 NCONGRS5 161 1 | Current Study | 2.85 | (246.00, 246.00) | 1221428.5714 | 28.5714 | 4275000 | 0.058277
GEN-2024-090 | 03 CENTRAL | TBD | ERIS | Rebuild line 541400 EASTOWN7 345 542982 IATAN 7 345 1 | Current Study | 23.71 | (1793.00, 1793.00) | 954081.2465 | 1.8291 | 52162000 | 0.040476
GEN-2024-090 | 03 CENTRAL | 171915 | ERIS | Smithville 161 kV Substation GEN-2024-090 Interconnection (Non-Shared NU) (WERE) | Interconnection |  |  | 3659394 | 100 | 3659394 | 1
GEN-2024-090 | 03 CENTRAL | 171914 | ERIS | Smithville 161 kV Substation GEN-2024-090 Interconnection (TOIF) (WERE) | Interconnection |  |  | 1061550 | 100 | 1061550 | 1
GEN-2024-099 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 62532.7648 | 4.5314 | 1380000 | 0.10558
GEN-2024-099 | 05 SOUTHWEST | TBD | ERIS | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV | Current Study |  |  | 43483.7847 | 3.151 | 1380000 | 0.10268
GEN-2024-099 | 05 SOUTHWEST | TBD | ERIS | Add 1.6 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 74593.6472 | 5.4053 | 1380000 | 0.13484
GEN-2024-099 | 05 SOUTHWEST | TBD | NRIS | Add 10 MVAR switched shunt at DEAFSMITH 6 230 kV | Current Study |  |  | 899136.2139 | 23.5068 | 3825000 | 0.041781
GEN-2024-099 | 05 SOUTHWEST | TBD | NRIS | Add 11 MVAR switched shunt at WWRDEHV4 138 kV | Current Study |  |  | 118623.4559 | 4.8766 | 2432500 | 0.06092
GEN-2024-099 | 05 SOUTHWEST | TBD | ERIS | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 63828.7159 | 4.6253 | 1380000 | 0.13484
GEN-2024-099 | 05 SOUTHWEST | TBD | ERIS | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV | Current Study |  |  | 63828.7159 | 4.6253 | 1380000 | 0.13484
GEN-2024-099 | 05 SOUTHWEST | TBD | NRIS | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV | Current Study |  |  | 69648.9109 | 3.0282 | 2300000 | 0.10565
GEN-2024-099 | 05 SOUTHWEST | TBD | ERIS | Add 3.6 MVAR switched shunt at HEDLEY 2 69 kV | Current Study |  |  | 93554.2012 | 6.7793 | 1380000 | 0.0041608
GEN-2024-099 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2 | Current Study |  | (339.00, 330.00) | 809717.2178 | 5.7837 | 14000000 | 0.027433
GEN-2024-099 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 531510 HARBNGR3 115 531511 HARBNGR-1 13 531512 HARBNGR7 345 M2 | Current Study |  | (350.00, 385.00) | 2069716.7856 | 12.3197 | 16800000 | 0.0089586
GEN-2024-099 | 05 SOUTHWEST | TBD | ERIS | Add line 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 P2 | Current Study | 66.8 | (1011.00, 1176.00) | 10047608.0414 | 4.6285 | 217080000 | 0.067759
GEN-2024-099 | 05 SOUTHWEST | TBD | ERIS | Apply contingent IDV 01_NewLine_Phantom_Crossroads_Potter_765_26SP.idv | Contingent |  |  | 0 | 0 | 3275253469 | N/A
GEN-2024-099 | 05 SOUTHWEST | TBD | ERIS | Apply contingent IDV 02_765_Phantom_Craw_1_DIS24_TC05ALL-26SP.idv | Contingent |  |  | 0 | 0 | 1366342009.82 | N/A
GEN-2024-099 | 05 SOUTHWEST | TBD | ERIS | Apply contingent IDV 02_765_Phantom_Craw_1_DIS24_TC05ALL-29SP.idv | Contingent |  |  | 0 | 0 | 1366342009.82 | N/A
GEN-2024-099 | 05 SOUTHWEST | 900427 | ERIS | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032 | Contingent |  |  | 0 | 0 | 1790026304.1702 | N/A
GEN-2024-099 | 05 SOUTHWEST | 171572 | ERIS | Newhart 230 kV Substation GEN-2024-099 Interconnection (Non-Shared NU) (SPS) | Interconnection |  |  | 1603584.62 | 100 | 1603584.62 | 1
GEN-2024-099 | 05 SOUTHWEST | 171571 | ERIS | Newhart 230 kV Substation GEN-2024-099 Interconnection (TOIF) (SPS) | Interconnection |  |  | 3214046.86 | 100 | 3214046.86 | 1
GEN-2024-099 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | Current Study | 18.75 | (519.00, 519.00) | 2060441.1345 | 5.7837 | 35625000 | 0.054866
GEN-2024-099 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Current Study | 57.98 | (1793.00, 1793.00) | 5899778.6327 | 4.6252 | 127556000 | 0.13483
GEN-2024-099 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | Current Study | 3.02 | (1793.00, 1793.00) | 337870.4433 | 5.0853 | 6644000 | 0.15632
GEN-2024-099 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 531405 WALKMYR3 115 531510 HARBNGR3 115 1 | Current Study | 1.28 | (598.00, 598.00) | 157692.7075 | 12.3197 | 1280000 | 0.017917
GEN-2024-109 | 05 SOUTHWEST | 94067 | ERIS | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028 | Contingent |  |  | 0 | 0 | 38846321 | N/A
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 74740.0594 | 5.4159 | 1380000 | 0.094524
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV | Current Study |  |  | 49803.3912 | 3.6089 | 1380000 | 0.088089
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Add 1.6 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 44214.1882 | 3.2039 | 1380000 | 0.059867
GEN-2024-109 | 05 SOUTHWEST | TBD | NRIS | Add 10 MVAR switched shunt at DEAFSMITH 6 230 kV | Current Study |  |  | 16617.5893 | 0.43445 | 3825000 | 0.00057841
GEN-2024-109 | 05 SOUTHWEST | TBD | NRIS | Add 11 MVAR switched shunt at WWRDEHV4 138 kV | Current Study |  |  | 157209.1479 | 6.4629 | 2432500 | 0.060476
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 75666.8956 | 5.4831 | 1380000 | 0.11973
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV | Current Study |  |  | 75666.8956 | 5.4831 | 1380000 | 0.11973
GEN-2024-109 | 05 SOUTHWEST | TBD | NRIS | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV | Current Study |  |  | 99675.9492 | 4.3337 | 2300000 | 0.11326
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Add 3.6 MVAR switched shunt at HEDLEY 2 69 kV | Current Study |  |  | 93845.116 | 6.8004 | 1380000 | 0.0031264
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2 | Current Study |  | (339.00, 330.00) | 967379.3084 | 6.9099 | 14000000 | 0.02455
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 531510 HARBNGR3 115 531511 HARBNGR-1 13 531512 HARBNGR7 345 M2 | Current Study |  | (350.00, 385.00) | 2601351.8816 | 15.4842 | 16800000 | 0.0084343
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Add line 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 P2 | Current Study | 66.8 | (1011.00, 1176.00) | 11908855.4706 | 5.4859 | 217080000 | 0.060158
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Apply contingent IDV 01_NewLine_Phantom_Crossroads_Potter_765_26SP.idv | Contingent |  |  | 0 | 0 | 3275253469 | N/A
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Apply contingent IDV 02_765_Phantom_Craw_1_DIS24_TC05ALL-26SP.idv | Contingent |  |  | 0 | 0 | 1366342009.82 | N/A
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Apply contingent IDV 02_765_Phantom_Craw_1_DIS24_TC05ALL-29SP.idv | Contingent |  |  | 0 | 0 | 1366342009.82 | N/A
GEN-2024-109 | 05 SOUTHWEST | 900427 | ERIS | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032 | Contingent |  |  | 0 | 0 | 1790026304.1702 | N/A
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | Current Study | 18.75 | (519.00, 519.00) | 2461634.8472 | 6.9099 | 35625000 | 0.0491
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 511541 DEMPSEYR POI 230 511557 CHISHOLM6 230 1 | Current Study | 11.15 | (519.00, 519.00) | 4786506.445 | 22.5938 | 21185000 | 0.045476
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Current Study | 57.98 | (1793.00, 1793.00) | 6993922.2644 | 5.483 | 127556000 | 0.11973
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | Current Study | 3.02 | (1793.00, 1793.00) | 291950.6943 | 4.3942 | 6644000 | 0.10118
GEN-2024-109 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 531405 WALKMYR3 115 531510 HARBNGR3 115 1 | Current Study | 1.28 | (598.00, 598.00) | 198198.2386 | 15.4842 | 1280000 | 0.016869
GEN-2024-109 | 05 SOUTHWEST | 171576 | ERIS | Tolk - Crossroads 345 kV line GEN-2024-109 Interconnection (Non-Shared NU) (SPS) | Interconnection |  |  | 27903630.08 | 100 | 27903630.08 | 1
GEN-2024-109 | 05 SOUTHWEST | 171575 | ERIS | Tolk - Crossroads 345 kV line GEN-2024-109 Interconnection (TOIF) (SPS) | Interconnection |  |  | 4671893.78 | 100 | 4671893.78 | 1
GEN-2024-113 | 04 SOUTHEAST | 94615 | ERIS | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029 | Contingent |  |  | 0 | 0 | 543515503 | N/A
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at MOUND 4 138 kV | Current Study |  |  | 54624.3488 | 2.2456 | 2432500 | 0.032318
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 100531.3777 | 7.2849 | 1380000 | 0.095032
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 48534.9992 | 1.9953 | 2432500 | 0.042714
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 0.09 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 101962.4402 | 3.1373 | 3250000 | 0.038837
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 132276.1444 | 2.4958 | 5300000 | 0.044969
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV | Current Study |  |  | 100531.3777 | 7.2849 | 1380000 | 0.095032
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 0.2 MVAR switched shunt at GROVE 5 161 kV | Current Study |  |  | 95186.9582 | 2.9288 | 3250000 | 0.056201
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 0.25 MVAR switched shunt at LABETTS2 69 kV | Current Study |  |  | 43837.6491 | 3.1766 | 1380000 | 0.056201
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 11 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 231379.3809 | 7.1194 | 3250000 | 0.095032
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 15 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 101962.4402 | 3.1373 | 3250000 | 0.038837
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 288521.7867 | 2.4043 | 12000000 | 0.044969
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR switched shunt at NEOSHO 4 138 kV | Current Study |  |  | 82305.8166 | 3.3836 | 2432500 | 0.095032
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at CPK446 5 161 kV | Current Study |  |  | 175630.886 | 5.404 | 3250000 | 0.095032
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV | Current Study |  |  | 102098.0679 | 3.1415 | 3250000 | 0.038837
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR switched shunt at WICHITA7 345 kV | Current Study |  |  | 122885.2462 | 2.3186 | 5300000 | 0.044969
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 177 MVAR switched shunt at SWISVAL7 345 kV | Current Study |  |  | 105141.0607 | 1.9838 | 5300000 | 0.022718
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 20 MVAR switched shunt at LIBERTY4 138 kV | Current Study |  |  | 54440.9584 | 2.2381 | 2432500 | 0.042714
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 102098.0679 | 3.1415 | 3250000 | 0.038837
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 24 MVAR switched shunt at GROVE 4 138 kV | Current Study |  |  | 45466.1626 | 1.8691 | 2432500 | 0.038837
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 280 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 166349.8998 | 1.3862 | 12000000 | 0.028263
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 295 MVAR switched shunt at G18-128-TAP 345 kV | Current Study |  |  | 100756.8417 | 1.9011 | 5300000 | 0.032368
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 3 MVAR switched shunt at NEOSHOS2 69 kV | Current Study |  |  | 33416.7256 | 2.4215 | 1380000 | 0.032368
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 515301 FTSMTHW5 161 515302 FTSMITH7 345 515728 FTSMTH51 13 M2 | Current Study |  | (493.00, 493.00) | 2282332.1297 | 11.243 | 20300000 | 0.034066
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 515302 FTSMITH7 345 515305 FTSMITH8 500 515726 FTSMTH11 13 M2 | Current Study |  | (660.00, 693.00) | 14322069.394 | 30.4725 | 47000000 | 0.063895
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at INDEPCO5 161 kV | Current Study |  |  | 231379.3809 | 7.1194 | 3250000 | 0.095032
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 81112.7301 | 2.4958 | 3250000 | 0.044969
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 45 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 243678.658 | 2.0307 | 12000000 | 0.032368
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 45 MVAR switched shunt at NEVADA 5 161 kV | Current Study |  |  | 57687.0327 | 1.775 | 3250000 | 0.022718
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 56 MVAR switched shunt at WHARV4 138 kV | Current Study |  |  | 54624.3488 | 2.2456 | 2432500 | 0.032318
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV | Current Study |  |  | 46596.0251 | 3.3765 | 1380000 | 0.038837
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Add line 515012 RVRVALY7 345 780360 G24-113-TAP 345 P2 | Current Study | 23.28 | (1195.00, 1195.00) | 21712206.5723 | 26.4242 | 82168000 | 0.21321
GEN-2024-113 | 04 SOUTHEAST | 94721 | ERIS | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 213682884 | N/A
GEN-2024-113 | 04 SOUTHEAST | 94929 | ERIS | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 413934522 | N/A
GEN-2024-113 | 04 SOUTHEAST | 171578 | ERIS | Muskogee - Ft. Smith 345 kV Line GEN-2024-113 Interconnection (Non-Shared NU) (OGE) | Interconnection |  |  | 18000000 | 100 | 18000000 | 1
GEN-2024-113 | 04 SOUTHEAST | 171577 | ERIS | Muskogee - Ft. Smith 345 kV Line GEN-2024-113 Interconnection (TOIF) (OGE) | Interconnection |  |  | 3000000 | 100 | 3000000 | 1
GEN-2024-113 | 04 SOUTHEAST | TBD | NRIS | Rebuild 3-winding transformer 516092 OKTAHA 5 161 516093 OKTAHA 2 69 516095 OKTAHA71 13 7 | Current Study |  | (186.00, 186.00) | 681688.7066 | 11.2212 | 6075000 | 0.0057925
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | Current Study | 21.38 | (1793.00, 1793.00) | 5185145.8457 | 11.0238 | 47036000 | 0.20198
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 1158791.4375 | 3.4494 | 33594000 | 0.073985
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 153422.5773 | 1.3158 | 11660000 | 0.042682
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Current Study | 14.6 | (1793.00, 1793.00) | 1107947.2814 | 3.4494 | 32120000 | 0.073985
GEN-2024-113 | 04 SOUTHEAST | TBD | NRIS | Rebuild line 515227 5TRIBES2 69 516093 OKTAHA 2 69 1 | Current Study | 13.49 | (140.00, 140.00) | 2603250.2985 | 22.7031 | 11466500 | 0.0045291
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | Current Study | 15.48 | (1793.00, 1793.00) | 1591070.4863 | 4.6719 | 34056000 | 0.029288
GEN-2024-113 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 1066543.3081 | 1.1348 | 93984000 | 0.042682
GEN-2024-117 | 04 SOUTHEAST | 94615 | ERIS | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029 | Contingent |  |  | 0 | 0 | 543515503 | N/A
GEN-2024-117 | 04 SOUTHEAST | 94811 | ERIS | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030 | Contingent |  |  | 0 | 0 | 1097029189 | N/A
GEN-2024-117 | 04 SOUTHEAST | 94911 | ERIS | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030 | Contingent |  |  | 0 | 0 | 143524375 | N/A
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at JAY 4 138 kV | Current Study |  |  | 104774.6382 | 4.3073 | 2432500 | 0.037029
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at MOUND 4 138 kV | Current Study |  |  | 60902.7716 | 2.5037 | 2432500 | 0.040837
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV | Current Study |  |  | 213374.8139 | 4.0259 | 5300000 | 0.040464
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 148207.7663 | 6.0928 | 2432500 | 0.14782
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 0.04 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 400651.8226 | 12.3277 | 3250000 | 0.053379
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 0.09 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 191694.3367 | 5.8983 | 3250000 | 0.082751
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 0.11 MVAR switched shunt at CHAMSPR7 345 kV | Current Study |  |  | 228285.9537 | 4.3073 | 5300000 | 0.037029
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 240904.5937 | 4.5454 | 5300000 | 0.092818
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 0.13 MVAR switched shunt at PECULR 7 345 kV | Current Study |  |  | 654351.7351 | 12.3463 | 5300000 | 0.040464
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 0.2 MVAR switched shunt at GROVE 5 161 kV | Current Study |  |  | 79770.8453 | 2.4545 | 3250000 | 0.053379
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 0.25 MVAR switched shunt at LABETTS2 69 kV | Current Study |  |  | 9519.0156 | 0.68978 | 1380000 | 0.013831
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at TONTITN7 345 kV | Current Study |  |  | 222547.427 | 4.199 | 5300000 | 0.037029
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 15 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 191694.3367 | 5.8983 | 3250000 | 0.082751
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 525463.0312 | 4.3789 | 12000000 | 0.092818
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR switched shunt at NEOSHO 4 138 kV | Current Study |  |  | 93734.8499 | 3.8534 | 2432500 | 0.12266
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at CPK446 5 161 kV | Current Study |  |  | 87044.3927 | 2.6783 | 3250000 | 0.053379
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV | Current Study |  |  | 191949.3235 | 5.9061 | 3250000 | 0.082751
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR switched shunt at WICHITA7 345 kV | Current Study |  |  | 223801.6571 | 4.2227 | 5300000 | 0.092818
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 177 MVAR switched shunt at SWISVAL7 345 kV | Current Study |  |  | 213634.101 | 4.0308 | 5300000 | 0.052315
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 20 MVAR switched shunt at LIBERTY4 138 kV | Current Study |  |  | 166242.3606 | 6.8342 | 2432500 | 0.14782
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 191949.3235 | 5.9061 | 3250000 | 0.082751
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR switched shunt at STILWEL7 345 kV | Current Study |  |  | 281275.3028 | 5.3071 | 5300000 | 0.052315
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 24 MVAR switched shunt at GROVE 4 138 kV | Current Study |  |  | 85478.5926 | 3.514 | 2432500 | 0.082751
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at G21-096-TAP 345 kV | Current Study |  |  | 252531.5353 | 4.7647 | 5300000 | 0.038544
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 280 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 224367.4939 | 1.8697 | 12000000 | 0.043203
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at G23-220-TAP 345 kV | Current Study |  |  | 239103.2301 | 4.5114 | 5300000 | 0.040464
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 316 MVAR switched shunt at W.GRDNR7 345 kV | Current Study |  |  | 281275.3028 | 5.3071 | 5300000 | 0.052315
GEN-2024-117 | 04 SOUTHEAST | TBD | NRIS | Add 3-winding transformer 532937 NEOSHO 5 161 532959 NEOSH5 1 13 533020 NEOSHOS4 138 M2 | Current Study |  | (150.00, 165.00) | 9880775.6794 | 79.6837 | 12400000 | 0.041852
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 147724.515 | 4.5454 | 3250000 | 0.092818
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 45 MVAR switched shunt at NEVADA 5 161 kV | Current Study |  |  | 117213.1733 | 3.6066 | 3250000 | 0.052315
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 56 MVAR switched shunt at WHARV4 138 kV | Current Study |  |  | 60902.7716 | 2.5037 | 2432500 | 0.040837
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV | Current Study |  |  | 56508.1674 | 4.0948 | 1380000 | 0.053379
GEN-2024-117 | 04 SOUTHEAST | 94721 | ERIS | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 213682884 | N/A
GEN-2024-117 | 04 SOUTHEAST | 94929 | ERIS | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 413934522 | N/A
GEN-2024-117 | 04 SOUTHEAST | 171582 | ERIS | Coffeyville Tap - North Bartlesville 138kV Line GEN-2024-117 Interconnection (Non-Shared NU) (AEP) | Interconnection |  |  | 17175000 | 100 | 17175000 | 1
GEN-2024-117 | 04 SOUTHEAST | 171581 | ERIS | Coffeyville Tap - North Bartlesville 138kV Line GEN-2024-117 Interconnection (TOIF) (AEP) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | DIS2301-1_G03_ERIS_TurnOffReactors_Carpenter_Finney.idv : Switch out Carpenter 25 MVAR line reactor on the Carpenter to Hitchland 345 kV line | Contingent |  |  | 0 | 0 | 1450000 | 0.0044691
GEN-2024-117 | 04 SOUTHEAST | 900427 | ERIS | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032 | Contingent |  |  | 0 | 0 | 1790026304.1702 | N/A
GEN-2024-117 | 04 SOUTHEAST | TBD | NRIS | Rebuild line 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | Current Study | 31.46 | (1793.00, 1793.00) | 2107125.4844 | 3.0445 | 69212000 | 0.088257
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 154311.677 | 1.3234 | 11660000 | 0.048653
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510422 COFFEYT4 138 533002 DEARING4 138 1 | Current Study | 5.02 | (717.00, 717.00) | 6024000 | 100 | 6024000 | 0.30529
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | Current Study | 15.48 | (1793.00, 1793.00) | 2024793.0073 | 5.9455 | 34056000 | 0.042242
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 1072724.0369 | 1.1414 | 93984000 | 0.048653
GEN-2024-117 | 04 SOUTHEAST | TBD | NRIS | Rebuild line 532937 NEOSHO 5 161 764310 G20-079-TAP 161 1 | Current Study | 20.67 | (551.00, 551.00) | 1685028.1905 | 5.4347 | 31005000 | 0.032283
GEN-2024-117 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 541198 PECULR 7 345 541200 PHILL 7 345 1 | Current Study | 11.9 | (1793.00, 1793.00) | 12603463.6767 | 48.1416 | 26180000 | 0.032658
GEN-2024-118 | 04 SOUTHEAST | 94615 | ERIS | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029 | Contingent |  |  | 0 | 0 | 543515503 | N/A
GEN-2024-118 | 04 SOUTHEAST | 94811 | ERIS | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030 | Contingent |  |  | 0 | 0 | 1097029189 | N/A
GEN-2024-118 | 04 SOUTHEAST | 94911 | ERIS | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030 | Contingent |  |  | 0 | 0 | 143524375 | N/A
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at JAY 4 138 kV | Current Study |  |  | 216516.7614 | 8.901 | 2432500 | 0.057679
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at MOUND 4 138 kV | Current Study |  |  | 80023.6132 | 3.2898 | 2432500 | 0.040446
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV | Current Study |  |  | 213123.6777 | 4.0212 | 5300000 | 0.030464
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 85136.2653 | 3.4999 | 2432500 | 0.064007
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 0.04 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 268627.5806 | 8.2655 | 3250000 | 0.026977
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 0.09 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 232545.7828 | 7.1553 | 3250000 | 0.075668
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 0.11 MVAR switched shunt at CHAMSPR7 345 kV | Current Study |  |  | 471752.8614 | 8.901 | 5300000 | 0.057679
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 222639.3433 | 4.2007 | 5300000 | 0.064659
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 0.13 MVAR switched shunt at PECULR 7 345 kV | Current Study |  |  | 649913.7507 | 12.2625 | 5300000 | 0.030293
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 0.2 MVAR switched shunt at GROVE 5 161 kV | Current Study |  |  | 150020.3207 | 4.616 | 3250000 | 0.075668
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 0.25 MVAR switched shunt at LABETTS2 69 kV | Current Study |  |  | 69090.7484 | 5.0066 | 1380000 | 0.075668
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at TONTITN7 345 kV | Current Study |  |  | 459894.1976 | 8.6772 | 5300000 | 0.057679
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 15 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 232545.7828 | 7.1553 | 3250000 | 0.075668
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 485622.7207 | 4.0469 | 12000000 | 0.064659
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR switched shunt at NEOSHO 4 138 kV | Current Study |  |  | 76714.3008 | 3.1537 | 2432500 | 0.075668
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at CPK446 5 161 kV | Current Study |  |  | 58361.2087 | 1.7957 | 3250000 | 0.026977
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV | Current Study |  |  | 232855.1092 | 7.1648 | 3250000 | 0.075668
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR switched shunt at WICHITA7 345 kV | Current Study |  |  | 206833.1417 | 3.9025 | 5300000 | 0.064659
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 177 MVAR switched shunt at SWISVAL7 345 kV | Current Study |  |  | 208051.5058 | 3.9255 | 5300000 | 0.038403
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 20 MVAR switched shunt at LIBERTY4 138 kV | Current Study |  |  | 95496.0327 | 3.9258 | 2432500 | 0.064007
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 232855.1092 | 7.1648 | 3250000 | 0.075668
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR switched shunt at STILWEL7 345 kV | Current Study |  |  | 273925.1366 | 5.1684 | 5300000 | 0.038403
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 24 MVAR switched shunt at GROVE 4 138 kV | Current Study |  |  | 103694.6974 | 4.2629 | 2432500 | 0.075668
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at G21-096-TAP 345 kV | Current Study |  |  | 278981.3822 | 5.2638 | 5300000 | 0.032096
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 280 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 181021.7322 | 1.5085 | 12000000 | 0.026274
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 295 MVAR switched shunt at G18-128-TAP 345 kV | Current Study |  |  | 152267.9608 | 2.873 | 5300000 | 0.041788
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 3 MVAR switched shunt at NEOSHOS2 69 kV | Current Study |  |  | 50500.7558 | 3.6595 | 1380000 | 0.041788
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at G23-220-TAP 345 kV | Current Study |  |  | 237481.5696 | 4.4808 | 5300000 | 0.030293
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 316 MVAR switched shunt at W.GRDNR7 345 kV | Current Study |  |  | 273925.1366 | 5.1684 | 5300000 | 0.038403
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 512623 CATSAGD4 138 512638 CATSAGR5 161 512833 CATTER1 1 13 M2 | Current Study |  | (150.00, 188.00) | 8097438.0156 | 65.3019 | 12400000 | 0.043479
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 512636 CATSAGR4 138 512638 CATSAGR5 161 512834 CATTER2 1 13 M2 | Current Study |  | (150.00, 188.00) | 8097438.0156 | 65.3019 | 12400000 | 0.044169
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 136524.1256 | 4.2007 | 3250000 | 0.064659
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 45 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 368257.398 | 3.0688 | 12000000 | 0.041788
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 45 MVAR switched shunt at NEVADA 5 161 kV | Current Study |  |  | 114150.2086 | 3.5123 | 3250000 | 0.038403
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 56 MVAR switched shunt at WHARV4 138 kV | Current Study |  |  | 80023.6132 | 3.2898 | 2432500 | 0.040446
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 57 MVAR switched shunt at GUAVA 4 138 kV | Current Study |  |  | 2432500 | 100 | 2432500 | 0.03469
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV | Current Study |  |  | 106271.5753 | 7.7008 | 1380000 | 0.075668
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Add line 515012 RVRVALY7 345 780360 G24-113-TAP 345 P2 | Current Study | 23.28 | (1195.00, 1195.00) | 2176286.8512 | 2.6486 | 82168000 | 0.018256
GEN-2024-118 | 04 SOUTHEAST | 94721 | ERIS | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 213682884 | N/A
GEN-2024-118 | 04 SOUTHEAST | 94929 | ERIS | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 413934522 | N/A
GEN-2024-118 | 04 SOUTHEAST | 900427 | ERIS | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032 | Contingent |  |  | 0 | 0 | 1790026304.1702 | N/A
GEN-2024-118 | 04 SOUTHEAST | 171584 | ERIS | Lynn Lane West Tap 138 kV Substation GEN-2024-118 Interconnection (Non-Shared NU) (AEP) | Interconnection |  |  | 2800000 | 100 | 2800000 | 1
GEN-2024-118 | 04 SOUTHEAST | 171583 | ERIS | Lynn Lane West Tap 138 kV Substation GEN-2024-118 Interconnection (TOIF) (AEP) | Interconnection |  |  | 3325000 | 100 | 3325000 | 1
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 509770 LLAN WT4 138 509803 DAWSONT4 138 1 | Current Study | 4.99 | (265.00, 265.00) | 5988000 | 100 | 5988000 | 0.14898
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 509770 LLAN WT4 138 509804 E 11TH ST 4 138 1 | Current Study | 0.48 | (265.00, 265.00) | 576000 | 100 | 576000 | 0.14898
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1 | Current Study | 1.8 | (472.00, 472.00) | 2160000 | 100 | 2160000 | 0.60379
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | Current Study | 0 | (382.00, 382.00) | 78362.3034 | 65.3019 | 120000 | 0.13258
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 509790 CATOOSA4 138 512636 CATSAGR4 138 Z1 | Current Study | 0 | (307.00, 307.00) | 78362.3034 | 65.3019 | 120000 | 0.088339
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 509792 DAWSON-4 138 509803 DAWSONT4 138 1 | Current Study | 2.41 | (265.00, 265.00) | 2892000 | 100 | 2892000 | 0.14898
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 1924868.8607 | 5.7298 | 33594000 | 0.10499
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 269122.022 | 2.3081 | 11660000 | 0.063958
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Current Study | 14.6 | (1793.00, 1793.00) | 1840411.6153 | 5.7298 | 32120000 | 0.10499
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | Current Study | 15.48 | (1793.00, 1793.00) | 2694711.2108 | 7.9126 | 34056000 | 0.042375
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 1870847.803 | 1.9906 | 93984000 | 0.063958
GEN-2024-118 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Current Study | 25.29 | (2390.00, 2390.00) | 1900243.9261 | 3.4154 | 55638000 | 0.041967
GEN-2024-120 | 04 SOUTHEAST | 94615 | ERIS | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029 | Contingent |  |  | 0 | 0 | 543515503 | N/A
GEN-2024-120 | 04 SOUTHEAST | 94811 | ERIS | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030 | Contingent |  |  | 0 | 0 | 1097029189 | N/A
GEN-2024-120 | 04 SOUTHEAST | 94911 | ERIS | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030 | Contingent |  |  | 0 | 0 | 143524375 | N/A
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 395521.2446 | 7.4627 | 5300000 | 0.032483
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at MOUND 4 138 kV | Current Study |  |  | 91692.5246 | 3.7695 | 2432500 | 0.046344
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV | Current Study |  |  | 265659.607 | 5.0124 | 5300000 | 0.037974
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 55765.0078 | 2.2925 | 2432500 | 0.041925
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 0.09 MVAR switched shunt at SWISVAL6 230 kV | Current Study |  |  | 337474.0024 | 8.8228 | 3825000 | 0.032483
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 13881.0832 | 1.0059 | 1380000 | 0.035331
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 141047.4601 | 2.6613 | 5300000 | 0.040963
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 307653.8509 | 2.5638 | 12000000 | 0.040963
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR switched shunt at NEOSHO 4 138 kV | Current Study |  |  | 57775.5406 | 2.3752 | 2432500 | 0.056988
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR switched shunt at WICHITA7 345 kV | Current Study |  |  | 159585.8946 | 3.0111 | 5300000 | 0.049889
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 177 MVAR switched shunt at SWISVAL7 345 kV | Current Study |  |  | 160128.4691 | 3.0213 | 5300000 | 0.029557
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 20 MVAR switched shunt at LIBERTY4 138 kV | Current Study |  |  | 62550.7473 | 2.5715 | 2432500 | 0.041925
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR switched shunt at STILWEL7 345 kV | Current Study |  |  | 210828.6244 | 3.9779 | 5300000 | 0.029557
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at G21-096-TAP 345 kV | Current Study |  |  | 293029.4055 | 5.5289 | 5300000 | 0.033712
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 280 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 465699.7701 | 3.8808 | 12000000 | 0.067593
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 295 MVAR switched shunt at G18-128-TAP 345 kV | Current Study |  |  | 207653.8523 | 3.918 | 5300000 | 0.056988
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 3 MVAR switched shunt at NEOSHOS2 69 kV | Current Study |  |  | 68869.882 | 4.9906 | 1380000 | 0.056988
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at G23-220-TAP 345 kV | Current Study |  |  | 254645.9131 | 4.8046 | 5300000 | 0.032483
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 316 MVAR switched shunt at W.GRDNR7 345 kV | Current Study |  |  | 210828.6244 | 3.9779 | 5300000 | 0.029557
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 86491.3671 | 2.6613 | 3250000 | 0.040963
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 45 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 502207.2072 | 4.1851 | 12000000 | 0.056988
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 45 MVAR switched shunt at NEVADA 5 161 kV | Current Study |  |  | 87856.6011 | 2.7033 | 3250000 | 0.029557
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add 56 MVAR switched shunt at WHARV4 138 kV | Current Study |  |  | 91692.5246 | 3.7695 | 2432500 | 0.046344
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Add line 515012 RVRVALY7 345 780360 G24-113-TAP 345 P2 | Current Study | 23.28 | (1195.00, 1195.00) | 2102105.7248 | 2.5583 | 82168000 | 0.017634
GEN-2024-120 | 04 SOUTHEAST | 94721 | ERIS | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 213682884 | N/A
GEN-2024-120 | 04 SOUTHEAST | 94929 | ERIS | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 413934522 | N/A
GEN-2024-120 | 04 SOUTHEAST | 171588 | ERIS | JNS KAMO 138 kV Substation GEN-2024-120 Interconnection (Non-Shared NU) (OGE) | Interconnection |  |  | 1500000 | 100 | 1500000 | 1
GEN-2024-120 | 04 SOUTHEAST | 171587 | ERIS | JNS KAMO 138 kV Substation GEN-2024-120 Interconnection (TOIF) (OGE) | Interconnection |  |  | 2000000 | 100 | 2000000 | 1
GEN-2024-120 | 04 SOUTHEAST | 900427 | ERIS | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032 | Contingent |  |  | 0 | 0 | 1790026304.1702 | N/A
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 945758.1288 | 2.8153 | 33594000 | 0.051584
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 176199.4435 | 1.5111 | 11660000 | 0.041875
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Current Study | 14.6 | (1793.00, 1793.00) | 904261.2103 | 2.8153 | 32120000 | 0.051584
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514715 WOODRNG7 345 515875 REDNGTN7 345 1 | Current Study | 19.2 | (1793.00, 1793.00) | 2440700.1638 | 5.7782 | 42240000 | 0.080363
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 2960467.8993 | 6.4479 | 45914000 | 0.067859
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 1224880.5925 | 1.3033 | 93984000 | 0.041875
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Current Study | 25.29 | (2390.00, 2390.00) | 2588750.0017 | 4.6528 | 55638000 | 0.057173
GEN-2024-120 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 1615703.372 | 6.4479 | 25058000 | 0.067859
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 77763.6853 | 5.635 | 1380000 | 0.078104
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at PHILL 7 345 kV | Current Study |  |  | 447192.6715 | 8.4376 | 5300000 | 0.034353
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV | Current Study |  |  | 77763.6853 | 5.635 | 1380000 | 0.078104
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add 0.2 MVAR switched shunt at GROVE 5 161 kV | Current Study |  |  | 95837.2269 | 2.9488 | 3250000 | 0.060122
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add 0.25 MVAR switched shunt at LABETTS2 69 kV | Current Study |  |  | 44137.1256 | 3.1983 | 1380000 | 0.060122
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add 11 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 178978.084 | 5.507 | 3250000 | 0.078104
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR switched shunt at NEOSHO 4 138 kV | Current Study |  |  | 63665.7307 | 2.6173 | 2432500 | 0.078104
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at CPK446 5 161 kV | Current Study |  |  | 135855.1456 | 4.1802 | 3250000 | 0.078104
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add 24 MVAR switched shunt at GROVE 4 138 kV | Current Study |  |  | 86056.9492 | 3.5378 | 2432500 | 0.078104
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV | Current Study |  |  | 46467.3918 | 3.3672 | 1380000 | 0.053525
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at INDEPCO5 161 kV | Current Study |  |  | 178978.084 | 5.507 | 3250000 | 0.078104
GEN-2024-122 | 04 SOUTHEAST | 171590 | ERIS | Lieberman - IPC Jefferson 138 kV Line GEN-2024-122 Interconnection (Non-Shared NU) (AEP) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-122 | 04 SOUTHEAST | 171589 | ERIS | Lieberman - IPC Jefferson 138 kV Line GEN-2024-122 Interconnection (TOIF) (AEP) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-122 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508806 LIEBERM4 138 780630 G24-122-TAP 138 1 | Current Study | 7.6 | (265.00, 265.00) | 8934242.3651 | 97.9632 | 9120000 | 0.70294
GEN-2024-125 | 03 CENTRAL | 94615 | ERIS | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029 | Contingent |  |  | 0 | 0 | 543515503 | N/A
GEN-2024-125 | 03 CENTRAL | TBD | NRIS | Add 3-winding transformer 532793 NEOSHO 7 345 532825 N345 2 1 13 532939 N345 4 5 161 M2 | Current Study |  | (500.00, 550.00) | 3643640.4506 | 17.949 | 20300000 | 0.026476
GEN-2024-125 | 03 CENTRAL | 94721 | ERIS | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 213682884 | N/A
GEN-2024-125 | 03 CENTRAL | 94929 | ERIS | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 413934522 | N/A
GEN-2024-125 | 03 CENTRAL | 171919 | ERIS | Neosho Ridge - Caney River 345 kV Line GEN-2024-125 Interconnection (Non-Shared NU) (WERE) | Interconnection |  |  | 31994301 | 100 | 31994301 | 1
GEN-2024-125 | 03 CENTRAL | 171918 | ERIS | Neosho Ridge - Caney River 345 kV Line GEN-2024-125 Interconnection (TOIF) (WERE) | Interconnection |  |  | 1958092 | 100 | 1958092 | 1
GEN-2024-125 | 03 CENTRAL | TBD | NRIS | Rebuild line 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | Current Study | 31.46 | (1793.00, 1793.00) | 9108367.2016 | 13.1601 | 69212000 | 0.14306
GEN-2024-125 | 03 CENTRAL | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 1007699.4579 | 8.6424 | 11660000 | 0.11914
GEN-2024-125 | 03 CENTRAL | TBD | NRIS | Rebuild line 532777 NRSS7 345 532793 NEOSHO 7 345 1 | Current Study | 18.17 | (1793.00, 1793.00) | 9555997.204 | 23.9055 | 39974000 | 0.47134
GEN-2024-125 | 03 CENTRAL | TBD | NRIS | Rebuild line 532777 NRSS7 345 780840 G24-129-TAP 345 1 | Current Study | 13.85 | (1793.00, 1793.00) | 7314109.3459 | 24.0043 | 30470000 | 0.48044
GEN-2024-125 | 03 CENTRAL | TBD | NRIS | Rebuild line 532780 CANEYRV7 345 780720 G24-125-TAP 345 1 | Current Study | 14.44 | (1793.00, 1793.00) | 12960412.9002 | 40.7971 | 31768000 | 0.51956
GEN-2024-125 | 03 CENTRAL | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 7005195.2749 | 7.4536 | 93984000 | 0.11914
GEN-2024-125 | 03 CENTRAL | TBD | NRIS | Rebuild line 532937 NEOSHO 5 161 532939 N345 4 5 161 1 | Current Study | 0.3 | (837.00, 837.00) | 80770.3548 | 17.949 | 450000 | 0.052953
GEN-2024-125 | 03 CENTRAL | TBD | NRIS | Rebuild line 532937 NEOSHO 5 161 764310 G20-079-TAP 161 1 | Current Study | 20.67 | (551.00, 551.00) | 5581537.0928 | 18.0021 | 31005000 | 0.040101
GEN-2024-128 | 04 SOUTHEAST | 900426 | ERIS | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030 | Contingent |  |  | 0 | 0 | 2372127948.71 | N/A
GEN-2024-128 | 04 SOUTHEAST | TBD | ERIS | Add 2 MVAR switched shunt at GEN-2017-140 345 kV | Current Study |  |  | 150240.6223 | 2.8347 | 5300000 | 0.047
GEN-2024-128 | 04 SOUTHEAST | TBD | ERIS | Add 23 MVAR switched shunt at FINNEY 7 345 kV | Current Study |  |  | 448316.1444 | 8.4588 | 5300000 | 0.040653
GEN-2024-128 | 04 SOUTHEAST | TBD | NRIS | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV | Current Study |  |  | 385036.3782 | 16.7407 | 2300000 | 0.25395
GEN-2024-128 | 04 SOUTHEAST | TBD | NRIS | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2 | Current Study |  | (484.00, 515.00) | 6276108.0034 | 34.6746 | 18100000 | 0.019785
GEN-2024-128 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 515800 GRACMNT7 345 515801 GRCMNT11 13 515802 GRACMNT4 138 M2 | Current Study |  | (478.00, 478.00) | 18100000 | 100 | 18100000 | 0.072861
GEN-2024-128 | 04 SOUTHEAST | 171596 | ERIS | Gracemont - Lawton 345 kV Line GEN-2024-128 Interconnection (Non-Shared NU) (OGE) | Interconnection |  |  | 18000000 | 100 | 18000000 | 1
GEN-2024-128 | 04 SOUTHEAST | 171595 | ERIS | Gracemont - Lawton 345 kV Line GEN-2024-128 Interconnection (TOIF) (OGE) | Interconnection |  |  | 3000000 | 100 | 3000000 | 1
GEN-2024-128 | 04 SOUTHEAST | 900298 | NRIS | Line - Duncan - Duncan Tap - Duncan Eastside - Rush Springs Tap - Marlow 138 kV Rebuild.idv : 2025 ITP, PID: 900298, NTC, ISD: Unknown | Contingent |  |  | 0 | 0 | 212560000 | N/A
GEN-2024-128 | 04 SOUTHEAST | TBD | NRIS | Rebuild line 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | Current Study | 1.6 | (211.00, 211.00) | 1920000 | 100 | 1920000 | 0.0072371
GEN-2024-128 | 04 SOUTHEAST | TBD | NRIS | Rebuild line 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | Current Study | 3.9 | (265.00, 265.00) | 2710819.0588 | 57.9235 | 4680000 | 0.01035
GEN-2024-128 | 04 SOUTHEAST | TBD | NRIS | Rebuild line 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | Current Study | 0.93 | (211.00, 211.00) | 706216.7752 | 63.2811 | 1116000 | 0.016911
GEN-2024-128 | 04 SOUTHEAST | TBD | NRIS | Rebuild line 511468 L.E.S.-7 345 764550 G20-087-TAP 345 1 | Current Study | 6.89 | (1793.00, 1793.00) | 15158000 | 100 | 15158000 | 0.27311
GEN-2024-128 | 04 SOUTHEAST | TBD | NRIS | Rebuild line 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | Current Study | 17.69 | (265.00, 265.00) | 12295997.2178 | 57.9235 | 21228000 | 0.01035
GEN-2024-128 | 04 SOUTHEAST | TBD | NRIS | Rebuild line 515802 GRACMNT4 138 520814 ANADARK4 138 1 | Current Study | 5.09 | (265.00, 265.00) | 5070371.5612 | 83.012 | 6108000 | 0.041719
GEN-2024-129 | 03 CENTRAL | TBD | ERIS | Add 23 MVAR switched shunt at FINNEY 7 345 kV | Current Study |  |  | 455163.4988 | 8.588 | 5300000 | 0.031295
GEN-2024-129 | 03 CENTRAL | TBD | ERIS | Add 3-winding transformer 532793 NEOSHO 7 345 532824 N345 1 1 13 533023 N345 3 4 138 M2 | Current Study |  | (400.00, 400.00) | 18100000 | 100 | 18100000 | 0.035645
GEN-2024-129 | 03 CENTRAL | TBD | NRIS | Add 3-winding transformer 532793 NEOSHO 7 345 532825 N345 2 1 13 532939 N345 4 5 161 M2 | Current Study |  | (500.00, 550.00) | 11659751.7337 | 57.4372 | 20300000 | 0.037242
GEN-2024-129 | 03 CENTRAL | TBD | NRIS | Add 3-winding transformer 532937 NEOSHO 5 161 532959 NEOSH5 1 13 533020 NEOSHOS4 138 M2 | Current Study |  | (150.00, 165.00) | 2519224.3206 | 20.3163 | 12400000 | 0.0017589
GEN-2024-129 | 03 CENTRAL | 171921 | ERIS | Caney River - Neosho 345 kV Line GEN-2024-129 Interconnection (Non-Shared NU) (WERE) | Interconnection |  |  | 31994301 | 100 | 31994301 | 1
GEN-2024-129 | 03 CENTRAL | 171920 | ERIS | Caney River - Neosho 345 kV Line GEN-2024-129 Interconnection (TOIF) (WERE) | Interconnection |  |  | 1958092 | 100 | 1958092 | 1
GEN-2024-129 | 03 CENTRAL | TBD | NRIS | Rebuild line 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | Current Study | 31.46 | (1793.00, 1793.00) | 29418093.2596 | 42.5043 | 69212000 | 0.20311
GEN-2024-129 | 03 CENTRAL | TBD | NRIS | Rebuild line 532777 NRSS7 345 532793 NEOSHO 7 345 1 | Current Study | 18.17 | (1793.00, 1793.00) | 30418002.796 | 76.0945 | 39974000 | 0.65948
GEN-2024-129 | 03 CENTRAL | TBD | NRIS | Rebuild line 532777 NRSS7 345 780840 G24-129-TAP 345 1 | Current Study | 13.85 | (1793.00, 1793.00) | 23155890.6541 | 75.9957 | 30470000 | 0.66859
GEN-2024-129 | 03 CENTRAL | TBD | ERIS | Rebuild line 532780 CANEYRV7 345 532800 LATHAMS7 345 1 | Current Study | 8.08 | (1793.00, 1793.00) | 17776000 | 100 | 17776000 | 0.33591
GEN-2024-129 | 03 CENTRAL | TBD | NRIS | Rebuild line 532780 CANEYRV7 345 780720 G24-125-TAP 345 1 | Current Study | 14.44 | (1793.00, 1793.00) | 18807587.0998 | 59.2029 | 31768000 | 0.33141
GEN-2024-129 | 03 CENTRAL | TBD | ERIS | Rebuild line 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 | Current Study | 30.44 | (1793.00, 1793.00) | 66968000 | 100 | 66968000 | 0.33565
GEN-2024-129 | 03 CENTRAL | TBD | NRIS | Rebuild line 532911 MUSTNG5 161 532937 NEOSHO 5 161 1 | Current Study | 27.08 | (246.00, 246.00) | 40620000 | 100 | 40620000 | 0.02588
GEN-2024-129 | 03 CENTRAL | TBD | NRIS | Rebuild line 532937 NEOSHO 5 161 532939 N345 4 5 161 1 | Current Study | 0.3 | (837.00, 837.00) | 258467.403 | 57.4372 | 450000 | 0.074483
GEN-2024-129 | 03 CENTRAL | TBD | NRIS | Rebuild line 532937 NEOSHO 5 161 764310 G20-079-TAP 161 1 | Current Study | 20.67 | (551.00, 551.00) | 16938683.293 | 54.6321 | 31005000 | 0.053493
GEN-2024-129 | 03 CENTRAL | TBD | ERIS | Rebuild line 533021 NEOSHO 4 138 533023 N345 3 4 138 1 | Current Study | 0.28 | (717.00, 717.00) | 336000 | 100 | 336000 | 0.07129
GEN-2024-139 | 03 CENTRAL | 94615 | ERIS | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029 | Contingent |  |  | 0 | 0 | 543515503 | N/A
GEN-2024-139 | 03 CENTRAL | TBD | ERIS | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV | Current Study |  |  | 46557.1396 | 3.3737 | 1380000 | 0.037285
GEN-2024-139 | 03 CENTRAL | TBD | ERIS | Add 16 MVAR switched shunt at HUMBOLT5 161 kV | Current Study |  |  | 113438.2071 | 3.4904 | 3250000 | 0.033911
GEN-2024-139 | 03 CENTRAL | TBD | ERIS | Add 21 MVAR switched shunt at S1263 5 161 kV | Current Study |  |  | 113438.2071 | 3.4904 | 3250000 | 0.033911
GEN-2024-139 | 03 CENTRAL | TBD | ERIS | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV | Current Study |  |  | 48167.6079 | 3.4904 | 1380000 | 0.033911
GEN-2024-139 | 03 CENTRAL | 94721 | ERIS | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 213682884 | N/A
GEN-2024-139 | 03 CENTRAL | 94929 | ERIS | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 413934522 | N/A
GEN-2024-139 | 03 CENTRAL | TBD | NRIS | Rebuild line 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | Current Study | 31.46 | (1793.00, 1793.00) | 2493410.982 | 3.6026 | 69212000 | 0.062662
GEN-2024-139 | 03 CENTRAL | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 347308.5051 | 2.9786 | 11660000 | 0.065702
GEN-2024-139 | 03 CENTRAL | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 2414374.5239 | 2.5689 | 93984000 | 0.065702
GEN-2024-139 | 03 CENTRAL | TBD | ERIS | Rebuild line 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | Current Study | 15.42 | (1793.00, 1793.00) | 13539713.504 | 39.9119 | 33924000 | 0.37481
GEN-2024-139 | 03 CENTRAL | TBD | ERIS | Rebuild line 541199 ST JOE 7 345 541400 EASTOWN7 345 1 | Current Study | 8.12 | (1793.00, 1793.00) | 793073.7192 | 4.4395 | 17864000 | 0.033703
GEN-2024-139 | 03 CENTRAL | TBD | ERIS | Rebuild line 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | Current Study | 28.98 | (1793.00, 1793.00) | 5105518.7648 | 8.0079 | 63756000 | 0.050635
GEN-2024-139 | 03 CENTRAL | TBD | ERIS | Rebuild line 541400 EASTOWN7 345 542982 IATAN 7 345 1 | Current Study | 23.71 | (1793.00, 1793.00) | 2275466.9765 | 4.3623 | 52162000 | 0.038614
GEN-2024-139 | 03 CENTRAL | 171607 | ERIS | Wolf Creek - Blackberry 345 kV Line GEN-2024-139 Interconnection (Non-Shared NU) (NEET) | Interconnection |  |  | 28818600 | 100 | 28818600 | 1
GEN-2024-139 | 03 CENTRAL | 171606 | ERIS | Wolf Creek - Blackberry 345 kV Line GEN-2024-139 Interconnection (TOIF) (NEET) | Interconnection |  |  | 840255 | 100 | 840255 | 1
GEN-2024-140 | 02 NEBRASKA | 94842 | ERIS | 640_NPPD_NewBranch_Holt-Antilope3_345.idv : 2024 ITP, PID: 94842, NTC, ISD: 12/31/2029 | Contingent |  |  | 0 | 0 | 78445357 | N/A
GEN-2024-140 | 02 NEBRASKA | TBD | NRIS | Add 108 MVAR switched shunt at MAURINE4 230 kV | Current Study |  |  | 338722.3591 | 8.8555 | 3825000 | 0.048989
GEN-2024-140 | 02 NEBRASKA | TBD | NRIS | Add 12 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 218889.0737 | 9.8933 | 2212500 | 0.048989
GEN-2024-140 | 02 NEBRASKA | TBD | NRIS | Add 154 MVAR SVC at WAYSIDE 4 230 kV | Current Study |  |  | 1077536.9339 | 12.5295 | 8600000 | 0.092442
GEN-2024-140 | 02 NEBRASKA | TBD | NRIS | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 83686.5801 | 3.7824 | 2212500 | 0.048989
GEN-2024-140 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 640227 HOSKINS4 230 640228 HOSKINS7 115 643083 HOSKINS T1 9 13 M2 | Current Study |  | (187.00, 187.00) | 13800000 | 100 | 13800000 | 0.0081325
GEN-2024-140 | 02 NEBRASKA | TBD | NRIS | Add 45 MVAR switched shunt at PR BRZ 4 230 kV | Current Study |  |  | 1614109.9629 | 42.199 | 3825000 | 0.57958
GEN-2024-140 | 02 NEBRASKA | 171609 | ERIS | Antelope - Hoskins 345 kV line GEN-2024-140 Interconnection (Non-Shared NU) (NPPD) | Interconnection |  |  | 4000000 | 100 | 4000000 | 1
GEN-2024-140 | 02 NEBRASKA | 171608 | ERIS | Antelope - Hoskins 345 kV line GEN-2024-140 Interconnection (TOIF) (NPPD) | Interconnection |  |  | 1000000 | 100 | 1000000 | 1
GEN-2024-140 | 02 NEBRASKA | TBD | NRIS | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | Current Study | 23.48 | (1793.00, 1793.00) | 2252450.7379 | 4.3605 | 51656000 | 0.028497
GEN-2024-140 | 02 NEBRASKA | TBD | NRIS | Rebuild line 640149 CREITON7 115 640521 ANTELOPE 7 115 1 | Current Study | 22.74 | (176.00, 176.00) | 22740000 | 100 | 22740000 | 0.020473
GEN-2024-140 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | Current Study | 23.61 | (519.00, 519.00) | 8078024.5516 | 18.0076 | 44859000 | 0.068189
GEN-2024-140 | 02 NEBRASKA | TBD | NRIS | Rebuild line 645454 S3454 3 345 650185 WAGENER 3 345 1 | Current Study | 33.67 | (1793.00, 1793.00) | 1845559.739 | 2.4915 | 74074000 | 0.044436
GEN-2024-141 | 01 NORTH | 171611 | ERIS | BASIN__-BE4 230 kV Substation GEN-2024-141 Interconnection (Non-Shared NU) (BEPC) | Interconnection |  |  | 7362181 | 100 | 7362181 | 1
GEN-2024-141 | 01 NORTH | 171610 | ERIS | BASIN__-BE4 230 kV Substation GEN-2024-141 Interconnection (TOIF) (BEPC) | Interconnection |  |  | 2270573 | 100 | 2270573 | 1
GEN-2024-143 | 05 SOUTHWEST | 220817 | ERIS | 526_New_MooreCounty_2ndTransformer_230_115.idv : PID: 220817, 2024 ITP, NTC, ISD: 5/15/2029 | Contingent |  |  | 0 | 0 | 30028000 | N/A
GEN-2024-143 | 05 SOUTHWEST | 220945 | ERIS | 526_SPS_New_Branch_MooreCo_XIT_230kv.idv : 2024 ITP upgrade, PID : 220945, NTC, ISD : 12/15/2028 | Contingent |  |  | 0 | 0 | 71837623 | N/A
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 44187.1228 | 3.202 | 1380000 | 0.089525
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV | Current Study |  |  | 39909.8548 | 2.892 | 1380000 | 0.11309
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Add 1.6 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 19407.3159 | 1.4063 | 1380000 | 0.042097
GEN-2024-143 | 05 SOUTHWEST | TBD | NRIS | Add 11 MVAR switched shunt at WWRDEHV4 138 kV | Current Study |  |  | 90025.3915 | 3.7009 | 2432500 | 0.05548
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 33213.1247 | 2.4067 | 1380000 | 0.084195
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Add 2.1 MVAR switched shunt at RB-TEXLINE 2 69 kV | Current Study |  |  | 690000 | 50 | 1380000 | 0.17973
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV | Current Study |  |  | 33213.1247 | 2.4067 | 1380000 | 0.084195
GEN-2024-143 | 05 SOUTHWEST | TBD | NRIS | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV | Current Study |  |  | 63188.5065 | 2.7473 | 2300000 | 0.11503
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Add 3.6 MVAR switched shunt at HEDLEY 2 69 kV | Current Study |  |  | 78069.9328 | 5.6572 | 1380000 | 0.0041666
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2 | Current Study |  | (339.00, 330.00) | 611328.639 | 4.3666 | 14000000 | 0.024854
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 523219 XIT_INTG TR1 13 523220 XIT_INTG 3 115 523221 XIT_INTG 6 230 M2 | Current Study |  | (247.00, 284.00) | 6900000 | 50 | 13800000 | 0.089863
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 531510 HARBNGR3 115 531511 HARBNGR-1 13 531512 HARBNGR7 345 M2 | Current Study |  | (350.00, 385.00) | 1761489.9375 | 10.4851 | 16800000 | 0.0091494
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Add 8 MVAR switched shunt at RB-N_SEDAN 2 69 kV | Current Study |  |  | 690000 | 50 | 1380000 | 0.17973
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Add line 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 P2 | Current Study | 66.8 | (1011.00, 1176.00) | 5240420.5514 | 2.4141 | 217080000 | 0.042408
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Apply contingent IDV 01_NewLine_Phantom_Crossroads_Potter_765_26SP.idv | Contingent |  |  | 0 | 0 | 3275253469 | N/A
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Apply contingent IDV 02_765_Phantom_Craw_1_DIS24_TC05ALL-26SP.idv | Contingent |  |  | 0 | 0 | 1366342009.82 | N/A
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Apply contingent IDV 02_765_Phantom_Craw_1_DIS24_TC05ALL-29SP.idv | Contingent |  |  | 0 | 0 | 1366342009.82 | N/A
GEN-2024-143 | 05 SOUTHWEST | 900427 | ERIS | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032 | Contingent |  |  | 0 | 0 | 1790026304.1702 | N/A
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | Current Study | 18.75 | (519.00, 519.00) | 1555613.0546 | 4.3666 | 35625000 | 0.049708
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 511541 DEMPSEYR POI 230 511557 CHISHOLM6 230 1 | Current Study | 11.15 | (519.00, 519.00) | 4652726.2294 | 21.9624 | 21185000 | 0.070817
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Current Study | 57.98 | (1793.00, 1793.00) | 3069824.9926 | 2.4066 | 127556000 | 0.084187
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523216 RB-HOGUE 3 115 523246 DALHART 3 115 1 | Current Study | 11.44 | (115.00, 115.00) | 5720000 | 50 | 11440000 | 0.050977
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523220 XIT_INTG 3 115 523228 DALLAM 3 115 1 | Current Study | 1.25 | (329.00, 329.00) | 625000 | 50 | 1250000 | 0.17973
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523959 POTTER_CO 6 230 524010 ROLLHILLS 6 230 1 | Current Study | 6.23 | (637.00, 637.00) | 1372346.0761 | 11.5937 | 11837000 | 0.045009
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | Current Study | 3.02 | (1793.00, 1793.00) | 96543.069 | 1.4531 | 6644000 | 0.053599
GEN-2024-143 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 531405 WALKMYR3 115 531510 HARBNGR3 115 1 | Current Study | 1.28 | (598.00, 598.00) | 134208.7571 | 10.4851 | 1280000 | 0.018299
GEN-2024-143 | 05 SOUTHWEST | 171612 | ERIS | XIT Interchange 230 kV Substation GEN-2024-143 Interconnection (TOIF) (SPS) | Interconnection |  |  | 4144145.19 | 100 | 4144145.19 | 1
GEN-2024-143 | 05 SOUTHWEST | 171616 | ERIS | XIT Interchange 230 kV Substation GEN-2024-143/145 Interconnection (Shared NU) (SPS) | Interconnection |  |  | 1221023.02 | 50 | 2442046.04 | 1
GEN-2024-145 | 05 SOUTHWEST | 220817 | ERIS | 526_New_MooreCounty_2ndTransformer_230_115.idv : PID: 220817, 2024 ITP, NTC, ISD: 5/15/2029 | Contingent |  |  | 0 | 0 | 30028000 | N/A
GEN-2024-145 | 05 SOUTHWEST | 220945 | ERIS | 526_SPS_New_Branch_MooreCo_XIT_230kv.idv : 2024 ITP upgrade, PID : 220945, NTC, ISD : 12/15/2028 | Contingent |  |  | 0 | 0 | 71837623 | N/A
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 44187.1228 | 3.202 | 1380000 | 0.089525
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV | Current Study |  |  | 39909.8548 | 2.892 | 1380000 | 0.11309
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Add 1.6 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 19407.3159 | 1.4063 | 1380000 | 0.042097
GEN-2024-145 | 05 SOUTHWEST | TBD | NRIS | Add 11 MVAR switched shunt at WWRDEHV4 138 kV | Current Study |  |  | 90025.3915 | 3.7009 | 2432500 | 0.05548
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 33213.1247 | 2.4067 | 1380000 | 0.084195
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Add 2.1 MVAR switched shunt at RB-TEXLINE 2 69 kV | Current Study |  |  | 690000 | 50 | 1380000 | 0.17973
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV | Current Study |  |  | 33213.1247 | 2.4067 | 1380000 | 0.084195
GEN-2024-145 | 05 SOUTHWEST | TBD | NRIS | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV | Current Study |  |  | 63188.5065 | 2.7473 | 2300000 | 0.11503
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Add 3.6 MVAR switched shunt at HEDLEY 2 69 kV | Current Study |  |  | 78069.9328 | 5.6572 | 1380000 | 0.0041666
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2 | Current Study |  | (339.00, 330.00) | 611328.639 | 4.3666 | 14000000 | 0.024854
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 523219 XIT_INTG TR1 13 523220 XIT_INTG 3 115 523221 XIT_INTG 6 230 M2 | Current Study |  | (247.00, 284.00) | 6900000 | 50 | 13800000 | 0.089863
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 531510 HARBNGR3 115 531511 HARBNGR-1 13 531512 HARBNGR7 345 M2 | Current Study |  | (350.00, 385.00) | 1761489.9375 | 10.4851 | 16800000 | 0.0091494
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Add 8 MVAR switched shunt at RB-N_SEDAN 2 69 kV | Current Study |  |  | 690000 | 50 | 1380000 | 0.17973
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Add line 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 P2 | Current Study | 66.8 | (1011.00, 1176.00) | 5240420.5514 | 2.4141 | 217080000 | 0.042408
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Apply contingent IDV 01_NewLine_Phantom_Crossroads_Potter_765_26SP.idv | Contingent |  |  | 0 | 0 | 3275253469 | N/A
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Apply contingent IDV 02_765_Phantom_Craw_1_DIS24_TC05ALL-26SP.idv | Contingent |  |  | 0 | 0 | 1366342009.82 | N/A
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Apply contingent IDV 02_765_Phantom_Craw_1_DIS24_TC05ALL-29SP.idv | Contingent |  |  | 0 | 0 | 1366342009.82 | N/A
GEN-2024-145 | 05 SOUTHWEST | 900427 | ERIS | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032 | Contingent |  |  | 0 | 0 | 1790026304.1702 | N/A
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | Current Study | 18.75 | (519.00, 519.00) | 1555613.0546 | 4.3666 | 35625000 | 0.049708
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 511541 DEMPSEYR POI 230 511557 CHISHOLM6 230 1 | Current Study | 11.15 | (519.00, 519.00) | 4652726.2294 | 21.9624 | 21185000 | 0.070817
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Current Study | 57.98 | (1793.00, 1793.00) | 3069824.9926 | 2.4066 | 127556000 | 0.084187
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523216 RB-HOGUE 3 115 523246 DALHART 3 115 1 | Current Study | 11.44 | (115.00, 115.00) | 5720000 | 50 | 11440000 | 0.050977
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523220 XIT_INTG 3 115 523228 DALLAM 3 115 1 | Current Study | 1.25 | (329.00, 329.00) | 625000 | 50 | 1250000 | 0.17973
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523959 POTTER_CO 6 230 524010 ROLLHILLS 6 230 1 | Current Study | 6.23 | (637.00, 637.00) | 1372346.0761 | 11.5937 | 11837000 | 0.045009
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | Current Study | 3.02 | (1793.00, 1793.00) | 96543.069 | 1.4531 | 6644000 | 0.053599
GEN-2024-145 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 531405 WALKMYR3 115 531510 HARBNGR3 115 1 | Current Study | 1.28 | (598.00, 598.00) | 134208.7571 | 10.4851 | 1280000 | 0.018299
GEN-2024-145 | 05 SOUTHWEST | 171616 | ERIS | XIT Interchange 230 kV Substation GEN-2024-143/145 Interconnection (Shared NU) (SPS) | Interconnection |  |  | 1221023.02 | 50 | 2442046.04 | 1
GEN-2024-145 | 05 SOUTHWEST | 171615 | ERIS | XIT Interchange 230 kV Substation GEN-2024-145 Interconnection (TOIF) (SPS) | Interconnection |  |  | 4144145.19 | 100 | 4144145.19 | 1
GEN-2024-154 | 04 SOUTHEAST | 94811 | ERIS | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030 | Contingent |  |  | 0 | 0 | 1097029189 | N/A
GEN-2024-154 | 04 SOUTHEAST | 94911 | ERIS | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030 | Contingent |  |  | 0 | 0 | 143524375 | N/A
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BUFFALO7 345 kV | Current Study |  |  | 1587757.3009 | 29.9577 | 5300000 | 0.07799
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 417619.3612 | 7.8796 | 5300000 | 0.034126
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at MOUND 4 138 kV | Current Study |  |  | 88654.2515 | 3.6446 | 2432500 | 0.044584
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV | Current Study |  |  | 286845.8751 | 5.4122 | 5300000 | 0.040797
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 123456.6957 | 5.0753 | 2432500 | 0.092353
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 0.09 MVAR switched shunt at SWISVAL6 230 kV | Current Study |  |  | 356328.969 | 9.3158 | 3825000 | 0.034126
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 37425.4912 | 2.712 | 1380000 | 0.094782
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 104907.4071 | 1.9794 | 5300000 | 0.030315
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 1 MVAR switched shunt at DIGHTON3 115 kV | Current Study |  |  | 2212500 | 100 | 2212500 | 0.03432
GEN-2024-154 | 04 SOUTHEAST | TBD | NRIS | Add 11 MVAR switched shunt at WWRDEHV4 138 kV | Current Study |  |  | 74498.831 | 3.0626 | 2432500 | 0.057389
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at GOODCTY3 115 kV | Current Study |  |  | 1601193.6278 | 72.3703 | 2212500 | 0.035076
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 588688.2785 | 4.9057 | 12000000 | 0.07799
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR switched shunt at WICHITA7 345 kV | Current Study |  |  | 250730.1264 | 4.7308 | 5300000 | 0.07799
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 177 MVAR switched shunt at SWISVAL7 345 kV | Current Study |  |  | 139589.9358 | 2.6338 | 5300000 | 0.025637
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 2 MVAR switched shunt at CLIFTON3 115 kV | Current Study |  |  | 299336.5813 | 13.5293 | 2212500 | 0.026164
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 20 MVAR switched shunt at RANSOM 3 115 kV | Current Study |  |  | 1601193.6278 | 72.3703 | 2212500 | 0.035076
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 23 MVAR switched shunt at FINNEY 7 345 kV | Current Study |  |  | 206522.2873 | 3.8966 | 5300000 | 0.064609
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 25 MVAR switched shunt at ATWOOD 3 115 kV | Current Study |  |  | 370630.3667 | 16.7517 | 2212500 | 0.034906
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at G21-096-TAP 345 kV | Current Study |  |  | 302604.9158 | 5.7095 | 5300000 | 0.03464
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 280 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 639487.2393 | 5.3291 | 12000000 | 0.092353
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 295 MVAR switched shunt at G18-128-TAP 345 kV | Current Study |  |  | 338210.9372 | 6.3813 | 5300000 | 0.092353
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV | Current Study |  |  | 1601193.6278 | 72.3703 | 2212500 | 0.035076
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 3.3 MVAR switched shunt at CHASE 3 115 kV | Current Study |  |  | 2212500 | 100 | 2212500 | 0.064609
GEN-2024-154 | 04 SOUTHEAST | TBD | NRIS | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV | Current Study |  |  | 37870.3635 | 1.6465 | 2300000 | 0.086172
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at G23-220-TAP 345 kV | Current Study |  |  | 270540.8738 | 5.1045 | 5300000 | 0.034338
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV | Current Study |  |  | 1601193.6278 | 72.3703 | 2212500 | 0.035076
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 64330.0138 | 1.9794 | 3250000 | 0.030315
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 45 MVAR switched shunt at NEVADA 5 161 kV | Current Study |  |  | 76587.8634 | 2.3565 | 3250000 | 0.025637
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 750375.1884 | 14.158 | 5300000 | 0.034906
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 56 MVAR switched shunt at WHARV4 138 kV | Current Study |  |  | 88654.2515 | 3.6446 | 2432500 | 0.044584
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Add 86 MVAR switched shunt at POSTROCK7 345 kV | Current Study |  |  | 840695.7124 | 15.8622 | 5300000 | 0.035076
GEN-2024-154 | 04 SOUTHEAST | 171620 | ERIS | Chisholm 345 kV Substation GEN-2024-154 Interconnection (Non-Shared NU) (AEP) | Interconnection |  |  | 3900000 | 100 | 3900000 | 1
GEN-2024-154 | 04 SOUTHEAST | 171619 | ERIS | Chisholm 345 kV Substation GEN-2024-154 Interconnection (TOIF) (AEP) | Interconnection |  |  | 5225000 | 100 | 5225000 | 1
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | DIS2301-1_G03_ERIS_TurnOffReactors_Carpenter_Finney.idv : Switch out Carpenter 25 MVAR line reactor on the Carpenter to Hitchland 345 kV line | Contingent |  |  | 0 | 0 | 1450000 | 0.079313
GEN-2024-154 | 04 SOUTHEAST | 900427 | ERIS | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032 | Contingent |  |  | 0 | 0 | 1790026304.1702 | N/A
GEN-2024-154 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514715 WOODRNG7 345 515875 REDNGTN7 345 1 | Current Study | 19.2 | (1793.00, 1793.00) | 2077948.1807 | 4.9194 | 42240000 | 0.068077
GEN-2024-154 | 04 SOUTHEAST | TBD | NRIS | Rebuild line 515802 GRACMNT4 138 520814 ANADARK4 138 1 | Current Study | 5.09 | (265.00, 265.00) | 543100.8659 | 8.8916 | 6108000 | 0.015417
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 63013.0139 | 4.5662 | 1380000 | 0.10639
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV | Current Study |  |  | 42676.3835 | 3.0925 | 1380000 | 0.10077
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Add 1.6 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 77138.8514 | 5.5898 | 1380000 | 0.13944
GEN-2024-159 | 05 SOUTHWEST | TBD | NRIS | Add 10 MVAR switched shunt at DEAFSMITH 6 230 kV | Current Study |  |  | 1663934.9029 | 43.5016 | 3825000 | 0.077319
GEN-2024-159 | 05 SOUTHWEST | TBD | NRIS | Add 11 MVAR switched shunt at WWRDEHV4 138 kV | Current Study |  |  | 120201.2098 | 4.9415 | 2432500 | 0.06173
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 66006.6107 | 4.7831 | 1380000 | 0.13944
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV | Current Study |  |  | 66006.6107 | 4.7831 | 1380000 | 0.13944
GEN-2024-159 | 05 SOUTHWEST | TBD | NRIS | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV | Current Study |  |  | 72692.7337 | 3.1606 | 2300000 | 0.11027
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Add 3.6 MVAR switched shunt at HEDLEY 2 69 kV | Current Study |  |  | 82545.2675 | 5.9815 | 1380000 | 0.0036712
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2 | Current Study |  | (339.00, 330.00) | 784296.8849 | 5.6021 | 14000000 | 0.026572
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Add line 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 P2 | Current Study | 66.8 | (1011.00, 1176.00) | 10392915.8867 | 4.7876 | 217080000 | 0.070087
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Apply contingent IDV 01_NewLine_Phantom_Crossroads_Potter_765_26SP.idv | Contingent |  |  | 0 | 0 | 3275253469 | N/A
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Apply contingent IDV 02_765_Phantom_Craw_1_DIS24_TC05ALL-26SP.idv | Contingent |  |  | 0 | 0 | 1366342009.82 | N/A
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Apply contingent IDV 02_765_Phantom_Craw_1_DIS24_TC05ALL-29SP.idv | Contingent |  |  | 0 | 0 | 1366342009.82 | N/A
GEN-2024-159 | 05 SOUTHWEST | 900427 | ERIS | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032 | Contingent |  |  | 0 | 0 | 1790026304.1702 | N/A
GEN-2024-159 | 05 SOUTHWEST | 171626 | ERIS | Oasis - San Juan Mesa Wind 230 kV Line GEN-2024-159 Interconnection (Non-Shared NU) (SPS) | Interconnection |  |  | 27237303 | 100 | 27237303 | 1
GEN-2024-159 | 05 SOUTHWEST | 171625 | ERIS | Oasis - San Juan Mesa Wind 230 kV Line GEN-2024-159 Interconnection (TOIF) (SPS) | Interconnection |  |  | 4119557 | 100 | 4119557 | 1
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | Current Study | 18.75 | (519.00, 519.00) | 1995755.466 | 5.6021 | 35625000 | 0.053143
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Current Study | 57.98 | (1793.00, 1793.00) | 6101095.0772 | 4.7831 | 127556000 | 0.13943
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 524875 OASIS 6 230 781740 G24-159-TAP 230 1 | Current Study | 4.87 | (519.00, 519.00) | 7308697.3067 | 78.9873 | 9253000 | 0.81223
GEN-2024-159 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | Current Study | 3.02 | (1793.00, 1793.00) | 295178.0507 | 4.4428 | 6644000 | 0.13656
GEN-2024-162 | 02 NEBRASKA | TBD | NRIS | Add 108 MVAR switched shunt at MAURINE4 230 kV | Current Study |  |  | 113343.6429 | 2.9632 | 3825000 | 0.037257
GEN-2024-162 | 02 NEBRASKA | TBD | NRIS | Add 12 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 73244.8991 | 3.3105 | 2212500 | 0.037257
GEN-2024-162 | 02 NEBRASKA | TBD | NRIS | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 28003.2941 | 1.2657 | 2212500 | 0.037257
GEN-2024-162 | 02 NEBRASKA | TBD | NRIS | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | Current Study | 23.48 | (1793.00, 1793.00) | 8731642.6318 | 16.9034 | 51656000 | 0.25107
GEN-2024-162 | 02 NEBRASKA | TBD | NRIS | Rebuild line 640080 BELDEN 7 115 640212 HARTGTN7 115 1 | Current Study | 12.27 | (176.00, 176.00) | 12270000 | 100 | 12270000 | 0.032731
GEN-2024-162 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | Current Study | 23.61 | (519.00, 519.00) | 32104887.1722 | 71.5684 | 44859000 | 0.61592
GEN-2024-162 | 02 NEBRASKA | TBD | NRIS | Rebuild line 652552 SIOUXCY2 230 659900 EAGLE___-NI4 230 1 | Current Study | 33.29 | (519.00, 519.00) | 32893012.497 | 52.0039 | 63251000 | 0.049115
GEN-2024-162 | 02 NEBRASKA | 171630 | ERIS | Twin Church 230 kV Substation GEN-2024-162 Interconnection (Non-Shared NU) (NPPD) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-162 | 02 NEBRASKA | 171629 | ERIS | Twin Church 230 kV Substation GEN-2024-162 Interconnection (TOIF) (NPPD) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-166 | 03 CENTRAL | TBD | ERIS | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV | Current Study |  |  | 12307.8174 | 0.89187 | 1380000 | 0.043593
GEN-2024-166 | 03 CENTRAL | 171925 | ERIS | Murray Gill 138 kV Substation GEN-2024-166 Interconnection (Non-Shared NU) (WERE) | Interconnection |  |  | 3654211 | 100 | 3654211 | 1
GEN-2024-166 | 03 CENTRAL | 171924 | ERIS | Murray Gill 138 kV Substation GEN-2024-166 Interconnection (TOIF) (WERE) | Interconnection |  |  | 1040242 | 100 | 1040242 | 1
GEN-2024-166 | 03 CENTRAL | TBD | NRIS | Rebuild line 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | Current Study | 31.46 | (1793.00, 1793.00) | 749376.9937 | 1.0827 | 69212000 | 0.023541
GEN-2024-166 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640525 TOBIAS 3 345 1 | Current Study | 26.47 | (1793.00, 1793.00) | 2485848.7433 | 4.2687 | 58234000 | 0.03506
GEN-2024-168 | 02 NEBRASKA | TBD | NRIS | Add 108 MVAR switched shunt at MAURINE4 230 kV | Current Study |  |  | 223280.8543 | 5.8374 | 3825000 | 0.040366
GEN-2024-168 | 02 NEBRASKA | TBD | NRIS | Add 12 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 144288.4949 | 6.5215 | 2212500 | 0.040366
GEN-2024-168 | 02 NEBRASKA | TBD | NRIS | Add 14 MVAR switched shunt at HASTING4 230 kV | Current Study |  |  | 3825000 | 100 | 3825000 | 0.049516
GEN-2024-168 | 02 NEBRASKA | TBD | NRIS | Add 154 MVAR SVC at WAYSIDE 4 230 kV | Current Study |  |  | 527664.2666 | 6.1356 | 8600000 | 0.056586
GEN-2024-168 | 02 NEBRASKA | TBD | NRIS | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 55164.9769 | 2.4933 | 2212500 | 0.040366
GEN-2024-168 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2 | Current Study |  | (110.00, 120.00) | 700472.0869 | 5.8373 | 12000000 | 0.012355
GEN-2024-168 | 02 NEBRASKA | TBD | NRIS | Add 45 MVAR switched shunt at PR BRZ 4 230 kV | Current Study |  |  | 139316.968 | 3.6423 | 3825000 | 0.06253
GEN-2024-168 | 02 NEBRASKA | 171636 | ERIS | Geneva 115 kV Substation GEN-2024-168 Interconnection (Non-Shared NU) (NPPD) | Interconnection |  |  | 13500000 | 100 | 13500000 | 1
GEN-2024-168 | 02 NEBRASKA | 171635 | ERIS | Geneva 115 kV Substation GEN-2024-168 Interconnection (TOIF) (NPPD) | Interconnection |  |  | 500000 | 100 | 500000 | 1
GEN-2024-168 | 02 NEBRASKA | TBD | NRIS | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | Current Study | 23.48 | (1793.00, 1793.00) | 2088387.7529 | 4.0429 | 51656000 | 0.033027
GEN-2024-168 | 02 NEBRASKA | TBD | NRIS | Rebuild line 640178 GENEVA 7 115 640272 MCCOOL 7 115 1 | Current Study | 11.26 | (217.00, 217.00) | 11260000 | 100 | 11260000 | 0.47805
GEN-2024-168 | 02 NEBRASKA | TBD | NRIS | Rebuild line 640272 MCCOOL 7 115 640413 YORK SW7 115 1 | Current Study | 9.46 | (176.00, 176.00) | 9460000 | 100 | 9460000 | 0.09736
GEN-2024-168 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640316 PAWNEEL7 115 650214 NW68HOLDRG7 115 1 | Current Study | 5.46 | (217.00, 217.00) | 225858.8716 | 4.1366 | 5460000 | 0.033908
GEN-2024-168 | 02 NEBRASKA | TBD | NRIS | Rebuild line 645454 S3454 3 345 650185 WAGENER 3 345 1 | Current Study | 33.67 | (1793.00, 1793.00) | 4398015.6366 | 5.9373 | 74074000 | 0.13236
GEN-2024-168 | 02 NEBRASKA | TBD | NRIS | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | Current Study | 17.69 | (246.00, 246.00) | 1548918.9021 | 5.8373 | 26535000 | 0.024711
GEN-2024-168 | 02 NEBRASKA | TBD | NRIS | Rebuild line 650185 WAGENER 3 345 650189 103&ROKEBY3 345 1 | Current Study | 9.45 | (1793.00, 1793.00) | 1136992.8059 | 5.4689 | 20790000 | 0.057381
GEN-2024-170 | 03 CENTRAL | 94615 | ERIS | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029 | Contingent |  |  | 0 | 0 | 543515503 | N/A
GEN-2024-170 | 03 CENTRAL | TBD | ERIS | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV | Current Study |  |  | 90684.8436 | 6.5714 | 1380000 | 0.064843
GEN-2024-170 | 03 CENTRAL | TBD | ERIS | Add 16 MVAR switched shunt at HUMBOLT5 161 kV | Current Study |  |  | 274887.0613 | 8.4581 | 3250000 | 0.07337
GEN-2024-170 | 03 CENTRAL | TBD | ERIS | Add 21 MVAR switched shunt at S1263 5 161 kV | Current Study |  |  | 274887.0613 | 8.4581 | 3250000 | 0.07337
GEN-2024-170 | 03 CENTRAL | TBD | ERIS | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV | Current Study |  |  | 116721.2753 | 8.4581 | 1380000 | 0.07337
GEN-2024-170 | 03 CENTRAL | TBD | ERIS | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2 | Current Study | 0.75 | (2390.00, 2390.00) | 143245.3636 | 0.80588 | 17775000 | 0.015786
GEN-2024-170 | 03 CENTRAL | 94721 | ERIS | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 213682884 | N/A
GEN-2024-170 | 03 CENTRAL | 94929 | ERIS | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 413934522 | N/A
GEN-2024-170 | 03 CENTRAL | 171929 | ERIS | Dogwood 345 kV Substation GEN-2024-170 Interconnection (Non-Shared NU) (WERE) | Interconnection |  |  | 4228553 | 100 | 4228553 | 1
GEN-2024-170 | 03 CENTRAL | 171928 | ERIS | Dogwood 345 kV Substation GEN-2024-170 Interconnection (TOIF) (WERE) | Interconnection |  |  | 1958092 | 100 | 1958092 | 1
GEN-2024-170 | 03 CENTRAL | TBD | ERIS | Rebuild line 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | Current Study | 3.02 | (551.00, 551.00) | 976277.2984 | 21.5514 | 4530000 | 0.051632
GEN-2024-170 | 03 CENTRAL | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 370362.6187 | 3.1764 | 11660000 | 0.062556
GEN-2024-170 | 03 CENTRAL | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 2574639.1411 | 2.7394 | 93984000 | 0.062556
GEN-2024-170 | 03 CENTRAL | TBD | ERIS | Rebuild line 541199 ST JOE 7 345 541400 EASTOWN7 345 1 | Current Study | 8.12 | (1793.00, 1793.00) | 809192.2378 | 4.5297 | 17864000 | 0.030703
GEN-2024-170 | 03 CENTRAL | TBD | ERIS | Rebuild line 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | Current Study | 28.98 | (1793.00, 1793.00) | 39199997.9858 | 61.4844 | 63756000 | 0.34712
GEN-2024-170 | 03 CENTRAL | TBD | ERIS | Rebuild line 541400 EASTOWN7 345 542982 IATAN 7 345 1 | Current Study | 23.71 | (1793.00, 1793.00) | 2405291.5716 | 4.6112 | 52162000 | 0.036444
GEN-2024-171 | 04 SOUTHEAST | 94615 | ERIS | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029 | Contingent |  |  | 0 | 0 | 543515503 | N/A
GEN-2024-171 | 04 SOUTHEAST | 94811 | ERIS | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030 | Contingent |  |  | 0 | 0 | 1097029189 | N/A
GEN-2024-171 | 04 SOUTHEAST | 94911 | ERIS | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030 | Contingent |  |  | 0 | 0 | 143524375 | N/A
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at JAY 4 138 kV | Current Study |  |  | 324593.6576 | 13.344 | 2432500 | 0.06883
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at MOUND 4 138 kV | Current Study |  |  | 107913.2945 | 4.4363 | 2432500 | 0.043415
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV | Current Study |  |  | 289930.6226 | 5.4704 | 5300000 | 0.032989
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 145918.1905 | 5.9987 | 2432500 | 0.087325
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 0.04 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 420711.8045 | 12.945 | 3250000 | 0.033631
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 0.09 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 262703.5494 | 8.0832 | 3250000 | 0.068043
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 0.11 MVAR switched shunt at CHAMSPR7 345 kV | Current Study |  |  | 707233.8685 | 13.344 | 5300000 | 0.06883
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 283368.8621 | 5.3466 | 5300000 | 0.065508
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 0.13 MVAR switched shunt at PECULR 7 345 kV | Current Study |  |  | 837290.9587 | 15.7979 | 5300000 | 0.031066
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 0.2 MVAR switched shunt at GROVE 5 161 kV | Current Study |  |  | 169475.749 | 5.2146 | 3250000 | 0.068043
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 0.25 MVAR switched shunt at LABETTS2 69 kV | Current Study |  |  | 78050.8019 | 5.6559 | 1380000 | 0.068043
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at TONTITN7 345 kV | Current Study |  |  | 689455.8126 | 13.0086 | 5300000 | 0.06883
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 15 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 262703.5494 | 8.0832 | 3250000 | 0.068043
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 618086.434 | 5.1507 | 12000000 | 0.065508
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR switched shunt at NEOSHO 4 138 kV | Current Study |  |  | 86663.0169 | 3.5627 | 2432500 | 0.068043
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at CPK446 5 161 kV | Current Study |  |  | 91402.5632 | 2.8124 | 3250000 | 0.033631
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV | Current Study |  |  | 263052.9907 | 8.0939 | 3250000 | 0.068043
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR switched shunt at WICHITA7 345 kV | Current Study |  |  | 263251.1897 | 4.967 | 5300000 | 0.065508
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 177 MVAR switched shunt at SWISVAL7 345 kV | Current Study |  |  | 274878.3731 | 5.1864 | 5300000 | 0.040388
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 20 MVAR switched shunt at LIBERTY4 138 kV | Current Study |  |  | 163674.1787 | 6.7286 | 2432500 | 0.087325
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 263052.9907 | 8.0939 | 3250000 | 0.068043
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR switched shunt at STILWEL7 345 kV | Current Study |  |  | 361910.8431 | 6.8285 | 5300000 | 0.040388
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 24 MVAR switched shunt at GROVE 4 138 kV | Current Study |  |  | 117142.374 | 4.8157 | 2432500 | 0.068043
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 280 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 259112.1472 | 2.1593 | 12000000 | 0.029936
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 295 MVAR switched shunt at G18-128-TAP 345 kV | Current Study |  |  | 251337.1507 | 4.7422 | 5300000 | 0.054905
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 3 MVAR switched shunt at NEOSHOS2 69 kV | Current Study |  |  | 83357.7596 | 6.0404 | 1380000 | 0.054905
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at G23-220-TAP 345 kV | Current Study |  |  | 305950.0908 | 5.7726 | 5300000 | 0.031066
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 316 MVAR switched shunt at W.GRDNR7 345 kV | Current Study |  |  | 361910.8431 | 6.8285 | 5300000 | 0.040388
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 173763.9249 | 5.3466 | 3250000 | 0.065508
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 45 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 607854.4996 | 5.0655 | 12000000 | 0.054905
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 45 MVAR switched shunt at NEVADA 5 161 kV | Current Study |  |  | 150815.6526 | 4.6405 | 3250000 | 0.040388
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 56 MVAR switched shunt at WHARV4 138 kV | Current Study |  |  | 107913.2945 | 4.4363 | 2432500 | 0.043415
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV | Current Study |  |  | 120053.435 | 8.6995 | 1380000 | 0.068043
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Add line 515012 RVRVALY7 345 780360 G24-113-TAP 345 P2 | Current Study | 23.28 | (1195.00, 1195.00) | 2546946.6194 | 3.0997 | 82168000 | 0.017007
GEN-2024-171 | 04 SOUTHEAST | 94721 | ERIS | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 213682884 | N/A
GEN-2024-171 | 04 SOUTHEAST | 94929 | ERIS | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 413934522 | N/A
GEN-2024-171 | 04 SOUTHEAST | 900427 | ERIS | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032 | Contingent |  |  | 0 | 0 | 1790026304.1702 | N/A
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 3257450.6939 | 9.6965 | 33594000 | 0.14142
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 461336.2995 | 3.9566 | 11660000 | 0.087273
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Current Study | 14.6 | (1793.00, 1793.00) | 3114523.9116 | 9.6965 | 32120000 | 0.14142
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 398776.2207 | 13.4268 | 2970000 | 0.16986
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 274989.9038 | 12.4995 | 2200000 | 0.16986
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | Current Study | 15.48 | (1793.00, 1793.00) | 3736372.5493 | 10.9713 | 34056000 | 0.046769
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 3207058.2554 | 3.4123 | 93984000 | 0.087273
GEN-2024-171 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Current Study | 25.29 | (2390.00, 2390.00) | 3134022.381 | 5.6329 | 55638000 | 0.055096
GEN-2024-171 | 04 SOUTHEAST | 171638 | ERIS | Tulsa North - GR Energy Center 345 kV Line GEN-2024-171 Interconnection (Non-Shared NU) (GRDA) | Interconnection |  |  | 14597250 | 100 | 14597250 | 1
GEN-2024-171 | 04 SOUTHEAST | 171637 | ERIS | Tulsa North - GR Energy Center 345 kV Line GEN-2024-171 Interconnection (TOIF) (GRDA) | Interconnection |  |  | 3797463 | 100 | 3797463 | 1
GEN-2024-173 | 02 NEBRASKA | TBD | NRIS | Add 108 MVAR switched shunt at MAURINE4 230 kV | Current Study |  |  | 210801.9005 | 5.5112 | 3825000 | 0.03811
GEN-2024-173 | 02 NEBRASKA | TBD | NRIS | Add 12 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 136224.3486 | 6.157 | 2212500 | 0.03811
GEN-2024-173 | 02 NEBRASKA | TBD | NRIS | Add 154 MVAR SVC at WAYSIDE 4 230 kV | Current Study |  |  | 407326.6767 | 4.7364 | 8600000 | 0.043681
GEN-2024-173 | 02 NEBRASKA | TBD | NRIS | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 52081.859 | 2.354 | 2212500 | 0.03811
GEN-2024-173 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2 | Current Study |  | (110.00, 120.00) | 2010237.0042 | 16.752 | 12000000 | 0.035458
GEN-2024-173 | 02 NEBRASKA | TBD | NRIS | Add 45 MVAR switched shunt at PR BRZ 4 230 kV | Current Study |  |  | 218840.7701 | 5.7213 | 3825000 | 0.098224
GEN-2024-173 | 02 NEBRASKA | 171640 | ERIS | Pawnee Lake 115 kV Substation GEN-2024-173 Interconnection (Non-Shared NU) (NPPD) | Interconnection |  |  | 7500000 | 100 | 7500000 | 1
GEN-2024-173 | 02 NEBRASKA | 171639 | ERIS | Pawnee Lake 115 kV Substation GEN-2024-173 Interconnection (TOIF) (NPPD) | Interconnection |  |  | 500000 | 100 | 500000 | 1
GEN-2024-173 | 02 NEBRASKA | TBD | NRIS | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | Current Study | 23.48 | (1793.00, 1793.00) | 2609687.2917 | 5.0521 | 51656000 | 0.041271
GEN-2024-173 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640316 PAWNEEL7 115 640340 SEWARD 7 115 1 | Current Study | 11.21 | (217.00, 217.00) | 11210000 | 100 | 11210000 | 0.21421
GEN-2024-173 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640316 PAWNEEL7 115 650214 NW68HOLDRG7 115 1 | Current Study | 5.46 | (217.00, 217.00) | 5234141.1284 | 95.8634 | 5460000 | 0.78579
GEN-2024-173 | 02 NEBRASKA | TBD | NRIS | Rebuild line 645454 S3454 3 345 650185 WAGENER 3 345 1 | Current Study | 33.67 | (1793.00, 1793.00) | 5856720.1213 | 7.9066 | 74074000 | 0.17627
GEN-2024-173 | 02 NEBRASKA | TBD | NRIS | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | Current Study | 17.69 | (246.00, 246.00) | 4445136.5756 | 16.752 | 26535000 | 0.070916
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 97119.751 | 7.0377 | 1380000 | 0.078428
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at PHILL 7 345 kV | Current Study |  |  | 559975.4085 | 10.5656 | 5300000 | 0.034587
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV | Current Study |  |  | 97119.751 | 7.0377 | 1380000 | 0.078428
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add 0.2 MVAR switched shunt at GROVE 5 161 kV | Current Study |  |  | 119305.4295 | 3.6709 | 3250000 | 0.060176
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add 0.25 MVAR switched shunt at LABETTS2 69 kV | Current Study |  |  | 54945.2326 | 3.9815 | 1380000 | 0.060176
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add 11 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 223527.3044 | 6.8778 | 3250000 | 0.078428
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR switched shunt at NEOSHO 4 138 kV | Current Study |  |  | 79512.6915 | 3.2688 | 2432500 | 0.078428
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at CPK446 5 161 kV | Current Study |  |  | 169670.687 | 5.2206 | 3250000 | 0.078428
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add 24 MVAR switched shunt at GROVE 4 138 kV | Current Study |  |  | 107477.2812 | 4.4184 | 2432500 | 0.078428
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV | Current Study |  |  | 44601.9695 | 3.232 | 1380000 | 0.041307
GEN-2024-177 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at INDEPCO5 161 kV | Current Study |  |  | 223527.3044 | 6.8778 | 3250000 | 0.078428
GEN-2024-177 | 04 SOUTHEAST | 171644 | ERIS | Red Point 138 kV Substation GEN-2024-177 Interconnection (Non-Shared NU) (AEP) | Interconnection |  |  | 2800000 | 100 | 2800000 | 1
GEN-2024-177 | 04 SOUTHEAST | 171643 | ERIS | Red Point 138 kV Substation GEN-2024-177 Interconnection (TOIF) (AEP) | Interconnection |  |  | 3325000 | 100 | 3325000 | 1
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 93298.2403 | 6.7607 | 1380000 | 0.075342
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at PHILL 7 345 kV | Current Study |  |  | 557437.3008 | 10.5177 | 5300000 | 0.03443
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV | Current Study |  |  | 93298.2403 | 6.7607 | 1380000 | 0.075342
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add 0.2 MVAR switched shunt at GROVE 5 161 kV | Current Study |  |  | 115440.6392 | 3.552 | 3250000 | 0.058227
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add 0.25 MVAR switched shunt at LABETTS2 69 kV | Current Study |  |  | 53165.332 | 3.8526 | 1380000 | 0.058227
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add 11 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 214731.8536 | 6.6071 | 3250000 | 0.075342
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR switched shunt at NEOSHO 4 138 kV | Current Study |  |  | 76383.9911 | 3.1401 | 2432500 | 0.075342
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at CPK446 5 161 kV | Current Study |  |  | 162994.4101 | 5.0152 | 3250000 | 0.075342
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add 24 MVAR switched shunt at GROVE 4 138 kV | Current Study |  |  | 103248.2178 | 4.2445 | 2432500 | 0.075342
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV | Current Study |  |  | 118207.4777 | 8.5658 | 1380000 | 0.10948
GEN-2024-178 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at INDEPCO5 161 kV | Current Study |  |  | 214731.8536 | 6.6071 | 3250000 | 0.075342
GEN-2024-178 | 04 SOUTHEAST | 171646 | ERIS | Pirkey 138 kV Substation GEN-2024-178 Interconnection (Non-Shared NU) (AEP) | Interconnection |  |  | 6300000 | 100 | 6300000 | 1
GEN-2024-178 | 04 SOUTHEAST | 171645 | ERIS | Pirkey 138 kV Substation GEN-2024-178 Interconnection (TOIF) (AEP) | Interconnection |  |  | 3325000 | 100 | 3325000 | 1
GEN-2024-181 | 03 CENTRAL | 171650 | ERIS | Brookline 161 kV Substation GEN-2024-181 Interconnection (Non-Shared NU) (CUS) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-181 | 03 CENTRAL | 171650 | ERIS | Brookline 161 kV Substation GEN-2024-181 Interconnection (Non-Shared NU) (CUS) | Interconnection |  |  | 1700000 | 100 | 1700000 | 1
GEN-2024-181 | 03 CENTRAL | 171649 | ERIS | Brookline 161 kV Substation GEN-2024-181 Interconnection (TOIF) (CUS) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-181 | 03 CENTRAL | 171649 | ERIS | Brookline 161 kV Substation GEN-2024-181 Interconnection (TOIF) (CUS) | Interconnection |  |  | 55000 | 100 | 55000 | 1
GEN-2024-181 | 03 CENTRAL | TBD | NRIS | Rebuild line 505492 SPRGFLD5 161 549970 CLAY 5 161 1 | Current Study | 6.73 | (246.00, 246.00) | 7673344.5123 | 76.0113 | 10095000 | 0.071817
GEN-2024-204 | 04 SOUTHEAST | 94615 | ERIS | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029 | Contingent |  |  | 0 | 0 | 543515503 | N/A
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at MOUND 4 138 kV | Current Study |  |  | 39392.3663 | 1.6194 | 2432500 | 0.039621
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 20494.8221 | 1.4851 | 1380000 | 0.032935
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 25042.9231 | 1.0295 | 2432500 | 0.037467
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 6433.3326 | 0.46618 | 1380000 | 0.032586
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 66995.2721 | 1.2641 | 5300000 | 0.038719
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV | Current Study |  |  | 20494.8221 | 1.4851 | 1380000 | 0.032935
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 0.2 MVAR switched shunt at GROVE 5 161 kV | Current Study |  |  | 33518.8914 | 1.0314 | 3250000 | 0.033644
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 0.25 MVAR switched shunt at LABETTS2 69 kV | Current Study |  |  | 15436.8774 | 1.1186 | 1380000 | 0.033644
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 11 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 48184.7949 | 1.4826 | 3250000 | 0.033644
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 146130.6248 | 1.2178 | 12000000 | 0.038719
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR switched shunt at NEOSHO 4 138 kV | Current Study |  |  | 13298.5804 | 0.5467 | 2432500 | 0.026103
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at CPK446 5 161 kV | Current Study |  |  | 36575.1615 | 1.1254 | 3250000 | 0.033644
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR switched shunt at WICHITA7 345 kV | Current Study |  |  | 63688.4346 | 1.2017 | 5300000 | 0.039621
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 177 MVAR switched shunt at SWISVAL7 345 kV | Current Study |  |  | 66737.3123 | 1.2592 | 5300000 | 0.024514
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 20 MVAR switched shunt at LIBERTY4 138 kV | Current Study |  |  | 28090.2597 | 1.1548 | 2432500 | 0.037467
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 24 MVAR switched shunt at GROVE 4 138 kV | Current Study |  |  | 17975.6871 | 0.73898 | 2432500 | 0.026103
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 280 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 169779.3132 | 1.4148 | 12000000 | 0.049038
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 295 MVAR switched shunt at G18-128-TAP 345 kV | Current Study |  |  | 77009.8287 | 1.453 | 5300000 | 0.042057
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 3 MVAR switched shunt at NEOSHOS2 69 kV | Current Study |  |  | 25540.8593 | 1.8508 | 1380000 | 0.042057
GEN-2024-204 | 04 SOUTHEAST | TBD | NRIS | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV | Current Study |  |  | 8706.7218 | 0.37855 | 2300000 | 0.039623
GEN-2024-204 | 04 SOUTHEAST | TBD | NRIS | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2 | Current Study |  | (484.00, 515.00) | 536778.2331 | 2.9656 | 18100000 | 0.011676
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at INDEPCO5 161 kV | Current Study |  |  | 48184.7949 | 1.4826 | 3250000 | 0.033644
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 41082.0065 | 1.2641 | 3250000 | 0.038719
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 45 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 186246.9228 | 1.5521 | 12000000 | 0.042057
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 45 MVAR switched shunt at NEVADA 5 161 kV | Current Study |  |  | 36616.3085 | 1.1267 | 3250000 | 0.024514
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Add 56 MVAR switched shunt at WHARV4 138 kV | Current Study |  |  | 39392.3663 | 1.6194 | 2432500 | 0.039621
GEN-2024-204 | 04 SOUTHEAST | 94721 | ERIS | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 213682884 | N/A
GEN-2024-204 | 04 SOUTHEAST | 94929 | ERIS | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 413934522 | N/A
GEN-2024-204 | 04 SOUTHEAST | 171663 | ERIS | Brown 138 kV Substation GEN-2024-204 Interconnection (Non-Shared NU) (OGE) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-204 | 04 SOUTHEAST | 171662 | ERIS | Brown 138 kV Substation GEN-2024-204 Interconnection (TOIF) (OGE) | Interconnection |  |  | 100000 | 100 | 100000 | 1
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 505600 TUPELO 4 138 505602 S BROWN4 138 1 | Current Study | 36.9 | (211.00, 211.00) | 24029218.8262 | 54.2665 | 44280000 | 0.24295
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508359 WELSH 7 345 508841 WILKES 7 345 1 | Current Study | 30.63 | (1793.00, 1793.00) | 1885391.2367 | 2.7979 | 67386000 | 0.036897
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | Current Study | 21.38 | (1793.00, 1793.00) | 996792.1913 | 2.1192 | 47036000 | 0.06601
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 463243.8023 | 1.3789 | 33594000 | 0.05028
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Current Study | 14.6 | (1793.00, 1793.00) | 442918.1083 | 1.3789 | 32120000 | 0.05028
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514715 WOODRNG7 345 515875 REDNGTN7 345 1 | Current Study | 19.2 | (1793.00, 1793.00) | 955267.6095 | 2.2615 | 42240000 | 0.062592
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 1079838.5555 | 2.3519 | 45914000 | 0.049256
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 550122.989 | 0.58534 | 93984000 | 0.037426
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Current Study | 25.29 | (2390.00, 2390.00) | 960398.5256 | 1.7262 | 55638000 | 0.042209
GEN-2024-204 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 589332.1106 | 2.3519 | 25058000 | 0.049256
GEN-2024-205 | 03 CENTRAL | TBD | ERIS | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV | Current Study |  |  | 15552.4666 | 1.127 | 1380000 | 0.071078
GEN-2024-205 | 03 CENTRAL | TBD | NRIS | Rebuild 3-winding transformer 530565 SEWARD 2 69 530631 SWRD1 1 12 530679 SEWRDMW3 115 1 | Current Study |  | (54.00, 54.00) | 4725000 | 100 | 4725000 | 0.090988
GEN-2024-205 | 03 CENTRAL | TBD | NRIS | Rebuild line 530679 SEWRDMW3 115 539692 SEWARD 3 115 1 | Current Study | 2.91 | (115.00, 115.00) | 2910000 | 100 | 2910000 | 0.090988
GEN-2024-205 | 03 CENTRAL | TBD | NRIS | Rebuild line 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | Current Study | 14.69 | (176.00, 176.00) | 14690000 | 100 | 14690000 | 0.4358
GEN-2024-205 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640525 TOBIAS 3 345 1 | Current Study | 26.47 | (1793.00, 1793.00) | 3274540.3617 | 5.6231 | 58234000 | 0.059592
GEN-2024-205 | 03 CENTRAL | 171665 | ERIS | St. John 115 kV Substation GEN-2024-205 Interconnection (Non-Shared NU) (SUNC) | Interconnection |  |  | 2800000 | 100 | 2800000 | 1
GEN-2024-205 | 03 CENTRAL | 171664 | ERIS | St. John 115 kV Substation GEN-2024-205 Interconnection (TOIF) (SUNC) | Interconnection |  |  | 1200000 | 100 | 1200000 | 1
GEN-2024-206 | 03 CENTRAL | TBD | ERIS | Add line 543004 BLUMILS5 161 548808 ECKLES-161 161 M2 | Current Study | 6.5 | (837.00, 837.00) | 4414404.9348 | 22.2388 | 19850000 | 0.19268
GEN-2024-206 | 03 CENTRAL | TBD | ERIS | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2 | Current Study | 6.85 | (837.00, 837.00) | 4663607.9037 | 22.6554 | 20585000 | 0.3066
GEN-2024-206 | 03 CENTRAL | TBD | ERIS | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2 | Current Study | 4.34 | (837.00, 837.00) | 3469590.8417 | 22.6563 | 15314000 | 0.31095
GEN-2024-206 | 03 CENTRAL | TBD | ERIS | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2 | Current Study | 0.75 | (2390.00, 2390.00) | 124015.3086 | 0.6977 | 17775000 | 0.01691
GEN-2024-206 | 03 CENTRAL | 171667 | ERIS | Blue Valley 161 kV Substation GEN-2024-206 Interconnection (Non-Shared NU) (INDN) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-206 | 03 CENTRAL | 171666 | ERIS | Blue Valley 161 kV Substation GEN-2024-206 Interconnection (TOIF) (INDN) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-206 | 03 CENTRAL | 900341 | ERIS | Line - Crosstown - Blue Valley Station 161 kV New Line.idv : 2025 ITP upgrade, PID : 900341, NO NTC | Current Study |  |  | 4892546.5913 | 22.6067 | 21642007.43 | 0.064502
GEN-2024-206 | 03 CENTRAL | TBD | ERIS | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | Current Study |  | (215.00, 215.00) | 1377705.6652 | 22.6783 | 6075000 | 0.025718
GEN-2024-206 | 03 CENTRAL | TBD | ERIS | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | Current Study |  | (221.00, 221.00) | 1377705.6652 | 22.6783 | 6075000 | 0.026423
GEN-2024-206 | 03 CENTRAL | TBD | ERIS | Rebuild 2-winding transformer 548814 SUB M-161 161 548815 SUB M 69 1 | Current Study |  | (169.00, 169.00) | 1380513.3523 | 22.7245 | 6075000 | 0.0086901
GEN-2024-206 | 03 CENTRAL | TBD | ERIS | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | Current Study | 6.07 | (364.00, 364.00) | 2014484.2488 | 22.125 | 9105000 | 0.076937
GEN-2024-206 | 03 CENTRAL | TBD | ERIS | Rebuild line 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 | Current Study | 3.09 | (551.00, 551.00) | 1031709.0487 | 22.2591 | 4635000 | 0.21245
GEN-2024-206 | 03 CENTRAL | TBD | ERIS | Rebuild line 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | Current Study | 4.5 | (837.00, 837.00) | 1501120.066 | 22.2388 | 6750000 | 0.32597
GEN-2024-206 | 03 CENTRAL | TBD | ERIS | Rebuild line 543085 COURTNY2 69 548802 SUB H 69 1 | Current Study | 2.57 | (69.00, 69.00) | 497541.3944 | 22.776 | 2184500 | 0.012466
GEN-2024-206 | 03 CENTRAL | TBD | ERIS | Rebuild line 543164 SUGRCK_TP_W2 69 543165 SUGRCK_TP_E2 69 1 | Current Study | 0.1 | (69.00, 69.00) | 19230.8031 | 22.6245 | 85000 | 0.013281
GEN-2024-206 | 03 CENTRAL | TBD | ERIS | Rebuild line 548802 SUB H 69 548806 BLUVLY 69 1 | Current Study | 3.8 | (106.00, 106.00) | 732347.1336 | 22.6733 | 3230000 | 0.013757
GEN-2024-206 | 03 CENTRAL | TBD | ERIS | Rebuild line 548802 SUB H 69 548815 SUB M 69 1 | Current Study | 1.1 | (106.00, 106.00) | 212483.607 | 22.7255 | 935000 | 0.011989
GEN-2024-206 | 03 CENTRAL | TBD | ERIS | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | Current Study | 45.48 | (1793.00, 1793.00) | 2464094.701 | 2.4627 | 100056000 | 0.028667
GEN-2024-207 | 03 CENTRAL | TBD | ERIS | Add line 543004 BLUMILS5 161 548808 ECKLES-161 161 M2 | Current Study | 6.5 | (837.00, 837.00) | 15435595.0652 | 77.7612 | 19850000 | 0.19582
GEN-2024-207 | 03 CENTRAL | TBD | ERIS | Add line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 M2 | Current Study | 0.2 | (837.00, 837.00) | 6620000 | 100 | 6620000 | 0.39546
GEN-2024-207 | 03 CENTRAL | TBD | ERIS | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2 | Current Study | 6.85 | (837.00, 837.00) | 15921392.0963 | 77.3446 | 20585000 | 0.30423
GEN-2024-207 | 03 CENTRAL | TBD | ERIS | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2 | Current Study | 4.34 | (837.00, 837.00) | 11844409.1583 | 77.3437 | 15314000 | 0.30852
GEN-2024-207 | 03 CENTRAL | TBD | ERIS | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2 | Current Study | 0.75 | (2390.00, 2390.00) | 426500.7627 | 2.3994 | 17775000 | 0.016903
GEN-2024-207 | 03 CENTRAL | 171669 | ERIS | Blue Valley - Blumil 161 kV Line GEN-2024-207 Interconnection (Non-Shared NU) (INDN) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-207 | 03 CENTRAL | 171668 | ERIS | Blue Valley - Blumil 161 kV Line GEN-2024-207 Interconnection (TOIF) (INDN) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-207 | 03 CENTRAL | 900341 | ERIS | Line - Crosstown - Blue Valley Station 161 kV New Line.idv : 2025 ITP upgrade, PID : 900341, NO NTC | Current Study |  |  | 16749460.8387 | 77.3933 | 21642007.43 | 0.064181
GEN-2024-207 | 03 CENTRAL | TBD | ERIS | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | Current Study |  | (215.00, 215.00) | 4697294.3348 | 77.3217 | 6075000 | 0.025486
GEN-2024-207 | 03 CENTRAL | TBD | ERIS | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | Current Study |  | (221.00, 221.00) | 4697294.3348 | 77.3217 | 6075000 | 0.026184
GEN-2024-207 | 03 CENTRAL | TBD | ERIS | Rebuild 2-winding transformer 548814 SUB M-161 161 548815 SUB M 69 1 | Current Study |  | (169.00, 169.00) | 4694486.6477 | 77.2755 | 6075000 | 0.008589
GEN-2024-207 | 03 CENTRAL | TBD | ERIS | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | Current Study | 6.07 | (364.00, 364.00) | 7090515.7512 | 77.875 | 9105000 | 0.078708
GEN-2024-207 | 03 CENTRAL | TBD | ERIS | Rebuild line 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 | Current Study | 3.09 | (551.00, 551.00) | 3603290.9513 | 77.7409 | 4635000 | 0.21566
GEN-2024-207 | 03 CENTRAL | TBD | ERIS | Rebuild line 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | Current Study | 4.5 | (837.00, 837.00) | 5248879.934 | 77.7612 | 6750000 | 0.33128
GEN-2024-207 | 03 CENTRAL | TBD | ERIS | Rebuild line 543085 COURTNY2 69 548802 SUB H 69 1 | Current Study | 2.57 | (69.00, 69.00) | 1686958.6056 | 77.224 | 2184500 | 0.012285
GEN-2024-207 | 03 CENTRAL | TBD | ERIS | Rebuild line 543164 SUGRCK_TP_W2 69 543165 SUGRCK_TP_E2 69 1 | Current Study | 0.1 | (69.00, 69.00) | 65769.1969 | 77.3755 | 85000 | 0.013201
GEN-2024-207 | 03 CENTRAL | TBD | ERIS | Rebuild line 548802 SUB H 69 548806 BLUVLY 69 1 | Current Study | 3.8 | (106.00, 106.00) | 2497652.8664 | 77.3267 | 3230000 | 0.013637
GEN-2024-207 | 03 CENTRAL | TBD | ERIS | Rebuild line 548802 SUB H 69 548815 SUB M 69 1 | Current Study | 1.1 | (106.00, 106.00) | 722516.393 | 77.2745 | 935000 | 0.011849
GEN-2024-207 | 03 CENTRAL | TBD | ERIS | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | Current Study | 45.48 | (1793.00, 1793.00) | 8477208.3974 | 8.4725 | 100056000 | 0.028665
GEN-2024-211 | 02 NEBRASKA | 900426 | ERIS | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030 | Contingent |  |  | 0 | 0 | 2372127948.71 | N/A
GEN-2024-211 | 02 NEBRASKA | TBD | ERIS | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV | Current Study |  |  | 16807.6503 | 1.2179 | 1380000 | 0.039294
GEN-2024-211 | 02 NEBRASKA | TBD | ERIS | Add 2 MVAR switched shunt at GEN-2017-140 345 kV | Current Study |  |  | 53411.3748 | 1.0078 | 5300000 | 0.03805
GEN-2024-211 | 02 NEBRASKA | TBD | ERIS | Add 23 MVAR switched shunt at FINNEY 7 345 kV | Current Study |  |  | 190291.2747 | 3.5904 | 5300000 | 0.039294
GEN-2024-211 | 02 NEBRASKA | 94788 | ERIS | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030 | Contingent |  |  | 0 | 0 | 106000000 | N/A
GEN-2024-211 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | Current Study | 45.48 | (1793.00, 1793.00) | 5982902.986 | 5.9796 | 100056000 | 0.051985
GEN-2024-211 | 02 NEBRASKA | TBD | ERIS | Rebuild line 645454 S3454 3 345 645455 S3455 3 345 1 | Current Study | 6.67 | (1793.00, 1793.00) | 28489.4307 | 0.19415 | 14674000 | 0.0008572
GEN-2024-211 | 02 NEBRASKA | TBD | ERIS | Rebuild line 645454 S3454 3 345 645740 S3740 3 345 1 | Current Study | 23.26 | (2390.00, 2390.00) | 16050844.7205 | 31.3665 | 51172000 | 0.25735
GEN-2024-211 | 02 NEBRASKA | TBD | ERIS | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1 | Current Study | 20.15 | (2390.00, 2390.00) | 13904751.5528 | 31.3665 | 44330000 | 0.2867
GEN-2024-211 | 02 NEBRASKA | TBD | ERIS | Rebuild line 646221 S1221 5 161 646231 S1231 5 161 1 | Current Study | 2.06 | (364.00, 364.00) | 969223.6025 | 31.3665 | 3090000 | 0.021396
GEN-2024-211 | 02 NEBRASKA | TBD | ERIS | Rebuild line 646259 S1259 5 161 646278 S1278 5 161 1 | Current Study | 2.61 | (246.00, 246.00) | 1227996.8944 | 31.3665 | 3915000 | 0.015463
GEN-2024-211 | 02 NEBRASKA | 171675 | ERIS | Substation 3740 345 kV GEN-2024-211 Interconnection (Non-Shared NU) (OPPD) | Interconnection |  |  | 2000000 | 100 | 2000000 | 1
GEN-2024-211 | 02 NEBRASKA | 171674 | ERIS | Substation 3740 345 kV GEN-2024-211 Interconnection (TOIF) (OPPD) | Interconnection |  |  | 1900000 | 100 | 1900000 | 1
GEN-2024-212 | 02 NEBRASKA | 900426 | ERIS | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030 | Contingent |  |  | 0 | 0 | 2372127948.71 | N/A
GEN-2024-212 | 02 NEBRASKA | TBD | ERIS | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV | Current Study |  |  | 16807.6503 | 1.2179 | 1380000 | 0.039294
GEN-2024-212 | 02 NEBRASKA | TBD | ERIS | Add 2 MVAR switched shunt at GEN-2017-140 345 kV | Current Study |  |  | 53411.3748 | 1.0078 | 5300000 | 0.03805
GEN-2024-212 | 02 NEBRASKA | TBD | ERIS | Add 23 MVAR switched shunt at FINNEY 7 345 kV | Current Study |  |  | 190291.2747 | 3.5904 | 5300000 | 0.039294
GEN-2024-212 | 02 NEBRASKA | 94788 | ERIS | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030 | Contingent |  |  | 0 | 0 | 106000000 | N/A
GEN-2024-212 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | Current Study | 45.48 | (1793.00, 1793.00) | 5982902.986 | 5.9796 | 100056000 | 0.051985
GEN-2024-212 | 02 NEBRASKA | TBD | ERIS | Rebuild line 645454 S3454 3 345 645455 S3455 3 345 1 | Current Study | 6.67 | (1793.00, 1793.00) | 28489.4307 | 0.19415 | 14674000 | 0.0008572
GEN-2024-212 | 02 NEBRASKA | TBD | ERIS | Rebuild line 645454 S3454 3 345 645740 S3740 3 345 1 | Current Study | 23.26 | (2390.00, 2390.00) | 16050844.7205 | 31.3665 | 51172000 | 0.25735
GEN-2024-212 | 02 NEBRASKA | TBD | ERIS | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1 | Current Study | 20.15 | (2390.00, 2390.00) | 13904751.5528 | 31.3665 | 44330000 | 0.2867
GEN-2024-212 | 02 NEBRASKA | TBD | ERIS | Rebuild line 646221 S1221 5 161 646231 S1231 5 161 1 | Current Study | 2.06 | (364.00, 364.00) | 969223.6025 | 31.3665 | 3090000 | 0.021396
GEN-2024-212 | 02 NEBRASKA | TBD | ERIS | Rebuild line 646259 S1259 5 161 646278 S1278 5 161 1 | Current Study | 2.61 | (246.00, 246.00) | 1227996.8944 | 31.3665 | 3915000 | 0.015463
GEN-2024-212 | 02 NEBRASKA | 171677 | ERIS | Substation 3740 345 kV GEN-2024-212 Interconnection (Non-Shared NU) (OPPD) | Interconnection |  |  | 2000000 | 100 | 2000000 | 1
GEN-2024-212 | 02 NEBRASKA | 171676 | ERIS | Substation 3740 345 kV GEN-2024-212 Interconnection (TOIF) (OPPD) | Interconnection |  |  | 1900000 | 100 | 1900000 | 1
GEN-2024-213 | 02 NEBRASKA | 900426 | ERIS | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030 | Contingent |  |  | 0 | 0 | 2372127948.71 | N/A
GEN-2024-213 | 02 NEBRASKA | TBD | ERIS | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV | Current Study |  |  | 19969.4855 | 1.4471 | 1380000 | 0.039294
GEN-2024-213 | 02 NEBRASKA | TBD | ERIS | Add 2 MVAR switched shunt at GEN-2017-140 345 kV | Current Study |  |  | 63459.0591 | 1.1973 | 5300000 | 0.03805
GEN-2024-213 | 02 NEBRASKA | TBD | ERIS | Add 23 MVAR switched shunt at FINNEY 7 345 kV | Current Study |  |  | 226088.6433 | 4.2658 | 5300000 | 0.039294
GEN-2024-213 | 02 NEBRASKA | 94788 | ERIS | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030 | Contingent |  |  | 0 | 0 | 106000000 | N/A
GEN-2024-213 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | Current Study | 45.48 | (1793.00, 1793.00) | 7108399.5874 | 7.1044 | 100056000 | 0.051985
GEN-2024-213 | 02 NEBRASKA | TBD | ERIS | Rebuild line 645454 S3454 3 345 645455 S3455 3 345 1 | Current Study | 6.67 | (1793.00, 1793.00) | 33848.8286 | 0.23067 | 14674000 | 0.0008572
GEN-2024-213 | 02 NEBRASKA | TBD | ERIS | Rebuild line 645454 S3454 3 345 645740 S3740 3 345 1 | Current Study | 23.26 | (2390.00, 2390.00) | 19070310.559 | 37.2671 | 51172000 | 0.25735
GEN-2024-213 | 02 NEBRASKA | TBD | ERIS | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1 | Current Study | 20.15 | (2390.00, 2390.00) | 16520496.8944 | 37.2671 | 44330000 | 0.2867
GEN-2024-213 | 02 NEBRASKA | TBD | ERIS | Rebuild line 646221 S1221 5 161 646231 S1231 5 161 1 | Current Study | 2.06 | (364.00, 364.00) | 1151552.795 | 37.2671 | 3090000 | 0.021396
GEN-2024-213 | 02 NEBRASKA | TBD | ERIS | Rebuild line 646259 S1259 5 161 646278 S1278 5 161 1 | Current Study | 2.61 | (246.00, 246.00) | 1459006.2112 | 37.2671 | 3915000 | 0.015463
GEN-2024-213 | 02 NEBRASKA | 171679 | ERIS | Substation 3740 345 kV GEN-2024-213 Interconnection (Non-Shared NU) (OPPD) | Interconnection |  |  | 2000000 | 100 | 2000000 | 1
GEN-2024-213 | 02 NEBRASKA | 171678 | ERIS | Substation 3740 345 kV GEN-2024-213 Interconnection (TOIF) (OPPD) | Interconnection |  |  | 1900000 | 100 | 1900000 | 1
GEN-2024-215 | 03 CENTRAL | 94615 | ERIS | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029 | Contingent |  |  | 0 | 0 | 543515503 | N/A
GEN-2024-215 | 03 CENTRAL | 94911 | ERIS | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030 | Contingent |  |  | 0 | 0 | 143524375 | N/A
GEN-2024-215 | 03 CENTRAL | TBD | ERIS | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV | Current Study |  |  | 17622.9999 | 1.277 | 1380000 | 0.041613
GEN-2024-215 | 03 CENTRAL | TBD | ERIS | Add 3-winding transformer 539657 CONCORD3 115 539658 CONCRD6 230 539904 CONCOD-1 13 M2 | Current Study |  | (205.00, 225.50) | 6414321.7068 | 46.4806 | 13800000 | 0.0231
GEN-2024-215 | 03 CENTRAL | TBD | ERIS | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2 | Current Study | 0.75 | (2390.00, 2390.00) | 135086.9634 | 0.75998 | 17775000 | 0.013894
GEN-2024-215 | 03 CENTRAL | 94721 | ERIS | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 213682884 | N/A
GEN-2024-215 | 03 CENTRAL | 94929 | ERIS | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 413934522 | N/A
GEN-2024-215 | 03 CENTRAL | 171681 | ERIS | Elm Creek 345 kV Substation GEN-2024-215 Interconnection (Non-Shared NU) (ITCGP) | Interconnection |  |  | 1856969 | 100 | 1856969 | 1
GEN-2024-215 | 03 CENTRAL | 171680 | ERIS | Elm Creek 345 kV Substation GEN-2024-215 Interconnection (TOIF) (ITCGP) | Interconnection |  |  | 1306438 | 100 | 1306438 | 1
GEN-2024-215 | 03 CENTRAL | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 1190551.3039 | 1.2668 | 93984000 | 0.026998
GEN-2024-215 | 03 CENTRAL | TBD | NRIS | Rebuild line 539656 CLIFTON3 115 539657 CONCORD3 115 1 | Current Study | 23.19 | (176.00, 176.00) | 10685743.529 | 46.0791 | 23190000 | 0.024715
GEN-2024-215 | 03 CENTRAL | TBD | ERIS | Rebuild line 640277 MOORE 3 345 640525 TOBIAS 3 345 1 | Current Study | 26.47 | (1793.00, 1793.00) | 23663129.8234 | 40.6346 | 58234000 | 0.2225
GEN-2024-215 | 03 CENTRAL | TBD | NRIS | Rebuild line 645454 S3454 3 345 650185 WAGENER 3 345 1 | Current Study | 33.67 | (1793.00, 1793.00) | 3277334.0401 | 4.4244 | 74074000 | 0.065757
GEN-2024-215 | 03 CENTRAL | TBD | NRIS | Rebuild line 650185 WAGENER 3 345 650189 103&ROKEBY3 345 1 | Current Study | 9.45 | (1793.00, 1793.00) | 812596.0581 | 3.9086 | 20790000 | 0.02734
GEN-2024-219 | 04 SOUTHEAST | 94615 | ERIS | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029 | Contingent |  |  | 0 | 0 | 543515503 | N/A
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 279299.8207 | 5.2698 | 5300000 | 0.028529
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at MOUND 4 138 kV | Current Study |  |  | 65431.4978 | 2.6899 | 2432500 | 0.041132
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV | Current Study |  |  | 188348.3866 | 3.5537 | 5300000 | 0.033485
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 40730.6215 | 1.6744 | 2432500 | 0.038086
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 10904.8985 | 0.79021 | 1380000 | 0.034522
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 107711.4037 | 2.0323 | 5300000 | 0.038906
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 11 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 72827.2842 | 2.2408 | 3250000 | 0.031781
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 234940.9772 | 1.9578 | 12000000 | 0.038906
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR switched shunt at NEOSHO 4 138 kV | Current Study |  |  | 20897.1749 | 0.85908 | 2432500 | 0.025636
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at CPK446 5 161 kV | Current Study |  |  | 55280.2951 | 1.7009 | 3250000 | 0.031781
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR switched shunt at WICHITA7 345 kV | Current Study |  |  | 105787.7468 | 1.996 | 5300000 | 0.041132
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 177 MVAR switched shunt at SWISVAL7 345 kV | Current Study |  |  | 111163.7594 | 2.0974 | 5300000 | 0.025521
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 20 MVAR switched shunt at LIBERTY4 138 kV | Current Study |  |  | 45686.9085 | 1.8782 | 2432500 | 0.038086
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 24 MVAR switched shunt at GROVE 4 138 kV | Current Study |  |  | 28246.7051 | 1.1612 | 2432500 | 0.025636
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 280 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 294196.2977 | 2.4516 | 12000000 | 0.053109
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 295 MVAR switched shunt at G18-128-TAP 345 kV | Current Study |  |  | 131008.9788 | 2.4719 | 5300000 | 0.044717
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 3 MVAR switched shunt at NEOSHOS2 69 kV | Current Study |  |  | 43450.0627 | 3.1486 | 1380000 | 0.044717
GEN-2024-219 | 04 SOUTHEAST | TBD | NRIS | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV | Current Study |  |  | 10611.1202 | 0.46135 | 2300000 | 0.030181
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at G23-220-TAP 345 kV | Current Study |  |  | 179819.8172 | 3.3928 | 5300000 | 0.028529
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at INDEPCO5 161 kV | Current Study |  |  | 72827.2842 | 2.2408 | 3250000 | 0.031781
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 66049.4456 | 2.0323 | 3250000 | 0.038906
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 45 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 316842.922 | 2.6404 | 12000000 | 0.044717
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 45 MVAR switched shunt at NEVADA 5 161 kV | Current Study |  |  | 60991.4659 | 1.8767 | 3250000 | 0.025521
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add 56 MVAR switched shunt at WHARV4 138 kV | Current Study |  |  | 65431.4978 | 2.6899 | 2432500 | 0.041132
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Add line 515012 RVRVALY7 345 780360 G24-113-TAP 345 P2 | Current Study | 23.28 | (1195.00, 1195.00) | 1579579.0452 | 1.9224 | 82168000 | 0.016481
GEN-2024-219 | 04 SOUTHEAST | 94721 | ERIS | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 213682884 | N/A
GEN-2024-219 | 04 SOUTHEAST | 94929 | ERIS | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 413934522 | N/A
GEN-2024-219 | 04 SOUTHEAST | 171687 | ERIS | Chigley - Oaklawn 138 kV Line GEN-2024-219 Interconnection (Non-Shared NU) (OGE) | Interconnection |  |  | 7000000 | 100 | 7000000 | 1
GEN-2024-219 | 04 SOUTHEAST | 171686 | ERIS | Chigley - Oaklawn 138 kV Line GEN-2024-219 Interconnection (TOIF) (OGE) | Interconnection |  |  | 2000000 | 100 | 2000000 | 1
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508359 WELSH 7 345 508841 WILKES 7 345 1 | Current Study | 30.63 | (1793.00, 1793.00) | 1504769.6449 | 2.2331 | 67386000 | 0.018405
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | Current Study | 21.38 | (1793.00, 1793.00) | 1455855.636 | 3.0952 | 47036000 | 0.060256
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 731705.0554 | 2.1781 | 33594000 | 0.049637
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 128703.697 | 1.1038 | 11660000 | 0.038043
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Current Study | 14.6 | (1793.00, 1793.00) | 699600.1184 | 2.1781 | 32120000 | 0.049637
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514715 WOODRNG7 345 515875 REDNGTN7 345 1 | Current Study | 19.2 | (1793.00, 1793.00) | 1731458.0805 | 4.0991 | 42240000 | 0.070907
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515055 MAUD 4 138 787770 G24-360-TAP 138 1 | Current Study | 5.11 | (395.00, 395.00) | 518041.6625 | 8.4482 | 6132000 | 0.037427
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 1870908.5652 | 4.0748 | 45914000 | 0.053338
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 894705.7804 | 0.95198 | 93984000 | 0.038043
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Current Study | 25.29 | (2390.00, 2390.00) | 1633754.1511 | 2.9364 | 55638000 | 0.044877
GEN-2024-219 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 1021066.0545 | 4.0748 | 25058000 | 0.053338
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 25021.8741 | 1.8132 | 1380000 | 0.07311
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at PHILL 7 345 kV | Current Study |  |  | 145490.0991 | 2.7451 | 5300000 | 0.032514
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 31089.0081 | 0.58659 | 5300000 | 0.032668
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV | Current Study |  |  | 25021.8741 | 1.8132 | 1380000 | 0.07311
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 0.2 MVAR switched shunt at GROVE 5 161 kV | Current Study |  |  | 31612.4513 | 0.97269 | 3250000 | 0.057691
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 0.25 MVAR switched shunt at LABETTS2 69 kV | Current Study |  |  | 14558.8805 | 1.055 | 1380000 | 0.057691
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 11 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 57589.4399 | 1.772 | 3250000 | 0.07311
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 67811.5938 | 0.5651 | 12000000 | 0.032668
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR switched shunt at NEOSHO 4 138 kV | Current Study |  |  | 20485.6019 | 0.84216 | 2432500 | 0.07311
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at CPK446 5 161 kV | Current Study |  |  | 43713.8535 | 1.345 | 3250000 | 0.07311
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 24 MVAR switched shunt at GROVE 4 138 kV | Current Study |  |  | 27690.3819 | 1.1384 | 2432500 | 0.07311
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV | Current Study |  |  | 16513.0276 | 1.1966 | 1380000 | 0.055334
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at INDEPCO5 161 kV | Current Study |  |  | 57589.4399 | 1.772 | 3250000 | 0.07311
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 19064.0144 | 0.58659 | 3250000 | 0.032668
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Add 45 MVAR switched shunt at NEVADA 5 161 kV | Current Study |  |  | 26837.6488 | 0.82577 | 3250000 | 0.032668
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | Current Study | 14.95 | (329.00, 329.00) | 617777.6056 | 4.1323 | 14950000 | 0.039232
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508055 BLOOMBG2 69 783570 G24-220-TAP 69 1 | Current Study | 1.23 | (69.00, 69.00) | 1045500 | 100 | 1045500 | 0.69641
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508804 HOSSTON2 69 508846 GODFREYRDTP2 69 1 | Current Study | 8.6 | (69.00, 69.00) | 4825450.0956 | 66.0116 | 7310000 | 0.30359
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508814 RODESSA2 69 508846 GODFREYRDTP2 69 1 | Current Study | 0.28 | (69.00, 69.00) | 157107.6775 | 66.0116 | 238000 | 0.30359
GEN-2024-220 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508814 RODESSA2 69 783570 G24-220-TAP 69 1 | Current Study | 10.34 | (69.00, 69.00) | 5801762.0917 | 66.0116 | 8789000 | 0.30359
GEN-2024-220 | 04 SOUTHEAST | 171689 | ERIS | Rodessa - Bloomberg 69 kV Line GEN-2024-220 Interconnection (Non-Shared NU) (AEP) | Interconnection |  |  | 16475000 | 100 | 16475000 | 1
GEN-2024-220 | 04 SOUTHEAST | 171688 | ERIS | Rodessa - Bloomberg 69 kV Line GEN-2024-220 Interconnection (TOIF) (AEP) | Interconnection |  |  | 3475000 | 100 | 3475000 | 1
GEN-2024-221 | 05 SOUTHWEST | 171691 | ERIS | 345 kV Crossroads - Eddy County 345 kV Line GEN-2024-221 Interconnection (Non-Shared NU) (SPS) | Interconnection |  |  | 45536712.63 | 100 | 45536712.63 | 1
GEN-2024-221 | 05 SOUTHWEST | 171690 | ERIS | 345 kV Crossroads - Eddy County 345 kV Line GEN-2024-221 Interconnection (TOIF) (SPS) | Interconnection |  |  | 4872126.25 | 100 | 4872126.25 | 1
GEN-2024-221 | 05 SOUTHWEST | 94067 | ERIS | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028 | Contingent |  |  | 0 | 0 | 38846321 | N/A
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 75092.9274 | 5.4415 | 1380000 | 0.095089
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV | Current Study |  |  | 48961.5797 | 3.5479 | 1380000 | 0.086708
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Add 1.6 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 45177.9774 | 3.2738 | 1380000 | 0.061249
GEN-2024-221 | 05 SOUTHWEST | TBD | NRIS | Add 11 MVAR switched shunt at WWRDEHV4 138 kV | Current Study |  |  | 158479.0817 | 6.5151 | 2432500 | 0.061041
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 77316.2969 | 5.6026 | 1380000 | 0.1225
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV | Current Study |  |  | 77316.2969 | 5.6026 | 1380000 | 0.1225
GEN-2024-221 | 05 SOUTHWEST | TBD | NRIS | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV | Current Study |  |  | 101987.0633 | 4.4342 | 2300000 | 0.11603
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Add 3.6 MVAR switched shunt at HEDLEY 2 69 kV | Current Study |  |  | 88065.6511 | 6.3816 | 1380000 | 0.0029375
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2 | Current Study |  | (339.00, 330.00) | 947902.8648 | 6.7707 | 14000000 | 0.024086
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Add line 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 P2 | Current Study | 66.8 | (1011.00, 1176.00) | 12167306.0627 | 5.605 | 217080000 | 0.06154
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Apply contingent IDV 01_NewLine_Phantom_Crossroads_Potter_765_26SP.idv | Contingent |  |  | 0 | 0 | 3275253469 | N/A
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Apply contingent IDV 02_765_Phantom_Craw_1_DIS24_TC05ALL-26SP.idv | Contingent |  |  | 0 | 0 | 1366342009.82 | N/A
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Apply contingent IDV 02_765_Phantom_Craw_1_DIS24_TC05ALL-29SP.idv | Contingent |  |  | 0 | 0 | 1366342009.82 | N/A
GEN-2024-221 | 05 SOUTHWEST | 900427 | ERIS | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032 | Contingent |  |  | 0 | 0 | 1790026304.1702 | N/A
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | Current Study | 18.75 | (519.00, 519.00) | 2412074.2541 | 6.7707 | 35625000 | 0.048172
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 511541 DEMPSEYR POI 230 511557 CHISHOLM6 230 1 | Current Study | 11.15 | (519.00, 519.00) | 4311525.6955 | 20.3518 | 21185000 | 0.041015
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Current Study | 57.98 | (1793.00, 1793.00) | 7146387.1254 | 5.6025 | 127556000 | 0.12249
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523959 POTTER_CO 6 230 524010 ROLLHILLS 6 230 1 | Current Study | 6.23 | (637.00, 637.00) | 2192851.3721 | 18.5254 | 11837000 | 0.04495
GEN-2024-221 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | Current Study | 3.02 | (1793.00, 1793.00) | 207540.0402 | 3.1237 | 6644000 | 0.072014
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 126535.093 | 9.1692 | 1380000 | 0.081337
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at PHILL 7 345 kV | Current Study |  |  | 817257.6549 | 15.42 | 5300000 | 0.04018
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV | Current Study |  |  | 126535.093 | 9.1692 | 1380000 | 0.081337
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Add 0.2 MVAR switched shunt at GROVE 5 161 kV | Current Study |  |  | 149259.7071 | 4.5926 | 3250000 | 0.059926
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Add 0.25 MVAR switched shunt at LABETTS2 69 kV | Current Study |  |  | 68740.4534 | 4.9812 | 1380000 | 0.059926
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Add 11 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 291228.5912 | 8.9609 | 3250000 | 0.081337
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR switched shunt at NEOSHO 4 138 kV | Current Study |  |  | 103595.2596 | 4.2588 | 2432500 | 0.081337
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at CPK446 5 161 kV | Current Study |  |  | 221060.0413 | 6.8018 | 3250000 | 0.081337
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Add 24 MVAR switched shunt at GROVE 4 138 kV | Current Study |  |  | 140029.6813 | 5.7566 | 2432500 | 0.081337
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV | Current Study |  |  | 519676.7154 | 37.6577 | 1380000 | 0.38311
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at INDEPCO5 161 kV | Current Study |  |  | 291228.5912 | 8.9609 | 3250000 | 0.081337
GEN-2024-232 | 04 SOUTHEAST | 171703 | ERIS | Crockett - Rocky Creek 345 kV line GEN-2024-232 Interconnection (Non-Shared NU) (AEP) | Interconnection |  |  | 28225000 | 100 | 28225000 | 1
GEN-2024-232 | 04 SOUTHEAST | 171702 | ERIS | Crockett - Rocky Creek 345 kV line GEN-2024-232 Interconnection (TOIF) (AEP) | Interconnection |  |  | 5225000 | 100 | 5225000 | 1
GEN-2024-232 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 334197 7ROCKYCRK% 345 783930 G24-232-TAP 345 1 | Current Study | 45.65 | (1793.00, 1793.00) | 100430000 | 100 | 100430000 | 0.38309
GEN-2024-234 | 02 NEBRASKA | TBD | NRIS | Add 108 MVAR switched shunt at MAURINE4 230 kV | Current Study |  |  | 190152.0635 | 4.9713 | 3825000 | 0.034377
GEN-2024-234 | 02 NEBRASKA | TBD | NRIS | Add 12 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 122880.0164 | 5.5539 | 2212500 | 0.034377
GEN-2024-234 | 02 NEBRASKA | TBD | NRIS | Add 154 MVAR SVC at WAYSIDE 4 230 kV | Current Study |  |  | 288751.0064 | 3.3576 | 8600000 | 0.030965
GEN-2024-234 | 02 NEBRASKA | TBD | NRIS | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 46979.9984 | 2.1234 | 2212500 | 0.034377
GEN-2024-234 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 652305 SIOUXC29 13 652552 SIOUXCY2 230 652564 SIOUXCY3 345 M2 | Current Study |  | (600.00, 750.00) | 1222928.866 | 4.8917 | 25000000 | 0.0011668
GEN-2024-234 | 02 NEBRASKA | TBD | NRIS | Add 45 MVAR switched shunt at PR BRZ 4 230 kV | Current Study |  |  | 58991.4489 | 1.5423 | 3825000 | 0.026477
GEN-2024-234 | 02 NEBRASKA | 171705 | ERIS | Raun - Tekamah 161 kV line GEN-2024-234 Interconnection (Non-Shared NU) (OPPD) | Interconnection |  |  | 350000 | 100 | 350000 | 1
GEN-2024-234 | 02 NEBRASKA | 171704 | ERIS | Raun - Tekamah 161 kV line GEN-2024-234 Interconnection (TOIF) (OPPD) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-234 | 02 NEBRASKA | TBD | NRIS | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | Current Study | 23.48 | (1793.00, 1793.00) | 3807661.3279 | 7.3712 | 51656000 | 0.060217
GEN-2024-234 | 02 NEBRASKA | TBD | ERIS | Rebuild line 635201 RAUN 5 161 646300 S1300 5 161 1 | Current Study | 34.12 | (309.00, 309.00) | 51180000 | 100 | 51180000 | 0.36952
GEN-2024-234 | 02 NEBRASKA | TBD | ERIS | Rebuild line 640377 TEKAMAH5 161 646300 S1300 5 161 1 | Current Study | 2.97 | (309.00, 309.00) | 4455000 | 100 | 4455000 | 0.63048
GEN-2024-234 | 02 NEBRASKA | TBD | ERIS | Rebuild line 647424 FREM D 8 69 647976 S976 8 69 1 | Current Study | 0.06 | (140.00, 140.00) | 3545.2731 | 6.9515 | 51000 | 0.022893
GEN-2024-234 | 02 NEBRASKA | TBD | NRIS | Rebuild line 652552 SIOUXCY2 230 659900 EAGLE___-NI4 230 1 | Current Study | 33.29 | (519.00, 519.00) | 30357987.503 | 47.9961 | 63251000 | 0.024931
GEN-2024-235 | 04 SOUTHEAST | 94615 | ERIS | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029 | Contingent |  |  | 0 | 0 | 543515503 | N/A
GEN-2024-235 | 04 SOUTHEAST | 94811 | ERIS | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030 | Contingent |  |  | 0 | 0 | 1097029189 | N/A
GEN-2024-235 | 04 SOUTHEAST | 94911 | ERIS | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030 | Contingent |  |  | 0 | 0 | 143524375 | N/A
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 309740.4097 | 5.8442 | 5300000 | 0.020249
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at JAY 4 138 kV | Current Study |  |  | 131654.7102 | 5.4123 | 2432500 | 0.027917
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at MOUND 4 138 kV | Current Study |  |  | 112167.3574 | 4.6112 | 2432500 | 0.045127
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV | Current Study |  |  | 279966.7557 | 5.2824 | 5300000 | 0.031855
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 76002.3856 | 3.1245 | 2432500 | 0.045484
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 0.04 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 299667.1675 | 9.2205 | 3250000 | 0.023955
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 0.09 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 132553.155 | 4.0786 | 3250000 | 0.034333
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 0.09 MVAR switched shunt at SWISVAL6 230 kV | Current Study |  |  | 264282.4809 | 6.9093 | 3825000 | 0.020249
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 0.11 MVAR switched shunt at CHAMSPR7 345 kV | Current Study |  |  | 286853.0171 | 5.4123 | 5300000 | 0.027917
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 168240.7646 | 3.1744 | 5300000 | 0.038893
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 0.2 MVAR switched shunt at GROVE 5 161 kV | Current Study |  |  | 59664.5314 | 1.8358 | 3250000 | 0.023955
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 0.25 MVAR switched shunt at LABETTS2 69 kV | Current Study |  |  | 39382.3383 | 2.8538 | 1380000 | 0.034333
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at TONTITN7 345 kV | Current Study |  |  | 279642.2638 | 5.2763 | 5300000 | 0.027917
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at RSS T1 4 138 kV | Current Study |  |  | 767543.2489 | 31.5537 | 2432500 | 0.040055
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 14 MVAR switched shunt at T.P.S.-2 69 kV | Current Study |  |  | 435440.7743 | 31.5537 | 1380000 | 0.040055
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 15 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 132553.155 | 4.0786 | 3250000 | 0.034333
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 369220.9145 | 3.0768 | 12000000 | 0.039132
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR switched shunt at NEOSHO 4 138 kV | Current Study |  |  | 43727.8306 | 1.7976 | 2432500 | 0.034333
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at CPK446 5 161 kV | Current Study |  |  | 65104.7746 | 2.0032 | 3250000 | 0.023955
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV | Current Study |  |  | 132729.4738 | 4.084 | 3250000 | 0.034333
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR switched shunt at WICHITA7 345 kV | Current Study |  |  | 217050.3811 | 4.0953 | 5300000 | 0.054011
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 177 MVAR switched shunt at SWISVAL7 345 kV | Current Study |  |  | 137812.5098 | 2.6002 | 5300000 | 0.020249
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 2 MVAR switched shunt at CLIFTON3 115 kV | Current Study |  |  | 19251.6631 | 0.87013 | 2212500 | 0.0013462
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 20 MVAR switched shunt at LIBERTY4 138 kV | Current Study |  |  | 85250.7012 | 3.5047 | 2432500 | 0.045484
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 132729.4738 | 4.084 | 3250000 | 0.034333
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR switched shunt at STILWEL7 345 kV | Current Study |  |  | 300156.0821 | 5.6633 | 5300000 | 0.033496
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 24 MVAR switched shunt at GROVE 4 138 kV | Current Study |  |  | 59106.8956 | 2.4299 | 2432500 | 0.034333
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at G21-096-TAP 345 kV | Current Study |  |  | 240063.6185 | 4.5295 | 5300000 | 0.021984
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 280 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 980898.1887 | 8.1742 | 12000000 | 0.11333
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 295 MVAR switched shunt at G18-128-TAP 345 kV | Current Study |  |  | 518775.7867 | 9.7882 | 5300000 | 0.11333
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 3 MVAR switched shunt at NEOSHOS2 69 kV | Current Study |  |  | 1184.6543 | 0.085845 | 1380000 | 0.00078029
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at G23-220-TAP 345 kV | Current Study |  |  | 252569.0032 | 4.7655 | 5300000 | 0.025646
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 316 MVAR switched shunt at W.GRDNR7 345 kV | Current Study |  |  | 300156.0821 | 5.6633 | 5300000 | 0.033496
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 103166.5066 | 3.1744 | 3250000 | 0.038893
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 45 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 1254650.1599 | 10.4554 | 12000000 | 0.11333
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 45 MVAR switched shunt at NEVADA 5 161 kV | Current Study |  |  | 145234.1784 | 4.4687 | 3250000 | 0.038893
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 375236.9519 | 7.0799 | 5300000 | 0.013964
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 56 MVAR switched shunt at WHARV4 138 kV | Current Study |  |  | 112167.3574 | 4.6112 | 2432500 | 0.045127
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV | Current Study |  |  | 60575.7388 | 4.3895 | 1380000 | 0.034333
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add 86 MVAR switched shunt at POSTROCK7 345 kV | Current Study |  |  | 814581.7402 | 15.3695 | 5300000 | 0.027189
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Add line 515012 RVRVALY7 345 780360 G24-113-TAP 345 P2 | Current Study | 23.28 | (1195.00, 1195.00) | 2094242.5058 | 2.5487 | 82168000 | 0.013984
GEN-2024-235 | 04 SOUTHEAST | 94721 | ERIS | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 213682884 | N/A
GEN-2024-235 | 04 SOUTHEAST | 94929 | ERIS | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 413934522 | N/A
GEN-2024-235 | 04 SOUTHEAST | 900427 | ERIS | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032 | Contingent |  |  | 0 | 0 | 1790026304.1702 | N/A
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 1731978.0003 | 5.1556 | 33594000 | 0.075195
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 240133.7255 | 2.0595 | 11660000 | 0.045427
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Current Study | 14.6 | (1793.00, 1793.00) | 1655984.2046 | 5.1556 | 32120000 | 0.075195
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 129241.8298 | 4.3516 | 2970000 | 0.05505
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 89123.1636 | 4.0511 | 2200000 | 0.05505
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 2309583.963 | 5.0302 | 45914000 | 0.04214
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | Current Study | 15.48 | (1793.00, 1793.00) | 5645601.8641 | 16.5774 | 34056000 | 0.070668
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 1669330.6979 | 1.7762 | 93984000 | 0.045427
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Current Study | 25.29 | (2390.00, 2390.00) | 6458299.0892 | 11.6077 | 55638000 | 0.11354
GEN-2024-235 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 1260477.3042 | 5.0302 | 25058000 | 0.04214
GEN-2024-235 | 04 SOUTHEAST | 171707 | ERIS | Sooner - Wekiwa 345 kV line GEN-2024-235 Interconnection (Non-Shared NU) (AEP) | Interconnection |  |  | 28225000 | 100 | 28225000 | 1
GEN-2024-235 | 04 SOUTHEAST | 171706 | ERIS | Sooner - Wekiwa 345 kV line GEN-2024-235 Interconnection (TOIF) (AEP) | Interconnection |  |  | 5225000 | 100 | 5225000 | 1
GEN-2024-236 | 04 SOUTHEAST | 94615 | ERIS | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029 | Contingent |  |  | 0 | 0 | 543515503 | N/A
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at MOUND 4 138 kV | Current Study |  |  | 80719.5951 | 3.3184 | 2432500 | 0.033632
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 58950.5386 | 4.2718 | 1380000 | 0.039244
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 53541.6486 | 2.2011 | 2432500 | 0.033183
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 0.09 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 117013.5394 | 3.6004 | 3250000 | 0.031387
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 130644.9444 | 2.465 | 5300000 | 0.031278
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV | Current Study |  |  | 58950.5386 | 4.2718 | 1380000 | 0.039244
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 0.2 MVAR switched shunt at GROVE 5 161 kV | Current Study |  |  | 78403.7732 | 2.4124 | 3250000 | 0.0326
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 0.25 MVAR switched shunt at LABETTS2 69 kV | Current Study |  |  | 36108.2775 | 2.6165 | 1380000 | 0.0326
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 11 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 135678.4264 | 4.1747 | 3250000 | 0.039244
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 15 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 117013.5394 | 3.6004 | 3250000 | 0.031387
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 284963.8002 | 2.3747 | 12000000 | 0.031278
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR switched shunt at NEOSHO 4 138 kV | Current Study |  |  | 38601.482 | 1.5869 | 2432500 | 0.031387
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at CPK446 5 161 kV | Current Study |  |  | 102988.0975 | 3.1689 | 3250000 | 0.039244
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV | Current Study |  |  | 117169.1877 | 3.6052 | 3250000 | 0.031387
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR switched shunt at WICHITA7 345 kV | Current Study |  |  | 130505.099 | 2.4624 | 5300000 | 0.033632
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 177 MVAR switched shunt at SWISVAL7 345 kV | Current Study |  |  | 205553.2563 | 3.8784 | 5300000 | 0.031278
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 20 MVAR switched shunt at LIBERTY4 138 kV | Current Study |  |  | 60056.8396 | 2.4689 | 2432500 | 0.033183
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 117169.1877 | 3.6052 | 3250000 | 0.031387
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR switched shunt at STILWEL7 345 kV | Current Study |  |  | 190902.4848 | 3.6019 | 5300000 | 0.022063
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 24 MVAR switched shunt at GROVE 4 138 kV | Current Study |  |  | 52177.6117 | 2.145 | 2432500 | 0.031387
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 280 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 254045.5138 | 2.117 | 12000000 | 0.030397
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 295 MVAR switched shunt at G18-128-TAP 345 kV | Current Study |  |  | 134359.1647 | 2.5351 | 5300000 | 0.030397
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 3 MVAR switched shunt at NEOSHOS2 69 kV | Current Study |  |  | 132.1612 | 0.0095769 | 1380000 | 9.0151e-05
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 316 MVAR switched shunt at W.GRDNR7 345 kV | Current Study |  |  | 190902.4848 | 3.6019 | 5300000 | 0.022063
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 515301 FTSMTHW5 161 515302 FTSMITH7 345 515728 FTSMTH51 13 M2 | Current Study |  | (493.00, 493.00) | 706907.613 | 3.4823 | 20300000 | 0.0074304
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 515302 FTSMITH7 345 515305 FTSMITH8 500 515726 FTSMTH11 13 M2 | Current Study |  | (660.00, 693.00) | 4679988.3605 | 9.9574 | 47000000 | 0.014703
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at INDEPCO5 161 kV | Current Study |  |  | 135678.4264 | 4.1747 | 3250000 | 0.039244
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 80112.4659 | 2.465 | 3250000 | 0.031278
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 45 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 324945.288 | 2.7079 | 12000000 | 0.030397
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 45 MVAR switched shunt at NEVADA 5 161 kV | Current Study |  |  | 112779.511 | 3.4701 | 3250000 | 0.031278
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 56 MVAR switched shunt at WHARV4 138 kV | Current Study |  |  | 80719.5951 | 3.3184 | 2432500 | 0.033632
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV | Current Study |  |  | 53474.2579 | 3.8749 | 1380000 | 0.031387
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Add line 515012 RVRVALY7 345 780360 G24-113-TAP 345 P2 | Current Study | 23.28 | (1195.00, 1195.00) | 4422985.2565 | 5.3829 | 82168000 | 0.030586
GEN-2024-236 | 04 SOUTHEAST | 94721 | ERIS | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 213682884 | N/A
GEN-2024-236 | 04 SOUTHEAST | 94929 | ERIS | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 413934522 | N/A
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | Current Study | 21.38 | (1793.00, 1793.00) | 4235919.6341 | 9.0057 | 47036000 | 0.1162
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 1329360.4936 | 3.9571 | 33594000 | 0.059771
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 169170.34 | 1.4509 | 11660000 | 0.033143
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Current Study | 14.6 | (1793.00, 1793.00) | 1271032.299 | 3.9571 | 32120000 | 0.059771
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514715 WOODRNG7 345 515875 REDNGTN7 345 1 | Current Study | 19.2 | (1793.00, 1793.00) | 2061846.98 | 4.8813 | 42240000 | 0.055965
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 1473803.8485 | 3.2099 | 45914000 | 0.027849
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 1176016.5764 | 1.2513 | 93984000 | 0.033143
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Current Study | 25.29 | (2390.00, 2390.00) | 1677839.66 | 3.0156 | 55638000 | 0.030547
GEN-2024-236 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 804342.3974 | 3.2099 | 25058000 | 0.027849
GEN-2024-236 | 04 SOUTHEAST | 171709 | ERIS | Seminole - Muskogee 345 kV line GEN-2024-236 Interconnection (Non-Shared NU) (OGE) | Interconnection |  |  | 18000000 | 100 | 18000000 | 1
GEN-2024-236 | 04 SOUTHEAST | 171708 | ERIS | Seminole - Muskogee 345 kV line GEN-2024-236 Interconnection (TOIF) (OGE) | Interconnection |  |  | 3000000 | 100 | 3000000 | 1
GEN-2024-239 | 04 SOUTHEAST | 94615 | ERIS | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029 | Contingent |  |  | 0 | 0 | 543515503 | N/A
GEN-2024-239 | 04 SOUTHEAST | 94811 | ERIS | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030 | Contingent |  |  | 0 | 0 | 1097029189 | N/A
GEN-2024-239 | 04 SOUTHEAST | 94911 | ERIS | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030 | Contingent |  |  | 0 | 0 | 143524375 | N/A
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BUFFALO7 345 kV | Current Study |  |  | 725232.3863 | 13.6836 | 5300000 | 0.035623
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 412771.1025 | 7.7881 | 5300000 | 0.03373
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at MOUND 4 138 kV | Current Study |  |  | 94779.0259 | 3.8964 | 2432500 | 0.047664
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV | Current Study |  |  | 279080.0999 | 5.2657 | 5300000 | 0.039693
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 59597.5453 | 2.4501 | 2432500 | 0.044583
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 0.09 MVAR switched shunt at SWISVAL6 230 kV | Current Study |  |  | 352192.2475 | 9.2076 | 3825000 | 0.03373
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 17603.7693 | 1.2756 | 1380000 | 0.044583
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 131849.4637 | 2.4877 | 5300000 | 0.0381
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 299612.804 | 2.4968 | 12000000 | 0.039693
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR switched shunt at NEOSHO 4 138 kV | Current Study |  |  | 57266.0232 | 2.3542 | 2432500 | 0.056203
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR switched shunt at WICHITA7 345 kV | Current Study |  |  | 173946.9608 | 3.282 | 5300000 | 0.054106
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 177 MVAR switched shunt at SWISVAL7 345 kV | Current Study |  |  | 157835.8031 | 2.978 | 5300000 | 0.028988
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 2 MVAR switched shunt at CLIFTON3 115 kV | Current Study |  |  | 301915.4239 | 13.6459 | 2212500 | 0.02639
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 20 MVAR switched shunt at LIBERTY4 138 kV | Current Study |  |  | 56847.0249 | 2.337 | 2432500 | 0.037912
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR switched shunt at STILWEL7 345 kV | Current Study |  |  | 207810.0505 | 3.9209 | 5300000 | 0.028988
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 25 MVAR switched shunt at ATWOOD 3 115 kV | Current Study |  |  | 279984.998 | 12.6547 | 2212500 | 0.026369
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at G21-096-TAP 345 kV | Current Study |  |  | 299143.9641 | 5.6442 | 5300000 | 0.034244
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 280 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 511697.8491 | 4.2641 | 12000000 | 0.073898
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 295 MVAR switched shunt at G18-128-TAP 345 kV | Current Study |  |  | 205822.5714 | 3.8834 | 5300000 | 0.056203
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 3 MVAR switched shunt at NEOSHOS2 69 kV | Current Study |  |  | 68262.5246 | 4.9466 | 1380000 | 0.056203
GEN-2024-239 | 04 SOUTHEAST | TBD | NRIS | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV | Current Study |  |  | 13544.6206 | 0.5889 | 2300000 | 0.03082
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at G23-220-TAP 345 kV | Current Study |  |  | 265751.7788 | 5.0142 | 5300000 | 0.03373
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 316 MVAR switched shunt at W.GRDNR7 345 kV | Current Study |  |  | 207810.0505 | 3.9209 | 5300000 | 0.028988
GEN-2024-239 | 04 SOUTHEAST | TBD | NRIS | Add 3-winding transformer 514898 CIMARON4 138 514901 CIMARON7 345 515715 CIMARO21 13 M2 | Current Study |  | (478.00, 478.00) | 5241555.8267 | 28.9589 | 18100000 | 0.038558
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 80851.0862 | 2.4877 | 3250000 | 0.0381
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 45 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 497778.2863 | 4.1482 | 12000000 | 0.056203
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 45 MVAR switched shunt at NEVADA 5 161 kV | Current Study |  |  | 86598.6996 | 2.6646 | 3250000 | 0.028988
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 567292.5823 | 10.7036 | 5300000 | 0.02639
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 56 MVAR switched shunt at WHARV4 138 kV | Current Study |  |  | 94779.0259 | 3.8964 | 2432500 | 0.047664
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add 86 MVAR switched shunt at POSTROCK7 345 kV | Current Study |  |  | 521220.1639 | 9.8343 | 5300000 | 0.021747
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Add line 515012 RVRVALY7 345 780360 G24-113-TAP 345 P2 | Current Study | 23.28 | (1195.00, 1195.00) | 2011382.3754 | 2.4479 | 82168000 | 0.016789
GEN-2024-239 | 04 SOUTHEAST | 94721 | ERIS | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 213682884 | N/A
GEN-2024-239 | 04 SOUTHEAST | 94929 | ERIS | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 413934522 | N/A
GEN-2024-239 | 04 SOUTHEAST | 171711 | ERIS | Cimarron 345 kV Substation GEN-2024-239 Interconnection (Non-Shared NU) (OGE) | Interconnection |  |  | 3000000 | 100 | 3000000 | 1
GEN-2024-239 | 04 SOUTHEAST | 171710 | ERIS | Cimarron 345 kV Substation GEN-2024-239 Interconnection (TOIF) (OGE) | Interconnection |  |  | 2500000 | 100 | 2500000 | 1
GEN-2024-239 | 04 SOUTHEAST | 900427 | ERIS | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032 | Contingent |  |  | 0 | 0 | 1790026304.1702 | N/A
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 764467.6086 | 2.2756 | 33594000 | 0.041487
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 160106.3687 | 1.3731 | 11660000 | 0.03786
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Current Study | 14.6 | (1793.00, 1793.00) | 730925.153 | 2.2756 | 32120000 | 0.041487
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514715 WOODRNG7 345 515875 REDNGTN7 345 1 | Current Study | 19.2 | (1793.00, 1793.00) | 4055096.4876 | 9.6001 | 42240000 | 0.13285
GEN-2024-239 | 04 SOUTHEAST | TBD | NRIS | Rebuild line 514894 CZECHAL4 138 514898 CIMARON4 138 1 | Current Study | 5.63 | (525.00, 525.00) | 1576105.7636 | 23.329 | 6756000 | 0.023381
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 3252111.1136 | 7.083 | 45914000 | 0.074171
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 1113006.8282 | 1.1843 | 93984000 | 0.03786
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Current Study | 25.29 | (2390.00, 2390.00) | 2566265.3017 | 4.6124 | 55638000 | 0.056393
GEN-2024-239 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 1774870.4161 | 7.083 | 25058000 | 0.074171
GEN-2024-240 | 04 SOUTHEAST | 94811 | ERIS | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030 | Contingent |  |  | 0 | 0 | 1097029189 | N/A
GEN-2024-240 | 04 SOUTHEAST | 94911 | ERIS | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030 | Contingent |  |  | 0 | 0 | 143524375 | N/A
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at MOUND 4 138 kV | Current Study |  |  | 60375.2183 | 2.482 | 2432500 | 0.040483
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at PHILL 7 345 kV | Current Study |  |  | 402670.398 | 7.5976 | 5300000 | 0.032995
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV | Current Study |  |  | 249186.9841 | 4.7016 | 5300000 | 0.047255
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 388738.8288 | 15.981 | 2432500 | 0.38773
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 0.04 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 508049.1333 | 15.6323 | 3250000 | 0.067687
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 0.09 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 319010.153 | 9.8157 | 3250000 | 0.13771
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 272922.1244 | 5.1495 | 5300000 | 0.10515
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 0.13 MVAR switched shunt at PECULR 7 345 kV | Current Study |  |  | 764176.1104 | 14.4184 | 5300000 | 0.047255
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 0.2 MVAR switched shunt at GROVE 5 161 kV | Current Study |  |  | 205800.3585 | 6.3323 | 3250000 | 0.13771
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 0.25 MVAR switched shunt at LABETTS2 69 kV | Current Study |  |  | 4550.686 | 0.32976 | 1380000 | 0.006612
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 15 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 319010.153 | 9.8157 | 3250000 | 0.13771
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 595299.926 | 4.9608 | 12000000 | 0.10515
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR switched shunt at NEOSHO 4 138 kV | Current Study |  |  | 105237.9473 | 4.3263 | 2432500 | 0.13771
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at CPK446 5 161 kV | Current Study |  |  | 224565.3428 | 6.9097 | 3250000 | 0.13771
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV | Current Study |  |  | 319434.492 | 9.8288 | 3250000 | 0.13771
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR switched shunt at WICHITA7 345 kV | Current Study |  |  | 253546.1145 | 4.7839 | 5300000 | 0.10515
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 177 MVAR switched shunt at SWISVAL7 345 kV | Current Study |  |  | 429408.3606 | 8.102 | 5300000 | 0.10515
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 20 MVAR switched shunt at LIBERTY4 138 kV | Current Study |  |  | 436042.3354 | 17.9257 | 2432500 | 0.38773
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 319434.492 | 9.8288 | 3250000 | 0.13771
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR switched shunt at STILWEL7 345 kV | Current Study |  |  | 315729.5665 | 5.9572 | 5300000 | 0.058723
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 24 MVAR switched shunt at GROVE 4 138 kV | Current Study |  |  | 142250.1019 | 5.8479 | 2432500 | 0.13771
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at G21-096-TAP 345 kV | Current Study |  |  | 312360.0542 | 5.8936 | 5300000 | 0.047675
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 280 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 247590.7016 | 2.0633 | 12000000 | 0.047675
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at G23-220-TAP 345 kV | Current Study |  |  | 279233.5782 | 5.2686 | 5300000 | 0.047255
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 316 MVAR switched shunt at W.GRDNR7 345 kV | Current Study |  |  | 315729.5665 | 5.9572 | 5300000 | 0.058723
GEN-2024-240 | 04 SOUTHEAST | TBD | NRIS | Add 3-winding transformer 532793 NEOSHO 7 345 532825 N345 2 1 13 532939 N345 4 5 161 M2 | Current Study |  | (500.00, 550.00) | 1089041.0549 | 5.3647 | 20300000 | 0.021103
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 167357.9065 | 5.1495 | 3250000 | 0.10515
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 45 MVAR switched shunt at NEVADA 5 161 kV | Current Study |  |  | 235600.5729 | 7.2492 | 3250000 | 0.10515
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 56 MVAR switched shunt at WHARV4 138 kV | Current Study |  |  | 60375.2183 | 2.482 | 2432500 | 0.040483
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV | Current Study |  |  | 71655.5469 | 5.1924 | 1380000 | 0.067687
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | DIS2301-1_G03_ERIS_TurnOffReactors_Carpenter_Finney.idv : Switch out Carpenter 25 MVAR line reactor on the Carpenter to Hitchland 345 kV line | Contingent |  |  | 0 | 0 | 1450000 | 0.0024778
GEN-2024-240 | 04 SOUTHEAST | 900427 | ERIS | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032 | Contingent |  |  | 0 | 0 | 1790026304.1702 | N/A
GEN-2024-240 | 04 SOUTHEAST | 171713 | ERIS | Neosho - Delaware 345 kV line GEN-2024-240 Interconnection (Non-Shared NU) (AEP) | Interconnection |  |  | 28225000 | 100 | 28225000 | 1
GEN-2024-240 | 04 SOUTHEAST | 171712 | ERIS | Neosho - Delaware 345 kV line GEN-2024-240 Interconnection (TOIF) (AEP) | Interconnection |  |  | 5225000 | 100 | 5225000 | 1
GEN-2024-240 | 04 SOUTHEAST | TBD | NRIS | Rebuild line 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | Current Study | 31.46 | (1793.00, 1793.00) | 3213594.7515 | 4.6431 | 69212000 | 0.1346
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 21849.4802 | 0.73567 | 2970000 | 0.015511
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 15067.063 | 0.68487 | 2200000 | 0.015511
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | Current Study | 15.48 | (1793.00, 1793.00) | 1829061.2582 | 5.3707 | 34056000 | 0.038158
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 8547679.0763 | 9.0948 | 93984000 | 0.38768
GEN-2024-240 | 04 SOUTHEAST | TBD | NRIS | Rebuild line 532937 NEOSHO 5 161 532939 N345 4 5 161 1 | Current Study | 0.3 | (837.00, 837.00) | 24141.3042 | 5.3647 | 450000 | 0.042205
GEN-2024-240 | 04 SOUTHEAST | TBD | NRIS | Rebuild line 532937 NEOSHO 5 161 764310 G20-079-TAP 161 1 | Current Study | 20.67 | (551.00, 551.00) | 1990130.8563 | 6.4187 | 31005000 | 0.038128
GEN-2024-240 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 541198 PECULR 7 345 541200 PHILL 7 345 1 | Current Study | 11.9 | (1793.00, 1793.00) | 13576536.3233 | 51.8584 | 26180000 | 0.035179
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 39646.5234 | 2.8729 | 1380000 | 0.063712
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at PHILL 7 345 kV | Current Study |  |  | 241741.1648 | 4.5612 | 5300000 | 0.029713
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 19455.2099 | 0.7998 | 2432500 | 0.029107
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 59134.481 | 1.1157 | 5300000 | 0.034176
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV | Current Study |  |  | 39646.5234 | 2.8729 | 1380000 | 0.063712
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 0.2 MVAR switched shunt at GROVE 5 161 kV | Current Study |  |  | 52197.5671 | 1.6061 | 3250000 | 0.052392
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 0.25 MVAR switched shunt at LABETTS2 69 kV | Current Study |  |  | 24039.2032 | 1.742 | 1380000 | 0.052392
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 11 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 91249.0036 | 2.8077 | 3250000 | 0.063712
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 128984.6041 | 1.0749 | 12000000 | 0.034176
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR switched shunt at NEOSHO 4 138 kV | Current Study |  |  | 32458.9154 | 1.3344 | 2432500 | 0.063712
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at CPK446 5 161 kV | Current Study |  |  | 69263.4896 | 2.1312 | 3250000 | 0.063712
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR switched shunt at WICHITA7 345 kV | Current Study |  |  | 54936.2494 | 1.0365 | 5300000 | 0.034176
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 177 MVAR switched shunt at SWISVAL7 345 kV | Current Study |  |  | 46989.941 | 0.8866 | 5300000 | 0.01726
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 24 MVAR switched shunt at GROVE 4 138 kV | Current Study |  |  | 14943.9314 | 0.61434 | 2432500 | 0.021701
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 280 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 133692.6441 | 1.1141 | 12000000 | 0.038615
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV | Current Study |  |  | 30639.7917 | 2.2203 | 1380000 | 0.056469
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at INDEPCO5 161 kV | Current Study |  |  | 91249.0036 | 2.8077 | 3250000 | 0.063712
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 36261.7101 | 1.1157 | 3250000 | 0.034176
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Add 45 MVAR switched shunt at NEVADA 5 161 kV | Current Study |  |  | 25781.6522 | 0.79328 | 3250000 | 0.01726
GEN-2024-241 | 04 SOUTHEAST | 171715 | ERIS | Lydia 345 kV Substation GEN-2024-241 Interconnection (Non-Shared NU) (AEP) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-241 | 04 SOUTHEAST | 171714 | ERIS | Lydia 345 kV Substation GEN-2024-241 Interconnection (TOIF) (AEP) | Interconnection |  |  | 200000 | 100 | 200000 | 1
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | Current Study | 14.95 | (329.00, 329.00) | 1052014.6162 | 7.0369 | 14950000 | 0.036744
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508359 WELSH 7 345 508841 WILKES 7 345 1 | Current Study | 30.63 | (1793.00, 1793.00) | 8422160.3738 | 12.4984 | 67386000 | 0.16482
GEN-2024-241 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | Current Study | 21.38 | (1793.00, 1793.00) | 1132431.0934 | 2.4076 | 47036000 | 0.074992
GEN-2024-249 | 03 CENTRAL | TBD | ERIS | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV | Current Study |  |  | 29259.7692 | 2.1203 | 1380000 | 0.02874
GEN-2024-249 | 03 CENTRAL | TBD | ERIS | Add 23 MVAR switched shunt at FINNEY 7 345 kV | Current Study |  |  | 331270.5028 | 6.2504 | 5300000 | 0.02874
GEN-2024-249 | 03 CENTRAL | TBD | ERIS | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2 | Current Study | 0.75 | (2390.00, 2390.00) | 346671.881 | 1.9503 | 17775000 | 0.014832
GEN-2024-249 | 03 CENTRAL | 171935 | ERIS | Jeffrey EC 345 kV Substation GEN-2024-249 Interconnection (Non-Shared NU) (WERE) | Interconnection |  |  | 5202083 | 100 | 5202083 | 1
GEN-2024-249 | 03 CENTRAL | 171934 | ERIS | Jeffrey EC 345 kV Substation GEN-2024-249 Interconnection (TOIF) (WERE) | Interconnection |  |  | 1742929 | 100 | 1742929 | 1
GEN-2024-252 | 04 SOUTHEAST | 94615 | ERIS | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029 | Contingent |  |  | 0 | 0 | 543515503 | N/A
GEN-2024-252 | 04 SOUTHEAST | 94811 | ERIS | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030 | Contingent |  |  | 0 | 0 | 1097029189 | N/A
GEN-2024-252 | 04 SOUTHEAST | 94911 | ERIS | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030 | Contingent |  |  | 0 | 0 | 143524375 | N/A
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BUFFALO7 345 kV | Current Study |  |  | 1087848.5794 | 20.5254 | 5300000 | 0.035623
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 619156.6538 | 11.6822 | 5300000 | 0.03373
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at MOUND 4 138 kV | Current Study |  |  | 142168.5388 | 5.8445 | 2432500 | 0.047664
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV | Current Study |  |  | 418620.1499 | 7.8985 | 5300000 | 0.039693
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 89396.3179 | 3.6751 | 2432500 | 0.044583
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 0.09 MVAR switched shunt at SWISVAL6 230 kV | Current Study |  |  | 528288.3712 | 13.8115 | 3825000 | 0.03373
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 26405.6539 | 1.9135 | 1380000 | 0.044583
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 197774.1955 | 3.7316 | 5300000 | 0.0381
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 449419.206 | 3.7452 | 12000000 | 0.039693
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR switched shunt at NEOSHO 4 138 kV | Current Study |  |  | 85899.0349 | 3.5313 | 2432500 | 0.056203
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR switched shunt at WICHITA7 345 kV | Current Study |  |  | 260920.4412 | 4.923 | 5300000 | 0.054106
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 177 MVAR switched shunt at SWISVAL7 345 kV | Current Study |  |  | 236753.7047 | 4.4671 | 5300000 | 0.028988
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 2 MVAR switched shunt at CLIFTON3 115 kV | Current Study |  |  | 452873.1359 | 20.4688 | 2212500 | 0.02639
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 2 MVAR switched shunt at GEN-2017-140 345 kV | Current Study |  |  | 45518.1592 | 0.85883 | 5300000 | 0.032751
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 20 MVAR switched shunt at LIBERTY4 138 kV | Current Study |  |  | 85270.5374 | 3.5055 | 2432500 | 0.037912
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR switched shunt at STILWEL7 345 kV | Current Study |  |  | 311715.0758 | 5.8814 | 5300000 | 0.028988
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 23 MVAR switched shunt at FINNEY 7 345 kV | Current Study |  |  | 135525.278 | 2.5571 | 5300000 | 0.028265
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 25 MVAR switched shunt at ATWOOD 3 115 kV | Current Study |  |  | 419977.497 | 18.982 | 2212500 | 0.026369
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at G21-096-TAP 345 kV | Current Study |  |  | 448715.9462 | 8.4663 | 5300000 | 0.034244
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 280 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 767546.7737 | 6.3962 | 12000000 | 0.073898
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 295 MVAR switched shunt at G18-128-TAP 345 kV | Current Study |  |  | 308733.8571 | 5.8252 | 5300000 | 0.056203
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 3 MVAR switched shunt at NEOSHOS2 69 kV | Current Study |  |  | 102393.7869 | 7.4198 | 1380000 | 0.056203
GEN-2024-252 | 04 SOUTHEAST | TBD | NRIS | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV | Current Study |  |  | 20316.9309 | 0.88334 | 2300000 | 0.03082
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at G23-220-TAP 345 kV | Current Study |  |  | 398627.6683 | 7.5213 | 5300000 | 0.03373
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 316 MVAR switched shunt at W.GRDNR7 345 kV | Current Study |  |  | 311715.0758 | 5.8814 | 5300000 | 0.028988
GEN-2024-252 | 04 SOUTHEAST | TBD | NRIS | Add 3-winding transformer 514898 CIMARON4 138 514901 CIMARON7 345 515715 CIMARO21 13 M2 | Current Study |  | (478.00, 478.00) | 7862333.7401 | 43.4383 | 18100000 | 0.038558
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 121276.6293 | 3.7316 | 3250000 | 0.0381
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 45 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 746667.4295 | 6.2222 | 12000000 | 0.056203
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 45 MVAR switched shunt at NEVADA 5 161 kV | Current Study |  |  | 129898.0494 | 3.9969 | 3250000 | 0.028988
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 850938.8734 | 16.0555 | 5300000 | 0.02639
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 56 MVAR switched shunt at WHARV4 138 kV | Current Study |  |  | 142168.5388 | 5.8445 | 2432500 | 0.047664
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add 86 MVAR switched shunt at POSTROCK7 345 kV | Current Study |  |  | 781830.2459 | 14.7515 | 5300000 | 0.021747
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Add line 515012 RVRVALY7 345 780360 G24-113-TAP 345 P2 | Current Study | 23.28 | (1195.00, 1195.00) | 3017073.5632 | 3.6718 | 82168000 | 0.016789
GEN-2024-252 | 04 SOUTHEAST | 94721 | ERIS | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 213682884 | N/A
GEN-2024-252 | 04 SOUTHEAST | 94929 | ERIS | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 413934522 | N/A
GEN-2024-252 | 04 SOUTHEAST | 171733 | ERIS | Cimmaron 345 kV Substation GEN-2024-252 Interconnection (Non-Shared NU) (OGE) | Interconnection |  |  | 3000000 | 100 | 3000000 | 1
GEN-2024-252 | 04 SOUTHEAST | 171732 | ERIS | Cimmaron 345 kV Substation GEN-2024-252 Interconnection (TOIF) (OGE) | Interconnection |  |  | 2500000 | 100 | 2500000 | 1
GEN-2024-252 | 04 SOUTHEAST | 900427 | ERIS | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032 | Contingent |  |  | 0 | 0 | 1790026304.1702 | N/A
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 1146701.413 | 3.4134 | 33594000 | 0.041487
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 240159.553 | 2.0597 | 11660000 | 0.03786
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Current Study | 14.6 | (1793.00, 1793.00) | 1096387.7295 | 3.4134 | 32120000 | 0.041487
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514715 WOODRNG7 345 515875 REDNGTN7 345 1 | Current Study | 19.2 | (1793.00, 1793.00) | 6082644.7314 | 14.4002 | 42240000 | 0.13285
GEN-2024-252 | 04 SOUTHEAST | TBD | NRIS | Rebuild line 514894 CZECHAL4 138 514898 CIMARON4 138 1 | Current Study | 5.63 | (525.00, 525.00) | 2364158.6454 | 34.9935 | 6756000 | 0.023381
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 4878166.6704 | 10.6246 | 45914000 | 0.074171
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 1669510.2423 | 1.7764 | 93984000 | 0.03786
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Current Study | 25.29 | (2390.00, 2390.00) | 3849397.9526 | 6.9186 | 55638000 | 0.056393
GEN-2024-252 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 2662305.6241 | 10.6246 | 25058000 | 0.074171
GEN-2024-253 | 03 CENTRAL | 94615 | ERIS | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029 | Contingent |  |  | 0 | 0 | 543515503 | N/A
GEN-2024-253 | 03 CENTRAL | TBD | ERIS | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV | Current Study |  |  | 141590.5553 | 10.2602 | 1380000 | 0.094493
GEN-2024-253 | 03 CENTRAL | TBD | ERIS | Add 16 MVAR switched shunt at HUMBOLT5 161 kV | Current Study |  |  | 279833.3786 | 8.6103 | 3250000 | 0.069711
GEN-2024-253 | 03 CENTRAL | TBD | ERIS | Add 21 MVAR switched shunt at S1263 5 161 kV | Current Study |  |  | 279833.3786 | 8.6103 | 3250000 | 0.069711
GEN-2024-253 | 03 CENTRAL | TBD | ERIS | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV | Current Study |  |  | 118821.5577 | 8.6103 | 1380000 | 0.069711
GEN-2024-253 | 03 CENTRAL | TBD | ERIS | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2 | Current Study | 0.75 | (2390.00, 2390.00) | 200787.3985 | 1.1296 | 17775000 | 0.020652
GEN-2024-253 | 03 CENTRAL | 94721 | ERIS | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 213682884 | N/A
GEN-2024-253 | 03 CENTRAL | 94929 | ERIS | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 413934522 | N/A
GEN-2024-253 | 03 CENTRAL | TBD | ERIS | Rebuild line 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | Current Study | 3.02 | (551.00, 551.00) | 769433.5342 | 16.9853 | 4530000 | 0.03798
GEN-2024-253 | 03 CENTRAL | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 352127.3205 | 3.02 | 11660000 | 0.055511
GEN-2024-253 | 03 CENTRAL | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 2447873.3438 | 2.6046 | 93984000 | 0.055511
GEN-2024-253 | 03 CENTRAL | TBD | ERIS | Rebuild line 533243 JAGGARD3 115 533261 PENTAGN3 115 1 | Current Study | 5.55 | (297.00, 297.00) | 4231.1105 | 0.076236 | 5550000 | 0.0003735
GEN-2024-253 | 03 CENTRAL | TBD | ERIS | Rebuild line 541199 ST JOE 7 345 541400 EASTOWN7 345 1 | Current Study | 8.12 | (1793.00, 1793.00) | 3729861.0909 | 20.8792 | 17864000 | 0.13209
GEN-2024-253 | 03 CENTRAL | TBD | ERIS | Rebuild line 541400 EASTOWN7 345 542982 IATAN 7 345 1 | Current Study | 23.71 | (1793.00, 1793.00) | 10386028.9659 | 19.9111 | 52162000 | 0.14687
GEN-2024-253 | 03 CENTRAL | TBD | ERIS | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | Current Study | 45.48 | (1793.00, 1793.00) | 3472817.8146 | 3.4709 | 100056000 | 0.030477
GEN-2024-253 | 03 CENTRAL | 171937 | ERIS | Stranger Creek - 87th Street 345 kV line GEN-2024-253 Interconnection (Non-Shared NU) (WERE) | Interconnection |  |  | 33058407 | 100 | 33058407 | 1
GEN-2024-253 | 03 CENTRAL | 171936 | ERIS | Stranger Creek - 87th Street 345 kV line GEN-2024-253 Interconnection (TOIF) (WERE) | Interconnection |  |  | 1958092 | 100 | 1958092 | 1
GEN-2024-254 | 04 SOUTHEAST | 94615 | ERIS | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029 | Contingent |  |  | 0 | 0 | 543515503 | N/A
GEN-2024-254 | 04 SOUTHEAST | 94811 | ERIS | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030 | Contingent |  |  | 0 | 0 | 1097029189 | N/A
GEN-2024-254 | 04 SOUTHEAST | 94911 | ERIS | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030 | Contingent |  |  | 0 | 0 | 143524375 | N/A
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BUFFALO7 345 kV | Current Study |  |  | 1093834.2872 | 20.6384 | 5300000 | 0.035819
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 633824.0939 | 11.9589 | 5300000 | 0.034529
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at MOUND 4 138 kV | Current Study |  |  | 145662.5405 | 5.9882 | 2432500 | 0.048836
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV | Current Study |  |  | 429884.4902 | 8.111 | 5300000 | 0.040761
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 92581.4452 | 3.806 | 2432500 | 0.046171
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 0.09 MVAR switched shunt at SWISVAL6 230 kV | Current Study |  |  | 540803.1976 | 14.1386 | 3825000 | 0.034529
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 27346.4686 | 1.9816 | 1380000 | 0.046171
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 196291.2604 | 3.7036 | 5300000 | 0.037815
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 461512.2953 | 3.8459 | 12000000 | 0.040761
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR switched shunt at NEOSHO 4 138 kV | Current Study |  |  | 86844.7258 | 3.5702 | 2432500 | 0.056821
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR switched shunt at WICHITA7 345 kV | Current Study |  |  | 280009.5055 | 5.2832 | 5300000 | 0.058065
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 177 MVAR switched shunt at SWISVAL7 345 kV | Current Study |  |  | 240402.8823 | 4.5359 | 5300000 | 0.029435
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 2 MVAR switched shunt at CLIFTON3 115 kV | Current Study |  |  | 464851.9114 | 21.0103 | 2212500 | 0.027088
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 2 MVAR switched shunt at GEN-2017-140 345 kV | Current Study |  |  | 45749.175 | 0.86319 | 5300000 | 0.032917
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 20 MVAR switched shunt at LIBERTY4 138 kV | Current Study |  |  | 84618.922 | 3.4787 | 2432500 | 0.037622
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR switched shunt at STILWEL7 345 kV | Current Study |  |  | 316519.6623 | 5.9721 | 5300000 | 0.029435
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 23 MVAR switched shunt at FINNEY 7 345 kV | Current Study |  |  | 136270.7343 | 2.5711 | 5300000 | 0.028421
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 25 MVAR switched shunt at ATWOOD 3 115 kV | Current Study |  |  | 430517.9683 | 19.4584 | 2212500 | 0.027031
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at G21-096-TAP 345 kV | Current Study |  |  | 459186.3654 | 8.6639 | 5300000 | 0.035043
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 280 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 825690.1517 | 6.8808 | 12000000 | 0.079496
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 295 MVAR switched shunt at G18-128-TAP 345 kV | Current Study |  |  | 312132.8105 | 5.8893 | 5300000 | 0.056821
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 3 MVAR switched shunt at NEOSHOS2 69 kV | Current Study |  |  | 103521.0741 | 7.5015 | 1380000 | 0.056821
GEN-2024-254 | 04 SOUTHEAST | TBD | NRIS | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV | Current Study |  |  | 21778.7771 | 0.9469 | 2300000 | 0.033038
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at G23-220-TAP 345 kV | Current Study |  |  | 408070.9124 | 7.6995 | 5300000 | 0.034529
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 316 MVAR switched shunt at W.GRDNR7 345 kV | Current Study |  |  | 316519.6623 | 5.9721 | 5300000 | 0.029435
GEN-2024-254 | 04 SOUTHEAST | TBD | NRIS | Add 3-winding transformer 514898 CIMARON4 138 514901 CIMARON7 345 515715 CIMARO21 13 M2 | Current Study |  | (478.00, 478.00) | 4996110.4332 | 27.6028 | 18100000 | 0.024502
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 120367.2823 | 3.7036 | 3250000 | 0.037815
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 45 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 754887.7389 | 6.2907 | 12000000 | 0.056821
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 45 MVAR switched shunt at NEVADA 5 161 kV | Current Study |  |  | 131900.219 | 4.0585 | 3250000 | 0.029435
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 873446.7346 | 16.4801 | 5300000 | 0.027088
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 56 MVAR switched shunt at WHARV4 138 kV | Current Study |  |  | 145662.5405 | 5.9882 | 2432500 | 0.048836
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add 86 MVAR switched shunt at POSTROCK7 345 kV | Current Study |  |  | 796757.4684 | 15.0332 | 5300000 | 0.022162
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Add line 515012 RVRVALY7 345 780360 G24-113-TAP 345 P2 | Current Study | 23.28 | (1195.00, 1195.00) | 2946189.1574 | 3.5856 | 82168000 | 0.016394
GEN-2024-254 | 04 SOUTHEAST | 94721 | ERIS | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 213682884 | N/A
GEN-2024-254 | 04 SOUTHEAST | 94929 | ERIS | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 413934522 | N/A
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | DIS2301-1_G03_ERIS_TurnOffReactors_Carpenter_Finney.idv : Switch out Carpenter 25 MVAR line reactor on the Carpenter to Hitchland 345 kV line | Contingent |  |  | 0 | 0 | 1450000 | 0.037557
GEN-2024-254 | 04 SOUTHEAST | 900427 | ERIS | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032 | Contingent |  |  | 0 | 0 | 1790026304.1702 | N/A
GEN-2024-254 | 04 SOUTHEAST | 171735 | ERIS | Mathewson 345 kV Substation GEN-2024-254 Interconnection (Non-Shared NU) (OGE) | Interconnection |  |  | 2000000 | 100 | 2000000 | 1
GEN-2024-254 | 04 SOUTHEAST | 171734 | ERIS | Mathewson 345 kV Substation GEN-2024-254 Interconnection (TOIF) (OGE) | Interconnection |  |  | 3000000 | 100 | 3000000 | 1
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 1096467.3106 | 3.2639 | 33594000 | 0.03967
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 238313.2294 | 2.0439 | 11660000 | 0.037569
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Current Study | 14.6 | (1793.00, 1793.00) | 1048357.7429 | 3.2639 | 32120000 | 0.03967
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514715 WOODRNG7 345 515875 REDNGTN7 345 1 | Current Study | 19.2 | (1793.00, 1793.00) | 7322543.2067 | 17.3356 | 42240000 | 0.15993
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 5246810.7832 | 11.4275 | 45914000 | 0.079776
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 1656675.2077 | 1.7627 | 93984000 | 0.037569
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Current Study | 25.29 | (2390.00, 2390.00) | 3891974.0487 | 6.9952 | 55638000 | 0.057017
GEN-2024-254 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 2863496.6373 | 11.4275 | 25058000 | 0.079776
GEN-2024-255 | 04 SOUTHEAST | 94615 | ERIS | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029 | Contingent |  |  | 0 | 0 | 543515503 | N/A
GEN-2024-255 | 04 SOUTHEAST | 94811 | ERIS | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030 | Contingent |  |  | 0 | 0 | 1097029189 | N/A
GEN-2024-255 | 04 SOUTHEAST | 94911 | ERIS | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030 | Contingent |  |  | 0 | 0 | 143524375 | N/A
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 643371.4321 | 12.1391 | 5300000 | 0.035049
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at MOUND 4 138 kV | Current Study |  |  | 146273.8753 | 6.0133 | 2432500 | 0.049041
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV | Current Study |  |  | 426418.6606 | 8.0456 | 5300000 | 0.040432
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 79080.7955 | 3.251 | 2432500 | 0.039438
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 0.09 MVAR switched shunt at SWISVAL6 230 kV | Current Study |  |  | 548949.3553 | 14.3516 | 3825000 | 0.035049
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 22014.7339 | 1.5953 | 1380000 | 0.037169
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 205848.1291 | 3.8839 | 5300000 | 0.039656
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 457791.475 | 3.8149 | 12000000 | 0.040432
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR switched shunt at NEOSHO 4 138 kV | Current Study |  |  | 112702.0274 | 4.6332 | 2432500 | 0.07374
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR switched shunt at WICHITA7 345 kV | Current Study |  |  | 266774.8733 | 5.0335 | 5300000 | 0.05532
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 177 MVAR switched shunt at SWISVAL7 345 kV | Current Study |  |  | 250519.9715 | 4.7268 | 5300000 | 0.030674
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 2 MVAR switched shunt at CLIFTON3 115 kV | Current Study |  |  | 468042.6157 | 21.1545 | 2212500 | 0.027274
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 2 MVAR switched shunt at GEN-2017-140 345 kV | Current Study |  |  | 48292.0058 | 0.91117 | 5300000 | 0.034747
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 20 MVAR switched shunt at LIBERTY4 138 kV | Current Study |  |  | 88703.7059 | 3.6466 | 2432500 | 0.039438
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR switched shunt at STILWEL7 345 kV | Current Study |  |  | 329840.042 | 6.2234 | 5300000 | 0.030674
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 23 MVAR switched shunt at FINNEY 7 345 kV | Current Study |  |  | 118446.5644 | 2.2348 | 5300000 | 0.024703
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 25 MVAR switched shunt at ATWOOD 3 115 kV | Current Study |  |  | 410867.9624 | 18.5703 | 2212500 | 0.025797
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at G21-096-TAP 345 kV | Current Study |  |  | 466001.7764 | 8.7925 | 5300000 | 0.035563
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 280 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 778469.4135 | 6.4872 | 12000000 | 0.07495
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 295 MVAR switched shunt at G18-128-TAP 345 kV | Current Study |  |  | 405067.7831 | 7.6428 | 5300000 | 0.07374
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 3 MVAR switched shunt at NEOSHOS2 69 kV | Current Study |  |  | 134343.6209 | 9.735 | 1380000 | 0.07374
GEN-2024-255 | 04 SOUTHEAST | TBD | NRIS | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV | Current Study |  |  | 20227.5597 | 0.87946 | 2300000 | 0.030684
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at G23-220-TAP 345 kV | Current Study |  |  | 414217.7141 | 7.8154 | 5300000 | 0.035049
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 316 MVAR switched shunt at W.GRDNR7 345 kV | Current Study |  |  | 329840.042 | 6.2234 | 5300000 | 0.030674
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 126227.6263 | 3.8839 | 3250000 | 0.039656
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 45 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 979649.3435 | 8.1637 | 12000000 | 0.07374
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 45 MVAR switched shunt at NEVADA 5 161 kV | Current Study |  |  | 137451.0937 | 4.2293 | 3250000 | 0.030674
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 879441.9994 | 16.5932 | 5300000 | 0.027274
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 56 MVAR switched shunt at WHARV4 138 kV | Current Study |  |  | 146273.8753 | 6.0133 | 2432500 | 0.049041
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add 86 MVAR switched shunt at POSTROCK7 345 kV | Current Study |  |  | 737984.5251 | 13.9242 | 5300000 | 0.020527
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Add line 515012 RVRVALY7 345 780360 G24-113-TAP 345 P2 | Current Study | 23.28 | (1195.00, 1195.00) | 2987806.6937 | 3.6362 | 82168000 | 0.016626
GEN-2024-255 | 04 SOUTHEAST | 94721 | ERIS | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 213682884 | N/A
GEN-2024-255 | 04 SOUTHEAST | 94929 | ERIS | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 413934522 | N/A
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | DIS2301-1_G03_ERIS_TurnOffReactors_Carpenter_Finney.idv : Switch out Carpenter 25 MVAR line reactor on the Carpenter to Hitchland 345 kV line | Contingent |  |  | 0 | 0 | 1450000 | 0.033191
GEN-2024-255 | 04 SOUTHEAST | 900427 | ERIS | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032 | Contingent |  |  | 0 | 0 | 1790026304.1702 | N/A
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 1238920.5986 | 3.6879 | 33594000 | 0.044824
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 249830.7142 | 2.1426 | 11660000 | 0.039384
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Current Study | 14.6 | (1793.00, 1793.00) | 1184560.6247 | 3.6879 | 32120000 | 0.044824
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 66945.5976 | 3.043 | 2200000 | 0.034459
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514715 WOODRNG7 345 515875 REDNGTN7 345 1 | Current Study | 19.2 | (1793.00, 1793.00) | 4288418.9806 | 10.1525 | 42240000 | 0.093664
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 4947956.7238 | 10.7766 | 45914000 | 0.075232
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 1736740.9744 | 1.8479 | 93984000 | 0.039384
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Current Study | 25.29 | (2390.00, 2390.00) | 5046920.7753 | 9.071 | 55638000 | 0.073937
GEN-2024-255 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 2700394.2062 | 10.7766 | 25058000 | 0.075232
GEN-2024-255 | 04 SOUTHEAST | 171737 | ERIS | Spring Creek 345 kV Substation GEN-2024-255 Interconnection (Non-Shared NU) (OGE) | Interconnection |  |  | 7500000 | 100 | 7500000 | 1
GEN-2024-255 | 04 SOUTHEAST | 171736 | ERIS | Spring Creek 345 kV Substation GEN-2024-255 Interconnection (TOIF) (OGE) | Interconnection |  |  | 2000000 | 100 | 2000000 | 1
GEN-2024-258 | 03 CENTRAL | 94615 | ERIS | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029 | Contingent |  |  | 0 | 0 | 543515503 | N/A
GEN-2024-258 | 03 CENTRAL | TBD | ERIS | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV | Current Study |  |  | 19101.3369 | 1.3842 | 1380000 | 0.012748
GEN-2024-258 | 03 CENTRAL | TBD | ERIS | Add 16 MVAR switched shunt at HUMBOLT5 161 kV | Current Study |  |  | 167853.0418 | 5.1647 | 3250000 | 0.041815
GEN-2024-258 | 03 CENTRAL | TBD | ERIS | Add 21 MVAR switched shunt at S1263 5 161 kV | Current Study |  |  | 167853.0418 | 5.1647 | 3250000 | 0.041815
GEN-2024-258 | 03 CENTRAL | TBD | NRIS | Add 3-winding transformer 532793 NEOSHO 7 345 532825 N345 2 1 13 532939 N345 4 5 161 M2 | Current Study |  | (500.00, 550.00) | 1493172.6779 | 7.3555 | 20300000 | 0.014467
GEN-2024-258 | 03 CENTRAL | TBD | ERIS | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV | Current Study |  |  | 71272.9839 | 5.1647 | 1380000 | 0.041815
GEN-2024-258 | 03 CENTRAL | 94721 | ERIS | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 213682884 | N/A
GEN-2024-258 | 03 CENTRAL | 94929 | ERIS | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 413934522 | N/A
GEN-2024-258 | 03 CENTRAL | TBD | NRIS | Rebuild line 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | Current Study | 31.46 | (1793.00, 1793.00) | 8463132.0073 | 12.2278 | 69212000 | 0.17724
GEN-2024-258 | 03 CENTRAL | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 554658.1965 | 4.7569 | 11660000 | 0.087439
GEN-2024-258 | 03 CENTRAL | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 3855801.3967 | 4.1026 | 93984000 | 0.087439
GEN-2024-258 | 03 CENTRAL | TBD | ERIS | Rebuild line 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | Current Study | 15.42 | (1793.00, 1793.00) | 12731653.0763 | 37.5299 | 33924000 | 0.2937
GEN-2024-258 | 03 CENTRAL | TBD | NRIS | Rebuild line 532937 NEOSHO 5 161 532939 N345 4 5 161 1 | Current Study | 0.3 | (837.00, 837.00) | 33099.8869 | 7.3555 | 450000 | 0.028933
GEN-2024-258 | 03 CENTRAL | TBD | NRIS | Rebuild line 532937 NEOSHO 5 161 764310 G20-079-TAP 161 1 | Current Study | 20.67 | (551.00, 551.00) | 1587924.014 | 5.1215 | 31005000 | 0.015211
GEN-2024-258 | 03 CENTRAL | TBD | ERIS | Rebuild line 541199 ST JOE 7 345 541400 EASTOWN7 345 1 | Current Study | 8.12 | (1793.00, 1793.00) | 1071331.9797 | 5.9972 | 17864000 | 0.03794
GEN-2024-258 | 03 CENTRAL | TBD | ERIS | Rebuild line 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | Current Study | 28.98 | (1793.00, 1793.00) | 6090537.2249 | 9.5529 | 63756000 | 0.050336
GEN-2024-258 | 03 CENTRAL | TBD | ERIS | Rebuild line 541400 EASTOWN7 345 542982 IATAN 7 345 1 | Current Study | 23.71 | (1793.00, 1793.00) | 3001943.168 | 5.755 | 52162000 | 0.042452
GEN-2024-258 | 03 CENTRAL | 171741 | ERIS | Wolf Creek - Blackberry 345 kV Line GEN-2024-258 Interconnection (Non-Shared NU) (NEET) | Interconnection |  |  | 28818600 | 100 | 28818600 | 1
GEN-2024-258 | 03 CENTRAL | 171740 | ERIS | Wolf Creek - Blackberry 345 kV Line GEN-2024-258 Interconnection (TOIF) (NEET) | Interconnection |  |  | 840255 | 100 | 840255 | 1
GEN-2024-259 | 03 CENTRAL | 94615 | ERIS | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029 | Contingent |  |  | 0 | 0 | 543515503 | N/A
GEN-2024-259 | 03 CENTRAL | 94721 | ERIS | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 213682884 | N/A
GEN-2024-259 | 03 CENTRAL | 171743 | ERIS | Asbury 161 kV Substation GEN-2024-259 Interconnection (Non-Shared NU) (EMDE) | Interconnection |  |  | 33306052 | 100 | 33306052 | 1
GEN-2024-259 | 03 CENTRAL | 171742 | ERIS | Asbury 161 kV Substation GEN-2024-259 Interconnection (TOIF) (EMDE) | Interconnection |  |  | 5877539 | 100 | 5877539 | 1
GEN-2024-259 | 03 CENTRAL | 94929 | ERIS | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 413934522 | N/A
GEN-2024-259 | 03 CENTRAL | TBD | NRIS | Carthage_Add_transformer_fixed.idv : | Current Study |  |  | 10475000 | 100 | 10475000 | 0.020065
GEN-2024-259 | 03 CENTRAL | TBD | ERIS | Rebuild line 505488 CARTHAG5 161 547485 CAR395 5 161 1 | Current Study | 4.14 | (446.00, 446.00) | 6210000 | 100 | 6210000 | 0.30825
GEN-2024-259 | 03 CENTRAL | TBD | NRIS | Rebuild line 505492 SPRGFLD5 161 549970 CLAY 5 161 1 | Current Study | 6.73 | (246.00, 246.00) | 2421655.4877 | 23.9887 | 10095000 | 0.022574
GEN-2024-259 | 03 CENTRAL | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 359701.3088 | 3.0849 | 11660000 | 0.085143
GEN-2024-259 | 03 CENTRAL | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 2500525.2202 | 2.6606 | 93984000 | 0.085143
GEN-2024-259 | 03 CENTRAL | TBD | ERIS | Rebuild line 547467 ORO110 5 161 547490 FIR417 5 161 1 | Current Study | 2.86 | (446.00, 446.00) | 4290000 | 100 | 4290000 | 0.40824
GEN-2024-259 | 03 CENTRAL | TBD | ERIS | Rebuild line 547467 ORO110 5 161 547494 OAK432 5 161 1 | Current Study | 1.38 | (364.00, 364.00) | 2070000 | 100 | 2070000 | 0.027467
GEN-2024-259 | 03 CENTRAL | TBD | ERIS | Rebuild line 547476 ASB349 5 161 547477 CJ 366 5 161 1 | Current Study | 12.3 | (446.00, 446.00) | 18450000 | 100 | 18450000 | 0.40824
GEN-2024-259 | 03 CENTRAL | TBD | ERIS | Rebuild line 547476 ASB349 5 161 547491 PUR421 5 161 1 | Current Study | 11.94 | (446.00, 446.00) | 17910000 | 100 | 17910000 | 0.30825
GEN-2024-259 | 03 CENTRAL | TBD | ERIS | Rebuild line 547477 CJ 366 5 161 547490 FIR417 5 161 1 | Current Study | 3.26 | (446.00, 446.00) | 4890000 | 100 | 4890000 | 0.40824
GEN-2024-259 | 03 CENTRAL | TBD | ERIS | Rebuild line 547485 CAR395 5 161 547491 PUR421 5 161 1 | Current Study | 7.89 | (446.00, 446.00) | 11835000 | 100 | 11835000 | 0.30825
GEN-2024-260 | 03 CENTRAL | 94615 | ERIS | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029 | Contingent |  |  | 0 | 0 | 543515503 | N/A
GEN-2024-260 | 03 CENTRAL | TBD | ERIS | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV | Current Study |  |  | 183064.1622 | 13.2655 | 1380000 | 0.18344
GEN-2024-260 | 03 CENTRAL | TBD | ERIS | Add 16 MVAR switched shunt at HUMBOLT5 161 kV | Current Study |  |  | 348486.0555 | 10.7226 | 3250000 | 0.13035
GEN-2024-260 | 03 CENTRAL | TBD | ERIS | Add 21 MVAR switched shunt at S1263 5 161 kV | Current Study |  |  | 348486.0555 | 10.7226 | 3250000 | 0.13035
GEN-2024-260 | 03 CENTRAL | TBD | ERIS | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV | Current Study |  |  | 147972.5405 | 10.7226 | 1380000 | 0.13035
GEN-2024-260 | 03 CENTRAL | TBD | ERIS | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2 | Current Study | 0.75 | (2390.00, 2390.00) | 200059.8643 | 1.1255 | 17775000 | 0.030897
GEN-2024-260 | 03 CENTRAL | 94721 | ERIS | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 213682884 | N/A
GEN-2024-260 | 03 CENTRAL | 94929 | ERIS | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 413934522 | N/A
GEN-2024-260 | 03 CENTRAL | 171939 | ERIS | East Town 161 kV Substation GEN-2024-260 Interconnection (Non-Shared NU) (WERE) | Interconnection |  |  | 1235193 | 100 | 1235193 | 1
GEN-2024-260 | 03 CENTRAL | 171938 | ERIS | East Town 161 kV Substation GEN-2024-260 Interconnection (TOIF) (WERE) | Interconnection |  |  | 1061551 | 100 | 1061551 | 1
GEN-2024-260 | 03 CENTRAL | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 202155.7445 | 1.7338 | 11660000 | 0.047851
GEN-2024-260 | 03 CENTRAL | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 1405320.262 | 1.4953 | 93984000 | 0.047851
GEN-2024-260 | 03 CENTRAL | TBD | ERIS | Rebuild line 541251 MARYVLE5 161 541369 MIDWAY_5 161 1 | Current Study | 19.5 | (246.00, 246.00) | 20046016.1006 | 68.5334 | 29250000 | 0.067518
GEN-2024-260 | 03 CENTRAL | TBD | ERIS | Rebuild line 541253 ST JOE 5 161 541394 AVENUECTY 5 161 1 | Current Study | 3.32 | (246.00, 246.00) | 3412962.7412 | 68.5334 | 4980000 | 0.067518
GEN-2024-260 | 03 CENTRAL | TBD | ERIS | Rebuild line 541254 EAST 5 161 541401 EASTOWN5 161 1 | Current Study | 4.02 | (446.00, 446.00) | 5389499.0891 | 89.3781 | 6030000 | 0.30305
GEN-2024-260 | 03 CENTRAL | TBD | ERIS | Rebuild line 541369 MIDWAY_5 161 541394 AVENUECTY 5 161 1 | Current Study | 20.54 | (246.00, 246.00) | 21115136.9593 | 68.5334 | 30810000 | 0.067518
GEN-2024-261 | 05 SOUTHWEST | 94067 | ERIS | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028 | Contingent |  |  | 0 | 0 | 38846321 | N/A
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 29685.7086 | 2.1511 | 1380000 | 0.1074
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV | Current Study |  |  | 19315.2375 | 1.3997 | 1380000 | 0.097732
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Add 1.6 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 37879.7626 | 2.7449 | 1380000 | 0.14673
GEN-2024-261 | 05 SOUTHWEST | TBD | NRIS | Add 11 MVAR switched shunt at WWRDEHV4 138 kV | Current Study |  |  | 57012.59 | 2.3438 | 2432500 | 0.062741
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 32413.1705 | 2.3488 | 1380000 | 0.14673
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV | Current Study |  |  | 32413.1705 | 2.3488 | 1380000 | 0.14673
GEN-2024-261 | 05 SOUTHWEST | TBD | NRIS | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV | Current Study |  |  | 36171.5135 | 1.5727 | 2300000 | 0.11758
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Add 3.6 MVAR switched shunt at HEDLEY 2 69 kV | Current Study |  |  | 34374.5713 | 2.4909 | 1380000 | 0.003276
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2 | Current Study |  | (339.00, 330.00) | 352792.9702 | 2.5199 | 14000000 | 0.025612
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Add line 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 P2 | Current Study | 66.8 | (1011.00, 1176.00) | 5101500.0053 | 2.3501 | 217080000 | 0.073722
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Apply contingent IDV 01_NewLine_Phantom_Crossroads_Potter_765_26SP.idv | Contingent |  |  | 0 | 0 | 3275253469 | N/A
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Apply contingent IDV 02_765_Phantom_Craw_1_DIS24_TC05ALL-26SP.idv | Contingent |  |  | 0 | 0 | 1366342009.82 | N/A
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Apply contingent IDV 02_765_Phantom_Craw_1_DIS24_TC05ALL-29SP.idv | Contingent |  |  | 0 | 0 | 1366342009.82 | N/A
GEN-2024-261 | 05 SOUTHWEST | 171745 | ERIS | Hobbs 115 kV Line GEN-2024-261 Interconnection (Non-Shared NU) (LCEC) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-261 | 05 SOUTHWEST | 171744 | ERIS | Hobbs 115 kV Line GEN-2024-261 Interconnection (TOIF) (LCEC) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-261 | 05 SOUTHWEST | 900427 | ERIS | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032 | Contingent |  |  | 0 | 0 | 1790026304.1702 | N/A
GEN-2024-261 | 05 SOUTHWEST | TBD | NRIS | Rebuild 2-winding transformer 528334 LE-NRTH_INT3 115 528618 LE-LOVINTON2 69 1 | Current Study |  | (127.00, 127.00) | 4725000 | 100 | 4725000 | 0.090097
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | Current Study | 18.75 | (519.00, 519.00) | 897732.1116 | 2.5199 | 35625000 | 0.051225
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Current Study | 57.98 | (1793.00, 1793.00) | 2996008.0716 | 2.3488 | 127556000 | 0.14672
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | Current Study | 3.02 | (1793.00, 1793.00) | 122574.2231 | 1.8449 | 6644000 | 0.12152
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 527891 HOBBS_INT 3 115 784800 G24-261-TAP 115 1 | Current Study | 11.57 | (217.00, 217.00) | 11570000 | 100 | 11570000 | 0.65253
GEN-2024-261 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528333 LE-WEST_SUB3 115 528334 LE-NRTH_INT3 115 1 | Current Study | 0.47 | (217.00, 217.00) | 470000 | 100 | 470000 | 0.34609
GEN-2024-265 | 05 SOUTHWEST | 94067 | ERIS | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028 | Contingent |  |  | 0 | 0 | 38846321 | N/A
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 32867.5058 | 2.3817 | 1380000 | 0.10741
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV | Current Study |  |  | 21367.6189 | 1.5484 | 1380000 | 0.097654
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Add 1.6 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 42017.3812 | 3.0447 | 1380000 | 0.147
GEN-2024-265 | 05 SOUTHWEST | TBD | NRIS | Add 11 MVAR switched shunt at WWRDEHV4 138 kV | Current Study |  |  | 63124.965 | 2.5951 | 2432500 | 0.062745
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 35953.6715 | 2.6053 | 1380000 | 0.147
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV | Current Study |  |  | 35953.6715 | 2.6053 | 1380000 | 0.147
GEN-2024-265 | 05 SOUTHWEST | TBD | NRIS | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV | Current Study |  |  | 40141.4443 | 1.7453 | 2300000 | 0.11786
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Add 3.6 MVAR switched shunt at HEDLEY 2 69 kV | Current Study |  |  | 38037.5988 | 2.7563 | 1380000 | 0.0032743
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2 | Current Study |  | (339.00, 330.00) | 390393.1 | 2.7885 | 14000000 | 0.025599
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Add line 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 P2 | Current Study | 66.8 | (1011.00, 1176.00) | 5658652.8781 | 2.6067 | 217080000 | 0.073859
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Apply contingent IDV 01_NewLine_Phantom_Crossroads_Potter_765_26SP.idv | Contingent |  |  | 0 | 0 | 3275253469 | N/A
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Apply contingent IDV 02_765_Phantom_Craw_1_DIS24_TC05ALL-26SP.idv | Contingent |  |  | 0 | 0 | 1366342009.82 | N/A
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Apply contingent IDV 02_765_Phantom_Craw_1_DIS24_TC05ALL-29SP.idv | Contingent |  |  | 0 | 0 | 1366342009.82 | N/A
GEN-2024-265 | 05 SOUTHWEST | 171747 | ERIS | Hobbs 115 kV Line GEN-2024-265 Interconnection (Non-Shared NU) (SPS) | Interconnection |  |  | 15220699.21 | 100 | 15220699.21 | 1
GEN-2024-265 | 05 SOUTHWEST | 171746 | ERIS | Hobbs 115 kV Line GEN-2024-265 Interconnection (TOIF) (SPS) | Interconnection |  |  | 3262876.57 | 100 | 3262876.57 | 1
GEN-2024-265 | 05 SOUTHWEST | 900427 | ERIS | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032 | Contingent |  |  | 0 | 0 | 1790026304.1702 | N/A
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | Current Study | 18.75 | (519.00, 519.00) | 993411.0134 | 2.7885 | 35625000 | 0.051199
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Current Study | 57.98 | (1793.00, 1793.00) | 3323263.3258 | 2.6053 | 127556000 | 0.14699
GEN-2024-265 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | Current Study | 3.02 | (1793.00, 1793.00) | 139692.5794 | 2.1025 | 6644000 | 0.12509
GEN-2024-268 | 04 SOUTHEAST | 94615 | ERIS | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029 | Contingent |  |  | 0 | 0 | 543515503 | N/A
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at MOUND 4 138 kV | Current Study |  |  | 140850.7388 | 5.7904 | 2432500 | 0.036325
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 153363.3519 | 11.1133 | 1380000 | 0.063194
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 134846.9496 | 5.5436 | 2432500 | 0.05173
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 0.09 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 263434.7923 | 8.1057 | 3250000 | 0.043739
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 333148.8788 | 6.2858 | 5300000 | 0.049369
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV | Current Study |  |  | 153363.3519 | 11.1133 | 1380000 | 0.063194
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 0.2 MVAR switched shunt at GROVE 5 161 kV | Current Study |  |  | 169947.4897 | 5.2292 | 3250000 | 0.043739
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 0.25 MVAR switched shunt at LABETTS2 69 kV | Current Study |  |  | 78268.0586 | 5.6716 | 1380000 | 0.043739
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 11 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 352975.5411 | 10.8608 | 3250000 | 0.063194
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 15 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 263434.7923 | 8.1057 | 3250000 | 0.043739
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 726667.0056 | 6.0556 | 12000000 | 0.049369
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR switched shunt at NEOSHO 4 138 kV | Current Study |  |  | 86904.2459 | 3.5726 | 2432500 | 0.043739
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at CPK446 5 161 kV | Current Study |  |  | 267929.6953 | 8.244 | 3250000 | 0.063194
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV | Current Study |  |  | 263785.2064 | 8.1165 | 3250000 | 0.043739
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR switched shunt at WICHITA7 345 kV | Current Study |  |  | 309497.0918 | 5.8396 | 5300000 | 0.049369
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 177 MVAR switched shunt at SWISVAL7 345 kV | Current Study |  |  | 292595.0045 | 5.5207 | 5300000 | 0.027558
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 20 MVAR switched shunt at LIBERTY4 138 kV | Current Study |  |  | 151255.739 | 6.2181 | 2432500 | 0.05173
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 263785.2064 | 8.1165 | 3250000 | 0.043739
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR switched shunt at STILWEL7 345 kV | Current Study |  |  | 385236.9453 | 7.2686 | 5300000 | 0.027558
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 24 MVAR switched shunt at GROVE 4 138 kV | Current Study |  |  | 117468.4432 | 4.8291 | 2432500 | 0.043739
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 280 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 439148.6742 | 3.6596 | 12000000 | 0.032523
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 295 MVAR switched shunt at G18-128-TAP 345 kV | Current Study |  |  | 269422.1068 | 5.0834 | 5300000 | 0.037728
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 3 MVAR switched shunt at NEOSHOS2 69 kV | Current Study |  |  | 89355.7644 | 6.4751 | 1380000 | 0.037728
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 316 MVAR switched shunt at W.GRDNR7 345 kV | Current Study |  |  | 385236.9453 | 7.2686 | 5300000 | 0.027558
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 515301 FTSMTHW5 161 515302 FTSMITH7 345 515728 FTSMTH51 13 M2 | Current Study |  | (493.00, 493.00) | 2556614.8392 | 12.5942 | 20300000 | 0.016634
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 515302 FTSMITH7 345 515305 FTSMITH8 500 515726 FTSMTH11 13 M2 | Current Study |  | (660.00, 693.00) | 18774120.1864 | 39.9449 | 47000000 | 0.03651
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at INDEPCO5 161 kV | Current Study |  |  | 352975.5411 | 10.8608 | 3250000 | 0.063194
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 204289.4068 | 6.2858 | 3250000 | 0.049369
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 45 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 651592.6496 | 5.4299 | 12000000 | 0.037728
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 45 MVAR switched shunt at NEVADA 5 161 kV | Current Study |  |  | 160536.1166 | 4.9396 | 3250000 | 0.027558
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 56 MVAR switched shunt at WHARV4 138 kV | Current Study |  |  | 140850.7388 | 5.7904 | 2432500 | 0.036325
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV | Current Study |  |  | 120387.6072 | 8.7237 | 1380000 | 0.043739
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Add line 515012 RVRVALY7 345 780360 G24-113-TAP 345 P2 | Current Study | 23.28 | (1195.00, 1195.00) | 16697121.206 | 20.3207 | 82168000 | 0.07147
GEN-2024-268 | 04 SOUTHEAST | 94721 | ERIS | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 213682884 | N/A
GEN-2024-268 | 04 SOUTHEAST | 94929 | ERIS | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 413934522 | N/A
GEN-2024-268 | 04 SOUTHEAST | 171753 | ERIS | Muskogee - Fort Smith 345 kV Line GEN-2024-268 Interconnection (Non-Shared NU) (OGE) | Interconnection |  |  | 3000000 | 100 | 3000000 | 1
GEN-2024-268 | 04 SOUTHEAST | 171752 | ERIS | Muskogee - Fort Smith 345 kV Line GEN-2024-268 Interconnection (TOIF) (OGE) | Interconnection |  |  | 2000000 | 100 | 2000000 | 1
GEN-2024-268 | 04 SOUTHEAST | TBD | NRIS | Rebuild 3-winding transformer 516092 OKTAHA 5 161 516093 OKTAHA 2 69 516095 OKTAHA71 13 7 | Current Study |  | (186.00, 186.00) | 2800738.8935 | 46.1027 | 6075000 | 0.010374
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | Current Study | 21.38 | (1793.00, 1793.00) | 14236138.4473 | 30.2665 | 47036000 | 0.24173
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 3083679.2671 | 9.1793 | 33594000 | 0.085821
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 426263.6938 | 3.6558 | 11660000 | 0.051691
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Current Study | 14.6 | (1793.00, 1793.00) | 2948377.0334 | 9.1793 | 32120000 | 0.085821
GEN-2024-268 | 04 SOUTHEAST | TBD | NRIS | Rebuild line 515227 5TRIBES2 69 516093 OKTAHA 2 69 1 | Current Study | 13.49 | (140.00, 140.00) | 8863249.7015 | 77.2969 | 11466500 | 0.0067216
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | Current Study | 15.48 | (1793.00, 1793.00) | 3920723.6486 | 11.5126 | 34056000 | 0.03146
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 2963245.0332 | 3.1529 | 93984000 | 0.051691
GEN-2024-268 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Current Study | 25.29 | (2390.00, 2390.00) | 3360644.5041 | 6.0402 | 55638000 | 0.037872
GEN-2024-276 | 03 CENTRAL | 94615 | ERIS | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029 | Contingent |  |  | 0 | 0 | 543515503 | N/A
GEN-2024-276 | 03 CENTRAL | TBD | ERIS | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV | Current Study |  |  | 35544.0695 | 2.5757 | 1380000 | 0.052713
GEN-2024-276 | 03 CENTRAL | TBD | ERIS | Add 16 MVAR switched shunt at HUMBOLT5 161 kV | Current Study |  |  | 92264.9467 | 2.8389 | 3250000 | 0.051077
GEN-2024-276 | 03 CENTRAL | TBD | ERIS | Add 21 MVAR switched shunt at S1263 5 161 kV | Current Study |  |  | 92264.9467 | 2.8389 | 3250000 | 0.051077
GEN-2024-276 | 03 CENTRAL | TBD | ERIS | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2 | Current Study |  | (280.00, 308.00) | 6900000 | 50 | 13800000 | 0.23149
GEN-2024-276 | 03 CENTRAL | TBD | ERIS | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV | Current Study |  |  | 39177.1158 | 2.8389 | 1380000 | 0.051077
GEN-2024-276 | 03 CENTRAL | TBD | ERIS | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2 | Current Study | 0.75 | (2390.00, 2390.00) | 78685.57 | 0.44268 | 17775000 | 0.017985
GEN-2024-276 | 03 CENTRAL | 94721 | ERIS | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 213682884 | N/A
GEN-2024-276 | 03 CENTRAL | 94929 | ERIS | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 413934522 | N/A
GEN-2024-276 | 03 CENTRAL | TBD | ERIS | Rebuild line 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | Current Study | 3.02 | (551.00, 551.00) | 291665.1741 | 6.4385 | 4530000 | 0.031993
GEN-2024-276 | 03 CENTRAL | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 140714.9237 | 1.2068 | 11660000 | 0.049295
GEN-2024-276 | 03 CENTRAL | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 978203.8788 | 1.0408 | 93984000 | 0.049295
GEN-2024-276 | 03 CENTRAL | TBD | ERIS | Rebuild line 532857 TECHILL6 230 785250 G24-276-TAP 230 1 | Current Study | 0.09 | (519.00, 519.00) | 85500 | 50 | 171000 | 0.46298
GEN-2024-276 | 03 CENTRAL | TBD | ERIS | Rebuild line 541199 ST JOE 7 345 541400 EASTOWN7 345 1 | Current Study | 8.12 | (1793.00, 1793.00) | 866453.8128 | 4.8503 | 17864000 | 0.068187
GEN-2024-276 | 03 CENTRAL | TBD | ERIS | Rebuild line 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | Current Study | 28.98 | (1793.00, 1793.00) | 1686777.1727 | 2.6457 | 63756000 | 0.030979
GEN-2024-276 | 03 CENTRAL | TBD | ERIS | Rebuild line 541400 EASTOWN7 345 542982 IATAN 7 345 1 | Current Study | 23.71 | (1793.00, 1793.00) | 2440147.3846 | 4.678 | 52162000 | 0.076683
GEN-2024-276 | 03 CENTRAL | 171940 | ERIS | Tecumseh Hill - Swissvale 230kV Line GEN-2024-276 Interconnection (TOIF) (WERE) | Interconnection |  |  | 1958092 | 100 | 1958092 | 1
GEN-2024-276 | 03 CENTRAL | 171942 | ERIS | Tecumseh Hill - Swissvale 230kV Line GEN-2024-276/277 Interconnection (Shared NU) (WERE) | Interconnection |  |  | 16322218.5 | 50 | 32644437 | 1
GEN-2024-277 | 03 CENTRAL | 94615 | ERIS | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029 | Contingent |  |  | 0 | 0 | 543515503 | N/A
GEN-2024-277 | 03 CENTRAL | TBD | ERIS | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV | Current Study |  |  | 35544.0695 | 2.5757 | 1380000 | 0.052713
GEN-2024-277 | 03 CENTRAL | TBD | ERIS | Add 16 MVAR switched shunt at HUMBOLT5 161 kV | Current Study |  |  | 92264.9467 | 2.8389 | 3250000 | 0.051077
GEN-2024-277 | 03 CENTRAL | TBD | ERIS | Add 21 MVAR switched shunt at S1263 5 161 kV | Current Study |  |  | 92264.9467 | 2.8389 | 3250000 | 0.051077
GEN-2024-277 | 03 CENTRAL | TBD | ERIS | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2 | Current Study |  | (280.00, 308.00) | 6900000 | 50 | 13800000 | 0.23149
GEN-2024-277 | 03 CENTRAL | TBD | ERIS | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV | Current Study |  |  | 39177.1158 | 2.8389 | 1380000 | 0.051077
GEN-2024-277 | 03 CENTRAL | TBD | ERIS | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2 | Current Study | 0.75 | (2390.00, 2390.00) | 78685.57 | 0.44268 | 17775000 | 0.017985
GEN-2024-277 | 03 CENTRAL | 94721 | ERIS | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 213682884 | N/A
GEN-2024-277 | 03 CENTRAL | 94929 | ERIS | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 413934522 | N/A
GEN-2024-277 | 03 CENTRAL | TBD | ERIS | Rebuild line 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | Current Study | 3.02 | (551.00, 551.00) | 291665.1741 | 6.4385 | 4530000 | 0.031993
GEN-2024-277 | 03 CENTRAL | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 140714.9237 | 1.2068 | 11660000 | 0.049295
GEN-2024-277 | 03 CENTRAL | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 978203.8788 | 1.0408 | 93984000 | 0.049295
GEN-2024-277 | 03 CENTRAL | TBD | ERIS | Rebuild line 532857 TECHILL6 230 785250 G24-276-TAP 230 1 | Current Study | 0.09 | (519.00, 519.00) | 85500 | 50 | 171000 | 0.46298
GEN-2024-277 | 03 CENTRAL | TBD | ERIS | Rebuild line 541199 ST JOE 7 345 541400 EASTOWN7 345 1 | Current Study | 8.12 | (1793.00, 1793.00) | 866453.8128 | 4.8503 | 17864000 | 0.068187
GEN-2024-277 | 03 CENTRAL | TBD | ERIS | Rebuild line 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | Current Study | 28.98 | (1793.00, 1793.00) | 1686777.1727 | 2.6457 | 63756000 | 0.030979
GEN-2024-277 | 03 CENTRAL | TBD | ERIS | Rebuild line 541400 EASTOWN7 345 542982 IATAN 7 345 1 | Current Study | 23.71 | (1793.00, 1793.00) | 2440147.3846 | 4.678 | 52162000 | 0.076683
GEN-2024-277 | 03 CENTRAL | 171942 | ERIS | Tecumseh Hill - Swissvale 230kV Line GEN-2024-276/277 Interconnection (Shared NU) (WERE) | Interconnection |  |  | 16322218.5 | 50 | 32644437 | 1
GEN-2024-277 | 03 CENTRAL | 171941 | ERIS | Tecumseh Hill - Swissvale 230kV Line GEN-2024-277 Interconnection (TOIF) (WERE) | Interconnection |  |  | 112911 | 100 | 112911 | 1
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | 22.DIS2001_ERIS_G00_Line_Uprate_Hobbs_to_Sidewinder_345kV_Line.idv : DISIS-2020-001 Upgrade | Contingent |  |  | 0 | 0 | 2659649 | 0.32091
GEN-2024-280 | 05 SOUTHWEST | 94067 | ERIS | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028 | Contingent |  |  | 0 | 0 | 38846321 | N/A
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 74198.0196 | 5.3767 | 1380000 | 0.10738
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV | Current Study |  |  | 48589.7666 | 3.521 | 1380000 | 0.098343
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Add 1.6 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 93288.6924 | 6.7601 | 1380000 | 0.14454
GEN-2024-280 | 05 SOUTHWEST | TBD | NRIS | Add 11 MVAR switched shunt at WWRDEHV4 138 kV | Current Study |  |  | 142478.2925 | 5.8573 | 2432500 | 0.062718
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 79825.7984 | 5.7845 | 1380000 | 0.14454
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV | Current Study |  |  | 79825.7984 | 5.7845 | 1380000 | 0.14454
GEN-2024-280 | 05 SOUTHWEST | TBD | NRIS | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV | Current Study |  |  | 88744.1422 | 3.8584 | 2300000 | 0.11539
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Add 3.6 MVAR switched shunt at HEDLEY 2 69 kV | Current Study |  |  | 86199.398 | 6.2463 | 1380000 | 0.0032861
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2 | Current Study |  | (339.00, 330.00) | 885356.4874 | 6.324 | 14000000 | 0.02571
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Add line 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 P2 | Current Study | 66.8 | (1011.00, 1176.00) | 12565157.6084 | 5.7883 | 217080000 | 0.072631
GEN-2024-280 | 05 SOUTHWEST | 171765 | ERIS | Andrews County 345 kV Substation GEN-2024-280 Interconnection (Non-Shared NU) (SPS) | Interconnection |  |  | 8636936.73 | 100 | 8636936.73 | 1
GEN-2024-280 | 05 SOUTHWEST | 171764 | ERIS | Andrews County 345 kV Substation GEN-2024-280 Interconnection (TOIF) (SPS) | Interconnection |  |  | 4502736.58 | 100 | 4502736.58 | 1
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Apply contingent IDV 01_NewLine_Phantom_Crossroads_Potter_765_26SP.idv | Contingent |  |  | 0 | 0 | 3275253469 | N/A
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Apply contingent IDV 02_765_Phantom_Craw_1_DIS24_TC05ALL-26SP.idv | Contingent |  |  | 0 | 0 | 1366342009.82 | N/A
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Apply contingent IDV 02_765_Phantom_Craw_1_DIS24_TC05ALL-29SP.idv | Contingent |  |  | 0 | 0 | 1366342009.82 | N/A
GEN-2024-280 | 05 SOUTHWEST | 900427 | ERIS | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032 | Contingent |  |  | 0 | 0 | 1790026304.1702 | N/A
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | Current Study | 18.75 | (519.00, 519.00) | 2252916.0618 | 6.324 | 35625000 | 0.051421
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Current Study | 57.98 | (1793.00, 1793.00) | 7378437.3505 | 5.7845 | 127556000 | 0.14453
GEN-2024-280 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | Current Study | 3.02 | (1793.00, 1793.00) | 233325.3655 | 3.5118 | 6644000 | 0.092527
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | 22.DIS2001_ERIS_G00_Line_Uprate_Hobbs_to_Sidewinder_345kV_Line.idv : DISIS-2020-001 Upgrade | Contingent |  |  | 0 | 0 | 2659649 | 0.14024
GEN-2024-281 | 05 SOUTHWEST | 94067 | ERIS | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028 | Contingent |  |  | 0 | 0 | 38846321 | N/A
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 53043.5757 | 3.8437 | 1380000 | 0.10747
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV | Current Study |  |  | 34618.5564 | 2.5086 | 1380000 | 0.098092
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Add 1.6 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 66866.8474 | 4.8454 | 1380000 | 0.14504
GEN-2024-281 | 05 SOUTHWEST | TBD | NRIS | Add 11 MVAR switched shunt at WWRDEHV4 138 kV | Current Study |  |  | 101918.0593 | 4.1898 | 2432500 | 0.062809
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 57217.004 | 4.1462 | 1380000 | 0.14504
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV | Current Study |  |  | 57217.004 | 4.1462 | 1380000 | 0.14504
GEN-2024-281 | 05 SOUTHWEST | TBD | NRIS | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV | Current Study |  |  | 63665.9099 | 2.7681 | 2300000 | 0.11589
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Add 3.6 MVAR switched shunt at HEDLEY 2 69 kV | Current Study |  |  | 61212.1154 | 4.4357 | 1380000 | 0.0032669
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2 | Current Study |  | (339.00, 330.00) | 630704.1027 | 4.505 | 14000000 | 0.025642
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Add line 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 P2 | Current Study | 66.8 | (1011.00, 1176.00) | 9002349.2903 | 4.147 | 217080000 | 0.072852
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Apply contingent IDV 01_NewLine_Phantom_Crossroads_Potter_765_26SP.idv | Contingent |  |  | 0 | 0 | 3275253469 | N/A
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Apply contingent IDV 02_765_Phantom_Craw_1_DIS24_TC05ALL-26SP.idv | Contingent |  |  | 0 | 0 | 1366342009.82 | N/A
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Apply contingent IDV 02_765_Phantom_Craw_1_DIS24_TC05ALL-29SP.idv | Contingent |  |  | 0 | 0 | 1366342009.82 | N/A
GEN-2024-281 | 05 SOUTHWEST | 171767 | ERIS | Jal - Teague 115 kV Line GEN-2024-281 Interconnection (Non-Shared NU) (SPS) | Interconnection |  |  | 22838049.8 | 100 | 22838049.8 | 1
GEN-2024-281 | 05 SOUTHWEST | 171766 | ERIS | Jal - Teague 115 kV Line GEN-2024-281 Interconnection (TOIF) (SPS) | Interconnection |  |  | 2804642.69 | 100 | 2804642.69 | 1
GEN-2024-281 | 05 SOUTHWEST | 900427 | ERIS | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032 | Contingent |  |  | 0 | 0 | 1790026304.1702 | N/A
GEN-2024-281 | 05 SOUTHWEST | 900119 | ERIS | Multi - Battle Axe - Wolfcamp Tap 115 kV DblCkt_Battle Axe - Ponderosa - Dollarhide 115 kV New Line.idv : PID : 900119, NTC, 2025 ITP, ISD: 6/1/2029 | Contingent |  |  | 0 | 0 | 224392680.0012 | N/A
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | Current Study | 18.75 | (519.00, 519.00) | 1604916.69 | 4.505 | 35625000 | 0.051283
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Current Study | 57.98 | (1793.00, 1793.00) | 5288668.0473 | 4.1462 | 127556000 | 0.14504
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | Current Study | 3.02 | (1793.00, 1793.00) | 158530.4947 | 2.3861 | 6644000 | 0.088013
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528526 TEAGUE 3 115 528596 CARDINAL 3 115 1 | Current Study | 6.81 | (260.00, 260.00) | 6810000 | 100 | 6810000 | 0.54748
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528526 TEAGUE 3 115 785400 G24-281-TAP 115 1 | Current Study | 2.6 | (260.00, 260.00) | 2600000 | 100 | 2600000 | 0.54748
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528547 S_JAL 3 115 528561 DOLLARHIDE 3 115 1 | Current Study | 3.7 | (176.00, 176.00) | 3700000 | 100 | 3700000 | 0.16547
GEN-2024-281 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 528547 S_JAL 3 115 785400 G24-281-TAP 115 1 | Current Study | 10.82 | (260.00, 260.00) | 10820000 | 100 | 10820000 | 0.45252
GEN-2024-286 | 04 SOUTHEAST | 900426 | ERIS | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030 | Contingent |  |  | 0 | 0 | 2372127948.71 | N/A
GEN-2024-286 | 04 SOUTHEAST | TBD | ERIS | Add 2 MVAR switched shunt at GEN-2017-140 345 kV | Current Study |  |  | 94932.84 | 1.7912 | 5300000 | 0.15067
GEN-2024-286 | 04 SOUTHEAST | 171776 | ERIS | AES 5 161 kV Substation GEN-2024-286 Interconnection (Non-Shared NU) (OGE) | Interconnection |  |  | 12000000 | 100 | 12000000 | 1
GEN-2024-286 | 04 SOUTHEAST | 171775 | ERIS | AES 5 161 kV Substation GEN-2024-286 Interconnection (TOIF) (OGE) | Interconnection |  |  | 5000000 | 100 | 5000000 | 1
GEN-2024-286 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 505522 VAN BUR5 161 505524 LIBERTY5 161 1 | Current Study | 12.1 | (309.00, 309.00) | 3120394.3818 | 17.1923 | 18150000 | 0.060642
GEN-2024-286 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 505552 GORE 5 161 505558 MUSKTAP5 161 1 | Current Study | 16 | (246.00, 246.00) | 7453233.9415 | 31.0551 | 24000000 | 0.085507
GEN-2024-286 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514934 DRAPER 7 345 515045 SEMINOL7 345 2 | Current Study | 44.14 | (1793.00, 1793.00) | 1081648.5549 | 1.1139 | 97108000 | 0.03358
GEN-2024-286 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515339 VBI 5 161 515406 ADABELL5 161 1 | Current Study | 2.16 | (309.00, 309.00) | 39022.1435 | 1.2044 | 3240000 | 0.0031664
GEN-2024-287 | 03 CENTRAL | 94615 | ERIS | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029 | Contingent |  |  | 0 | 0 | 543515503 | N/A
GEN-2024-287 | 03 CENTRAL | TBD | ERIS | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV | Current Study |  |  | 31506.0831 | 2.283 | 1380000 | 0.031571
GEN-2024-287 | 03 CENTRAL | TBD | ERIS | Add 16 MVAR switched shunt at HUMBOLT5 161 kV | Current Study |  |  | 80055.7538 | 2.4633 | 3250000 | 0.029945
GEN-2024-287 | 03 CENTRAL | TBD | ERIS | Add 21 MVAR switched shunt at S1263 5 161 kV | Current Study |  |  | 80055.7538 | 2.4633 | 3250000 | 0.029945
GEN-2024-287 | 03 CENTRAL | TBD | NRIS | Add 3-winding transformer 532793 NEOSHO 7 345 532825 N345 2 1 13 532939 N345 4 5 161 M2 | Current Study |  | (500.00, 550.00) | 1031167.1255 | 5.0796 | 20300000 | 0.015001
GEN-2024-287 | 03 CENTRAL | TBD | ERIS | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV | Current Study |  |  | 33992.9047 | 2.4633 | 1380000 | 0.029945
GEN-2024-287 | 03 CENTRAL | 94721 | ERIS | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 213682884 | N/A
GEN-2024-287 | 03 CENTRAL | 94929 | ERIS | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 413934522 | N/A
GEN-2024-287 | 03 CENTRAL | TBD | NRIS | Rebuild line 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | Current Study | 31.46 | (1793.00, 1793.00) | 8531165.0206 | 12.3261 | 69212000 | 0.26827
GEN-2024-287 | 03 CENTRAL | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 429971.3909 | 3.6876 | 11660000 | 0.10178
GEN-2024-287 | 03 CENTRAL | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 2989019.7244 | 3.1803 | 93984000 | 0.10178
GEN-2024-287 | 03 CENTRAL | TBD | ERIS | Rebuild line 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | Current Study | 15.42 | (1793.00, 1793.00) | 6045151.3284 | 17.8197 | 33924000 | 0.20939
GEN-2024-287 | 03 CENTRAL | TBD | NRIS | Rebuild line 532937 NEOSHO 5 161 532939 N345 4 5 161 1 | Current Study | 0.3 | (837.00, 837.00) | 22858.3846 | 5.0796 | 450000 | 0.030002
GEN-2024-287 | 03 CENTRAL | TBD | NRIS | Rebuild line 532937 NEOSHO 5 161 764310 G20-079-TAP 161 1 | Current Study | 20.67 | (551.00, 551.00) | 1187174.714 | 3.829 | 31005000 | 0.017076
GEN-2024-287 | 03 CENTRAL | TBD | ERIS | Rebuild line 541400 EASTOWN7 345 542982 IATAN 7 345 1 | Current Study | 23.71 | (1793.00, 1793.00) | 1324558.989 | 2.5393 | 52162000 | 0.028125
GEN-2024-287 | 03 CENTRAL | 171778 | ERIS | Wolf Creek - Blackberry 345 kV Line GEN-2024-287 Interconnection (Non-Shared NU) (NEET) | Interconnection |  |  | 28818600 | 100 | 28818600 | 1
GEN-2024-287 | 03 CENTRAL | 171777 | ERIS | Wolf Creek - Blackberry 345 kV Line GEN-2024-287 Interconnection (TOIF) (NEET) | Interconnection |  |  | 840255 | 100 | 840255 | 1
GEN-2024-293 | 04 SOUTHEAST | 900426 | ERIS | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030 | Contingent |  |  | 0 | 0 | 2372127948.71 | N/A
GEN-2024-293 | 04 SOUTHEAST | TBD | ERIS | Add 2 MVAR switched shunt at GEN-2017-140 345 kV | Current Study |  |  | 1148929.4976 | 21.6779 | 5300000 | 1
GEN-2024-293 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 515301 FTSMTHW5 161 515302 FTSMITH7 345 515728 FTSMTH51 13 M2 | Current Study |  | (493.00, 493.00) | 1362809.6423 | 6.7133 | 20300000 | 0.013943
GEN-2024-293 | 04 SOUTHEAST | 171784 | ERIS | Muskoge7 345 kV Substation GEN-2024-293 Interconnection (Non-Shared NU) (OGE) | Interconnection |  |  | 5000000 | 100 | 5000000 | 1
GEN-2024-293 | 04 SOUTHEAST | 171783 | ERIS | Muskoge7 345 kV Substation GEN-2024-293 Interconnection (TOIF) (OGE) | Interconnection |  |  | 3000000 | 100 | 3000000 | 1
GEN-2024-293 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514934 DRAPER 7 345 515045 SEMINOL7 345 2 | Current Study | 44.14 | (1793.00, 1793.00) | 2009655.3227 | 2.0695 | 97108000 | 0.034214
GEN-2024-294 | 04 SOUTHEAST | 94615 | ERIS | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029 | Contingent |  |  | 0 | 0 | 543515503 | N/A
GEN-2024-294 | 04 SOUTHEAST | 94811 | ERIS | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030 | Contingent |  |  | 0 | 0 | 1097029189 | N/A
GEN-2024-294 | 04 SOUTHEAST | 94911 | ERIS | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030 | Contingent |  |  | 0 | 0 | 143524375 | N/A
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at JAY 4 138 kV | Current Study |  |  | 1431333.625 | 58.8421 | 2432500 | 0.15176
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at MOUND 4 138 kV | Current Study |  |  | 191150.6673 | 7.8582 | 2432500 | 0.038452
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV | Current Study |  |  | 565424.7858 | 10.6684 | 5300000 | 0.032168
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 199253.2157 | 8.1913 | 2432500 | 0.059621
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 0.04 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 877137.1803 | 26.9888 | 3250000 | 0.035058
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 0.09 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 1037531.641 | 31.9241 | 3250000 | 0.13437
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 0.11 MVAR switched shunt at CHAMSPR7 345 kV | Current Study |  |  | 3118630.3032 | 58.8421 | 5300000 | 0.15176
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 581741.5086 | 10.9763 | 5300000 | 0.067242
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 0.13 MVAR switched shunt at PECULR 7 345 kV | Current Study |  |  | 1733975.453 | 32.7165 | 5300000 | 0.032168
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 0.2 MVAR switched shunt at GROVE 5 161 kV | Current Study |  |  | 669334.1313 | 20.5949 | 3250000 | 0.13437
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 0.25 MVAR switched shunt at LABETTS2 69 kV | Current Study |  |  | 308256.8804 | 22.3375 | 1380000 | 0.13437
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at TONTITN7 345 kV | Current Study |  |  | 3040235.8906 | 57.3629 | 5300000 | 0.15176
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 15 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 1037531.641 | 31.9241 | 3250000 | 0.13437
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 1268899.2427 | 10.5742 | 12000000 | 0.067242
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR switched shunt at NEOSHO 4 138 kV | Current Study |  |  | 342270.2981 | 14.0707 | 2432500 | 0.13437
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at CPK446 5 161 kV | Current Study |  |  | 190564.1479 | 5.8635 | 3250000 | 0.035058
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV | Current Study |  |  | 1038911.7384 | 31.9665 | 3250000 | 0.13437
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR switched shunt at WICHITA7 345 kV | Current Study |  |  | 540440.9755 | 10.197 | 5300000 | 0.067242
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 177 MVAR switched shunt at SWISVAL7 345 kV | Current Study |  |  | 544210.6167 | 10.2681 | 5300000 | 0.03998
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 20 MVAR switched shunt at LIBERTY4 138 kV | Current Study |  |  | 173480.8163 | 7.1318 | 2432500 | 0.046278
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 1038911.7384 | 31.9665 | 3250000 | 0.13437
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR switched shunt at STILWEL7 345 kV | Current Study |  |  | 716519.5317 | 13.5192 | 5300000 | 0.03998
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 24 MVAR switched shunt at GROVE 4 138 kV | Current Study |  |  | 462646.6593 | 19.0194 | 2432500 | 0.13437
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at G21-096-TAP 345 kV | Current Study |  |  | 889860.2298 | 16.7898 | 5300000 | 0.040746
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 280 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 1032101.8889 | 8.6008 | 12000000 | 0.059621
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 295 MVAR switched shunt at G18-128-TAP 345 kV | Current Study |  |  | 326839.1291 | 6.1668 | 5300000 | 0.035699
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 3 MVAR switched shunt at NEOSHOS2 69 kV | Current Study |  |  | 108398.5296 | 7.855 | 1380000 | 0.035699
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at G23-220-TAP 345 kV | Current Study |  |  | 633602.8615 | 11.9548 | 5300000 | 0.032168
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 316 MVAR switched shunt at W.GRDNR7 345 kV | Current Study |  |  | 716519.5317 | 13.5192 | 5300000 | 0.03998
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 356728.2836 | 10.9763 | 3250000 | 0.067242
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 45 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 790454.7129 | 6.5871 | 12000000 | 0.035699
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 45 MVAR switched shunt at NEVADA 5 161 kV | Current Study |  |  | 298588.3481 | 9.1873 | 3250000 | 0.03998
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 56 MVAR switched shunt at WHARV4 138 kV | Current Study |  |  | 191150.6673 | 7.8582 | 2432500 | 0.038452
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV | Current Study |  |  | 474143.7172 | 34.3582 | 1380000 | 0.13437
GEN-2024-294 | 04 SOUTHEAST | 94721 | ERIS | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 213682884 | N/A
GEN-2024-294 | 04 SOUTHEAST | 94929 | ERIS | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 413934522 | N/A
GEN-2024-294 | 04 SOUTHEAST | 900427 | ERIS | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032 | Contingent |  |  | 0 | 0 | 1790026304.1702 | N/A
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 4272571.5358 | 12.7183 | 33594000 | 0.092748
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 488756.2128 | 4.1917 | 11660000 | 0.04623
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Current Study | 14.6 | (1793.00, 1793.00) | 4085104.4154 | 12.7183 | 32120000 | 0.092748
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 2289623.2057 | 77.0917 | 2970000 | 0.48763
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 1578888.6908 | 71.7677 | 2200000 | 0.48763
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | Current Study | 15.48 | (1793.00, 1793.00) | 7094653.923 | 20.8323 | 34056000 | 0.044403
GEN-2024-294 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 3397672.4762 | 3.6152 | 93984000 | 0.04623
GEN-2024-294 | 04 SOUTHEAST | 171786 | ERIS | Tulsa North - Igloo Valley 345 kV line GEN-2024-294 Interconnection (Non-Shared NU) (GRDA) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-294 | 04 SOUTHEAST | 171786 | ERIS | Tulsa North - Igloo Valley 345 kV line GEN-2024-294 Interconnection (Non-Shared NU) (GRDA) | Interconnection |  |  | 130000 | 100 | 130000 | 1
GEN-2024-294 | 04 SOUTHEAST | 171785 | ERIS | Tulsa North - Igloo Valley 345 kV line GEN-2024-294 Interconnection (TOIF) (GRDA) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-295 | 05 SOUTHWEST | 94067 | ERIS | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028 | Contingent |  |  | 0 | 0 | 38846321 | N/A
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 24447.7919 | 1.7716 | 1380000 | 0.10768
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV | Current Study |  |  | 15876.6415 | 1.1505 | 1380000 | 0.097797
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Add 1.6 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 30778.9997 | 2.2304 | 1380000 | 0.14514
GEN-2024-295 | 05 SOUTHWEST | TBD | NRIS | Add 11 MVAR switched shunt at WWRDEHV4 138 kV | Current Study |  |  | 47039.2641 | 1.9338 | 2432500 | 0.063019
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 26337.1494 | 1.9085 | 1380000 | 0.14514
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV | Current Study |  |  | 26337.1494 | 1.9085 | 1380000 | 0.14514
GEN-2024-295 | 05 SOUTHWEST | TBD | NRIS | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV | Current Study |  |  | 32746.1133 | 1.4237 | 2300000 | 0.12959
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Add 3.6 MVAR switched shunt at HEDLEY 2 69 kV | Current Study |  |  | 27799.6582 | 2.0145 | 1380000 | 0.0032254
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2 | Current Study |  | (339.00, 330.00) | 288797.5827 | 2.0628 | 14000000 | 0.025524
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Add 69 MVAR switched shunt at SENDERO +3 115 kV | Current Study |  |  | 1983290.614 | 89.6403 | 2212500 | 1
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Add line 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 P2 | Current Study | 66.8 | (1011.00, 1176.00) | 4147069.8731 | 1.9104 | 217080000 | 0.072957
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Apply contingent IDV 01_NewLine_Phantom_Crossroads_Potter_765_26SP.idv | Contingent |  |  | 0 | 0 | 3275253469 | N/A
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Apply contingent IDV 02_765_Phantom_Craw_1_DIS24_TC05ALL-26SP.idv | Contingent |  |  | 0 | 0 | 1366342009.82 | N/A
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Apply contingent IDV 02_765_Phantom_Craw_1_DIS24_TC05ALL-29SP.idv | Contingent |  |  | 0 | 0 | 1366342009.82 | N/A
GEN-2024-295 | 05 SOUTHWEST | 900427 | ERIS | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032 | Contingent |  |  | 0 | 0 | 1790026304.1702 | N/A
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | Current Study | 18.75 | (519.00, 519.00) | 734886.706 | 2.0628 | 35625000 | 0.051049
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Current Study | 57.98 | (1793.00, 1793.00) | 2434388.9031 | 1.9085 | 127556000 | 0.14513
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523959 POTTER_CO 6 230 524010 ROLLHILLS 6 230 1 | Current Study | 6.23 | (637.00, 637.00) | 496539.171 | 4.1948 | 11837000 | 0.035403
GEN-2024-295 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | Current Study | 3.02 | (1793.00, 1793.00) | 51339.2543 | 0.77272 | 6644000 | 0.061962
GEN-2024-295 | 05 SOUTHWEST | 171788 | ERIS | S Loving 115 kV Substation GEN-2024-295 Interconnection (Non-Shared NU) (SPS) | Interconnection |  |  | 2172444.84 | 100 | 2172444.84 | 1
GEN-2024-295 | 05 SOUTHWEST | 171787 | ERIS | S Loving 115 kV Substation GEN-2024-295 Interconnection (TOIF) (SPS) | Interconnection |  |  | 3362273.9 | 100 | 3362273.9 | 1
GEN-2024-296 | 04 SOUTHEAST | 94615 | ERIS | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029 | Contingent |  |  | 0 | 0 | 543515503 | N/A
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at MOUND 4 138 kV | Current Study |  |  | 62756.5262 | 2.5799 | 2432500 | 0.037797
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 50075.3705 | 3.6287 | 1380000 | 0.048187
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 50943.2207 | 2.0943 | 2432500 | 0.045639
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 0.09 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 93484.2395 | 2.8764 | 3250000 | 0.036248
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 129570.0408 | 2.4447 | 5300000 | 0.04484
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV | Current Study |  |  | 50075.3705 | 3.6287 | 1380000 | 0.048187
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 0.2 MVAR switched shunt at GROVE 5 161 kV | Current Study |  |  | 60308.7075 | 1.8557 | 3250000 | 0.036248
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 0.25 MVAR switched shunt at LABETTS2 69 kV | Current Study |  |  | 27774.7289 | 2.0127 | 1380000 | 0.036248
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 11 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 115251.6606 | 3.5462 | 3250000 | 0.048187
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 15 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 93484.2395 | 2.8764 | 3250000 | 0.036248
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 282619.2119 | 2.3552 | 12000000 | 0.04484
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR switched shunt at NEOSHO 4 138 kV | Current Study |  |  | 30839.4243 | 1.2678 | 2432500 | 0.036248
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at CPK446 5 161 kV | Current Study |  |  | 87482.9519 | 2.6918 | 3250000 | 0.048187
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV | Current Study |  |  | 93608.5898 | 2.8803 | 3250000 | 0.036248
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR switched shunt at WICHITA7 345 kV | Current Study |  |  | 120371.2615 | 2.2712 | 5300000 | 0.04484
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 177 MVAR switched shunt at SWISVAL7 345 kV | Current Study |  |  | 119415.8092 | 2.2531 | 5300000 | 0.026266
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 20 MVAR switched shunt at LIBERTY4 138 kV | Current Study |  |  | 57142.2232 | 2.3491 | 2432500 | 0.045639
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 93608.5898 | 2.8803 | 3250000 | 0.036248
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 24 MVAR switched shunt at GROVE 4 138 kV | Current Study |  |  | 41685.6406 | 1.7137 | 2432500 | 0.036248
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 280 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 233162.2398 | 1.943 | 12000000 | 0.040327
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 295 MVAR switched shunt at G18-128-TAP 345 kV | Current Study |  |  | 122949.9613 | 2.3198 | 5300000 | 0.040207
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 3 MVAR switched shunt at NEOSHOS2 69 kV | Current Study |  |  | 40777.2321 | 2.9549 | 1380000 | 0.040207
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 515301 FTSMTHW5 161 515302 FTSMITH7 345 515728 FTSMTH51 13 M2 | Current Study |  | (493.00, 493.00) | 575489.4479 | 2.8349 | 20300000 | 0.008744
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 515302 FTSMITH7 345 515305 FTSMITH8 500 515726 FTSMTH11 13 M2 | Current Study |  | (660.00, 693.00) | 4611911.0296 | 9.8126 | 47000000 | 0.020945
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at INDEPCO5 161 kV | Current Study |  |  | 115251.6606 | 3.5462 | 3250000 | 0.048187
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 79453.3269 | 2.4447 | 3250000 | 0.04484
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 45 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 297352.3294 | 2.4779 | 12000000 | 0.040207
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 45 MVAR switched shunt at NEVADA 5 161 kV | Current Study |  |  | 65519.0621 | 2.016 | 3250000 | 0.026266
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 56 MVAR switched shunt at WHARV4 138 kV | Current Study |  |  | 62756.5262 | 2.5799 | 2432500 | 0.037797
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV | Current Study |  |  | 42721.5548 | 3.0958 | 1380000 | 0.036248
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Add line 515012 RVRVALY7 345 780360 G24-113-TAP 345 P2 | Current Study | 23.28 | (1195.00, 1195.00) | 3787016.1322 | 4.6089 | 82168000 | 0.037856
GEN-2024-296 | 04 SOUTHEAST | 94721 | ERIS | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 213682884 | N/A
GEN-2024-296 | 04 SOUTHEAST | 94929 | ERIS | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 413934522 | N/A
GEN-2024-296 | 04 SOUTHEAST | 171789 | ERIS | Muskogee - Pittsburg 345 kV Line GEN-2024-296 Interconnection (TOIF) (OGE) | Interconnection |  |  | 3000000 | 100 | 3000000 | 1
GEN-2024-296 | 04 SOUTHEAST | 171792 | ERIS | Muskogee - Pittsburg 345 kV Line GEN-2024-296/297/298 Interconnection (Shared NU) (OGE) | Interconnection |  |  | 9000000 | 33.3333 | 18000000 | 1
GEN-2024-296 | 04 SOUTHEAST | TBD | NRIS | Rebuild 3-winding transformer 516092 OKTAHA 5 161 516093 OKTAHA 2 69 516095 OKTAHA71 13 7 | Current Study |  | (186.00, 186.00) | 1296286.2 | 21.338 | 6075000 | 0.011213
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | Current Study | 21.38 | (1793.00, 1793.00) | 4093575.1969 | 8.7031 | 47036000 | 0.16233
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 1088112.8633 | 3.239 | 33594000 | 0.07072
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 161016.5638 | 1.3809 | 11660000 | 0.045599
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Current Study | 14.6 | (1793.00, 1793.00) | 1040369.8628 | 3.239 | 32120000 | 0.07072
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 1484131.2928 | 3.2324 | 45914000 | 0.040537
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 1119334.2051 | 1.191 | 93984000 | 0.045599
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Current Study | 25.29 | (2390.00, 2390.00) | 1533394.4886 | 2.756 | 55638000 | 0.040355
GEN-2024-296 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 809978.6979 | 3.2324 | 25058000 | 0.040537
GEN-2024-297 | 04 SOUTHEAST | 94615 | ERIS | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029 | Contingent |  |  | 0 | 0 | 543515503 | N/A
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at MOUND 4 138 kV | Current Study |  |  | 62756.5262 | 2.5799 | 2432500 | 0.037797
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 50075.3705 | 3.6287 | 1380000 | 0.048187
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 50943.2207 | 2.0943 | 2432500 | 0.045639
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 0.09 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 93484.2395 | 2.8764 | 3250000 | 0.036248
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 129570.0408 | 2.4447 | 5300000 | 0.04484
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV | Current Study |  |  | 50075.3705 | 3.6287 | 1380000 | 0.048187
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 0.2 MVAR switched shunt at GROVE 5 161 kV | Current Study |  |  | 60308.7075 | 1.8557 | 3250000 | 0.036248
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 0.25 MVAR switched shunt at LABETTS2 69 kV | Current Study |  |  | 27774.7289 | 2.0127 | 1380000 | 0.036248
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 11 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 115251.6606 | 3.5462 | 3250000 | 0.048187
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 15 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 93484.2395 | 2.8764 | 3250000 | 0.036248
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 282619.2119 | 2.3552 | 12000000 | 0.04484
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR switched shunt at NEOSHO 4 138 kV | Current Study |  |  | 30839.4243 | 1.2678 | 2432500 | 0.036248
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at CPK446 5 161 kV | Current Study |  |  | 87482.9519 | 2.6918 | 3250000 | 0.048187
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV | Current Study |  |  | 93608.5898 | 2.8803 | 3250000 | 0.036248
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR switched shunt at WICHITA7 345 kV | Current Study |  |  | 120371.2615 | 2.2712 | 5300000 | 0.04484
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 177 MVAR switched shunt at SWISVAL7 345 kV | Current Study |  |  | 119415.8092 | 2.2531 | 5300000 | 0.026266
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 20 MVAR switched shunt at LIBERTY4 138 kV | Current Study |  |  | 57142.2232 | 2.3491 | 2432500 | 0.045639
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 93608.5898 | 2.8803 | 3250000 | 0.036248
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 24 MVAR switched shunt at GROVE 4 138 kV | Current Study |  |  | 41685.6406 | 1.7137 | 2432500 | 0.036248
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 280 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 233162.2398 | 1.943 | 12000000 | 0.040327
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 295 MVAR switched shunt at G18-128-TAP 345 kV | Current Study |  |  | 122949.9613 | 2.3198 | 5300000 | 0.040207
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 3 MVAR switched shunt at NEOSHOS2 69 kV | Current Study |  |  | 40777.2321 | 2.9549 | 1380000 | 0.040207
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 515301 FTSMTHW5 161 515302 FTSMITH7 345 515728 FTSMTH51 13 M2 | Current Study |  | (493.00, 493.00) | 575489.4479 | 2.8349 | 20300000 | 0.008744
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 515302 FTSMITH7 345 515305 FTSMITH8 500 515726 FTSMTH11 13 M2 | Current Study |  | (660.00, 693.00) | 4611911.0296 | 9.8126 | 47000000 | 0.020945
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at INDEPCO5 161 kV | Current Study |  |  | 115251.6606 | 3.5462 | 3250000 | 0.048187
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 79453.3269 | 2.4447 | 3250000 | 0.04484
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 45 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 297352.3294 | 2.4779 | 12000000 | 0.040207
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 45 MVAR switched shunt at NEVADA 5 161 kV | Current Study |  |  | 65519.0621 | 2.016 | 3250000 | 0.026266
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 56 MVAR switched shunt at WHARV4 138 kV | Current Study |  |  | 62756.5262 | 2.5799 | 2432500 | 0.037797
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV | Current Study |  |  | 42721.5548 | 3.0958 | 1380000 | 0.036248
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Add line 515012 RVRVALY7 345 780360 G24-113-TAP 345 P2 | Current Study | 23.28 | (1195.00, 1195.00) | 3787016.1322 | 4.6089 | 82168000 | 0.037856
GEN-2024-297 | 04 SOUTHEAST | 94721 | ERIS | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 213682884 | N/A
GEN-2024-297 | 04 SOUTHEAST | 94929 | ERIS | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 413934522 | N/A
GEN-2024-297 | 04 SOUTHEAST | 171792 | ERIS | Muskogee - Pittsburg 345 kV Line GEN-2024-296/297/298 Interconnection (Shared NU) (OGE) | Interconnection |  |  | 9000000 | 33.3333 | 18000000 | 1
GEN-2024-297 | 04 SOUTHEAST | 171790 | ERIS | Muskogee - Pittsburg 345 kV Line GEN-2024-297 Interconnection (TOIF) (OGE) | Interconnection |  |  | 3000000 | 100 | 3000000 | 1
GEN-2024-297 | 04 SOUTHEAST | TBD | NRIS | Rebuild 3-winding transformer 516092 OKTAHA 5 161 516093 OKTAHA 2 69 516095 OKTAHA71 13 7 | Current Study |  | (186.00, 186.00) | 1296286.2 | 21.338 | 6075000 | 0.011213
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | Current Study | 21.38 | (1793.00, 1793.00) | 4093575.1969 | 8.7031 | 47036000 | 0.16233
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 1088112.8633 | 3.239 | 33594000 | 0.07072
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 161016.5638 | 1.3809 | 11660000 | 0.045599
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Current Study | 14.6 | (1793.00, 1793.00) | 1040369.8628 | 3.239 | 32120000 | 0.07072
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 1484131.2928 | 3.2324 | 45914000 | 0.040537
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 1119334.2051 | 1.191 | 93984000 | 0.045599
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Current Study | 25.29 | (2390.00, 2390.00) | 1533394.4886 | 2.756 | 55638000 | 0.040355
GEN-2024-297 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 809978.6979 | 3.2324 | 25058000 | 0.040537
GEN-2024-299 | 04 SOUTHEAST | 900426 | ERIS | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030 | Contingent |  |  | 0 | 0 | 2372127948.71 | N/A
GEN-2024-299 | 04 SOUTHEAST | TBD | ERIS | Add 2 MVAR switched shunt at GEN-2017-140 345 kV | Current Study |  |  | 689026.6587 | 13.0005 | 5300000 | 0.1999
GEN-2024-299 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 515301 FTSMTHW5 161 515302 FTSMITH7 345 515728 FTSMTH51 13 M2 | Current Study |  | (493.00, 493.00) | 12240356.88 | 60.2973 | 20300000 | 0.041745
GEN-2024-299 | 04 SOUTHEAST | 171794 | ERIS | AES 5 345 kV Substation GEN-2024-299 Interconnection (Non-Shared NU) (OGE) | Interconnection |  |  | 20000000 | 100 | 20000000 | 1
GEN-2024-299 | 04 SOUTHEAST | 171793 | ERIS | AES 5 345 kV Substation GEN-2024-299 Interconnection (TOIF) (OGE) | Interconnection |  |  | 8000000 | 100 | 8000000 | 1
GEN-2024-299 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 505522 VAN BUR5 161 505524 LIBERTY5 161 1 | Current Study | 12.1 | (309.00, 309.00) | 10708941.0284 | 59.0024 | 18150000 | 0.038043
GEN-2024-299 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 505552 GORE 5 161 505558 MUSKTAP5 161 1 | Current Study | 16 | (246.00, 246.00) | 11494816.574 | 47.8951 | 24000000 | 0.024106
GEN-2024-299 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514934 DRAPER 7 345 515045 SEMINOL7 345 2 | Current Study | 44.14 | (1793.00, 1793.00) | 6402152.0021 | 6.5928 | 97108000 | 0.036332
GEN-2024-299 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515301 FTSMTHW5 161 515306 ARKOMA 5 161 1 | Current Study | 4.48 | (446.00, 446.00) | 6720000 | 100 | 6720000 | 0.039084
GEN-2024-299 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515306 ARKOMA 5 161 515308 3RDST 5 161 1 | Current Study | 2.44 | (364.00, 364.00) | 3660000 | 100 | 3660000 | 0.039084
GEN-2024-299 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515308 3RDST 5 161 515356 JSTREET5 161 1 | Current Study | 0.45 | (246.00, 246.00) | 675000 | 100 | 675000 | 0.031332
GEN-2024-299 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515339 VBI 5 161 515406 ADABELL5 161 1 | Current Study | 2.16 | (309.00, 309.00) | 3200977.8565 | 98.7956 | 3240000 | 0.047479
GEN-2024-303 | 05 SOUTHWEST | 94067 | ERIS | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028 | Contingent |  |  | 0 | 0 | 38846321 | N/A
GEN-2024-303 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 105218.346 | 7.6245 | 1380000 | 0.10659
GEN-2024-303 | 05 SOUTHWEST | TBD | ERIS | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV | Current Study |  |  | 71512.7123 | 5.1821 | 1380000 | 0.10132
GEN-2024-303 | 05 SOUTHWEST | TBD | ERIS | Add 1.6 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 126362.4161 | 9.1567 | 1380000 | 0.13705
GEN-2024-303 | 05 SOUTHWEST | TBD | NRIS | Add 11 MVAR switched shunt at WWRDEHV4 138 kV | Current Study |  |  | 200981.5468 | 8.2623 | 2432500 | 0.061929
GEN-2024-303 | 05 SOUTHWEST | TBD | ERIS | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 108126.5103 | 7.8353 | 1380000 | 0.13705
GEN-2024-303 | 05 SOUTHWEST | TBD | ERIS | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV | Current Study |  |  | 108126.5103 | 7.8353 | 1380000 | 0.13705
GEN-2024-303 | 05 SOUTHWEST | TBD | NRIS | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV | Current Study |  |  | 118526.9126 | 5.1533 | 2300000 | 0.10788
GEN-2024-303 | 05 SOUTHWEST | TBD | ERIS | Add 3.6 MVAR switched shunt at HEDLEY 2 69 kV | Current Study |  |  | 130543.2972 | 9.4597 | 1380000 | 0.0034836
GEN-2024-303 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2 | Current Study |  | (339.00, 330.00) | 1301008.735 | 9.2929 | 14000000 | 0.026446
GEN-2024-303 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 531510 HARBNGR3 115 531511 HARBNGR-1 13 531512 HARBNGR7 345 M2 | Current Study |  | (350.00, 385.00) | 3492529.7731 | 20.7889 | 16800000 | 0.0090703
GEN-2024-303 | 05 SOUTHWEST | TBD | ERIS | Add line 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 P2 | Current Study | 66.8 | (1011.00, 1176.00) | 17031124.3441 | 7.8456 | 217080000 | 0.068912
GEN-2024-303 | 05 SOUTHWEST | TBD | ERIS | Apply contingent IDV 01_NewLine_Phantom_Crossroads_Potter_765_26SP.idv | Contingent |  |  | 0 | 0 | 3275253469 | N/A
GEN-2024-303 | 05 SOUTHWEST | TBD | ERIS | Apply contingent IDV 02_765_Phantom_Craw_1_DIS24_TC05ALL-26SP.idv | Contingent |  |  | 0 | 0 | 1366342009.82 | N/A
GEN-2024-303 | 05 SOUTHWEST | TBD | ERIS | Apply contingent IDV 02_765_Phantom_Craw_1_DIS24_TC05ALL-29SP.idv | Contingent |  |  | 0 | 0 | 1366342009.82 | N/A
GEN-2024-303 | 05 SOUTHWEST | 171796 | ERIS | Crossroads 345 kV Substation GEN-2024-303 Interconnection (Non-Shared NU) (SPS) | Interconnection |  |  | 8636936.73 | 100 | 8636936.73 | 1
GEN-2024-303 | 05 SOUTHWEST | 171795 | ERIS | Crossroads 345 kV Substation GEN-2024-303 Interconnection (TOIF) (SPS) | Interconnection |  |  | 4502736.58 | 100 | 4502736.58 | 1
GEN-2024-303 | 05 SOUTHWEST | 900427 | ERIS | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032 | Contingent |  |  | 0 | 0 | 1790026304.1702 | N/A
GEN-2024-303 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | Current Study | 18.75 | (519.00, 519.00) | 3310602.5847 | 9.2929 | 35625000 | 0.052893
GEN-2024-303 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Current Study | 57.98 | (1793.00, 1793.00) | 9994293.8987 | 7.8352 | 127556000 | 0.13704
GEN-2024-303 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523959 POTTER_CO 6 230 524010 ROLLHILLS 6 230 1 | Current Study | 6.23 | (637.00, 637.00) | 2501736.0528 | 21.1349 | 11837000 | 0.041025
GEN-2024-303 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | Current Study | 3.02 | (1793.00, 1793.00) | 303604.3983 | 4.5696 | 6644000 | 0.084278
GEN-2024-303 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 531405 WALKMYR3 115 531510 HARBNGR3 115 1 | Current Study | 1.28 | (598.00, 598.00) | 266097.5065 | 20.7889 | 1280000 | 0.018141
GEN-2024-304 | 05 SOUTHWEST | 94067 | ERIS | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028 | Contingent |  |  | 0 | 0 | 38846321 | N/A
GEN-2024-304 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 105218.346 | 7.6245 | 1380000 | 0.10659
GEN-2024-304 | 05 SOUTHWEST | TBD | ERIS | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV | Current Study |  |  | 71512.7123 | 5.1821 | 1380000 | 0.10132
GEN-2024-304 | 05 SOUTHWEST | TBD | ERIS | Add 1.6 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 126362.4161 | 9.1567 | 1380000 | 0.13705
GEN-2024-304 | 05 SOUTHWEST | TBD | NRIS | Add 11 MVAR switched shunt at WWRDEHV4 138 kV | Current Study |  |  | 200981.5468 | 8.2623 | 2432500 | 0.061929
GEN-2024-304 | 05 SOUTHWEST | TBD | ERIS | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 108126.5103 | 7.8353 | 1380000 | 0.13705
GEN-2024-304 | 05 SOUTHWEST | TBD | ERIS | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV | Current Study |  |  | 108126.5103 | 7.8353 | 1380000 | 0.13705
GEN-2024-304 | 05 SOUTHWEST | TBD | NRIS | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV | Current Study |  |  | 118526.9126 | 5.1533 | 2300000 | 0.10788
GEN-2024-304 | 05 SOUTHWEST | TBD | ERIS | Add 3.6 MVAR switched shunt at HEDLEY 2 69 kV | Current Study |  |  | 130543.2972 | 9.4597 | 1380000 | 0.0034836
GEN-2024-304 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2 | Current Study |  | (339.00, 330.00) | 1301008.735 | 9.2929 | 14000000 | 0.026446
GEN-2024-304 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 531510 HARBNGR3 115 531511 HARBNGR-1 13 531512 HARBNGR7 345 M2 | Current Study |  | (350.00, 385.00) | 3492529.7731 | 20.7889 | 16800000 | 0.0090703
GEN-2024-304 | 05 SOUTHWEST | TBD | ERIS | Add line 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 P2 | Current Study | 66.8 | (1011.00, 1176.00) | 17031124.3441 | 7.8456 | 217080000 | 0.068912
GEN-2024-304 | 05 SOUTHWEST | TBD | ERIS | Apply contingent IDV 01_NewLine_Phantom_Crossroads_Potter_765_26SP.idv | Contingent |  |  | 0 | 0 | 3275253469 | N/A
GEN-2024-304 | 05 SOUTHWEST | TBD | ERIS | Apply contingent IDV 02_765_Phantom_Craw_1_DIS24_TC05ALL-26SP.idv | Contingent |  |  | 0 | 0 | 1366342009.82 | N/A
GEN-2024-304 | 05 SOUTHWEST | TBD | ERIS | Apply contingent IDV 02_765_Phantom_Craw_1_DIS24_TC05ALL-29SP.idv | Contingent |  |  | 0 | 0 | 1366342009.82 | N/A
GEN-2024-304 | 05 SOUTHWEST | 171798 | ERIS | Crossroads 345 kV Substation GEN-2024-304 Interconnection (Non-Shared NU) (SPS) | Interconnection |  |  | 8636936.73 | 100 | 8636936.73 | 1
GEN-2024-304 | 05 SOUTHWEST | 171797 | ERIS | Crossroads 345 kV Substation GEN-2024-304 Interconnection (TOIF) (SPS) | Interconnection |  |  | 4502736.58 | 100 | 4502736.58 | 1
GEN-2024-304 | 05 SOUTHWEST | 900427 | ERIS | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032 | Contingent |  |  | 0 | 0 | 1790026304.1702 | N/A
GEN-2024-304 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | Current Study | 18.75 | (519.00, 519.00) | 3310602.5847 | 9.2929 | 35625000 | 0.052893
GEN-2024-304 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Current Study | 57.98 | (1793.00, 1793.00) | 9994293.8987 | 7.8352 | 127556000 | 0.13704
GEN-2024-304 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 523959 POTTER_CO 6 230 524010 ROLLHILLS 6 230 1 | Current Study | 6.23 | (637.00, 637.00) | 2501736.0528 | 21.1349 | 11837000 | 0.041025
GEN-2024-304 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | Current Study | 3.02 | (1793.00, 1793.00) | 303604.3983 | 4.5696 | 6644000 | 0.084278
GEN-2024-304 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 531405 WALKMYR3 115 531510 HARBNGR3 115 1 | Current Study | 1.28 | (598.00, 598.00) | 266097.5065 | 20.7889 | 1280000 | 0.018141
GEN-2024-310 | 05 SOUTHWEST | 94067 | ERIS | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028 | Contingent |  |  | 0 | 0 | 38846321 | N/A
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 15858.8631 | 1.1492 | 1380000 | 0.1071
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV | Current Study |  |  | 10493.626 | 0.76041 | 1380000 | 0.099113
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Add 1.6 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 19746.2955 | 1.4309 | 1380000 | 0.14278
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 16896.6223 | 1.2244 | 1380000 | 0.14278
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV | Current Study |  |  | 16896.6223 | 1.2244 | 1380000 | 0.14278
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Add 3.6 MVAR switched shunt at HEDLEY 2 69 kV | Current Study |  |  | 19062.537 | 1.3813 | 1380000 | 0.0033912
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2 | Current Study |  | (339.00, 330.00) | 191572.4001 | 1.3684 | 14000000 | 0.025961
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Add 69 MVAR switched shunt at SENDERO +3 115 kV | Current Study |  |  | 57302.3465 | 2.5899 | 2212500 | 0.044302
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Add line 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 P2 | Current Study | 66.8 | (1011.00, 1176.00) | 2660143.4378 | 1.2254 | 217080000 | 0.071758
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Apply contingent IDV 01_NewLine_Phantom_Crossroads_Potter_765_26SP.idv | Contingent |  |  | 0 | 0 | 3275253469 | N/A
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Apply contingent IDV 02_765_Phantom_Craw_1_DIS24_TC05ALL-26SP.idv | Contingent |  |  | 0 | 0 | 1366342009.82 | N/A
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Apply contingent IDV 02_765_Phantom_Craw_1_DIS24_TC05ALL-29SP.idv | Contingent |  |  | 0 | 0 | 1366342009.82 | N/A
GEN-2024-310 | 05 SOUTHWEST | 171805 | ERIS | Eddy - Chaves 230 kV line GEN-2024-310 Interconnection (TOIF) (SPS) | Interconnection |  |  | 4549755.92 | 100 | 4549755.92 | 1
GEN-2024-310 | 05 SOUTHWEST | 171807 | ERIS | Eddy - Chaves 230 kV line GEN-2024-310/311 Interconnection (Shared NU) (SPS) | Interconnection |  |  | 0 |  | 0 | 1
GEN-2024-310 | 05 SOUTHWEST | 900427 | ERIS | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032 | Contingent |  |  | 0 | 0 | 1790026304.1702 | N/A
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | Current Study | 18.75 | (519.00, 519.00) | 487483.3396 | 1.3684 | 35625000 | 0.051923
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Current Study | 57.98 | (1793.00, 1793.00) | 1561783.2344 | 1.2244 | 127556000 | 0.14277
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 524875 OASIS 6 230 781740 G24-159-TAP 230 1 | Current Study | 4.87 | (519.00, 519.00) | 486075.6733 | 5.2532 | 9253000 | 0.21607
GEN-2024-310 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | Current Study | 3.02 | (1793.00, 1793.00) | 53968.6743 | 0.81229 | 6644000 | 0.099875
GEN-2024-311 | 05 SOUTHWEST | 94067 | ERIS | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028 | Contingent |  |  | 0 | 0 | 38846321 | N/A
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 47576.5892 | 3.4476 | 1380000 | 0.1071
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV | Current Study |  |  | 31480.8779 | 2.2812 | 1380000 | 0.099113
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Add 1.6 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 59238.8864 | 4.2927 | 1380000 | 0.14278
GEN-2024-311 | 05 SOUTHWEST | TBD | NRIS | Add 10 MVAR switched shunt at DEAFSMITH 6 230 kV | Current Study |  |  | 512739.1624 | 13.4049 | 3825000 | 0.031768
GEN-2024-311 | 05 SOUTHWEST | TBD | NRIS | Add 11 MVAR switched shunt at WWRDEHV4 138 kV | Current Study |  |  | 91191.9075 | 3.7489 | 2432500 | 0.062443
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 50689.867 | 3.6732 | 1380000 | 0.14278
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV | Current Study |  |  | 50689.867 | 3.6732 | 1380000 | 0.14278
GEN-2024-311 | 05 SOUTHWEST | TBD | NRIS | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV | Current Study |  |  | 56174.6372 | 2.4424 | 2300000 | 0.11362
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Add 3.6 MVAR switched shunt at HEDLEY 2 69 kV | Current Study |  |  | 57187.6109 | 4.144 | 1380000 | 0.0033912
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2 | Current Study |  | (339.00, 330.00) | 574717.2004 | 4.1051 | 14000000 | 0.025961
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Add 69 MVAR switched shunt at SENDERO +3 115 kV | Current Study |  |  | 171907.0395 | 7.7698 | 2212500 | 0.044302
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Add line 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 P2 | Current Study | 66.8 | (1011.00, 1176.00) | 7980430.3135 | 3.6763 | 217080000 | 0.071758
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Apply contingent IDV 01_NewLine_Phantom_Crossroads_Potter_765_26SP.idv | Contingent |  |  | 0 | 0 | 3275253469 | N/A
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Apply contingent IDV 02_765_Phantom_Craw_1_DIS24_TC05ALL-26SP.idv | Contingent |  |  | 0 | 0 | 1366342009.82 | N/A
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Apply contingent IDV 02_765_Phantom_Craw_1_DIS24_TC05ALL-29SP.idv | Contingent |  |  | 0 | 0 | 1366342009.82 | N/A
GEN-2024-311 | 05 SOUTHWEST | 171807 | ERIS | Eddy - Chaves 230 kV line GEN-2024-310/311 Interconnection (Shared NU) (SPS) | Interconnection |  |  | 0 |  | 0 | 1
GEN-2024-311 | 05 SOUTHWEST | 171806 | ERIS | Eddy - Chaves 230 kV line GEN-2024-311 Interconnection (TOIF) (SPS) | Interconnection |  |  | 4549755.92 | 100 | 4549755.92 | 1
GEN-2024-311 | 05 SOUTHWEST | 900427 | ERIS | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032 | Contingent |  |  | 0 | 0 | 1790026304.1702 | N/A
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | Current Study | 18.75 | (519.00, 519.00) | 1462450.0188 | 4.1051 | 35625000 | 0.051923
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Current Study | 57.98 | (1793.00, 1793.00) | 4685349.7031 | 3.6732 | 127556000 | 0.14277
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 524875 OASIS 6 230 781740 G24-159-TAP 230 1 | Current Study | 4.87 | (519.00, 519.00) | 1458227.02 | 15.7595 | 9253000 | 0.21607
GEN-2024-311 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | Current Study | 3.02 | (1793.00, 1793.00) | 161906.023 | 2.4369 | 6644000 | 0.099875
GEN-2024-317 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 42778.0999 | 3.0999 | 1380000 | 0.08667
GEN-2024-317 | 05 SOUTHWEST | TBD | ERIS | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV | Current Study |  |  | 175510.1412 | 12.7181 | 1380000 | 0.49731
GEN-2024-317 | 05 SOUTHWEST | TBD | ERIS | Add 1.6 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 229265.8282 | 16.6135 | 1380000 | 0.49731
GEN-2024-317 | 05 SOUTHWEST | TBD | NRIS | Add 11 MVAR switched shunt at WWRDEHV4 138 kV | Current Study |  |  | 68130.2661 | 2.8008 | 2432500 | 0.041987
GEN-2024-317 | 05 SOUTHWEST | TBD | ERIS | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 196179.4867 | 14.2159 | 1380000 | 0.49731
GEN-2024-317 | 05 SOUTHWEST | TBD | ERIS | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV | Current Study |  |  | 196179.4867 | 14.2159 | 1380000 | 0.49731
GEN-2024-317 | 05 SOUTHWEST | TBD | NRIS | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV | Current Study |  |  | 257609.6735 | 11.2004 | 2300000 | 0.46894
GEN-2024-317 | 05 SOUTHWEST | TBD | ERIS | Add 3.6 MVAR switched shunt at HEDLEY 2 69 kV | Current Study |  |  | 5969.0818 | 0.43254 | 1380000 | 0.00031857
GEN-2024-317 | 05 SOUTHWEST | TBD | NRIS | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2 | Current Study |  | (484.00, 515.00) | 4694251.3373 | 25.9351 | 18100000 | 0.040843
GEN-2024-317 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2 | Current Study |  | (339.00, 330.00) | 229545.57 | 1.6396 | 14000000 | 0.0093323
GEN-2024-317 | 05 SOUTHWEST | TBD | ERIS | Add line 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 P2 | Current Study | 66.8 | (1011.00, 1176.00) | 30742106.5276 | 14.1616 | 217080000 | 0.24878
GEN-2024-317 | 05 SOUTHWEST | TBD | ERIS | Apply contingent IDV 01_NewLine_Phantom_Crossroads_Potter_765_26SP.idv | Contingent |  |  | 0 | 0 | 3275253469 | N/A
GEN-2024-317 | 05 SOUTHWEST | TBD | ERIS | Apply contingent IDV 02_765_Phantom_Craw_1_DIS24_TC05ALL-26SP.idv | Contingent |  |  | 0 | 0 | 1366342009.82 | N/A
GEN-2024-317 | 05 SOUTHWEST | TBD | ERIS | Apply contingent IDV 02_765_Phantom_Craw_1_DIS24_TC05ALL-29SP.idv | Contingent |  |  | 0 | 0 | 1366342009.82 | N/A
GEN-2024-317 | 05 SOUTHWEST | 171813 | ERIS | Dragon 345 kV Substation GEN-2024-317 Interconnection (Non-Shared NU) (SPS) | Interconnection |  |  | 6564758.74 | 100 | 6564758.74 | 1
GEN-2024-317 | 05 SOUTHWEST | 171812 | ERIS | Dragon 345 kV Substation GEN-2024-317 Interconnection (TOIF) (SPS) | Interconnection |  |  | 2882135.29 | 100 | 2882135.29 | 1
GEN-2024-317 | 05 SOUTHWEST | 900427 | ERIS | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032 | Contingent |  |  | 0 | 0 | 1790026304.1702 | N/A
GEN-2024-317 | 05 SOUTHWEST | TBD | NRIS | Rebuild line 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | Current Study | 3.9 | (265.00, 265.00) | 1969180.9412 | 42.0765 | 4680000 | 0.020751
GEN-2024-317 | 05 SOUTHWEST | TBD | NRIS | Rebuild line 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | Current Study | 0.93 | (211.00, 211.00) | 409783.2248 | 36.7189 | 1116000 | 0.027082
GEN-2024-317 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | Current Study | 18.75 | (519.00, 519.00) | 584111.4951 | 1.6396 | 35625000 | 0.018665
GEN-2024-317 | 05 SOUTHWEST | TBD | NRIS | Rebuild line 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | Current Study | 17.69 | (265.00, 265.00) | 8932002.7822 | 42.0765 | 21228000 | 0.020751
GEN-2024-317 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Current Study | 57.98 | (1793.00, 1793.00) | 18133934.0382 | 14.2164 | 127556000 | 0.4973
GEN-2024-317 | 05 SOUTHWEST | TBD | NRIS | Rebuild line 515802 GRACMNT4 138 520814 ANADARK4 138 1 | Current Study | 5.09 | (265.00, 265.00) | 494527.5729 | 8.0964 | 6108000 | 0.01123
GEN-2024-318 | 04 SOUTHEAST | 93019 | NRIS | 520_T.NO.4-46ST-TP-PPTAP_rebuild.idv : 2023 ITP, PID: 93019, NTC, ISD: 1/21/2027 | Contingent |  |  | 0 | 0 | 16346806 | N/A
GEN-2024-318 | 04 SOUTHEAST | 94615 | ERIS | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029 | Contingent |  |  | 0 | 0 | 543515503 | N/A
GEN-2024-318 | 04 SOUTHEAST | 94811 | ERIS | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030 | Contingent |  |  | 0 | 0 | 1097029189 | N/A
GEN-2024-318 | 04 SOUTHEAST | 94911 | ERIS | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030 | Contingent |  |  | 0 | 0 | 143524375 | N/A
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at JAY 4 138 kV | Current Study |  |  | 223626.6077 | 9.1933 | 2432500 | 0.059573
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at MOUND 4 138 kV | Current Study |  |  | 83417.917 | 3.4293 | 2432500 | 0.042161
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV | Current Study |  |  | 223445.912 | 4.216 | 5300000 | 0.03194
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 99319.3306 | 4.083 | 2432500 | 0.07467
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 0.04 MVAR switched shunt at AUR124 5 161 kV | Current Study |  |  | 303842.1731 | 9.349 | 3250000 | 0.030513
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 0.09 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 208897.1615 | 6.4276 | 3250000 | 0.067973
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 0.11 MVAR switched shunt at CHAMSPR7 345 kV | Current Study |  |  | 487243.9961 | 9.1933 | 5300000 | 0.059573
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 225091.6477 | 4.247 | 5300000 | 0.065371
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 0.13 MVAR switched shunt at PECULR 7 345 kV | Current Study |  |  | 660291.9922 | 12.4583 | 5300000 | 0.030777
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 0.2 MVAR switched shunt at GROVE 5 161 kV | Current Study |  |  | 134764.0829 | 4.1466 | 3250000 | 0.067973
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 0.25 MVAR switched shunt at LABETTS2 69 kV | Current Study |  |  | 62064.601 | 4.4974 | 1380000 | 0.067973
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 0.4 MVAR switched shunt at TONTITN7 345 kV | Current Study |  |  | 474995.9246 | 8.9622 | 5300000 | 0.059573
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 15 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 208897.1615 | 6.4276 | 3250000 | 0.067973
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 490971.7067 | 4.0914 | 12000000 | 0.065371
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR switched shunt at NEOSHO 4 138 kV | Current Study |  |  | 68912.8802 | 2.833 | 2432500 | 0.067973
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at CPK446 5 161 kV | Current Study |  |  | 66011.8236 | 2.0311 | 3250000 | 0.030513
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV | Current Study |  |  | 209175.031 | 6.4362 | 3250000 | 0.067973
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR switched shunt at WICHITA7 345 kV | Current Study |  |  | 209111.3456 | 3.9455 | 5300000 | 0.065371
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 177 MVAR switched shunt at SWISVAL7 345 kV | Current Study |  |  | 214622.0385 | 4.0495 | 5300000 | 0.039616
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 20 MVAR switched shunt at LIBERTY4 138 kV | Current Study |  |  | 111404.9579 | 4.5799 | 2432500 | 0.07467
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 209175.031 | 6.4362 | 3250000 | 0.067973
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR switched shunt at STILWEL7 345 kV | Current Study |  |  | 282576.0427 | 5.3316 | 5300000 | 0.039616
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 24 MVAR switched shunt at GROVE 4 138 kV | Current Study |  |  | 93149.5196 | 3.8294 | 2432500 | 0.067973
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 280 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 196307.8665 | 1.6359 | 12000000 | 0.028493
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 295 MVAR switched shunt at G18-128-TAP 345 kV | Current Study |  |  | 177455.7001 | 3.3482 | 5300000 | 0.0487
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 3 MVAR switched shunt at NEOSHOS2 69 kV | Current Study |  |  | 58854.4493 | 4.2648 | 1380000 | 0.0487
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at G23-220-TAP 345 kV | Current Study |  |  | 241273.8283 | 4.5523 | 5300000 | 0.030777
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 316 MVAR switched shunt at W.GRDNR7 345 kV | Current Study |  |  | 282576.0427 | 5.3316 | 5300000 | 0.039616
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 512623 CATSAGD4 138 512638 CATSAGR5 161 512833 CATTER1 1 13 M2 | Current Study |  | (150.00, 188.00) | 4302561.9844 | 34.6981 | 12400000 | 0.023102
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 512636 CATSAGR4 138 512638 CATSAGR5 161 512834 CATTER2 1 13 M2 | Current Study |  | (150.00, 188.00) | 4302561.9844 | 34.6981 | 12400000 | 0.023469
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 138027.8972 | 4.247 | 3250000 | 0.065371
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 45 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 429173.5046 | 3.5764 | 12000000 | 0.0487
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 45 MVAR switched shunt at NEVADA 5 161 kV | Current Study |  |  | 117755.2182 | 3.6232 | 3250000 | 0.039616
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 56 MVAR switched shunt at WHARV4 138 kV | Current Study |  |  | 83417.917 | 3.4293 | 2432500 | 0.042161
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV | Current Study |  |  | 95464.3432 | 6.9177 | 1380000 | 0.067973
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Add line 515012 RVRVALY7 345 780360 G24-113-TAP 345 P2 | Current Study | 23.28 | (1195.00, 1195.00) | 2070773.3626 | 2.5202 | 82168000 | 0.017371
GEN-2024-318 | 04 SOUTHEAST | 94721 | ERIS | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 213682884 | N/A
GEN-2024-318 | 04 SOUTHEAST | 94929 | ERIS | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 413934522 | N/A
GEN-2024-318 | 04 SOUTHEAST | 900427 | ERIS | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032 | Contingent |  |  | 0 | 0 | 1790026304.1702 | N/A
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | Current Study | 0 | (382.00, 382.00) | 41637.6966 | 34.6981 | 120000 | 0.070444
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 509790 CATOOSA4 138 512636 CATSAGR4 138 Z1 | Current Study | 0 | (307.00, 307.00) | 41637.6966 | 34.6981 | 120000 | 0.046939
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 2161245.6535 | 6.4334 | 33594000 | 0.11788
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 313982.2585 | 2.6928 | 11660000 | 0.07462
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Current Study | 14.6 | (1793.00, 1793.00) | 2066416.9313 | 6.4334 | 32120000 | 0.11788
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | Current Study | 1.35 | (1793.00, 1793.00) | 130509.2636 | 4.3943 | 2970000 | 0.069837
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 89997.1663 | 4.0908 | 2200000 | 0.069837
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | Current Study | 15.48 | (1793.00, 1793.00) | 2847508.6455 | 8.3613 | 34056000 | 0.044778
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 2182701.4161 | 2.3224 | 93984000 | 0.07462
GEN-2024-318 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Current Study | 25.29 | (2390.00, 2390.00) | 2213541.695 | 3.9785 | 55638000 | 0.048887
GEN-2024-318 | 04 SOUTHEAST | 171815 | ERIS | Tulsa North - American Airlines 138 kV Line GEN-2024-318 Interconnection (Non-Shared NU) (AEP) | Interconnection |  |  | 17175000 | 100 | 17175000 | 1
GEN-2024-318 | 04 SOUTHEAST | 171814 | ERIS | Tulsa North - American Airlines 138 kV Line GEN-2024-318 Interconnection (TOIF) (AEP) | Interconnection |  |  | 3325000 | 100 | 3325000 | 1
GEN-2024-319 | 03 CENTRAL | 94615 | ERIS | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029 | Contingent |  |  | 0 | 0 | 543515503 | N/A
GEN-2024-319 | 03 CENTRAL | TBD | ERIS | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV | Current Study |  |  | 83156.1094 | 6.0258 | 1380000 | 0.083662
GEN-2024-319 | 03 CENTRAL | TBD | ERIS | Add 16 MVAR switched shunt at HUMBOLT5 161 kV | Current Study |  |  | 157537.0623 | 4.8473 | 3250000 | 0.059163
GEN-2024-319 | 03 CENTRAL | TBD | ERIS | Add 21 MVAR switched shunt at S1263 5 161 kV | Current Study |  |  | 157537.0623 | 4.8473 | 3250000 | 0.059163
GEN-2024-319 | 03 CENTRAL | TBD | ERIS | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV | Current Study |  |  | 66892.6603 | 4.8473 | 1380000 | 0.059163
GEN-2024-319 | 03 CENTRAL | TBD | ERIS | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2 | Current Study | 0.75 | (2390.00, 2390.00) | 121387.9785 | 0.68291 | 17775000 | 0.018822
GEN-2024-319 | 03 CENTRAL | 94721 | ERIS | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 213682884 | N/A
GEN-2024-319 | 03 CENTRAL | 94929 | ERIS | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 413934522 | N/A
GEN-2024-319 | 03 CENTRAL | 171817 | ERIS | Metro 5 161 kV Substation GEN-2024-319 Interconnection (Non-Shared NU) (KACY) | Interconnection |  |  | 2757867 | 100 | 2757867 | 1
GEN-2024-319 | 03 CENTRAL | 171816 | ERIS | Metro 5 161 kV Substation GEN-2024-319 Interconnection (TOIF) (KACY) | Interconnection |  |  | 200000 | 100 | 200000 | 1
GEN-2024-319 | 03 CENTRAL | TBD | ERIS | Rebuild line 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | Current Study | 3.02 | (551.00, 551.00) | 562962.6758 | 12.4274 | 4530000 | 0.041892
GEN-2024-319 | 03 CENTRAL | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 245549.5556 | 2.1059 | 11660000 | 0.058356
GEN-2024-319 | 03 CENTRAL | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 1706979.7678 | 1.8162 | 93984000 | 0.058356
GEN-2024-319 | 03 CENTRAL | TBD | ERIS | Rebuild line 541199 ST JOE 7 345 541400 EASTOWN7 345 1 | Current Study | 8.12 | (1793.00, 1793.00) | 1088817.5449 | 6.095 | 17864000 | 0.058129
GEN-2024-319 | 03 CENTRAL | TBD | ERIS | Rebuild line 541400 EASTOWN7 345 542982 IATAN 7 345 1 | Current Study | 23.71 | (1793.00, 1793.00) | 3129892.6882 | 6.0003 | 52162000 | 0.066725
GEN-2024-320 | 03 CENTRAL | 94615 | ERIS | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029 | Contingent |  |  | 0 | 0 | 543515503 | N/A
GEN-2024-320 | 03 CENTRAL | TBD | ERIS | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV | Current Study |  |  | 83583.2639 | 6.0568 | 1380000 | 0.084092
GEN-2024-320 | 03 CENTRAL | TBD | ERIS | Add 16 MVAR switched shunt at HUMBOLT5 161 kV | Current Study |  |  | 169592.6297 | 5.2182 | 3250000 | 0.063691
GEN-2024-320 | 03 CENTRAL | TBD | ERIS | Add 21 MVAR switched shunt at S1263 5 161 kV | Current Study |  |  | 169592.6297 | 5.2182 | 3250000 | 0.063691
GEN-2024-320 | 03 CENTRAL | TBD | ERIS | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV | Current Study |  |  | 72011.6397 | 5.2182 | 1380000 | 0.063691
GEN-2024-320 | 03 CENTRAL | TBD | ERIS | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2 | Current Study | 0.75 | (2390.00, 2390.00) | 127225.9786 | 0.71576 | 17775000 | 0.019727
GEN-2024-320 | 03 CENTRAL | 94721 | ERIS | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 213682884 | N/A
GEN-2024-320 | 03 CENTRAL | 94929 | ERIS | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 413934522 | N/A
GEN-2024-320 | 03 CENTRAL | 171946 | ERIS | Jaggard 115 kV Substation GEN-2024-320 Interconnection (Non-Shared NU) (WERE) | Interconnection |  |  | 16424539 | 100 | 16424539 | 1
GEN-2024-320 | 03 CENTRAL | 171945 | ERIS | Jaggard 115 kV Substation GEN-2024-320 Interconnection (TOIF) (WERE) | Interconnection |  |  | 1040242 | 100 | 1040242 | 1
GEN-2024-320 | 03 CENTRAL | TBD | ERIS | Rebuild line 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | Current Study | 3.02 | (551.00, 551.00) | 529689.0027 | 11.6929 | 4530000 | 0.039416
GEN-2024-320 | 03 CENTRAL | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 234810.5994 | 2.0138 | 11660000 | 0.055804
GEN-2024-320 | 03 CENTRAL | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 1632326.0755 | 1.7368 | 93984000 | 0.055804
GEN-2024-320 | 03 CENTRAL | TBD | ERIS | Rebuild line 533238 EDWARVL3 115 533282 MUND 3 115 1 | Current Study | 3.33 | (260.00, 260.00) | 2479225.7345 | 74.4512 | 3330000 | 0.17107
GEN-2024-320 | 03 CENTRAL | TBD | ERIS | Rebuild line 533243 JAGGARD3 115 533261 PENTAGN3 115 1 | Current Study | 5.55 | (297.00, 297.00) | 4500802.8628 | 81.0955 | 5550000 | 0.59896
GEN-2024-320 | 03 CENTRAL | TBD | ERIS | Rebuild line 541199 ST JOE 7 345 541400 EASTOWN7 345 1 | Current Study | 8.12 | (1793.00, 1793.00) | 1943158.6849 | 10.8775 | 17864000 | 0.10374
GEN-2024-320 | 03 CENTRAL | TBD | ERIS | Rebuild line 541400 EASTOWN7 345 542982 IATAN 7 345 1 | Current Study | 23.71 | (1793.00, 1793.00) | 5439598.1039 | 10.4283 | 52162000 | 0.11597
GEN-2024-321 | 04 SOUTHEAST | TBD | ERIS | Add 2 MVAR switched shunt at GEN-2017-140 345 kV | Current Study |  |  | 186846.7131 | 3.5254 | 5300000 | 0.081808
GEN-2024-321 | 04 SOUTHEAST | TBD | ERIS | Add 23 MVAR switched shunt at FINNEY 7 345 kV | Current Study |  |  | 188139.8829 | 3.5498 | 5300000 | 0.023877
GEN-2024-321 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514934 DRAPER 7 345 515045 SEMINOL7 345 2 | Current Study | 44.14 | (1793.00, 1793.00) | 14872041.6625 | 15.315 | 97108000 | 0.12737
GEN-2024-321 | 04 SOUTHEAST | 171819 | ERIS | Seminole 345 kV Substation GEN-2024-321 Interconnection (Non-Shared NU) (OGE) | Interconnection |  |  | 5000000 | 100 | 5000000 | 1
GEN-2024-321 | 04 SOUTHEAST | 171818 | ERIS | Seminole 345 kV Substation GEN-2024-321 Interconnection (TOIF) (OGE) | Interconnection |  |  | 3000000 | 100 | 3000000 | 1
GEN-2024-323 | 04 SOUTHEAST | 900426 | ERIS | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030 | Contingent |  |  | 0 | 0 | 2372127948.71 | N/A
GEN-2024-323 | 04 SOUTHEAST | TBD | ERIS | Add 2 MVAR switched shunt at GEN-2017-140 345 kV | Current Study |  |  | 153529.3948 | 2.8968 | 5300000 | 0.092881
GEN-2024-323 | 04 SOUTHEAST | 171823 | ERIS | ITC Hugo 7 345 kV Substation GEN-2024-323 Interconnection (Non-Shared NU) (ITCGP) | Interconnection |  |  | 4630437 | 100 | 4630437 | 1
GEN-2024-323 | 04 SOUTHEAST | 171822 | ERIS | ITC Hugo 7 345 kV Substation GEN-2024-323 Interconnection (TOIF) (ITCGP) | Interconnection |  |  | 1306438 | 100 | 1306438 | 1
GEN-2024-323 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 507760 SW SHV 7 345 508809 LONGWD 7 345 1 | Current Study | 19.02 | (1793.00, 1793.00) | 821556.5058 | 1.9634 | 41844000 | 0.035081
GEN-2024-323 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514934 DRAPER 7 345 515045 SEMINOL7 345 2 | Current Study | 44.14 | (1793.00, 1793.00) | 4860245.023 | 5.005 | 97108000 | 0.057514
GEN-2024-323 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 | Current Study | 13.16 | (211.00, 211.00) | 4001184.1777 | 25.3368 | 15792000 | 0.022414
GEN-2024-327 | 01 NORTH | 171831 | ERIS | Berthold 115 kV Substation GEN-2024-327 Interconnection (Non-Shared NU) (CPEC) | Interconnection |  |  | 1395000 | 100 | 1395000 | 1
GEN-2024-327 | 01 NORTH | 171830 | ERIS | Berthold 115 kV Substation GEN-2024-327 Interconnection (TOIF) (CPEC) | Interconnection |  |  | 214000 | 100 | 214000 | 1
GEN-2024-327 | 01 NORTH | TBD | ERIS | Rebuild the SOURIS 7 to MALLARD7 115kV Line 1 | JTIQ Expanded Scope Analysis | 5.3 | (125, 125) | 4088950 | 100 | 4088950 | 0.11792
GEN-2024-329 | 01 NORTH | TBD | NRIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | Current Study |  |  | 2212500 | 100 | 2212500 | 1
GEN-2024-329 | 01 NORTH | TBD | NRIS | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 1366607.8071 | 61.7676 | 2212500 | 1
GEN-2024-329 | 01 NORTH | 171835 | ERIS | Pleasant Valley 115 kV Substation GEN-2024-329 Interconnection (Non-Shared NU) (MWEC) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-329 | 01 NORTH | 171834 | ERIS | Pleasant Valley 115 kV Substation GEN-2024-329 Interconnection (TOIF) (MWEC) | Interconnection |  |  | 1200000 | 100 | 1200000 | 1
GEN-2024-330 | 03 CENTRAL | 94615 | ERIS | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029 | Contingent |  |  | 0 | 0 | 543515503 | N/A
GEN-2024-330 | 03 CENTRAL | TBD | ERIS | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV | Current Study |  |  | 12443.1066 | 0.90167 | 1380000 | 0.039175
GEN-2024-330 | 03 CENTRAL | 94721 | ERIS | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 213682884 | N/A
GEN-2024-330 | 03 CENTRAL | 94929 | ERIS | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 413934522 | N/A
GEN-2024-330 | 03 CENTRAL | 171948 | ERIS | Butler 138 kV Substation GEN-2024-330 Interconnection (Non-Shared NU) (WERE) | Interconnection |  |  | 1289137 | 100 | 1289137 | 1
GEN-2024-330 | 03 CENTRAL | 171947 | ERIS | Butler 138 kV Substation GEN-2024-330 Interconnection (TOIF) (WERE) | Interconnection |  |  | 1040242 | 100 | 1040242 | 1
GEN-2024-330 | 03 CENTRAL | TBD | NRIS | Rebuild line 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | Current Study | 31.46 | (1793.00, 1793.00) | 1407034.0606 | 2.0329 | 69212000 | 0.039289
GEN-2024-330 | 03 CENTRAL | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 110905.7788 | 0.95116 | 11660000 | 0.023312
GEN-2024-330 | 03 CENTRAL | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 770980.5059 | 0.82033 | 93984000 | 0.023312
GEN-2024-330 | 03 CENTRAL | TBD | ERIS | Rebuild line 532987 BUTLER 4 138 532990 MIDIAN 4 138 1 | Current Study | 3 | (211.00, 211.00) | 3600000 | 100 | 3600000 | 0.40341
GEN-2024-330 | 03 CENTRAL | TBD | ERIS | Rebuild line 532995 OTTRCRK4 138 533001 ALTOONA4 138 1 | Current Study | 35 | (134.00, 134.00) | 42000000 | 100 | 42000000 | 0.11243
GEN-2024-330 | 03 CENTRAL | TBD | ERIS | Rebuild line 533583 BUTLERN2 69 533597 MIDIAN 2 69 1 | Current Study | 3.04 | (106.00, 106.00) | 2584000 | 100 | 2584000 | 0.011948
GEN-2024-333 | 04 SOUTHEAST | 94615 | ERIS | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029 | Contingent |  |  | 0 | 0 | 543515503 | N/A
GEN-2024-333 | 04 SOUTHEAST | 94811 | ERIS | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030 | Contingent |  |  | 0 | 0 | 1097029189 | N/A
GEN-2024-333 | 04 SOUTHEAST | 94911 | ERIS | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030 | Contingent |  |  | 0 | 0 | 143524375 | N/A
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BUFFALO7 345 kV | Current Study |  |  | 331016.9182 | 6.2456 | 5300000 | 0.032519
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 201389.5314 | 3.7998 | 5300000 | 0.032914
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at MOUND 4 138 kV | Current Study |  |  | 46470.9121 | 1.9104 | 2432500 | 0.04674
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV | Current Study |  |  | 135581.3101 | 2.5581 | 5300000 | 0.038567
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 26591.4111 | 1.0932 | 2432500 | 0.039784
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 0.09 MVAR switched shunt at SWISVAL6 230 kV | Current Study |  |  | 171833.3266 | 4.4924 | 3825000 | 0.032914
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 7756.4484 | 0.56206 | 1380000 | 0.039287
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 68373.6545 | 1.2901 | 5300000 | 0.039516
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 149137.1633 | 1.2428 | 12000000 | 0.039516
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR switched shunt at NEOSHO 4 138 kV | Current Study |  |  | 28950.4473 | 1.1902 | 2432500 | 0.056826
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR switched shunt at WICHITA7 345 kV | Current Study |  |  | 82530.3845 | 1.5572 | 5300000 | 0.051342
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 177 MVAR switched shunt at SWISVAL7 345 kV | Current Study |  |  | 79252.8626 | 1.4953 | 5300000 | 0.029111
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 20 MVAR switched shunt at LIBERTY4 138 kV | Current Study |  |  | 29827.1748 | 1.2262 | 2432500 | 0.039784
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR switched shunt at STILWEL7 345 kV | Current Study |  |  | 104346.0422 | 1.9688 | 5300000 | 0.029111
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 25 MVAR switched shunt at ATWOOD 3 115 kV | Current Study |  |  | 133464.5925 | 6.0323 | 2212500 | 0.02514
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at G21-096-TAP 345 kV | Current Study |  |  | 146005.5504 | 2.7548 | 5300000 | 0.033427
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 280 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 241589.0936 | 2.0132 | 12000000 | 0.069779
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 295 MVAR switched shunt at G18-128-TAP 345 kV | Current Study |  |  | 104052.1964 | 1.9632 | 5300000 | 0.056826
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 3 MVAR switched shunt at NEOSHOS2 69 kV | Current Study |  |  | 34509.6535 | 2.5007 | 1380000 | 0.056826
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at G23-220-TAP 345 kV | Current Study |  |  | 129659.3339 | 2.4464 | 5300000 | 0.032914
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 316 MVAR switched shunt at W.GRDNR7 345 kV | Current Study |  |  | 104346.0422 | 1.9688 | 5300000 | 0.029111
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 41927.2409 | 1.2901 | 3250000 | 0.039516
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 45 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 251648.4158 | 2.0971 | 12000000 | 0.056826
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 45 MVAR switched shunt at NEVADA 5 161 kV | Current Study |  |  | 43483.1306 | 1.3379 | 3250000 | 0.029111
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 277546.994 | 5.2367 | 5300000 | 0.025822
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 56 MVAR switched shunt at WHARV4 138 kV | Current Study |  |  | 46470.9121 | 1.9104 | 2432500 | 0.04674
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add 86 MVAR switched shunt at POSTROCK7 345 kV | Current Study |  |  | 244701.166 | 4.617 | 5300000 | 0.020419
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Add line 515012 RVRVALY7 345 780360 G24-113-TAP 345 P2 | Current Study | 23.28 | (1195.00, 1195.00) | 1040083.6742 | 1.2658 | 82168000 | 0.017363
GEN-2024-333 | 04 SOUTHEAST | 94721 | ERIS | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 213682884 | N/A
GEN-2024-333 | 04 SOUTHEAST | 94929 | ERIS | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 413934522 | N/A
GEN-2024-333 | 04 SOUTHEAST | 171841 | ERIS | Kelley Avenue 138 kV GEN-2024-333 Interconnection (Non-Shared NU) (OGE) | Interconnection |  |  | 4500000 | 100 | 4500000 | 1
GEN-2024-333 | 04 SOUTHEAST | 171840 | ERIS | Kelley Avenue 138 kV GEN-2024-333 Interconnection (TOIF) (OGE) | Interconnection |  |  | 2000000 | 100 | 2000000 | 1
GEN-2024-333 | 04 SOUTHEAST | 900427 | ERIS | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032 | Contingent |  |  | 0 | 0 | 1790026304.1702 | N/A
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 430280.6779 | 1.2808 | 33594000 | 0.046702
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 84014.1564 | 0.72053 | 11660000 | 0.039733
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Current Study | 14.6 | (1793.00, 1793.00) | 411401.303 | 1.2808 | 32120000 | 0.046702
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514715 WOODRNG7 345 515875 REDNGTN7 345 1 | Current Study | 19.2 | (1793.00, 1793.00) | 1437323.1429 | 3.4028 | 42240000 | 0.094178
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 1535638.0778 | 3.3446 | 45914000 | 0.070047
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 584038.7895 | 0.62142 | 93984000 | 0.039733
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Current Study | 25.29 | (2390.00, 2390.00) | 1297221.8865 | 2.3315 | 55638000 | 0.057012
GEN-2024-333 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 838089.0132 | 3.3446 | 25058000 | 0.070047
GEN-2024-334 | 04 SOUTHEAST | TBD | ERIS | Add 23 MVAR switched shunt at FINNEY 7 345 kV | Current Study |  |  | 11644.5766 | 0.21971 | 5300000 | 0.0070736
GEN-2024-334 | 04 SOUTHEAST | 171843 | ERIS | OMPA 345 kV Switchyard GEN-2024-334 Interconnection (Non-Shared NU) (OGE) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-334 | 04 SOUTHEAST | 171842 | ERIS | OMPA 345 kV Switchyard GEN-2024-334 Interconnection (TOIF) (OGE) | Interconnection |  |  | 100000 | 100 | 100000 | 1
GEN-2024-334 | 04 SOUTHEAST | TBD | NRIS | Rebuild line 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | Current Study | 31.46 | (1793.00, 1793.00) | 459805.7262 | 0.66434 | 69212000 | 0.028047
GEN-2024-336 | 05 SOUTHWEST | 94067 | ERIS | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028 | Contingent |  |  | 0 | 0 | 38846321 | N/A
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 63624.6652 | 4.6105 | 1380000 | 0.10742
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV | Current Study |  |  | 41184.7771 | 2.9844 | 1380000 | 0.097248
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Add 1.6 MVAR switched shunt at NP-BOOKER 2 69 kV | Current Study |  |  | 82135.1405 | 5.9518 | 1380000 | 0.14847
GEN-2024-336 | 05 SOUTHWEST | TBD | NRIS | Add 11 MVAR switched shunt at WWRDEHV4 138 kV | Current Study |  |  | 122210.5367 | 5.0241 | 2432500 | 0.062762
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV | Current Study |  |  | 70281.8638 | 5.0929 | 1380000 | 0.14847
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV | Current Study |  |  | 70281.8638 | 5.0929 | 1380000 | 0.14847
GEN-2024-336 | 05 SOUTHWEST | TBD | NRIS | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV | Current Study |  |  | 78661.8655 | 3.4201 | 2300000 | 0.11933
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Add 3.6 MVAR switched shunt at HEDLEY 2 69 kV | Current Study |  |  | 73360.0961 | 5.3159 | 1380000 | 0.0032627
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2 | Current Study |  | (339.00, 330.00) | 753534.5849 | 5.3824 | 14000000 | 0.025529
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Add line 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 P2 | Current Study | 66.8 | (1011.00, 1176.00) | 11060890.2775 | 5.0953 | 217080000 | 0.074592
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Apply contingent IDV 01_NewLine_Phantom_Crossroads_Potter_765_26SP.idv | Contingent |  |  | 0 | 0 | 3275253469 | N/A
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Apply contingent IDV 02_765_Phantom_Craw_1_DIS24_TC05ALL-26SP.idv | Contingent |  |  | 0 | 0 | 1366342009.82 | N/A
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Apply contingent IDV 02_765_Phantom_Craw_1_DIS24_TC05ALL-29SP.idv | Contingent |  |  | 0 | 0 | 1366342009.82 | N/A
GEN-2024-336 | 05 SOUTHWEST | 171845 | ERIS | Ink Basin 230 kV Substation GEN-2024-336 Interconnection (Non-Shared NU) (SPS) | Interconnection |  |  | 6052126.09 | 100 | 6052126.09 | 1
GEN-2024-336 | 05 SOUTHWEST | 171844 | ERIS | Ink Basin 230 kV Substation GEN-2024-336 Interconnection (TOIF) (SPS) | Interconnection |  |  | 3955290.56 | 100 | 3955290.56 | 1
GEN-2024-336 | 05 SOUTHWEST | 900427 | ERIS | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032 | Contingent |  |  | 0 | 0 | 1790026304.1702 | N/A
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | Current Study | 18.75 | (519.00, 519.00) | 1917476.3992 | 5.3824 | 35625000 | 0.051059
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Current Study | 57.98 | (1793.00, 1793.00) | 6496283.9808 | 5.0929 | 127556000 | 0.14846
GEN-2024-336 | 05 SOUTHWEST | TBD | ERIS | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | Current Study | 3.02 | (1793.00, 1793.00) | 312588.7472 | 4.7048 | 6644000 | 0.14462
GEN-2024-338 | 04 SOUTHEAST | 94615 | ERIS | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029 | Contingent |  |  | 0 | 0 | 543515503 | N/A
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at MOUND 4 138 kV | Current Study |  |  | 137530.089 | 5.6539 | 2432500 | 0.039522
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 73705.0531 | 5.3409 | 1380000 | 0.033841
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 88179.4638 | 3.6251 | 2432500 | 0.037693
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 22714.8366 | 1.646 | 1380000 | 0.032872
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 234999.2639 | 4.4339 | 5300000 | 0.038804
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV | Current Study |  |  | 73705.0531 | 5.3409 | 1380000 | 0.033841
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 0.2 MVAR switched shunt at GROVE 5 161 kV | Current Study |  |  | 116893.0567 | 3.5967 | 3250000 | 0.033523
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 0.25 MVAR switched shunt at LABETTS2 69 kV | Current Study |  |  | 53834.2321 | 3.901 | 1380000 | 0.033523
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 11 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 169636.8831 | 5.2196 | 3250000 | 0.033841
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 512582.2786 | 4.2715 | 12000000 | 0.038804
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR switched shunt at NEOSHO 4 138 kV | Current Study |  |  | 46656.8743 | 1.9181 | 2432500 | 0.026166
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at CPK446 5 161 kV | Current Study |  |  | 128764.6114 | 3.962 | 3250000 | 0.033841
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR switched shunt at WICHITA7 345 kV | Current Study |  |  | 222354.6569 | 4.1954 | 5300000 | 0.039522
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 177 MVAR switched shunt at SWISVAL7 345 kV | Current Study |  |  | 233673.0593 | 4.4089 | 5300000 | 0.024524
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 20 MVAR switched shunt at LIBERTY4 138 kV | Current Study |  |  | 98909.5415 | 4.0662 | 2432500 | 0.037693
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 24 MVAR switched shunt at GROVE 4 138 kV | Current Study |  |  | 63066.083 | 2.5926 | 2432500 | 0.026166
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 280 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 585546.0418 | 4.8796 | 12000000 | 0.048322
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 295 MVAR switched shunt at G18-128-TAP 345 kV | Current Study |  |  | 265526.7001 | 5.0099 | 5300000 | 0.041432
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 3 MVAR switched shunt at NEOSHOS2 69 kV | Current Study |  |  | 88063.825 | 6.3814 | 1380000 | 0.041432
GEN-2024-338 | 04 SOUTHEAST | TBD | NRIS | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV | Current Study |  |  | 34749.8945 | 1.5109 | 2300000 | 0.045184
GEN-2024-338 | 04 SOUTHEAST | TBD | NRIS | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2 | Current Study |  | (484.00, 515.00) | 3159943.4455 | 17.4583 | 18100000 | 0.019638
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at INDEPCO5 161 kV | Current Study |  |  | 169636.8831 | 5.2196 | 3250000 | 0.033841
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 144103.3222 | 4.4339 | 3250000 | 0.038804
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 45 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 642171.6766 | 5.3514 | 12000000 | 0.041432
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 45 MVAR switched shunt at NEVADA 5 161 kV | Current Study |  |  | 128207.8126 | 3.9449 | 3250000 | 0.024524
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Add 56 MVAR switched shunt at WHARV4 138 kV | Current Study |  |  | 137530.089 | 5.6539 | 2432500 | 0.039522
GEN-2024-338 | 04 SOUTHEAST | 94721 | ERIS | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 213682884 | N/A
GEN-2024-338 | 04 SOUTHEAST | 94929 | ERIS | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 413934522 | N/A
GEN-2024-338 | 04 SOUTHEAST | 171849 | ERIS | Pittsburg - Johnston County 345 kV line GEN-2024-338 Interconnection (Non-Shared NU) (AEP) | Interconnection |  |  | 28225000 | 100 | 28225000 | 1
GEN-2024-338 | 04 SOUTHEAST | 171848 | ERIS | Pittsburg - Johnston County 345 kV line GEN-2024-338 Interconnection (TOIF) (AEP) | Interconnection |  |  | 5225000 | 100 | 5225000 | 1
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 505600 TUPELO 4 138 505602 S BROWN4 138 1 | Current Study | 36.9 | (211.00, 211.00) | 10905480.8333 | 24.6285 | 44280000 | 0.031504
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508359 WELSH 7 345 508841 WILKES 7 345 1 | Current Study | 30.63 | (1793.00, 1793.00) | 6096366.7021 | 9.0469 | 67386000 | 0.034087
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | Current Study | 21.38 | (1793.00, 1793.00) | 4130376.6455 | 8.7813 | 47036000 | 0.078149
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 1635964.0591 | 4.8698 | 33594000 | 0.050733
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 278648.2806 | 2.3898 | 11660000 | 0.037652
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Current Study | 14.6 | (1793.00, 1793.00) | 1564183.0558 | 4.8698 | 32120000 | 0.050733
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514715 WOODRNG7 345 515875 REDNGTN7 345 1 | Current Study | 19.2 | (1793.00, 1793.00) | 3324788.6958 | 7.8712 | 42240000 | 0.062243
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 3724445.2919 | 8.1118 | 45914000 | 0.048539
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 1937071.2205 | 2.0611 | 93984000 | 0.037652
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Current Study | 25.29 | (2390.00, 2390.00) | 3311582.3854 | 5.952 | 55638000 | 0.041584
GEN-2024-338 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 2032651.2638 | 8.1118 | 25058000 | 0.048539
GEN-2024-339 | 03 CENTRAL | 94615 | ERIS | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029 | Contingent |  |  | 0 | 0 | 543515503 | N/A
GEN-2024-339 | 03 CENTRAL | TBD | ERIS | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV | Current Study |  |  | 143577.5531 | 10.4042 | 1380000 | 0.095819
GEN-2024-339 | 03 CENTRAL | TBD | ERIS | Add 16 MVAR switched shunt at HUMBOLT5 161 kV | Current Study |  |  | 294346.1781 | 9.0568 | 3250000 | 0.073326
GEN-2024-339 | 03 CENTRAL | TBD | ERIS | Add 21 MVAR switched shunt at S1263 5 161 kV | Current Study |  |  | 294346.1781 | 9.0568 | 3250000 | 0.073326
GEN-2024-339 | 03 CENTRAL | TBD | ERIS | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV | Current Study |  |  | 124983.9156 | 9.0568 | 1380000 | 0.073326
GEN-2024-339 | 03 CENTRAL | TBD | ERIS | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2 | Current Study | 0.75 | (2390.00, 2390.00) | 211622.6257 | 1.1906 | 17775000 | 0.021767
GEN-2024-339 | 03 CENTRAL | 94721 | ERIS | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 213682884 | N/A
GEN-2024-339 | 03 CENTRAL | 94929 | ERIS | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 413934522 | N/A
GEN-2024-339 | 03 CENTRAL | TBD | ERIS | Rebuild line 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | Current Study | 3.02 | (551.00, 551.00) | 669937.2689 | 14.7889 | 4530000 | 0.033069
GEN-2024-339 | 03 CENTRAL | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 333070.3168 | 2.8565 | 11660000 | 0.052507
GEN-2024-339 | 03 CENTRAL | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 2315395.3206 | 2.4636 | 93984000 | 0.052507
GEN-2024-339 | 03 CENTRAL | TBD | ERIS | Rebuild line 533238 EDWARVL3 115 533282 MUND 3 115 1 | Current Study | 3.33 | (260.00, 260.00) | 850774.2655 | 25.5488 | 3330000 | 0.038941
GEN-2024-339 | 03 CENTRAL | TBD | ERIS | Rebuild line 533243 JAGGARD3 115 533261 PENTAGN3 115 1 | Current Study | 5.55 | (297.00, 297.00) | 1044966.0266 | 18.8282 | 5550000 | 0.092245
GEN-2024-339 | 03 CENTRAL | TBD | ERIS | Rebuild line 541199 ST JOE 7 345 541400 EASTOWN7 345 1 | Current Study | 8.12 | (1793.00, 1793.00) | 4148169.4768 | 23.2208 | 17864000 | 0.1469
GEN-2024-339 | 03 CENTRAL | TBD | ERIS | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | Current Study | 2.29 | (551.00, 551.00) | 46540.3966 | 1.3549 | 3435000 | 0.013004
GEN-2024-339 | 03 CENTRAL | TBD | ERIS | Rebuild line 541400 EASTOWN7 345 542982 IATAN 7 345 1 | Current Study | 23.71 | (1793.00, 1793.00) | 11523176.8059 | 22.0911 | 52162000 | 0.16295
GEN-2024-339 | 03 CENTRAL | 171950 | ERIS | Stranger Creek 115 kV Substation GEN-2024-339 Interconnection (Non-Shared NU) (WERE) | Interconnection |  |  | 1289137 | 100 | 1289137 | 1
GEN-2024-339 | 03 CENTRAL | 171949 | ERIS | Stranger Creek 115 kV Substation GEN-2024-339 Interconnection (TOIF) (WERE) | Interconnection |  |  | 1040242 | 100 | 1040242 | 1
GEN-2024-340 | 04 SOUTHEAST | TBD | ERIS | Add 2 MVAR switched shunt at GEN-2017-140 345 kV | Current Study |  |  | 173676.6663 | 3.2769 | 5300000 | 0.026778
GEN-2024-340 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 514907 ARCADIA4 138 514908 ARCADIA7 345 515700 ARCADI41 13 M2 | Current Study |  | (448.00, 448.00) | 18100000 | 100 | 18100000 | 0.03069
GEN-2024-340 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1 | Current Study | 44.59 | (1793.00, 1793.00) | 98098000 | 100 | 98098000 | 0.46481
GEN-2024-340 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514909 REDBUD 7 345 787290 G24-344-TAP 345 1 | Current Study | 26.49 | (1793.00, 1793.00) | 58278000 | 100 | 58278000 | 0.53519
GEN-2024-340 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 787170 G24-340-TAP 345 787290 G24-344-TAP 345 1 | Current Study | 8.4 | (1793.00, 1793.00) | 18480000 | 100 | 18480000 | 0.53519
GEN-2024-340 | 04 SOUTHEAST | 171851 | ERIS | Riverside – Redbud 345 kV line GEN-2024-340 Interconnection (Non-Shared NU) (AEP) | Interconnection |  |  | 28225000 | 100 | 28225000 | 1
GEN-2024-340 | 04 SOUTHEAST | 171850 | ERIS | Riverside – Redbud 345 kV line GEN-2024-340 Interconnection (TOIF) (AEP) | Interconnection |  |  | 5225000 | 100 | 5225000 | 1
GEN-2024-341 | 04 SOUTHEAST | 900426 | ERIS | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030 | Contingent |  |  | 0 | 0 | 2372127948.71 | N/A
GEN-2024-341 | 04 SOUTHEAST | TBD | ERIS | Add 2 MVAR switched shunt at GEN-2017-140 345 kV | Current Study |  |  | 554238.5836 | 10.4573 | 5300000 | 0.11448
GEN-2024-341 | 04 SOUTHEAST | 171853 | ERIS | Pittsburgh 345 kV Substation GEN-2024-341 Interconnection (Non-Shared NU) (AEP) | Interconnection |  |  | 9250000 | 100 | 9250000 | 1
GEN-2024-341 | 04 SOUTHEAST | 171852 | ERIS | Pittsburgh 345 kV Substation GEN-2024-341 Interconnection (TOIF) (AEP) | Interconnection |  |  | 5225000 | 100 | 5225000 | 1
GEN-2024-341 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514934 DRAPER 7 345 515045 SEMINOL7 345 2 | Current Study | 44.14 | (1793.00, 1793.00) | 18151832.2191 | 18.6924 | 97108000 | 0.07334
GEN-2024-341 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 | Current Study | 13.16 | (211.00, 211.00) | 11790815.8223 | 74.6632 | 15792000 | 0.022552
GEN-2024-343 | 04 SOUTHEAST | 900426 | ERIS | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030 | Contingent |  |  | 0 | 0 | 2372127948.71 | N/A
GEN-2024-343 | 04 SOUTHEAST | TBD | ERIS | Add 2 MVAR switched shunt at GEN-2017-140 345 kV | Current Study |  |  | 64209.7631 | 1.2115 | 5300000 | 0.058978
GEN-2024-343 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 508562 PIRKEY 4 138 508563 PIRKEY 7 345 508587 PIRKY1-1 13 M2 | Current Study |  | (600.00, 600.00) | 2650415.3058 | 14.6432 | 18100000 | 0.10503
GEN-2024-343 | 04 SOUTHEAST | 171855 | ERIS | LeBrock 345 kV Substation GEN-2024-343 Interconnection (Non-Shared NU) (AEP) | Interconnection |  |  | 59500000 | 100 | 59500000 | 1
GEN-2024-343 | 04 SOUTHEAST | 171854 | ERIS | LeBrock 345 kV Substation GEN-2024-343 Interconnection (TOIF) (AEP) | Interconnection |  |  | 9700000 | 100 | 9700000 | 1
GEN-2024-343 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 507727 FLOURNY4 138 507732 GENMOTR4 138 1 | Current Study | 1.56 | (395.00, 395.00) | 103422.9678 | 5.5247 | 1872000 | 0.013546
GEN-2024-343 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 507727 FLOURNY4 138 508816 OAKPH 4 138 1 | Current Study | 10.42 | (472.00, 472.00) | 497881.8164 | 3.9818 | 12504000 | 0.0093815
GEN-2024-343 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 507732 GENMOTR4 138 507759 SW SHV 4 138 1 | Current Study | 4.34 | (395.00, 395.00) | 287728.0003 | 5.5247 | 5208000 | 0.013546
GEN-2024-343 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 507760 SW SHV 7 345 508809 LONGWD 7 345 1 | Current Study | 19.02 | (1793.00, 1793.00) | 1135742.7622 | 2.7142 | 41844000 | 0.073634
GEN-2024-343 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508072 NWTXARK7 345 508359 WELSH 7 345 1 | Current Study | 56.1 | (1793.00, 1793.00) | 12420930.4279 | 10.064 | 123420000 | 0.095025
GEN-2024-343 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508548 KNOXLEE4 138 509059 CHEROKE4 138 1 | Current Study | 3.35 | (472.00, 472.00) | 590661.1056 | 14.6931 | 4020000 | 0.075094
GEN-2024-343 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508548 KNOXLEE4 138 509092 EASTON 4 138 1 | Current Study | 0.69 | (717.00, 717.00) | 120560.5557 | 14.5605 | 828000 | 0.084104
GEN-2024-343 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508557 MARSHL-4 138 508562 PIRKEY 4 138 1 | Current Study | 8.85 | (525.00, 525.00) | 1559778.8301 | 14.6872 | 10620000 | 0.092475
GEN-2024-343 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508562 PIRKEY 4 138 508566 SABMINT4 138 1 | Current Study | 0.88 | (472.00, 472.00) | 155152.0181 | 14.6924 | 1056000 | 0.09095
GEN-2024-343 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508562 PIRKEY 4 138 508596 BRANDYBR4 138 1 | Current Study | 3.14 | (717.00, 717.00) | 548637.8911 | 14.5605 | 3768000 | 0.084104
GEN-2024-343 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508563 PIRKEY 7 345 508832 DIANA 7 345 1 | Current Study | 24.75 | (1793.00, 1793.00) | 8002039.4347 | 14.6961 | 54450000 | 0.53545
GEN-2024-343 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508566 SABMINT4 138 508569 SEMRSHL4 138 1 | Current Study | 10.52 | (395.00, 395.00) | 1854771.8522 | 14.6924 | 12624000 | 0.09095
GEN-2024-343 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508567 SCOTTSV4 138 508569 SEMRSHL4 138 1 | Current Study | 6.08 | (395.00, 395.00) | 1071959.3975 | 14.6924 | 7296000 | 0.09095
GEN-2024-343 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508596 BRANDYBR4 138 509092 EASTON 4 138 1 | Current Study | 9.88 | (717.00, 717.00) | 1726287.3771 | 14.5605 | 11856000 | 0.084104
GEN-2024-343 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508808 LONGWD 4 138 508816 OAKPH 4 138 1 | Current Study | 1.8 | (472.00, 472.00) | 86006.4558 | 3.9818 | 2160000 | 0.0093815
GEN-2024-343 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 509059 CHEROKE4 138 509087 TATUM 4 138 1 | Current Study | 5.09 | (472.00, 472.00) | 897452.247 | 14.6931 | 6108000 | 0.075094
GEN-2024-343 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 509083 ROKHILL4 138 509087 TATUM 4 138 1 | Current Study | 6.5 | (472.00, 472.00) | 1146058.8616 | 14.6931 | 7800000 | 0.075094
GEN-2024-343 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 509083 ROKHILL4 138 509102 NEWPROS4 138 1 | Current Study | 4.82 | (395.00, 395.00) | 845866.8666 | 14.6243 | 5784000 | 0.043282
GEN-2024-343 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514934 DRAPER 7 345 515045 SEMINOL7 345 2 | Current Study | 44.14 | (1793.00, 1793.00) | 3934098.5807 | 4.0513 | 97108000 | 0.070683
GEN-2024-343 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1 | Current Study | 6.93 | (1793.00, 1793.00) | 1492345.6857 | 9.7884 | 15246000 | 0.17358
GEN-2024-344 | 04 SOUTHEAST | 94615 | ERIS | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029 | Contingent |  |  | 0 | 0 | 543515503 | N/A
GEN-2024-344 | 04 SOUTHEAST | 94811 | ERIS | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030 | Contingent |  |  | 0 | 0 | 1097029189 | N/A
GEN-2024-344 | 04 SOUTHEAST | 94911 | ERIS | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030 | Contingent |  |  | 0 | 0 | 143524375 | N/A
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 426800.3038 | 8.0528 | 5300000 | 0.034877
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at MOUND 4 138 kV | Current Study |  |  | 77830.7668 | 3.1996 | 2432500 | 0.039141
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV | Current Study |  |  | 196305.2178 | 3.7039 | 5300000 | 0.02792
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 57150.368 | 2.3494 | 2432500 | 0.042752
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 0.09 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 101038.3788 | 3.1089 | 3250000 | 0.032713
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 0.09 MVAR switched shunt at SWISVAL6 230 kV | Current Study |  |  | 146837.2002 | 3.8389 | 3825000 | 0.014063
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 120693.4609 | 2.2772 | 5300000 | 0.034877
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 0.2 MVAR switched shunt at GROVE 5 161 kV | Current Study |  |  | 65182.0463 | 2.0056 | 3250000 | 0.032713
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 0.25 MVAR switched shunt at LABETTS2 69 kV | Current Study |  |  | 30019.109 | 2.1753 | 1380000 | 0.032713
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 13 MVAR switched shunt at RSS T1 4 138 kV | Current Study |  |  | 1664956.7511 | 68.4463 | 2432500 | 0.10861
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 14 MVAR switched shunt at T.P.S.-2 69 kV | Current Study |  |  | 944559.2257 | 68.4463 | 1380000 | 0.10861
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 15 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 101038.3788 | 3.1089 | 3250000 | 0.032713
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 263257.5445 | 2.1938 | 12000000 | 0.034877
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR switched shunt at NEOSHO 4 138 kV | Current Study |  |  | 33331.4519 | 1.3703 | 2432500 | 0.032713
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV | Current Study |  |  | 101172.7774 | 3.113 | 3250000 | 0.032713
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR switched shunt at WICHITA7 345 kV | Current Study |  |  | 125834.5251 | 2.3742 | 5300000 | 0.039141
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 177 MVAR switched shunt at SWISVAL7 345 kV | Current Study |  |  | 189895.8587 | 3.5829 | 5300000 | 0.034877
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 20 MVAR switched shunt at LIBERTY4 138 kV | Current Study |  |  | 64104.6843 | 2.6353 | 2432500 | 0.042752
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 101172.7774 | 3.113 | 3250000 | 0.032713
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR switched shunt at STILWEL7 345 kV | Current Study |  |  | 195194.0796 | 3.6829 | 5300000 | 0.027228
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 24 MVAR switched shunt at GROVE 4 138 kV | Current Study |  |  | 45054.1136 | 1.8522 | 2432500 | 0.032713
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at G21-096-TAP 345 kV | Current Study |  |  | 173589.4603 | 3.2753 | 5300000 | 0.019871
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 280 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 289394.9971 | 2.4116 | 12000000 | 0.041794
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 295 MVAR switched shunt at G18-128-TAP 345 kV | Current Study |  |  | 153054.7401 | 2.8878 | 5300000 | 0.041794
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 3 MVAR switched shunt at NEOSHOS2 69 kV | Current Study |  |  | 448.9976 | 0.032536 | 1380000 | 0.00036967
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at G23-220-TAP 345 kV | Current Study |  |  | 171055.3622 | 3.2275 | 5300000 | 0.021711
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 316 MVAR switched shunt at W.GRDNR7 345 kV | Current Study |  |  | 195194.0796 | 3.6829 | 5300000 | 0.027228
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 74010.1411 | 2.2772 | 3250000 | 0.034877
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 45 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 370160.2098 | 3.0847 | 12000000 | 0.041794
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 45 MVAR switched shunt at NEVADA 5 161 kV | Current Study |  |  | 104188.8728 | 3.2058 | 3250000 | 0.034877
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 56 MVAR switched shunt at WHARV4 138 kV | Current Study |  |  | 77830.7668 | 3.1996 | 2432500 | 0.039141
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV | Current Study |  |  | 46173.7364 | 3.3459 | 1380000 | 0.032713
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Add line 515012 RVRVALY7 345 780360 G24-113-TAP 345 P2 | Current Study | 23.28 | (1195.00, 1195.00) | 2145239.7766 | 2.6108 | 82168000 | 0.017906
GEN-2024-344 | 04 SOUTHEAST | 94721 | ERIS | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 213682884 | N/A
GEN-2024-344 | 04 SOUTHEAST | 94929 | ERIS | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 413934522 | N/A
GEN-2024-344 | 04 SOUTHEAST | 900427 | ERIS | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032 | Contingent |  |  | 0 | 0 | 1790026304.1702 | N/A
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 1294461.3588 | 3.8533 | 33594000 | 0.07025
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 180588.5063 | 1.5488 | 11660000 | 0.042703
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Current Study | 14.6 | (1793.00, 1793.00) | 1237664.4295 | 3.8533 | 32120000 | 0.07025
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 30757.8846 | 1.3981 | 2200000 | 0.023748
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514715 WOODRNG7 345 515875 REDNGTN7 345 1 | Current Study | 19.2 | (1793.00, 1793.00) | 2073160.1896 | 4.908 | 42240000 | 0.06792
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 1696213.2705 | 3.6943 | 45914000 | 0.038686
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 1255391.914 | 1.3358 | 93984000 | 0.042703
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Current Study | 25.29 | (2390.00, 2390.00) | 1910075.4242 | 3.433 | 55638000 | 0.041973
GEN-2024-344 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 925724.4442 | 3.6943 | 25058000 | 0.038686
GEN-2024-344 | 04 SOUTHEAST | 171857 | ERIS | Riverside - Redbud Switch 345 kV Line GEN-2024-344 Interconnection (Non-Shared NU) (AEP) | Interconnection |  |  | 500000 | 100 | 500000 | 1
GEN-2024-344 | 04 SOUTHEAST | 171859 | ERIS | Riverside - Redbud Switch 345 kV Line GEN-2024-344 Interconnection (Non-Shared NU) (OGE) | Interconnection |  |  | 18000000 | 100 | 18000000 | 1
GEN-2024-344 | 04 SOUTHEAST | 171856 | ERIS | Riverside - Redbud Switch 345 kV Line GEN-2024-344 Interconnection (TOIF) (AEP) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-344 | 04 SOUTHEAST | 171858 | ERIS | Riverside - Redbud Switch 345 kV Line GEN-2024-344 Interconnection (TOIF) (OGE) | Interconnection |  |  | 3000000 | 100 | 3000000 | 1
GEN-2024-352 | 03 CENTRAL | 94615 | ERIS | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029 | Contingent |  |  | 0 | 0 | 543515503 | N/A
GEN-2024-352 | 03 CENTRAL | TBD | ERIS | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV | Current Study |  |  | 63914.962 | 4.6315 | 1380000 | 0.064304
GEN-2024-352 | 03 CENTRAL | TBD | ERIS | Add 16 MVAR switched shunt at HUMBOLT5 161 kV | Current Study |  |  | 286715.5798 | 8.822 | 3250000 | 0.10768
GEN-2024-352 | 03 CENTRAL | TBD | ERIS | Add 21 MVAR switched shunt at S1263 5 161 kV | Current Study |  |  | 286715.5798 | 8.822 | 3250000 | 0.10768
GEN-2024-352 | 03 CENTRAL | TBD | ERIS | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV | Current Study |  |  | 121743.8462 | 8.822 | 1380000 | 0.10768
GEN-2024-352 | 03 CENTRAL | TBD | ERIS | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2 | Current Study | 0.75 | (2390.00, 2390.00) | 101222.2072 | 0.56946 | 17775000 | 0.015695
GEN-2024-352 | 03 CENTRAL | 94721 | ERIS | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 213682884 | N/A
GEN-2024-352 | 03 CENTRAL | 94929 | ERIS | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 413934522 | N/A
GEN-2024-352 | 03 CENTRAL | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 231963.4137 | 1.9894 | 11660000 | 0.055127
GEN-2024-352 | 03 CENTRAL | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 1612533.3767 | 1.7158 | 93984000 | 0.055127
GEN-2024-352 | 03 CENTRAL | TBD | ERIS | Rebuild line 541199 ST JOE 7 345 541400 EASTOWN7 345 1 | Current Study | 8.12 | (1793.00, 1793.00) | 206982.9338 | 1.1587 | 17864000 | 0.01105
GEN-2024-352 | 03 CENTRAL | TBD | ERIS | Rebuild line 541400 EASTOWN7 345 542982 IATAN 7 345 1 | Current Study | 23.71 | (1793.00, 1793.00) | 720621.9189 | 1.3815 | 52162000 | 0.015363
GEN-2024-352 | 03 CENTRAL | 171951 | ERIS | Sibley 345 kV Substation GEN-2024-352 Interconnection (TOIF) (WERE) | Interconnection |  |  | 1958092 | 100 | 1958092 | 1
GEN-2024-360 | 04 SOUTHEAST | 94615 | ERIS | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029 | Contingent |  |  | 0 | 0 | 543515503 | N/A
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 283074.3956 | 5.341 | 5300000 | 0.028915
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at MOUND 4 138 kV | Current Study |  |  | 66505.5139 | 2.734 | 2432500 | 0.041807
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 31893.8819 | 2.3112 | 1380000 | 0.032034
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV | Current Study |  |  | 190506.4891 | 3.5945 | 5300000 | 0.033869
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 42412.2843 | 1.7436 | 2432500 | 0.039659
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 10123.4793 | 0.73359 | 1380000 | 0.032048
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 110740.7439 | 2.0894 | 5300000 | 0.040001
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV | Current Study |  |  | 31893.8819 | 2.3112 | 1380000 | 0.032034
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 11 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 73405.8044 | 2.2586 | 3250000 | 0.032034
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 241548.5986 | 2.0129 | 12000000 | 0.040001
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR switched shunt at NEOSHO 4 138 kV | Current Study |  |  | 22005.6337 | 0.90465 | 2432500 | 0.026996
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at CPK446 5 161 kV | Current Study |  |  | 55719.4267 | 1.7144 | 3250000 | 0.032034
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR switched shunt at WICHITA7 345 kV | Current Study |  |  | 107524.1849 | 2.0288 | 5300000 | 0.041807
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 177 MVAR switched shunt at SWISVAL7 345 kV | Current Study |  |  | 114885.4231 | 2.1676 | 5300000 | 0.026375
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 20 MVAR switched shunt at LIBERTY4 138 kV | Current Study |  |  | 47573.2037 | 1.9557 | 2432500 | 0.039659
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR switched shunt at STILWEL7 345 kV | Current Study |  |  | 151260.6462 | 2.854 | 5300000 | 0.026375
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 24 MVAR switched shunt at GROVE 4 138 kV | Current Study |  |  | 29745.0085 | 1.2228 | 2432500 | 0.026996
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at G21-096-TAP 345 kV | Current Study |  |  | 225493.4224 | 4.2546 | 5300000 | 0.032266
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 280 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 305852.3183 | 2.5488 | 12000000 | 0.055213
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 295 MVAR switched shunt at G18-128-TAP 345 kV | Current Study |  |  | 138472.2559 | 2.6127 | 5300000 | 0.047265
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 3 MVAR switched shunt at NEOSHOS2 69 kV | Current Study |  |  | 45925.3118 | 3.3279 | 1380000 | 0.047265
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at G23-220-TAP 345 kV | Current Study |  |  | 182249.9776 | 3.4387 | 5300000 | 0.028915
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 316 MVAR switched shunt at W.GRDNR7 345 kV | Current Study |  |  | 151260.6462 | 2.854 | 5300000 | 0.026375
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at INDEPCO5 161 kV | Current Study |  |  | 73405.8044 | 2.2586 | 3250000 | 0.032034
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 67907.06 | 2.0894 | 3250000 | 0.040001
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 45 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 334892.727 | 2.7908 | 12000000 | 0.047265
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 45 MVAR switched shunt at NEVADA 5 161 kV | Current Study |  |  | 63033.4059 | 1.9395 | 3250000 | 0.026375
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add 56 MVAR switched shunt at WHARV4 138 kV | Current Study |  |  | 66505.5139 | 2.734 | 2432500 | 0.041807
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Add line 515012 RVRVALY7 345 780360 G24-113-TAP 345 P2 | Current Study | 23.28 | (1195.00, 1195.00) | 1829792.1382 | 2.2269 | 82168000 | 0.019091
GEN-2024-360 | 04 SOUTHEAST | 94721 | ERIS | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 213682884 | N/A
GEN-2024-360 | 04 SOUTHEAST | 94929 | ERIS | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 413934522 | N/A
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | Current Study | 21.38 | (1793.00, 1793.00) | 1318103.1659 | 2.8023 | 47036000 | 0.054555
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 773764.2795 | 2.3033 | 33594000 | 0.05249
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 134020.4804 | 1.1494 | 11660000 | 0.039614
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Current Study | 14.6 | (1793.00, 1793.00) | 739813.9149 | 2.3033 | 32120000 | 0.05249
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514715 WOODRNG7 345 515875 REDNGTN7 345 1 | Current Study | 19.2 | (1793.00, 1793.00) | 1730429.9649 | 4.0967 | 42240000 | 0.070865
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515055 MAUD 4 138 787770 G24-360-TAP 138 1 | Current Study | 5.11 | (395.00, 395.00) | 5613958.3375 | 91.5518 | 6132000 | 0.40559
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 1944888.7978 | 4.2359 | 45914000 | 0.055447
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 931666.3105 | 0.9913 | 93984000 | 0.039614
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Current Study | 25.29 | (2390.00, 2390.00) | 1726619.4486 | 3.1033 | 55638000 | 0.047428
GEN-2024-360 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 1061441.4665 | 4.2359 | 25058000 | 0.055447
GEN-2024-360 | 04 SOUTHEAST | 171871 | ERIS | Seminole - Maud 138 kV Line GEN-2024-360 Interconnection (Non-Shared NU) (OGE) | Interconnection |  |  | 3000000 | 100 | 3000000 | 1
GEN-2024-360 | 04 SOUTHEAST | 171870 | ERIS | Seminole - Maud 138 kV Line GEN-2024-360 Interconnection (TOIF) (OGE) | Interconnection |  |  | 2000000 | 100 | 2000000 | 1
GEN-2024-361 | 04 SOUTHEAST | 94615 | ERIS | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029 | Contingent |  |  | 0 | 0 | 543515503 | N/A
GEN-2024-361 | 04 SOUTHEAST | 94811 | ERIS | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030 | Contingent |  |  | 0 | 0 | 1097029189 | N/A
GEN-2024-361 | 04 SOUTHEAST | 94911 | ERIS | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030 | Contingent |  |  | 0 | 0 | 143524375 | N/A
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 157727.3581 | 2.976 | 5300000 | 0.032222
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at MOUND 4 138 kV | Current Study |  |  | 36850.8899 | 1.5149 | 2432500 | 0.046331
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV | Current Study |  |  | 104306.7367 | 1.9681 | 5300000 | 0.037088
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 26567.7195 | 1.0922 | 2432500 | 0.049686
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 0.09 MVAR switched shunt at NOL435 5 161 kV | Current Study |  |  | 41774.5445 | 1.2854 | 3250000 | 0.033813
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 0.09 MVAR switched shunt at SWISVAL6 230 kV | Current Study |  |  | 134579.074 | 3.5184 | 3825000 | 0.032222
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 64328.0045 | 1.2137 | 5300000 | 0.046472
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 0.2 MVAR switched shunt at GROVE 5 161 kV | Current Study |  |  | 17202.7289 | 0.52931 | 3250000 | 0.021584
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 0.25 MVAR switched shunt at LABETTS2 69 kV | Current Study |  |  | 12411.468 | 0.89938 | 1380000 | 0.033813
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 15 MVAR switched shunt at NEO184 5 161 kV | Current Study |  |  | 41774.5445 | 1.2854 | 3250000 | 0.033813
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 140312.7592 | 1.1693 | 12000000 | 0.046472
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR switched shunt at NEOSHO 4 138 kV | Current Study |  |  | 13780.9636 | 0.56653 | 2432500 | 0.033813
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV | Current Study |  |  | 41830.1119 | 1.2871 | 3250000 | 0.033813
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR switched shunt at WICHITA7 345 kV | Current Study |  |  | 59853.4318 | 1.1293 | 5300000 | 0.046544
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 177 MVAR switched shunt at SWISVAL7 345 kV | Current Study |  |  | 70239.4461 | 1.3253 | 5300000 | 0.032251
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 20 MVAR switched shunt at LIBERTY4 138 kV | Current Study |  |  | 29800.6003 | 1.2251 | 2432500 | 0.049686
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 21 MVAR switched shunt at MON383 5 161 kV | Current Study |  |  | 41830.1119 | 1.2871 | 3250000 | 0.033813
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR switched shunt at STILWEL7 345 kV | Current Study |  |  | 92478.7821 | 1.7449 | 5300000 | 0.032251
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 24 MVAR switched shunt at GROVE 4 138 kV | Current Study |  |  | 18627.7244 | 0.76579 | 2432500 | 0.033813
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at G21-096-TAP 345 kV | Current Study |  |  | 130278.0232 | 2.4581 | 5300000 | 0.037283
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 280 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 168436.7074 | 1.4036 | 12000000 | 0.060813
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 295 MVAR switched shunt at G18-128-TAP 345 kV | Current Study |  |  | 92690.3608 | 1.7489 | 5300000 | 0.063276
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 3 MVAR switched shunt at NEOSHOS2 69 kV | Current Study |  |  | 30741.4196 | 2.2276 | 1380000 | 0.063276
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at G23-220-TAP 345 kV | Current Study |  |  | 101548.5962 | 1.916 | 5300000 | 0.032222
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 316 MVAR switched shunt at W.GRDNR7 345 kV | Current Study |  |  | 92478.7821 | 1.7449 | 5300000 | 0.032251
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 39446.4178 | 1.2137 | 3250000 | 0.046472
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 45 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 224170.0152 | 1.8681 | 12000000 | 0.063276
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 45 MVAR switched shunt at NEVADA 5 161 kV | Current Study |  |  | 38537.8005 | 1.1858 | 3250000 | 0.032251
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 56 MVAR switched shunt at WHARV4 138 kV | Current Study |  |  | 36850.8899 | 1.5149 | 2432500 | 0.046331
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV | Current Study |  |  | 19090.635 | 1.3834 | 1380000 | 0.033813
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Add line 515012 RVRVALY7 345 780360 G24-113-TAP 345 P2 | Current Study | 23.28 | (1195.00, 1195.00) | 907584.4675 | 1.1045 | 82168000 | 0.018939
GEN-2024-361 | 04 SOUTHEAST | 94721 | ERIS | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 213682884 | N/A
GEN-2024-361 | 04 SOUTHEAST | 94929 | ERIS | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 413934522 | N/A
GEN-2024-361 | 04 SOUTHEAST | 900427 | ERIS | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032 | Contingent |  |  | 0 | 0 | 1790026304.1702 | N/A
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 500991.5003 | 1.4913 | 33594000 | 0.067972
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 83959.9027 | 0.72007 | 11660000 | 0.049634
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Current Study | 14.6 | (1793.00, 1793.00) | 479009.555 | 1.4913 | 32120000 | 0.067972
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | Current Study | 1 | (1793.00, 1793.00) | 19299.7306 | 0.87726 | 2200000 | 0.037254
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 1071297.6414 | 2.3333 | 45914000 | 0.061083
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | Current Study | 15.48 | (1793.00, 1793.00) | 885052.2397 | 2.5988 | 34056000 | 0.03462
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 583661.6358 | 0.62102 | 93984000 | 0.049634
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Current Study | 25.29 | (2390.00, 2390.00) | 1155221.3996 | 2.0763 | 55638000 | 0.063464
GEN-2024-361 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 584670.8258 | 2.3333 | 25058000 | 0.061083
GEN-2024-361 | 04 SOUTHEAST | 171873 | ERIS | Spring Valley - Warwick 138 kV line GEN-2024-361 Interconnection (Non-Shared NU) (OGE) | Interconnection |  |  | 7000000 | 100 | 7000000 | 1
GEN-2024-361 | 04 SOUTHEAST | 171872 | ERIS | Spring Valley - Warwick 138 kV line GEN-2024-361 Interconnection (TOIF) (OGE) | Interconnection |  |  | 2000000 | 100 | 2000000 | 1
GEN-2024-362 | 04 SOUTHEAST | 94615 | ERIS | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029 | Contingent |  |  | 0 | 0 | 543515503 | N/A
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at BUFFALO7 345 kV | Current Study |  |  | 474310.528 | 8.9493 | 5300000 | 0.03883
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV | Current Study |  |  | 238972.307 | 4.5089 | 5300000 | 0.032547
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at MOUND 4 138 kV | Current Study |  |  | 54639.8699 | 2.2462 | 2432500 | 0.045797
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV | Current Study |  |  | 161727.0058 | 3.0515 | 5300000 | 0.038337
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 37787.9339 | 1.5535 | 2432500 | 0.047113
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 0.09 MVAR switched shunt at SWISVAL6 230 kV | Current Study |  |  | 203900.4024 | 5.3307 | 3825000 | 0.032547
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | Current Study |  |  | 11161.7025 | 0.80882 | 1380000 | 0.047113
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 78207.0422 | 1.4756 | 5300000 | 0.037666
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 12 MVAR switched shunt at GOODCTY3 115 kV | Current Study |  |  | 611306.3722 | 27.6297 | 2212500 | 0.022319
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 175858.7714 | 1.4655 | 12000000 | 0.03883
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR switched shunt at NEOSHO 4 138 kV | Current Study |  |  | 30674.8937 | 1.261 | 2432500 | 0.050176
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR switched shunt at WICHITA7 345 kV | Current Study |  |  | 91478.175 | 1.726 | 5300000 | 0.047424
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 177 MVAR switched shunt at SWISVAL7 345 kV | Current Study |  |  | 91229.7152 | 1.7213 | 5300000 | 0.027926
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 20 MVAR switched shunt at LIBERTY4 138 kV | Current Study |  |  | 33677.7204 | 1.3845 | 2432500 | 0.037433
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 20 MVAR switched shunt at RANSOM 3 115 kV | Current Study |  |  | 611306.3722 | 27.6297 | 2212500 | 0.022319
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 213 MVAR switched shunt at STILWEL7 345 kV | Current Study |  |  | 120115.0268 | 2.2663 | 5300000 | 0.027926
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 25 MVAR switched shunt at ATWOOD 3 115 kV | Current Study |  |  | 167056.615 | 7.5506 | 2212500 | 0.026223
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 28 MVAR switched shunt at G21-096-TAP 345 kV | Current Study |  |  | 173282.7292 | 3.2695 | 5300000 | 0.03306
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 280 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 268075.0102 | 2.234 | 12000000 | 0.064525
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 295 MVAR switched shunt at G18-128-TAP 345 kV | Current Study |  |  | 110250.1122 | 2.0802 | 5300000 | 0.050176
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 3 MVAR switched shunt at NEOSHOS2 69 kV | Current Study |  |  | 36565.2365 | 2.6497 | 1380000 | 0.050176
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV | Current Study |  |  | 611306.3722 | 27.6297 | 2212500 | 0.022319
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 30 MVAR switched shunt at G23-220-TAP 345 kV | Current Study |  |  | 153856.0119 | 2.9029 | 5300000 | 0.032547
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 316 MVAR switched shunt at W.GRDNR7 345 kV | Current Study |  |  | 120115.0268 | 2.2663 | 5300000 | 0.027926
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV | Current Study |  |  | 611306.3722 | 27.6297 | 2212500 | 0.022319
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 47957.1485 | 1.4756 | 3250000 | 0.037666
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 45 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 266637.9667 | 2.222 | 12000000 | 0.050176
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 45 MVAR switched shunt at NEVADA 5 161 kV | Current Study |  |  | 50054.3891 | 1.5401 | 3250000 | 0.027926
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 48 MVAR switched shunt at MACON 3 345 kV | Current Study |  |  | 338221.4471 | 6.3815 | 5300000 | 0.026223
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 56 MVAR switched shunt at WHARV4 138 kV | Current Study |  |  | 54639.8699 | 2.2462 | 2432500 | 0.045797
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add 86 MVAR switched shunt at POSTROCK7 345 kV | Current Study |  |  | 320962.2104 | 6.0559 | 5300000 | 0.022319
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Add line 515012 RVRVALY7 345 780360 G24-113-TAP 345 P2 | Current Study | 23.28 | (1195.00, 1195.00) | 1178523.3623 | 1.4343 | 82168000 | 0.016395
GEN-2024-362 | 04 SOUTHEAST | 94721 | ERIS | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 213682884 | N/A
GEN-2024-362 | 04 SOUTHEAST | 94929 | ERIS | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 413934522 | N/A
GEN-2024-362 | 04 SOUTHEAST | 171875 | ERIS | Leonard 138 kV Substation GEN-2024-362 Interconnection (Non-Shared NU) (AEP) | Interconnection |  |  | 2800000 | 100 | 2800000 | 1
GEN-2024-362 | 04 SOUTHEAST | 171874 | ERIS | Leonard 138 kV SubstationGEN-2024-362 Interconnection (TOIF) (AEP) | Interconnection |  |  | 3525000 | 100 | 3525000 | 1
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 458746.1802 | 1.3656 | 33594000 | 0.041493
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Current Study | 14.6 | (1793.00, 1793.00) | 438617.8278 | 1.3656 | 32120000 | 0.041493
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514715 WOODRNG7 345 515875 REDNGTN7 345 1 | Current Study | 19.2 | (1793.00, 1793.00) | 1799022.6972 | 4.259 | 42240000 | 0.098232
GEN-2024-362 | 04 SOUTHEAST | TBD | NRIS | Rebuild line 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | Current Study | 4.8 | (395.00, 395.00) | 5760000 | 100 | 5760000 | 0.071495
GEN-2024-362 | 04 SOUTHEAST | TBD | NRIS | Rebuild line 514893 XEROX 4 138 514894 CZECHAL4 138 1 | Current Study | 1.17 | (472.00, 472.00) | 1404000 | 100 | 1404000 | 0.069616
GEN-2024-362 | 04 SOUTHEAST | TBD | NRIS | Rebuild line 514894 CZECHAL4 138 514898 CIMARON4 138 1 | Current Study | 5.63 | (525.00, 525.00) | 2815735.5909 | 41.6776 | 6756000 | 0.069616
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 1704385.9004 | 3.7121 | 45914000 | 0.064787
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 659399.6998 | 0.70161 | 93984000 | 0.037383
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Current Study | 25.29 | (2390.00, 2390.00) | 1374989.1261 | 2.4713 | 55638000 | 0.050358
GEN-2024-362 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 930184.7343 | 3.7121 | 25058000 | 0.064787
GEN-2024-370 | 03 CENTRAL | 94615 | ERIS | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029 | Contingent |  |  | 0 | 0 | 543515503 | N/A
GEN-2024-370 | 03 CENTRAL | TBD | ERIS | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV | Current Study |  |  | 131902.4262 | 9.5581 | 1380000 | 0.10563
GEN-2024-370 | 03 CENTRAL | TBD | ERIS | Add 16 MVAR switched shunt at HUMBOLT5 161 kV | Current Study |  |  | 243857.9849 | 7.5033 | 3250000 | 0.072899
GEN-2024-370 | 03 CENTRAL | TBD | ERIS | Add 21 MVAR switched shunt at S1263 5 161 kV | Current Study |  |  | 243857.9849 | 7.5033 | 3250000 | 0.072899
GEN-2024-370 | 03 CENTRAL | TBD | ERIS | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV | Current Study |  |  | 103545.8521 | 7.5033 | 1380000 | 0.072899
GEN-2024-370 | 03 CENTRAL | TBD | ERIS | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2 | Current Study | 0.75 | (2390.00, 2390.00) | 174546.9639 | 0.98198 | 17775000 | 0.021544
GEN-2024-370 | 03 CENTRAL | 94721 | ERIS | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 213682884 | N/A
GEN-2024-370 | 03 CENTRAL | 94929 | ERIS | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 413934522 | N/A
GEN-2024-370 | 03 CENTRAL | TBD | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Current Study | 5.3 | (1793.00, 1793.00) | 286093.5632 | 2.4536 | 11660000 | 0.054121
GEN-2024-370 | 03 CENTRAL | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 1988828.3767 | 2.1161 | 93984000 | 0.054121
GEN-2024-370 | 03 CENTRAL | TBD | ERIS | Rebuild line 541199 ST JOE 7 345 541400 EASTOWN7 345 1 | Current Study | 8.12 | (1793.00, 1793.00) | 772528.9718 | 4.3245 | 17864000 | 0.03283
GEN-2024-370 | 03 CENTRAL | TBD | ERIS | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | Current Study | 2.29 | (551.00, 551.00) | 2420328.2882 | 70.4608 | 3435000 | 0.81151
GEN-2024-370 | 03 CENTRAL | TBD | ERIS | Rebuild line 541204 SMTHVL 5 161 541221 PLTCTY 5 161 1 | Current Study | 7.49 | (364.00, 364.00) | 8025000 | 71.4286 | 11235000 | 0.18849
GEN-2024-370 | 03 CENTRAL | TBD | ERIS | Rebuild line 541214 TWA 5 161 541318 NCONGRS5 161 1 | Current Study | 2.85 | (246.00, 246.00) | 3053571.4286 | 71.4286 | 4275000 | 0.058277
GEN-2024-370 | 03 CENTRAL | TBD | ERIS | Rebuild line 541400 EASTOWN7 345 542982 IATAN 7 345 1 | Current Study | 23.71 | (1793.00, 1793.00) | 2385203.1163 | 4.5727 | 52162000 | 0.040476
GEN-2024-370 | 03 CENTRAL | 171954 | ERIS | Smithville 161 kV Substation GEN-2024-370 Interconnection (Non-Shared NU) (WERE) | Interconnection |  |  | 3659394 | 100 | 3659394 | 1
GEN-2024-370 | 03 CENTRAL | 171953 | ERIS | Smithville 161 kV Substation GEN-2024-370 Interconnection (TOIF) (WERE) | Interconnection |  |  | 1061551 | 100 | 1061551 | 1
GEN-2024-372 | 02 NEBRASKA | TBD | NRIS | Add 108 MVAR switched shunt at MAURINE4 230 kV | Current Study |  |  | 232364.0358 | 6.0749 | 3825000 | 0.033607
GEN-2024-372 | 02 NEBRASKA | TBD | NRIS | Add 12 MVAR switched shunt at L11_____-MK7 115 kV | Current Study |  |  | 150158.226 | 6.7868 | 2212500 | 0.033607
GEN-2024-372 | 02 NEBRASKA | TBD | NRIS | Add 154 MVAR SVC at WAYSIDE 4 230 kV | Current Study |  |  | 350058.486 | 4.0704 | 8600000 | 0.030032
GEN-2024-372 | 02 NEBRASKA | TBD | NRIS | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV | Current Study |  |  | 57409.1169 | 2.5948 | 2212500 | 0.033607
GEN-2024-372 | 02 NEBRASKA | TBD | NRIS | Add 3-winding transformer 652305 SIOUXC29 13 652552 SIOUXCY2 230 652564 SIOUXCY3 345 M2 | Current Study |  | (600.00, 750.00) | 18047049.5895 | 72.1882 | 25000000 | 0.013775
GEN-2024-372 | 02 NEBRASKA | TBD | NRIS | Add 45 MVAR switched shunt at PR BRZ 4 230 kV | Current Study |  |  | 87922.1722 | 2.2986 | 3825000 | 0.03157
GEN-2024-372 | 02 NEBRASKA | TBD | NRIS | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | Current Study | 23.48 | (1793.00, 1793.00) | 5388609.3509 | 10.4317 | 51656000 | 0.068175
GEN-2024-372 | 02 NEBRASKA | TBD | ERIS | Rebuild line 646226 S1226 5 161 646247 S1247 5 161 1 | Current Study | 13.54 | (246.00, 246.00) | 20310000 | 100 | 20310000 | 0.22217
GEN-2024-372 | 02 NEBRASKA | 171891 | ERIS | S1252 161 kV Substation GEN-2024-372 Interconnection (Non-Shared NU) (OPPD) | Interconnection |  |  | 1500000 | 100 | 1500000 | 1
GEN-2024-372 | 02 NEBRASKA | 171890 | ERIS | S1252 161 kV Substation GEN-2024-372 Interconnection (TOIF) (OPPD) | Interconnection |  |  | 476039 | 100 | 476039 | 1
GEN-2024-373 | 04 SOUTHEAST | 94615 | ERIS | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029 | Contingent |  |  | 0 | 0 | 543515503 | N/A
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at MOUND 4 138 kV | Current Study |  |  | 36832.9455 | 1.5142 | 2432500 | 0.037046
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 26487.6754 | 1.9194 | 1380000 | 0.042566
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV | Current Study |  |  | 23365.4164 | 0.96055 | 2432500 | 0.034958
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV | Current Study |  |  | 64756.611 | 1.2218 | 5300000 | 0.037425
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV | Current Study |  |  | 26487.6754 | 1.9194 | 1380000 | 0.042566
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 0.2 MVAR switched shunt at GROVE 5 161 kV | Current Study |  |  | 39964.3695 | 1.2297 | 3250000 | 0.040113
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 0.25 MVAR switched shunt at LABETTS2 69 kV | Current Study |  |  | 18405.2946 | 1.3337 | 1380000 | 0.040113
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 11 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 60963.0752 | 1.8758 | 3250000 | 0.042566
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR SVC at G16-111-TAP 345 kV | Current Study |  |  | 141247.639 | 1.1771 | 12000000 | 0.037425
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR switched shunt at NEOSHO 4 138 kV | Current Study |  |  | 12746.8502 | 0.52402 | 2432500 | 0.02502
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at CPK446 5 161 kV | Current Study |  |  | 46274.6458 | 1.4238 | 3250000 | 0.042566
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 160 MVAR switched shunt at WICHITA7 345 kV | Current Study |  |  | 60159.2382 | 1.1351 | 5300000 | 0.037425
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 177 MVAR switched shunt at SWISVAL7 345 kV | Current Study |  |  | 60289.7343 | 1.1375 | 5300000 | 0.022146
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 20 MVAR switched shunt at LIBERTY4 138 kV | Current Study |  |  | 26208.6264 | 1.0774 | 2432500 | 0.034958
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 24 MVAR switched shunt at GROVE 4 138 kV | Current Study |  |  | 17229.9136 | 0.70832 | 2432500 | 0.02502
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 280 MVAR SVC at G15052_1 345 kV | Current Study |  |  | 156297.2649 | 1.3025 | 12000000 | 0.045144
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 295 MVAR switched shunt at G18-128-TAP 345 kV | Current Study |  |  | 71408.6376 | 1.3473 | 5300000 | 0.038998
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 3 MVAR switched shunt at NEOSHOS2 69 kV | Current Study |  |  | 23683.1843 | 1.7162 | 1380000 | 0.038998
GEN-2024-373 | 04 SOUTHEAST | TBD | NRIS | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV | Current Study |  |  | 6319.9273 | 0.27478 | 2300000 | 0.028761
GEN-2024-373 | 04 SOUTHEAST | TBD | NRIS | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2 | Current Study |  | (484.00, 515.00) | 568956.8002 | 3.1434 | 18100000 | 0.012376
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at INDEPCO5 161 kV | Current Study |  |  | 60963.0752 | 1.8758 | 3250000 | 0.042566
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 42 MVAR switched shunt at CNTRVIL5 161 kV | Current Study |  |  | 39709.2426 | 1.2218 | 3250000 | 0.037425
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 45 MVAR SVC at G15052_T 345 kV | Current Study |  |  | 172700.5402 | 1.4392 | 12000000 | 0.038998
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 45 MVAR switched shunt at NEVADA 5 161 kV | Current Study |  |  | 33078.7596 | 1.0178 | 3250000 | 0.022146
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Add 56 MVAR switched shunt at WHARV4 138 kV | Current Study |  |  | 36832.9455 | 1.5142 | 2432500 | 0.037046
GEN-2024-373 | 04 SOUTHEAST | 94721 | ERIS | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 213682884 | N/A
GEN-2024-373 | 04 SOUTHEAST | 94929 | ERIS | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025 | Contingent |  |  | 0 | 0 | 413934522 | N/A
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 505600 TUPELO 4 138 505602 S BROWN4 138 1 | Current Study | 36.9 | (211.00, 211.00) | 9345300.3404 | 21.105 | 44280000 | 0.094488
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 505602 S BROWN4 138 769060 G22-104-TAP 138 1 | Current Study | 1.62 | (395.00, 395.00) | 1944000 | 100 | 1944000 | 0.34469
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508359 WELSH 7 345 508841 WILKES 7 345 1 | Current Study | 30.63 | (1793.00, 1793.00) | 3597068.1963 | 5.338 | 67386000 | 0.070395
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | Current Study | 21.38 | (1793.00, 1793.00) | 1091210.7078 | 2.3199 | 47036000 | 0.072262
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Current Study | 15.27 | (1793.00, 1793.00) | 450480.9963 | 1.341 | 33594000 | 0.048895
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Current Study | 14.6 | (1793.00, 1793.00) | 430715.2945 | 1.341 | 32120000 | 0.048895
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514715 WOODRNG7 345 515875 REDNGTN7 345 1 | Current Study | 19.2 | (1793.00, 1793.00) | 859350.8889 | 2.0344 | 42240000 | 0.056308
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Current Study | 20.87 | (1793.00, 1793.00) | 993999.0624 | 2.1649 | 45914000 | 0.045341
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | Current Study | 42.72 | (1793.00, 1793.00) | 513291.4375 | 0.54615 | 93984000 | 0.03492
GEN-2024-373 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Current Study | 11.39 | (1793.00, 1793.00) | 542484.3949 | 2.1649 | 25058000 | 0.045341
GEN-2024-373 | 04 SOUTHEAST | 171893 | ERIS | Unger - West Bank Tap 138 kV Line GEN-2024-052/373 Interconnection (Shared NU) (WFEC) | Interconnection |  |  | 0 |  | 0 | 1
GEN-2024-373 | 04 SOUTHEAST | 171893 | ERIS | Unger - West Bank Tap 138 kV Line GEN-2024-052/373 Interconnection (Shared NU) (WFEC) | Interconnection |  |  | 7000000 | 100 | 7000000 | 1
GEN-2024-373 | 04 SOUTHEAST | 171892 | ERIS | Unger - West Bank Tap 138 kV Line GEN-2024-373 Interconnection (TOIF) (WFEC) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-373 | 04 SOUTHEAST | 171892 | ERIS | Unger - West Bank Tap 138 kV Line GEN-2024-373 Interconnection (TOIF) (WFEC) | Interconnection |  |  | 2000000 | 100 | 2000000 | 1
GEN-2024-374 | 02 NEBRASKA | TBD | NRIS | 640_NPPD_Rebuild_Morill_Gering_115.idv : 2024 ITP, PID: TBD, ISD: Unknown | Contingent |  |  | 0 | 0 | 24272842 | N/A
GEN-2024-374 | 02 NEBRASKA | 94819 | NRIS | 640_NPPD_Rebuild_Scotsbluff_Gering_115.idv : 2024 ITP, PID: 94819, NTC, ISD: Unknown | Contingent |  |  | 0 | 0 | 385333 | N/A
GEN-2024-374 | 02 NEBRASKA | TBD | NRIS | Add 0.04 MVAR switched shunt at VICTRYH4 230 kV | Current Study |  |  | 3825000 | 100 | 3825000 | 0.16894
GEN-2024-374 | 02 NEBRASKA | TBD | NRIS | Add 108 MVAR switched shunt at MAURINE4 230 kV | Current Study |  |  | 401241.9894 | 10.49 | 3825000 | 0.06448
GEN-2024-374 | 02 NEBRASKA | TBD | NRIS | Add 154 MVAR SVC at WAYSIDE 4 230 kV | Current Study |  |  | 1979234.9981 | 23.0144 | 8600000 | 0.18867
GEN-2024-374 | 02 NEBRASKA | TBD | NRIS | Add 23 MVAR switched shunt at STEGALL-LNX3 230 kV | Current Study |  |  | 3825000 | 100 | 3825000 | 0.13822
GEN-2024-374 | 02 NEBRASKA | TBD | NRIS | Add 45 MVAR switched shunt at PR BRZ 4 230 kV | Current Study |  |  | 158695.2428 | 4.1489 | 3825000 | 0.063314
GEN-2024-374 | 02 NEBRASKA | TBD | NRIS | Add 60 MVAR switched shunt at NUNDRWD-LNX3 230 kV | Current Study |  |  | 3825000 | 100 | 3825000 | 0.068235
GEN-2024-374 | 02 NEBRASKA | TBD | NRIS | Add 78 MVAR switched shunt at DH_CS_EA-TS4 230 kV | Current Study |  |  | 3825000 | 100 | 3825000 | 0.16894
GEN-2024-374 | 02 NEBRASKA | TBD | NRIS | Rebuild line 640404 WAYSIDE 4 230 652484 NUNDRWD4 230 1 | Current Study | 80.12 | (519.00, 519.00) | 152228000 | 100 | 152228000 | 0.15676
GEN-2024-374 | 02 NEBRASKA | TBD | NRIS | Rebuild line 640404 WAYSIDE 4 230 652873 STEGALL-LNX3 230 1 | Current Study | 92.96 | (386.00, 386.00) | 176624000 | 100 | 176624000 | 0.13822
GEN-2024-374 | 02 NEBRASKA | TBD | NRIS | Rebuild line 645454 S3454 3 345 650185 WAGENER 3 345 1 | Current Study | 33.67 | (1793.00, 1793.00) | 2324886.8496 | 3.1386 | 74074000 | 0.062196
GEN-2024-374 | 02 NEBRASKA | TBD | NRIS | Rebuild line 652425 BELFELD4 230 659124 DICKINSN-BE4 230 1 | Current Study | 15.17 | (386.00, 386.00) | 28823000 | 100 | 28823000 | 0.012531
GEN-2024-374 | 02 NEBRASKA | TBD | NRIS | Rebuild line 652484 NUNDRWD4 230 652884 NUNDRWD-LNX3 230 Z | Current Study | 0.14514 | (519.00, 519.00) | 275765.6361 | 100 | 275765.6361 | 0.06241
GEN-2024-374 | 02 NEBRASKA | TBD | NRIS | Rebuild line 652497 MAURINE4 230 652884 NUNDRWD-LNX3 230 1 | Current Study | 72.13 | (519.00, 519.00) | 137047000 | 100 | 137047000 | 0.06241
GEN-2024-374 | 02 NEBRASKA | TBD | NRIS | Rebuild line 652497 MAURINE4 230 659351 BISON___-GE4 230 1 | Current Study | 38.56 | (519.00, 519.00) | 73264000 | 100 | 73264000 | 0.06448
GEN-2024-374 | 02 NEBRASKA | TBD | NRIS | Rebuild line 652573 STEGALL 4 230 652873 STEGALL-LNX3 230 Z | Current Study | 0 | (355.00, 355.00) | 190000 | 100 | 190000 | 0.13822
GEN-2024-374 | 02 NEBRASKA | TBD | NRIS | Rebuild line 653312 MORRILL 7 115 659814 SNAKECK-TS7 115 1 | Current Study | 8.93 | (176.00, 176.00) | 8930000 | 100 | 8930000 | 0.05119
GEN-2024-374 | 02 NEBRASKA | TBD | NRIS | Rebuild line 653570 ALIANCE 7 115 659814 SNAKECK-TS7 115 1 | Current Study | 14.87 | (176.00, 176.00) | 14870000 | 100 | 14870000 | 0.020238
GEN-2024-374 | 02 NEBRASKA | TBD | NRIS | Rebuild line 653570 ALIANCE 7 115 659815 BOXBUTE-TS7 115 1 | Current Study | 13.7 | (115.00, 115.00) | 13700000 | 100 | 13700000 | 0.020238
GEN-2024-374 | 02 NEBRASKA | TBD | NRIS | Rebuild line 659339 BOWMAN__-BE4 230 661047 HETINGR4 230 1 | Current Study | 36.35 | (519.00, 519.00) | 69065000 | 100 | 69065000 | 0.051104
GEN-2024-374 | 02 NEBRASKA | 171895 | ERIS | Stegall 345 kV Substation GEN-2024-374 Interconnection (Non-Shared NU) (BEPC) | Interconnection |  |  | 7125379 | 100 | 7125379 | 1
GEN-2024-374 | 02 NEBRASKA | 171894 | ERIS | Stegall 345 kV Substation GEN-2024-374 Interconnection (TOIF) (BEPC) | Interconnection |  |  | 2834775 | 100 | 2834775 | 1
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at NEOSHON2 69 kV | Current Study |  |  | 75940.3393 | 5.5029 | 1380000 | 0.085831
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Add 0.02 MVAR switched shunt at PHILL 7 345 kV | Current Study |  |  | 492922.4978 | 9.3004 | 5300000 | 0.042611
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV | Current Study |  |  | 75940.3393 | 5.5029 | 1380000 | 0.085831
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Add 0.2 MVAR switched shunt at GROVE 5 161 kV | Current Study |  |  | 87747.4028 | 2.6999 | 3250000 | 0.061944
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Add 0.25 MVAR switched shunt at LABETTS2 69 kV | Current Study |  |  | 40411.417 | 2.9284 | 1380000 | 0.061944
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Add 11 MVAR switched shunt at DAD368 5 161 kV | Current Study |  |  | 174781.5369 | 5.3779 | 3250000 | 0.085831
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Add 150 MVAR switched shunt at NEOSHO 4 138 kV | Current Study |  |  | 62172.9433 | 2.5559 | 2432500 | 0.085831
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Add 16 MVAR switched shunt at CPK446 5 161 kV | Current Study |  |  | 132669.7135 | 4.0821 | 3250000 | 0.085831
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Add 24 MVAR switched shunt at GROVE 4 138 kV | Current Study |  |  | 84039.1488 | 3.4548 | 2432500 | 0.085831
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV | Current Study |  |  | 410820.2862 | 29.7696 | 1380000 | 0.53251
GEN-2024-376 | 04 SOUTHEAST | TBD | ERIS | Add 40 MVAR switched shunt at INDEPCO5 161 kV | Current Study |  |  | 174781.5369 | 5.3779 | 3250000 | 0.085831
GEN-2024-376 | 04 SOUTHEAST | 171897 | ERIS | Hemphill 138 kV Substation GEN-2024-376 Interconnection (Non-Shared NU) (ETEC) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-376 | 04 SOUTHEAST | 171896 | ERIS | Hemphill 138 kV Substation GEN-2024-376 Interconnection (TOIF) (ETEC) | Interconnection |  |  | 0 | 100 | 0 | 1
GEN-2024-376 | 04 SOUTHEAST | TBD | NRIS | Rebuild line 509690 4PINELND 138 509691 4BROADUS 138 1 | Current Study | 17 | (211.00, 211.00) | 20400000 | 100 | 20400000 | 0.093708
GEN-2024-376 | 04 SOUTHEAST | TBD | NRIS | Rebuild line 509691 4BROADUS 138 509692 4ETOIL 138 1 | Current Study | 8.51 | (211.00, 211.00) | 10212000 | 100 | 10212000 | 0.093708
GEN-2024-377 | 04 SOUTHEAST | 900426 | ERIS | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030 | Contingent |  |  | 0 | 0 | 2372127948.71 | N/A
GEN-2024-377 | 04 SOUTHEAST | TBD | ERIS | Add 2 MVAR switched shunt at GEN-2017-140 345 kV | Current Study |  |  | 363361.8125 | 6.8559 | 5300000 | 0.058098
GEN-2024-377 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 508562 PIRKEY 4 138 508563 PIRKEY 7 345 508587 PIRKY1-1 13 M2 | Current Study |  | (600.00, 600.00) | 15449584.6942 | 85.3568 | 18100000 | 0.10657
GEN-2024-377 | 04 SOUTHEAST | 171899 | ERIS | Pirkey 345 kV Substation GEN-2024-377 Interconnection (Non-Shared NU) (AEP) | Interconnection |  |  | 12750000 | 100 | 12750000 | 1
GEN-2024-377 | 04 SOUTHEAST | 171898 | ERIS | Pirkey 345 kV Substation GEN-2024-377 Interconnection (TOIF) (AEP) | Interconnection |  |  | 5225000 | 100 | 5225000 | 1
GEN-2024-377 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 507727 FLOURNY4 138 507732 GENMOTR4 138 1 | Current Study | 1.56 | (395.00, 395.00) | 601197.7807 | 32.1153 | 1872000 | 0.013707
GEN-2024-377 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 507727 FLOURNY4 138 508816 OAKPH 4 138 1 | Current Study | 10.42 | (472.00, 472.00) | 2899096.1942 | 23.1854 | 12504000 | 0.0095091
GEN-2024-377 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 507732 GENMOTR4 138 507759 SW SHV 4 138 1 | Current Study | 4.34 | (395.00, 395.00) | 1672563.0564 | 32.1153 | 5208000 | 0.013707
GEN-2024-377 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 507760 SW SHV 7 345 508809 LONGWD 7 345 1 | Current Study | 19.02 | (1793.00, 1793.00) | 6565143.004 | 15.6896 | 41844000 | 0.074093
GEN-2024-377 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508072 NWTXARK7 345 508359 WELSH 7 345 1 | Current Study | 56.1 | (1793.00, 1793.00) | 71887551.9613 | 58.2463 | 123420000 | 0.095736
GEN-2024-377 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508548 KNOXLEE4 138 509059 CHEROKE4 138 1 | Current Study | 3.35 | (472.00, 472.00) | 3429338.8944 | 85.3069 | 4020000 | 0.075895
GEN-2024-377 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508548 KNOXLEE4 138 509092 EASTON 4 138 1 | Current Study | 0.69 | (717.00, 717.00) | 707439.4443 | 85.4395 | 828000 | 0.085908
GEN-2024-377 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508557 MARSHL-4 138 508562 PIRKEY 4 138 1 | Current Study | 8.85 | (525.00, 525.00) | 9060221.1699 | 85.3128 | 10620000 | 0.093505
GEN-2024-377 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508562 PIRKEY 4 138 508566 SABMINT4 138 1 | Current Study | 0.88 | (472.00, 472.00) | 900847.9819 | 85.3076 | 1056000 | 0.091924
GEN-2024-377 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508562 PIRKEY 4 138 508596 BRANDYBR4 138 1 | Current Study | 3.14 | (717.00, 717.00) | 3219362.1089 | 85.4395 | 3768000 | 0.085908
GEN-2024-377 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508563 PIRKEY 7 345 508832 DIANA 7 345 1 | Current Study | 24.75 | (1793.00, 1793.00) | 46447960.5653 | 85.3039 | 54450000 | 0.54102
GEN-2024-377 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508566 SABMINT4 138 508569 SEMRSHL4 138 1 | Current Study | 10.52 | (395.00, 395.00) | 10769228.1478 | 85.3076 | 12624000 | 0.091924
GEN-2024-377 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508567 SCOTTSV4 138 508569 SEMRSHL4 138 1 | Current Study | 6.08 | (395.00, 395.00) | 6224040.6025 | 85.3076 | 7296000 | 0.091924
GEN-2024-377 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508596 BRANDYBR4 138 509092 EASTON 4 138 1 | Current Study | 9.88 | (717.00, 717.00) | 10129712.6229 | 85.4395 | 11856000 | 0.085908
GEN-2024-377 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508808 LONGWD 4 138 508816 OAKPH 4 138 1 | Current Study | 1.8 | (472.00, 472.00) | 500803.5652 | 23.1854 | 2160000 | 0.0095091
GEN-2024-377 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 509059 CHEROKE4 138 509087 TATUM 4 138 1 | Current Study | 5.09 | (472.00, 472.00) | 5210547.753 | 85.3069 | 6108000 | 0.075895
GEN-2024-377 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 509083 ROKHILL4 138 509087 TATUM 4 138 1 | Current Study | 6.5 | (472.00, 472.00) | 6653941.1384 | 85.3069 | 7800000 | 0.075895
GEN-2024-377 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 509083 ROKHILL4 138 509102 NEWPROS4 138 1 | Current Study | 4.82 | (395.00, 395.00) | 4938133.1334 | 85.3757 | 5784000 | 0.043985
GEN-2024-377 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514934 DRAPER 7 345 515045 SEMINOL7 345 2 | Current Study | 44.14 | (1793.00, 1793.00) | 22663194.6423 | 23.3381 | 97108000 | 0.07088
GEN-2024-377 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1 | Current Study | 6.93 | (1793.00, 1793.00) | 8631411.1869 | 56.6143 | 15246000 | 0.17476
GEN-2024-379 | 04 SOUTHEAST | 900426 | ERIS | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030 | Contingent |  |  | 0 | 0 | 2372127948.71 | N/A
GEN-2024-379 | 04 SOUTHEAST | TBD | ERIS | Add 2 MVAR switched shunt at GEN-2017-140 345 kV | Current Study |  |  | 552089.4868 | 10.4168 | 5300000 | 0.088274
GEN-2024-379 | 04 SOUTHEAST | TBD | ERIS | Add 3-winding transformer 508808 LONGWD 4 138 508809 LONGWD 7 345 508819 LONGW1-1 13 M2 | Current Study |  | (580.00, 580.00) | 18100000 | 100 | 18100000 | 0.060313
GEN-2024-379 | 04 SOUTHEAST | 171901 | ERIS | Longwood - El Dorado 345 kV Line GEN-2024-379 Interconnection (Non-Shared NU) (AEP) | Interconnection |  |  | 28225000 | 100 | 28225000 | 1
GEN-2024-379 | 04 SOUTHEAST | 171900 | ERIS | Longwood - El Dorado 345 kV Line GEN-2024-379 Interconnection (TOIF) (AEP) | Interconnection |  |  | 5225000 | 100 | 5225000 | 1
GEN-2024-379 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 337376 7SAREPTA% 345 788340 G24-379-TAP 345 1 | Current Study | 21.32 | (1793.00, 1793.00) | 46904000 | 100 | 46904000 | 0.34378
GEN-2024-379 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 507711 ARSHILL4 138 507742 MCWILLI4 138 1 | Current Study | 3.09 | (395.00, 395.00) | 3708000 | 100 | 3708000 | 0.01301
GEN-2024-379 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 507711 ARSHILL4 138 507749 RAINES 4 138 1 | Current Study | 5.92 | (395.00, 395.00) | 7104000 | 100 | 7104000 | 0.025433
GEN-2024-379 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 507727 FLOURNY4 138 507732 GENMOTR4 138 1 | Current Study | 1.56 | (395.00, 395.00) | 1167379.2515 | 62.36 | 1872000 | 0.026616
GEN-2024-379 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 507727 FLOURNY4 138 508816 OAKPH 4 138 1 | Current Study | 10.42 | (472.00, 472.00) | 9107021.9894 | 72.8329 | 12504000 | 0.029871
GEN-2024-379 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 507732 GENMOTR4 138 507759 SW SHV 4 138 1 | Current Study | 4.34 | (395.00, 395.00) | 3247708.9433 | 62.36 | 5208000 | 0.026616
GEN-2024-379 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 507760 SW SHV 7 345 508809 LONGWD 7 345 1 | Current Study | 19.02 | (1793.00, 1793.00) | 33321557.728 | 79.6328 | 41844000 | 0.37606
GEN-2024-379 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 507774 NORAM 4 138 508808 LONGWD 4 138 1 | Current Study | 4.8 | (395.00, 395.00) | 5760000 | 100 | 5760000 | 0.025433
GEN-2024-379 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508072 NWTXARK7 345 508359 WELSH 7 345 1 | Current Study | 56.1 | (1793.00, 1793.00) | 39111517.6108 | 31.6898 | 123420000 | 0.052086
GEN-2024-379 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508808 LONGWD 4 138 508816 OAKPH 4 138 1 | Current Study | 1.8 | (472.00, 472.00) | 1573189.979 | 72.8329 | 2160000 | 0.029871
GEN-2024-379 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 508809 LONGWD 7 345 788340 G24-379-TAP 345 1 | Current Study | 19.1 | (1793.00, 1793.00) | 42020000 | 100 | 42020000 | 0.65622
GEN-2024-379 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 514934 DRAPER 7 345 515045 SEMINOL7 345 2 | Current Study | 44.14 | (1793.00, 1793.00) | 22319148.7888 | 22.9838 | 97108000 | 0.069804
GEN-2024-379 | 04 SOUTHEAST | TBD | ERIS | Rebuild line 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1 | Current Study | 6.93 | (1793.00, 1793.00) | 5122243.1274 | 33.5973 | 15246000 | 0.10371
GEN-2024-379 | 04 SOUTHEAST | TBD | ERIS | Rebuild the 3MINDEN_LA! to 3SAREPTA! 115kV Line 1 | JTIQ Expanded Scope Analysis | 21.84 | (228, 228) | 16849560 | 100 | 16849560 | 0.03126

## Upgrade Summary
Upgrade Type | Study Type | Group | Assigned Study Number | Service Type | Upgrade Name | Upgrade ID | Upgrade length (miles) | Upgrade Rating (MVA) | Transmission Owner(s) | Estimated Lead Time | Total Upgrade Cost
Contingent | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026 | 92168 |  |  |  |  | 358995074
Contingent | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | 21ITP_Multi - Tande - Finstad - Leland Olds 345 kV.idv : 2021 ITP, PID: 92168, NTC, ISD: 11/30/2026 | 92168 |  |  |  |  | 346873086
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | NRIS | Rebuild line 640404 WAYSIDE 4 230 652873 STEGALL-LNX3 230 1 | TBD | 92.96 | (386.00, 386.00) | WAPA |  | 176624000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | NRIS | Rebuild line 640404 WAYSIDE 4 230 652484 NUNDRWD4 230 1 | TBD | 80.12 | (519.00, 519.00) | WAPA |  | 152228000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | NRIS | Rebuild line 652497 MAURINE4 230 652884 NUNDRWD-LNX3 230 1 | TBD | 72.13 | (519.00, 519.00) | WAPA |  | 137047000
Contingent | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032 | 94673 |  |  |  |  | 79492390
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Rebuild line 659427 TN.LS-JD-BE3 345 779400 G24-081-TAP 345 1 | TBD | 33.88 | (1793.00, 1793.00) | WAPA |  | 74536000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | NRIS | Rebuild line 652497 MAURINE4 230 659351 BISON___-GE4 230 1 | TBD | 38.56 | (519.00, 519.00) | WAPA |  | 73264000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | NRIS | Rebuild line 659339 BOWMAN__-BE4 230 661047 HETINGR4 230 1 | TBD | 36.35 | (519.00, 519.00) | WAPA |  | 69065000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | NRIS | Rebuild line 652552 SIOUXCY2 230 659900 EAGLE___-NI4 230 1 | TBD | 33.29 | (519.00, 519.00) | WAPA |  | 63251000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | NRIS | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | TBD | 23.48 | (1793.00, 1793.00) | MEC/WAPA |  | 51656000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Rebuild line 652522 SUMMIT-7 115 655457 BRISTOL-ER7 115 1 | TBD | 32.97 | (176.00, 176.00) | WAPA |  | 32970000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | NRIS | Rebuild line 652425 BELFELD4 230 659124 DICKINSN-BE4 230 1 | TBD | 15.17 | (386.00, 386.00) | WAPA |  | 28823000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | NRIS | Rebuild line 652512 GROTON 7 115 660001 ABR SIEBRCHT 115 1 | TBD | 25.8 | (260.00, 260.00) | WAPA |  | 25800000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | NRIS | Add 3-winding transformer 652305 SIOUXC29 13 652552 SIOUXCY2 230 652564 SIOUXCY3 345 M2 | TBD |  | (600.00, 750.00) | WAPA |  | 25000000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Add 3-winding transformer 659336 TANDE___-BE3 345 659337 TANDE___-BE4 230 659338 TND.KU3A-BE9 13 M2 | TBD |  | (600.00, 637.00) | WAPA |  | 25000000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Rebuild line 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1 | TBD | 21.31 | (176.00, 176.00) | WAPA |  | 21310000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TBD | 9 | (1793.00, 1793.00) | WAPA |  | 19800000
Contingent | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024 | 92211 |  |  |  |  | 9200000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | NRIS | Add 154 MVAR SVC at WAYSIDE 4 230 kV | TBD |  |  | WAPA |  | 8600000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Add 0.02 MVAR switched shunt at GEN-2017-214 230 kV | TBD |  |  | WAPA |  | 3825000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | NRIS | Add 108 MVAR switched shunt at MAURINE4 230 kV | TBD |  |  | WAPA |  | 3825000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | NRIS | Add 23 MVAR switched shunt at STEGALL-LNX3 230 kV | TBD |  |  | WAPA |  | 3825000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | NRIS | Add 60 MVAR switched shunt at NUNDRWD-LNX3 230 kV | TBD |  |  | WAPA |  | 3825000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | NRIS | Add 78 MVAR switched shunt at DH_CS_EA-TS4 230 kV | TBD |  |  | WAPA |  | 3825000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | NRIS | Add 0.22 MVAR switched shunt at MOCCASIN-MK7 115 kV | TBD |  |  | WAPA |  | 2212500
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | NRIS | Add 12 MVAR switched shunt at L11_____-MK7 115 kV | TBD |  |  | WAPA |  | 2212500
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | NRIS | Add 3 MVAR switched shunt at SNDCRKTP-MK7 115 kV | TBD |  |  | WAPA |  | 2212500
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Rebuild line 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1 | TBD | 1.04 | (772.00, 772.00) | WAPA |  | 1976000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Add 0.02 MVAR switched shunt at RUSHMORE-RM8 69 kV | TBD |  |  | WAPA |  | 1380000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | NRIS | Add 2.8 MVAR switched shunt at WEBSTER CITY 69 kV | TBD |  |  | WAPA |  | 1380000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | NRIS | Rebuild line 652484 NUNDRWD4 230 652884 NUNDRWD-LNX3 230 Z | TBD | 0.14514 | (519.00, 519.00) | WAPA |  | 275765.6361
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Rebuild line 659336 TANDE___-BE3 345 659427 TN.LS-JD-BE3 345 Z | TBD |  | (1501.00, 1501.00) | WAPA |  | 220000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | NRIS | Rebuild line 652573 STEGALL 4 230 652873 STEGALL-LNX3 230 Z | TBD |  | (355.00, 355.00) | WAPA |  | 190000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Rebuild line 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z | TBD | 1 | (580.00, 580.00) | WAPA |  | 190000
Current Study | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Rebuild line 652391 WILLISTON27 115 652421 WILISTN7 115 Z1 | TBD | 0.035484 | (260.00, 260.00) | WAPA |  | 35483.8712
Interconnection | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | BASIN__-BE4 230 kV Substation GEN-2024-141 Interconnection (Non-Shared NU) (BEPC) | 171611 |  |  | BEPC | 60 | 7362181
Interconnection | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | BASIN__-BE4 230 kV Substation GEN-2024-141 Interconnection (TOIF) (BEPC) | 171610 |  |  | BEPC | 60 | 2270573
Interconnection | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Berthold 115 kV Substation GEN-2024-327 Interconnection (Non-Shared NU) (CPEC) | 171831 |  |  | CPEC | 24 | 1395000
Interconnection | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Berthold 115 kV Substation GEN-2024-327 Interconnection (TOIF) (CPEC) | 171830 |  |  | CPEC | 24 | 214000
Interconnection | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Groton 345 kV Substation GEN-2024-035 Interconnection (Non-Shared NU) (BEPC) | 171505 |  |  | BEPC | 60 | 7125379
Interconnection | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Groton 345 kV Substation GEN-2024-035 Interconnection (TOIF) (BEPC) | 171504 |  |  | BEPC | 60 | 2834775
Interconnection | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Pleasant Valley 115 kV Substation GEN-2024-329 Interconnection (Non-Shared NU) (MWEC) | 171835 |  |  | MWE | 0 | 0
Interconnection | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Pleasant Valley 115 kV Substation GEN-2024-329 Interconnection (TOIF) (MWEC) | 171834 |  |  | MWE | 0 | 1200000
Interconnection | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Springbrook - Tande 345 kV Line GEN-2024-081 Interconnection (TOIF) (BEPC) | 171554 |  |  | BEPC | 60 | 3093490
Interconnection | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Springbrook - Tande 345 kV Line GEN-2024-081/082 Interconnection (Shared NU) (BEPC) | 171555 |  |  | BEPC | 60 | 3093486
Interconnection | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Springbrook - Tande 345 kV Line GEN-2024-082 Interconnection (TOIF) (BEPC) | 171556 |  |  | BEPC | 60 | 38027515
Contingent | Steady State | 01 NORTH/ 02 NEBRASKA | DISIS-2024-001 | ERIS | 640_NPPD_NewBranch_Holt-Antilope3_345.idv : 2024 ITP, PID: 94842, NTC, ISD: 12/31/2029 | 94842 |  |  |  |  | 78445357
Current Study | Steady State | 01 NORTH/ 02 NEBRASKA | DISIS-2024-001 | ERIS | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | TBD | 23.61 | (519.00, 519.00) | NPPD/WAPA |  | 44859000
Contingent | Steady State | 01 NORTH/ 03 CENTRAL | DISIS-2024-001 | ERIS | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030 | 94811 |  |  |  |  | 1097029189
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Rebuild line 640139 COOPER 3 345 640590 OLIVECREEK 3 345 1 | TBD | 62.88 | (1793.00, 1793.00) | NPPD |  | 138336000
Contingent | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030 | 94788 |  |  |  |  | 106000000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | TBD | 45.48 | (1793.00, 1793.00) | NPPD |  | 100056000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | NRIS | Rebuild line 645456 S3456 3 345 645458 S3458 3 345 1 | TBD | 44.95 | (1793.00, 1793.00) | OPPD |  | 98890000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | NRIS | Rebuild line 645454 S3454 3 345 650185 WAGENER 3 345 1 | TBD | 33.67 | (1793.00, 1793.00) | LES/OPPD |  | 74074000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Rebuild line 640277 MOORE 3 345 640525 TOBIAS 3 345 1 | TBD | 26.47 | (1793.00, 1793.00) | NPPD |  | 58234000
Contingent | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | DIS2301_P2_G00_ERIS_3_640_NPPD_TO_2000_add_BPS_345_Lines_Rev34.idv : DISIS_2023 Identified Upgrade | TBD |  |  |  |  | 53000000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Rebuild line 635201 RAUN 5 161 646300 S1300 5 161 1 | TBD | 34.12 | (309.00, 309.00) | MEC/OPPD |  | 51180000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Rebuild line 645454 S3454 3 345 645740 S3740 3 345 1 | TBD | 23.26 | (2390.00, 2390.00) | OPPD |  | 51172000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1 | TBD | 20.15 | (2390.00, 2390.00) | OPPD |  | 44330000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Rebuild line 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 | TBD | 19.87 | (1793.00, 1793.00) | LES/NPPD |  | 43714000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Rebuild line 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 | TBD | 16.71 | (1793.00, 1793.00) | LES/NPPD |  | 36762000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Rebuild line 640076 BEATRCE7 115 640361 STEINER7 115 1 | TBD | 30.1 | (217.00, 217.00) | NPPD |  | 30100000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Add line 640088 BPS SUB7 115 640278 SHELDON7 115 M2 | TBD | 16.85 | (598.00, 598.00) | NPPD |  | 27790000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | NRIS | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | TBD | 17.69 | (246.00, 246.00) | LES/OPPD |  | 26535000
Contingent | Steady State | 02 NEBRASKA | DISIS-2024-001 | NRIS | 640_NPPD_Rebuild_Morill_Gering_115.idv : 2024 ITP, PID: TBD, ISD: Unknown | TBD |  |  |  |  | 24272842
Contingent | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | DIS2301_P2_G00_ERIS_2_640_NPPD_TO_1000_DAYKIN_345KV_SUB.idv : DISIS_2023 Identified Upgrade | TBD |  |  |  |  | 23000000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | NRIS | Rebuild line 640149 CREITON7 115 640521 ANTELOPE 7 115 1 | TBD | 22.74 | (176.00, 176.00) | NPPD |  | 22740000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Rebuild line 640169 FAIRBRY7 115 640218 HEBRN N7 115 1 | TBD | 22.1 | (176.00, 176.00) | NPPD |  | 22100000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | NRIS | Rebuild line 650185 WAGENER 3 345 650189 103&ROKEBY3 345 1 | TBD | 9.45 | (1793.00, 1793.00) | LES |  | 20790000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Rebuild line 646226 S1226 5 161 646247 S1247 5 161 1 | TBD | 13.54 | (246.00, 246.00) | OPPD |  | 20310000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2 | TBD | 0.75 | (2390.00, 2390.00) | NPPD |  | 17775000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Rebuild line 640235 HUMBOLT7 115 640361 STEINER7 115 1 | TBD | 17.7 | (217.00, 217.00) | NPPD |  | 17700000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2 | TBD |  | (417.00, 417.00) | NPPD |  | 16800000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | NRIS | Add 3-winding transformer 640125 COLMB.E3 345 640127 COLMB.E7 115 640129 COLMB.T9 13 M2 | TBD |  | (336.00, 336.00) | NPPD |  | 16800000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Add 3-winding transformer 640277 MOORE 3 345 640278 SHELDON7 115 640280 MOORE 9 13 M2 | TBD |  | (336.00, 400.00) | NPPD |  | 16800000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2 | TBD |  | (417.00, 417.00) | NPPD |  | 16800000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2 | TBD |  | (417.00, 417.00) | NPPD |  | 16800000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Rebuild line 640278 SHELDON7 115 650242 FOLSM&PHIL7 115 1 | TBD | 15.49 | (329.00, 329.00) | LES/NPPD |  | 15490000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | NRIS | Rebuild line 653570 ALIANCE 7 115 659814 SNAKECK-TS7 115 1 | TBD | 14.87 | (176.00, 176.00) | NPPD |  | 14870000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Rebuild line 645454 S3454 3 345 645455 S3455 3 345 1 | TBD | 6.67 | (1793.00, 1793.00) | OPPD |  | 14674000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | NRIS | Add 3-winding transformer 640227 HOSKINS4 230 640228 HOSKINS7 115 643083 HOSKINS T1 9 13 M2 | TBD |  | (187.00, 187.00) | NPPD |  | 13800000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | NRIS | Rebuild line 653570 ALIANCE 7 115 659815 BOXBUTE-TS7 115 1 | TBD | 13.7 | (115.00, 115.00) | NPPD |  | 13700000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Rebuild line 640111 CLATONA7 115 640278 SHELDON7 115 1 | TBD | 12.41 | (598.00, 598.00) | NPPD |  | 12410000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | NRIS | Rebuild line 640080 BELDEN 7 115 640212 HARTGTN7 115 1 | TBD | 12.27 | (176.00, 176.00) | NPPD |  | 12270000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Add 3-winding transformer 640234 HUMBOLT5 161 640235 HUMBOLT7 115 643087 HUMBOLDT T29 13 M2 | TBD |  | (126.00, 126.00) | NPPD/OPPD |  | 12000000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | NRIS | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2 | TBD |  | (110.00, 120.00) | LES |  | 12000000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | NRIS | Rebuild line 640178 GENEVA 7 115 640272 MCCOOL 7 115 1 | TBD | 11.26 | (217.00, 217.00) | NPPD |  | 11260000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Rebuild line 640316 PAWNEEL7 115 640340 SEWARD 7 115 1 | TBD | 11.21 | (217.00, 217.00) | NPPD |  | 11210000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Rebuild line 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1 | TBD | 10.55 | (598.00, 598.00) | LES/NPPD |  | 10550000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Rebuild line 640169 FAIRBRY7 115 640208 HARBINE7 115 1 | TBD | 9.82 | (217.00, 217.00) | NPPD |  | 9820000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | NRIS | Rebuild line 640272 MCCOOL 7 115 640413 YORK SW7 115 1 | TBD | 9.46 | (176.00, 176.00) | NPPD |  | 9460000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Rebuild line 640088 BPS SUB7 115 640111 CLATONA7 115 1 | TBD | 8.96 | (598.00, 598.00) | NPPD |  | 8960000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | NRIS | Rebuild line 653312 MORRILL 7 115 659814 SNAKECK-TS7 115 1 | TBD | 8.93 | (176.00, 176.00) | NPPD |  | 8930000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Fremont_Add_transformer_fixed.idv : | TBD |  |  |  |  | 8125000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | NRIS | Rebuild line 646221 S1221 5 161 646255 S1255 5 161 1 | TBD | 4.09 | (446.00, 446.00) | OPPD |  | 6135000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Rebuild line 640316 PAWNEEL7 115 650214 NW68HOLDRG7 115 1 | TBD | 5.46 | (217.00, 217.00) | LES/NPPD |  | 5460000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Add 48 MVAR switched shunt at MACON 3 345 kV | TBD |  |  | NPPD |  | 5300000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Rebuild line 640377 TEKAMAH5 161 646300 S1300 5 161 1 | TBD | 2.97 | (309.00, 309.00) | OPPD |  | 4455000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Rebuild line 646259 S1259 5 161 646278 S1278 5 161 1 | TBD | 2.61 | (246.00, 246.00) | OPPD |  | 3915000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | NRIS | Add 0.04 MVAR switched shunt at VICTRYH4 230 kV | TBD |  |  | NPPD |  | 3825000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | NRIS | Add 14 MVAR switched shunt at HASTING4 230 kV | TBD |  |  | NPPD |  | 3825000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | NRIS | Add 45 MVAR switched shunt at PR BRZ 4 230 kV | TBD |  |  | OPPD |  | 3825000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Add 16 MVAR switched shunt at HUMBOLT5 161 kV | TBD |  |  | OPPD |  | 3250000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Add 21 MVAR switched shunt at S1263 5 161 kV | TBD |  |  | OPPD |  | 3250000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Rebuild line 646221 S1221 5 161 646231 S1231 5 161 1 | TBD | 2.06 | (364.00, 364.00) | OPPD |  | 3090000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Rebuild line 640278 SHELDON7 115 640591 OLIVECREEK 7 115 1 | TBD | 1 | (598.00, 598.00) | NPPD |  | 1000000
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Rebuild line 640278 SHELDON7 115 640591 OLIVECREEK 7 115 2 | TBD | 1 | (598.00, 598.00) | NPPD |  | 1000000
Contingent | Steady State | 02 NEBRASKA | DISIS-2024-001 | NRIS | 640_NPPD_Rebuild_Scotsbluff_Gering_115.idv : 2024 ITP, PID: 94819, NTC, ISD: Unknown | 94819 |  |  |  |  | 385333
Current Study | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Rebuild line 647424 FREM D 8 69 647976 S976 8 69 1 | TBD | 0.06 | (140.00, 140.00) | OPPD |  | 51000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Antelope - Hoskins 345 kV line GEN-2024-140 Interconnection (Non-Shared NU) (NPPD) | 171609 |  |  | NPPD | 60 | 4000000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Antelope - Hoskins 345 kV line GEN-2024-140 Interconnection (TOIF) (NPPD) | 171608 |  |  | NPPD | 60 | 1000000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | FREMONT7 115 kV Substation GEN-2024-065 Interconnection (Non-Shared NU) (NPPD) | 171536 |  |  | NPPD | 48 | 9500000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | FREMONT7 115 kV Substation GEN-2024-065 Interconnection (TOIF) (NPPD) | 171535 |  |  | NPPD | 48 | 500000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Geneva 115 kV Substation GEN-2024-168 Interconnection (Non-Shared NU) (NPPD) | 171636 |  |  | NPPD | 48 | 13500000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Geneva 115 kV Substation GEN-2024-168 Interconnection (TOIF) (NPPD) | 171635 |  |  | NPPD | 48 | 500000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | New Beatrice Power Station 345 kV GEN-2024-018 Interconnection (TOIF) (NPPD) | 171485 |  |  | NPPD | 60 | 0
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | New Beatrice Power Station 345 kV GEN-2024-018/019/022/023 Interconnection (Shared NU) (NPPD) | 171492 |  |  | NPPD | 60 | 7000000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | New Beatrice Power Station 345 kV GEN-2024-022 Interconnection (TOIF) (NPPD) | 171491 |  |  | NPPD | 60 | 1000000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | New Beatrice Power Station 345 kV GEN-2024-023 Interconnection (TOIF) (NPPD) | 171493 |  |  | NPPD | 60 | 1000000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | New Beatrice Power Station 345 kV Substation GEN-2024-019 Interconnection (TOIF) (NPPD) | 171486 |  |  | NPPD | 60 | 0
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Olive Creek 345 kV Substation GEN-2024-017 Interconnection (Non-Shared NU) (NPPD) | 171484 |  |  | NPPD | 60 | 0
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Olive Creek 345 kV Substation GEN-2024-017 Interconnection (TOIF) (NPPD) | 171483 |  |  | NPPD | 60 | 0
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Olive Creek 345 kV Substation GEN-2024-020 Interconnection (Non-Shared NU) (NPPD) | 171488 |  |  | NPPD | 60 | 5000000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Olive Creek 345 kV Substation GEN-2024-020 Interconnection (TOIF) (NPPD) | 171487 |  |  | NPPD | 60 | 1000000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Olive Creek 345 kV Substation GEN-2024-021 Interconnection (Non-Shared NU) (NPPD) | 171490 |  |  | NPPD | 60 | 5000000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Olive Creek 345 kV Substation GEN-2024-021 Interconnection (TOIF) (NPPD) | 171489 |  |  | NPPD | 60 | 1000000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Pawnee Lake 115 kV Substation GEN-2024-173 Interconnection (Non-Shared NU) (NPPD) | 171640 |  |  | NPPD | 48 | 7500000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Pawnee Lake 115 kV Substation GEN-2024-173 Interconnection (TOIF) (NPPD) | 171639 |  |  | NPPD | 48 | 500000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Raun - Tekamah 161 kV line GEN-2024-234 Interconnection (Non-Shared NU) (OPPD) | 171705 |  |  | OPPD | 18 | 350000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Raun - Tekamah 161 kV line GEN-2024-234 Interconnection (TOIF) (OPPD) | 171704 |  |  | OPPD | 0 | 0
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | S1252 161 kV Substation GEN-2024-372 Interconnection (Non-Shared NU) (OPPD) | 171891 |  |  | OPPD | 40 | 1500000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | S1252 161 kV Substation GEN-2024-372 Interconnection (TOIF) (OPPD) | 171890 |  |  | OPPD | 30 | 476039
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Stegall 345 kV Substation GEN-2024-374 Interconnection (Non-Shared NU) (BEPC) | 171895 |  |  | BEPC | 60 | 7125379
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Stegall 345 kV Substation GEN-2024-374 Interconnection (TOIF) (BEPC) | 171894 |  |  | BEPC | 60 | 2834775
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Substation 3740 345 kV GEN-2024-211 Interconnection (Non-Shared NU) (OPPD) | 171675 |  |  | OPPD | 40 | 2000000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Substation 3740 345 kV GEN-2024-211 Interconnection (TOIF) (OPPD) | 171674 |  |  | OPPD | 36 | 1900000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Substation 3740 345 kV GEN-2024-212 Interconnection (Non-Shared NU) (OPPD) | 171677 |  |  | OPPD | 40 | 2000000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Substation 3740 345 kV GEN-2024-212 Interconnection (TOIF) (OPPD) | 171676 |  |  | OPPD | 36 | 1900000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Substation 3740 345 kV GEN-2024-213 Interconnection (Non-Shared NU) (OPPD) | 171679 |  |  | OPPD | 40 | 2000000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Substation 3740 345 kV GEN-2024-213 Interconnection (TOIF) (OPPD) | 171678 |  |  | OPPD | 36 | 1900000
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Twin Church 230 kV Substation GEN-2024-162 Interconnection (Non-Shared NU) (NPPD) | 171630 |  |  | NPPD | 48 | 0
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Twin Church 230 kV Substation GEN-2024-162 Interconnection (TOIF) (NPPD) | 171629 |  |  | NPPD | 48 | 0
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Waverly 115 kV Substation GEN-2024-051 Interconnection (Non-Shared NU) (LES) | 171525 |  |  | LES | 0 | 0
Interconnection | Steady State | 02 NEBRASKA | DISIS-2024-001 | ERIS | Waverly 115 kV Substation GEN-2024-051 Interconnection (TOIF) (LES) | 171524 |  |  | LES | 9 | 7533500
Contingent | Steady State | 02 NEBRASKA/ 03 CENTRAL | DISIS-2024-001 | ERIS | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030 | 94911 |  |  |  |  | 143524375
Contingent | Steady State | 02 NEBRASKA/ 04 SOUTHEAST | DISIS-2024-001 | NRIS | Line - Duncan - Duncan Tap - Duncan Eastside - Rush Springs Tap - Marlow 138 kV Rebuild.idv : 2025 ITP, PID: 900298, NTC, ISD: Unknown | 900298 |  |  |  |  | 212560000
Current Study | Steady State | 02 NEBRASKA/ 04 SOUTHEAST | DISIS-2024-001 | NRIS | Rebuild line 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | TBD | 17.69 | (265.00, 265.00) | AEPW/OMPA |  | 21228000
Current Study | Steady State | 02 NEBRASKA/ 04 SOUTHEAST | DISIS-2024-001 | NRIS | Rebuild line 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | TBD | 3.9 | (265.00, 265.00) | AEPW/OMPA |  | 4680000
Contingent | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025 | 94721 |  |  |  |  | 213682884
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | NRIS | Rebuild line 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | TBD | 31.46 | (1793.00, 1793.00) | AECI/WERE |  | 69212000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 | TBD | 30.44 | (1793.00, 1793.00) | WERE |  | 66968000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | TBD | 28.98 | (1793.00, 1793.00) | KCPL |  | 63756000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TBD | 25.29 | (2390.00, 2390.00) | WERE |  | 55638000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | TBD | 25.07 | (1793.00, 1793.00) | WERE |  | 55154000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 541400 EASTOWN7 345 542982 IATAN 7 345 1 | TBD | 23.71 | (1793.00, 1793.00) | KCPL |  | 52162000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 532995 OTTRCRK4 138 533001 ALTOONA4 138 1 | TBD | 35 | (134.00, 134.00) | WERE |  | 42000000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | NRIS | Rebuild line 532911 MUSTNG5 161 532937 NEOSHO 5 161 1 | TBD | 27.08 | (246.00, 246.00) | WERE |  | 40620000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | NRIS | Rebuild line 532777 NRSS7 345 532793 NEOSHO 7 345 1 | TBD | 18.17 | (1793.00, 1793.00) | WERE |  | 39974000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | TBD | 15.48 | (1793.00, 1793.00) | WERE |  | 34056000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | TBD | 15.42 | (1793.00, 1793.00) | WERE |  | 33924000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | NRIS | Rebuild line 532780 CANEYRV7 345 780720 G24-125-TAP 345 1 | TBD | 14.44 | (1793.00, 1793.00) | WERE |  | 31768000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | NRIS | Rebuild line 532937 NEOSHO 5 161 764310 G20-079-TAP 161 1 | TBD | 20.67 | (551.00, 551.00) | EMDE/WERE |  | 31005000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 541369 MIDWAY_5 161 541394 AVENUECTY 5 161 1 | TBD | 20.54 | (246.00, 246.00) | KCPL |  | 30810000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | NRIS | Rebuild line 532777 NRSS7 345 780840 G24-129-TAP 345 1 | TBD | 13.85 | (1793.00, 1793.00) | WERE |  | 30470000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 541251 MARYVLE5 161 541369 MIDWAY_5 161 1 | TBD | 19.5 | (246.00, 246.00) | KCPL |  | 29250000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | NRIS | Rebuild line 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | TBD | 27.23 | (217.00, 217.00) | SUNC |  | 27230000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 532768 EMPEC 7 345 776400 G23-221-TAP 345 1 | TBD | 12 | (1793.00, 1793.00) | WERE |  | 26400000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 541198 PECULR 7 345 541200 PHILL 7 345 1 | TBD | 11.9 | (1793.00, 1793.00) | KCPL |  | 26180000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 541251 MARYVLE5 161 635038 BRADDYVILLE5 161 1 | TBD | 16.92 | (246.00, 246.00) | KCPL/MEC |  | 25380000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | TBD | 11.39 | (1793.00, 1793.00) | WERE |  | 25058000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | NRIS | Rebuild line 539656 CLIFTON3 115 539657 CONCORD3 115 1 | TBD | 23.19 | (176.00, 176.00) | SUNC |  | 23190000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Line - Crosstown - Blue Valley Station 161 kV New Line.idv : 2025 ITP upgrade, PID : 900341, NO NTC | 900341 |  |  |  |  | 21642007.43
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2 | TBD | 6.85 | (837.00, 837.00) | INDN/KCPL |  | 20585000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | NRIS | Add 3-winding transformer 532793 NEOSHO 7 345 532825 N345 2 1 13 532939 N345 4 5 161 M2 | TBD |  | (500.00, 550.00) | WERE |  | 20300000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add line 543004 BLUMILS5 161 548808 ECKLES-161 161 M2 | TBD | 6.5 | (837.00, 837.00) | INDN/KCPL |  | 19850000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 547476 ASB349 5 161 547477 CJ 366 5 161 1 | TBD | 12.3 | (446.00, 446.00) | EMDE |  | 18450000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | NRIS | Rebuild line 531481 HUGOTON3 115 531483 GRANTTP3 115 1 | TBD | 18.19 | (260.00, 260.00) | SUNC |  | 18190000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 3-winding transformer 532793 NEOSHO 7 345 532824 N345 1 1 13 533023 N345 3 4 138 M2 | TBD |  | (400.00, 400.00) | WERE |  | 18100000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 547476 ASB349 5 161 547491 PUR421 5 161 1 | TBD | 11.94 | (446.00, 446.00) | EMDE |  | 17910000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 541199 ST JOE 7 345 541400 EASTOWN7 345 1 | TBD | 8.12 | (1793.00, 1793.00) | KCPL |  | 17864000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 532780 CANEYRV7 345 532800 LATHAMS7 345 1 | TBD | 8.08 | (1793.00, 1793.00) | WERE |  | 17776000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 3-winding transformer 531510 HARBNGR3 115 531511 HARBNGR-1 13 531512 HARBNGR7 345 M2 | TBD |  | (350.00, 385.00) | SUNC |  | 16800000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2 | TBD | 4.34 | (837.00, 837.00) | INDN |  | 15314000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | NRIS | Rebuild line 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | TBD | 14.69 | (176.00, 176.00) | SUNC |  | 14690000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2 | TBD |  | (280.00, 308.00) | WERE |  | 13800000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 3-winding transformer 539657 CONCORD3 115 539658 CONCRD6 230 539904 CONCOD-1 13 M2 | TBD |  | (205.00, 225.50) | SUNC |  | 13800000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | NRIS | Add 3-winding transformer 532937 NEOSHO 5 161 532959 NEOSH5 1 13 533020 NEOSHOS4 138 M2 | TBD |  | (150.00, 165.00) | WERE |  | 12400000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 150 MVAR SVC at G16-111-TAP 345 kV | TBD |  |  | WERE |  | 12000000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 280 MVAR SVC at G15052_1 345 kV | TBD |  |  | WERE |  | 12000000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 45 MVAR SVC at G15052_T 345 kV | TBD |  |  | WERE |  | 12000000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 547485 CAR395 5 161 547491 PUR421 5 161 1 | TBD | 7.89 | (446.00, 446.00) | EMDE |  | 11835000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 541204 SMTHVL 5 161 541221 PLTCTY 5 161 1 | TBD | 7.49 | (364.00, 364.00) | KCPL |  | 11235000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | TBD | 6.07 | (364.00, 364.00) | AECI/INDN |  | 9105000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | TBD | 4.5 | (837.00, 837.00) | INDN/KCPL |  | 6750000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 M2 | TBD | 0.2 | (837.00, 837.00) | INDN |  | 6620000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | TBD |  | (215.00, 215.00) | INDN |  | 6075000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | TBD |  | (221.00, 221.00) | INDN |  | 6075000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild 2-winding transformer 548814 SUB M-161 161 548815 SUB M 69 1 | TBD |  | (169.00, 169.00) | INDN |  | 6075000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 541254 EAST 5 161 541401 EASTOWN5 161 1 | TBD | 4.02 | (446.00, 446.00) | KCPL |  | 6030000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 533417 EMCPHER3 115 533426 MANVILE3 115 1 | TBD | 5.7 | (176.00, 176.00) | WERE |  | 5700000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 533243 JAGGARD3 115 533261 PENTAGN3 115 1 | TBD | 5.55 | (297.00, 297.00) | WERE |  | 5550000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 0.02 MVAR switched shunt at BUFFALO7 345 kV | TBD |  |  | WERE |  | 5300000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV | TBD |  |  | WERE |  | 5300000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 0.02 MVAR switched shunt at PHILL 7 345 kV | TBD |  |  | KCPL |  | 5300000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 0.02 MVAR switched shunt at SUMMIT 7 345 kV | TBD |  |  | WERE |  | 5300000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV | TBD |  |  | KCPL |  | 5300000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 0.13 MVAR switched shunt at PECULR 7 345 kV | TBD |  |  | KCPL |  | 5300000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 160 MVAR switched shunt at WICHITA7 345 kV | TBD |  |  | WERE |  | 5300000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 177 MVAR switched shunt at SWISVAL7 345 kV | TBD |  |  | WERE |  | 5300000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 213 MVAR switched shunt at STILWEL7 345 kV | TBD |  |  | KCPL |  | 5300000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 28 MVAR switched shunt at G21-096-TAP 345 kV | TBD |  |  | WERE |  | 5300000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 295 MVAR switched shunt at G18-128-TAP 345 kV | TBD |  |  | WERE |  | 5300000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 30 MVAR switched shunt at G23-220-TAP 345 kV | TBD |  |  | WERE |  | 5300000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 316 MVAR switched shunt at W.GRDNR7 345 kV | TBD |  |  | KCPL |  | 5300000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 86 MVAR switched shunt at POSTROCK7 345 kV | TBD |  |  | MIDW |  | 5300000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 541253 ST JOE 5 161 541394 AVENUECTY 5 161 1 | TBD | 3.32 | (246.00, 246.00) | KCPL |  | 4980000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 547477 CJ 366 5 161 547490 FIR417 5 161 1 | TBD | 3.26 | (446.00, 446.00) | EMDE |  | 4890000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | NRIS | Rebuild 3-winding transformer 530565 SEWARD 2 69 530631 SWRD1 1 12 530679 SEWRDMW3 115 1 | TBD |  | (54.00, 54.00) | MIDW |  | 4725000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 | TBD | 3.09 | (551.00, 551.00) | INDN/KCPL |  | 4635000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | TBD | 3.02 | (551.00, 551.00) | AECI/KCPL |  | 4530000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 547467 ORO110 5 161 547490 FIR417 5 161 1 | TBD | 2.86 | (446.00, 446.00) | EMDE |  | 4290000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 541214 TWA 5 161 541318 NCONGRS5 161 1 | TBD | 2.85 | (246.00, 246.00) | KCPL |  | 4275000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 0.09 MVAR switched shunt at SWISVAL6 230 kV | TBD |  |  | WERE |  | 3825000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 532987 BUTLER 4 138 532990 MIDIAN 4 138 1 | TBD | 3 | (211.00, 211.00) | WERE |  | 3600000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | TBD | 2.29 | (551.00, 551.00) | KCPL |  | 3435000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 533238 EDWARVL3 115 533282 MUND 3 115 1 | TBD | 3.33 | (260.00, 260.00) | WERE |  | 3330000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 0.04 MVAR switched shunt at AUR124 5 161 kV | TBD |  |  | EMDE |  | 3250000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 0.09 MVAR switched shunt at NOL435 5 161 kV | TBD |  |  | EMDE |  | 3250000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 11 MVAR switched shunt at DAD368 5 161 kV | TBD |  |  | EMDE |  | 3250000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 15 MVAR switched shunt at NEO184 5 161 kV | TBD |  |  | EMDE |  | 3250000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 16 MVAR switched shunt at CPK446 5 161 kV | TBD |  |  | EMDE |  | 3250000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV | TBD |  |  | EMDE |  | 3250000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 21 MVAR switched shunt at MON383 5 161 kV | TBD |  |  | EMDE |  | 3250000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 42 MVAR switched shunt at CNTRVIL5 161 kV | TBD |  |  | KCPL |  | 3250000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 45 MVAR switched shunt at NEVADA 5 161 kV | TBD |  |  | KCPL |  | 3250000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 7 MVAR switched shunt at SWAVRLY5 161 kV | TBD |  |  | KCPL |  | 3250000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 548802 SUB H 69 548806 BLUVLY 69 1 | TBD | 3.8 | (106.00, 106.00) | INDN |  | 3230000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | NRIS | Rebuild line 530679 SEWRDMW3 115 539692 SEWARD 3 115 1 | TBD | 2.91 | (115.00, 115.00) | MIDW/SUNC |  | 2910000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 533583 BUTLERN2 69 533597 MIDIAN 2 69 1 | TBD | 3.04 | (106.00, 106.00) | WERE |  | 2584000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 0.02 MVAR switched shunt at MOUND 4 138 kV | TBD |  |  | WERE |  | 2432500
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV | TBD |  |  | WERE |  | 2432500
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 150 MVAR switched shunt at NEOSHO 4 138 kV | TBD |  |  | WERE |  | 2432500
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 20 MVAR switched shunt at LIBERTY4 138 kV | TBD |  |  | WERE |  | 2432500
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 56 MVAR switched shunt at WHARV4 138 kV | TBD |  |  | WERE |  | 2432500
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 1 MVAR switched shunt at DIGHTON3 115 kV | TBD |  |  | SUNC |  | 2212500
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 12 MVAR switched shunt at GOODCTY3 115 kV | TBD |  |  | SUNC |  | 2212500
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 2 MVAR switched shunt at CLIFTON3 115 kV | TBD |  |  | SUNC |  | 2212500
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 20 MVAR switched shunt at RANSOM 3 115 kV | TBD |  |  | SUNC |  | 2212500
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 25 MVAR switched shunt at ATWOOD 3 115 kV | TBD |  |  | MIDW |  | 2212500
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV | TBD |  |  | SUNC |  | 2212500
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 3.3 MVAR switched shunt at CHASE 3 115 kV | TBD |  |  | SUNC |  | 2212500
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV | TBD |  |  | SUNC |  | 2212500
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | NRIS | Add 7 MVAR switched shunt at EHALLTP3 115 kV | TBD |  |  | SUNC |  | 2212500
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | NRIS | Add 8 MVAR switched shunt at JHNCRSOL 115 kV | TBD |  |  | SUNC |  | 2212500
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | TBD | 1 | (1793.00, 1793.00) | WERE |  | 2200000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 543085 COURTNY2 69 548802 SUB H 69 1 | TBD | 2.57 | (69.00, 69.00) | INDN/KCPL |  | 2184500
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 547467 ORO110 5 161 547494 OAK432 5 161 1 | TBD | 1.38 | (364.00, 364.00) | EMDE |  | 2070000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 0.02 MVAR switched shunt at NEOSHON2 69 kV | TBD |  |  | WERE |  | 1380000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV | TBD |  |  | KCPL |  | 1380000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV | TBD |  |  | WERE |  | 1380000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 0.25 MVAR switched shunt at LABETTS2 69 kV | TBD |  |  | WERE |  | 1380000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 3 MVAR switched shunt at NEOSHOS2 69 kV | TBD |  |  | WERE |  | 1380000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV | TBD |  |  | EMDE |  | 1380000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV | TBD |  |  | KCPL |  | 1380000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 531405 WALKMYR3 115 531510 HARBNGR3 115 1 | TBD | 1.28 | (598.00, 598.00) | SUNC |  | 1280000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 548802 SUB H 69 548815 SUB M 69 1 | TBD | 1.1 | (106.00, 106.00) | INDN |  | 935000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | NRIS | Rebuild line 532937 NEOSHO 5 161 532939 N345 4 5 161 1 | TBD | 0.3 | (837.00, 837.00) | WERE |  | 450000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 533021 NEOSHO 4 138 533023 N345 3 4 138 1 | TBD | 0.28 | (717.00, 717.00) | WERE |  | 336000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 532857 TECHILL6 230 785250 G24-276-TAP 230 1 | TBD | 0.09 | (519.00, 519.00) | WERE |  | 171000
Current Study | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild line 543164 SUGRCK_TP_W2 69 543165 SUGRCK_TP_E2 69 1 | TBD | 0.1 | (69.00, 69.00) | KCPL |  | 85000
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Asbury 161 kV Substation GEN-2024-259 Interconnection (Non-Shared NU) (EMDE) | 171743 |  |  | EDE | 42 | 33306052
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Asbury 161 kV Substation GEN-2024-259 Interconnection (TOIF) (EMDE) | 171742 |  |  | EDE | 42 | 5877539
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Blue Valley - Blumil 161 kV Line GEN-2024-207 Interconnection (Non-Shared NU) (INDN) | 171669 |  |  | INDN | 0 | 0
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Blue Valley - Blumil 161 kV Line GEN-2024-207 Interconnection (TOIF) (INDN) | 171668 |  |  | INDN | 0 | 0
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Blue Valley 161 kV Substation GEN-2024-206 Interconnection (Non-Shared NU) (INDN) | 171667 |  |  | INDN | 0 | 0
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Blue Valley 161 kV Substation GEN-2024-206 Interconnection (TOIF) (INDN) | 171666 |  |  | INDN | 0 | 0
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Brookline 161 kV Substation GEN-2024-181 Interconnection (Non-Shared NU) (CUS) | 171650 |  |  | CUS | 30 | 1700000
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Brookline 161 kV Substation GEN-2024-181 Interconnection (TOIF) (CUS) | 171649 |  |  | CUS | 18 | 55000
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Butler - Nevada 161 kV line GEN-2024-055 Interconnection (Non-Shared NU) (WERE) | 171905 |  |  | WERE | 48 | 15550547
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Butler - Nevada 161 kV line GEN-2024-055 Interconnection (TOIF) (WERE) | 171904 |  |  | WERE | 48 | 1495123
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Butler 138 kV Substation GEN-2024-330 Interconnection (Non-Shared NU) (WERE) | 171948 |  |  | WERE | 48 | 1289137
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Butler 138 kV Substation GEN-2024-330 Interconnection (TOIF) (WERE) | 171947 |  |  | WERE | 48 | 1040242
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Caney River - Neosho 345 kV Line GEN-2024-129 Interconnection (Non-Shared NU) (WERE) | 171921 |  |  | WERE | 60 | 31994301
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Caney River - Neosho 345 kV Line GEN-2024-129 Interconnection (TOIF) (WERE) | 171920 |  |  | WERE | 60 | 1958092
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Cirrus 345 kV Substation GEN-2024-067 Interconnection (Non-Shared NU) (ITCGP) | 171538 |  |  | ITCGP | 30 | 4630435
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Cirrus 345 kV Substation GEN-2024-067 Interconnection (TOIF) (ITCGP) | 171537 |  |  | ITCGP | 30 | 1306438
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Dogwood 345 kV Substation GEN-2024-170 Interconnection (Non-Shared NU) (WERE) | 171929 |  |  | WERE | 60 | 4228553
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Dogwood 345 kV Substation GEN-2024-170 Interconnection (TOIF) (WERE) | 171928 |  |  | WERE | 60 | 1958092
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Duncan Road 161 kV Substation GEN-2024-074 Interconnection (Non-Shared NU) (WERE) | 171911 |  |  | WERE | 42 | 1235193
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Duncan Road 161 kV Substation GEN-2024-074 Interconnection (TOIF) (WERE) | 171910 |  |  | WERE | 42 | 1061550
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | East Town 161 kV Substation GEN-2024-260 Interconnection (Non-Shared NU) (WERE) | 171939 |  |  | WERE | 42 | 1235193
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | East Town 161 kV Substation GEN-2024-260 Interconnection (TOIF) (WERE) | 171938 |  |  | WERE | 42 | 1061551
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Elm Creek 345 kV Substation GEN-2024-215 Interconnection (Non-Shared NU) (ITCGP) | 171681 |  |  | ITCGP | 30 | 1856969
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Elm Creek 345 kV Substation GEN-2024-215 Interconnection (TOIF) (ITCGP) | 171680 |  |  | ITCGP | 30 | 1306438
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Jaggard 115 kV Substation GEN-2024-320 Interconnection (Non-Shared NU) (WERE) | 171946 |  |  | WERE | 48 | 16424539
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Jaggard 115 kV Substation GEN-2024-320 Interconnection (TOIF) (WERE) | 171945 |  |  | WERE | 48 | 1040242
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Jeffrey EC 345 kV Substation GEN-2024-249 Interconnection (Non-Shared NU) (WERE) | 171935 |  |  | WERE | 60 | 5202083
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Jeffrey EC 345 kV Substation GEN-2024-249 Interconnection (TOIF) (WERE) | 171934 |  |  | WERE | 60 | 1742929
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | McCartney 161 kV Substation GEN-2024-088 Interconnection (Non-Shared NU) (CUS) | 171564 |  |  | CUS | 26 | 2930000
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | McCartney 161 kV Substation GEN-2024-088 Interconnection (TOIF) (CUS) | 171563 |  |  | CUS | 26 | 2700000
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Metro 5 161 kV Substation GEN-2024-319 Interconnection (Non-Shared NU) (KACY) | 171817 |  |  | KACY | 25 | 2757867
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Metro 5 161 kV Substation GEN-2024-319 Interconnection (TOIF) (KACY) | 171816 |  |  | KACY | 0 | 200000
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Murray Gill 138 kV Substation GEN-2024-166 Interconnection (Non-Shared NU) (WERE) | 171925 |  |  | WERE | 48 | 3654211
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Murray Gill 138 kV Substation GEN-2024-166 Interconnection (TOIF) (WERE) | 171924 |  |  | WERE | 48 | 1040242
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Neosho - LaCygne 345 kV Line GEN-2024-076 Interconnection (Non-Shared NU) (WERE) | 171913 |  |  | WERE | 60 | 1958090
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Neosho - LaCygne 345 kV Line GEN-2024-076 Interconnection (TOIF) (WERE) | 171912 |  |  | WERE | 60 | 1958090
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Neosho Ridge - Caney River 345 kV Line GEN-2024-125 Interconnection (Non-Shared NU) (WERE) | 171919 |  |  | WERE | 60 | 31994301
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Neosho Ridge - Caney River 345 kV Line GEN-2024-125 Interconnection (TOIF) (WERE) | 171918 |  |  | WERE | 60 | 1958092
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Overton - Sedalia East 161 kV line GEN-2024-054 Interconnection (Non-Shared NU) (WERE) | 171903 |  |  | WERE | 36 | 0
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Overton - Sedalia East 161 kV line GEN-2024-054 Interconnection (TOIF) (WERE) | 171902 |  |  | WERE | 36 | 112911
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Sibley 345 kV Substation GEN-2024-352 Interconnection (TOIF) (WERE) | 171951 |  |  | WERE | 60 | 1958092
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Smithville 161 kV Substation GEN-2024-090 Interconnection (Non-Shared NU) (WERE) | 171915 |  |  | WERE | 42 | 3659394
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Smithville 161 kV Substation GEN-2024-090 Interconnection (TOIF) (WERE) | 171914 |  |  | WERE | 42 | 1061550
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Smithville 161 kV Substation GEN-2024-370 Interconnection (Non-Shared NU) (WERE) | 171954 |  |  | WERE | 42 | 3659394
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Smithville 161 kV Substation GEN-2024-370 Interconnection (TOIF) (WERE) | 171953 |  |  | WERE | 42 | 1061551
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | St. John 115 kV Substation GEN-2024-205 Interconnection (Non-Shared NU) (SUNC) | 171665 |  |  | SEPC | 40 | 2800000
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | St. John 115 kV Substation GEN-2024-205 Interconnection (TOIF) (SUNC) | 171664 |  |  | SEPC | 40 | 1200000
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Stranger Creek - 87th Street 345 kV line GEN-2024-253 Interconnection (Non-Shared NU) (WERE) | 171937 |  |  | WERE | 60 | 33058407
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Stranger Creek - 87th Street 345 kV line GEN-2024-253 Interconnection (TOIF) (WERE) | 171936 |  |  | WERE | 60 | 1958092
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Stranger Creek 115 kV Substation GEN-2024-339 Interconnection (Non-Shared NU) (WERE) | 171950 |  |  | WERE | 48 | 1289137
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Stranger Creek 115 kV Substation GEN-2024-339 Interconnection (TOIF) (WERE) | 171949 |  |  | WERE | 48 | 1040242
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Tecumseh Hill - Swissvale 230kV Line GEN-2024-276 Interconnection (TOIF) (WERE) | 171940 |  |  | WERE | 60 | 1958092
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Tecumseh Hill - Swissvale 230kV Line GEN-2024-276/277 Interconnection (Shared NU) (WERE) | 171942 |  |  | WERE | 60 | 32644437
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Tecumseh Hill - Swissvale 230kV Line GEN-2024-277 Interconnection (TOIF) (WERE) | 171941 |  |  | WERE | 60 | 112911
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Wolf Creek - Blackberry 345 kV Line GEN-2024-139 Interconnection (Non-Shared NU) (NEET) | 171607 |  |  | NEET | 0 | 28818600
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Wolf Creek - Blackberry 345 kV Line GEN-2024-139 Interconnection (TOIF) (NEET) | 171606 |  |  | NEET | 0 | 840255
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Wolf Creek - Blackberry 345 kV Line GEN-2024-258 Interconnection (Non-Shared NU) (NEET) | 171741 |  |  | NEET | 0 | 28818600
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Wolf Creek - Blackberry 345 kV Line GEN-2024-258 Interconnection (TOIF) (NEET) | 171740 |  |  | NEET | 0 | 840255
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Wolf Creek - Blackberry 345 kV Line GEN-2024-287 Interconnection (Non-Shared NU) (NEET) | 171778 |  |  | NEET | 0 | 28818600
Interconnection | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Wolf Creek - Blackberry 345 kV Line GEN-2024-287 Interconnection (TOIF) (NEET) | 171777 |  |  | NEET | 0 | 840255
Contingent | Steady State | 03 CENTRAL/ 04 SOUTHEAST | DISIS-2024-001 | ERIS | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029 | 94615 |  |  |  |  | 543515503
Contingent | Steady State | 03 CENTRAL/ 04 SOUTHEAST | DISIS-2024-001 | ERIS | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025 | 94929 |  |  |  |  | 413934522
Current Study | Steady State | 03 CENTRAL/ 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | TBD | 42.72 | (1793.00, 1793.00) | AEPW/WERE |  | 93984000
Current Study | Steady State | 03 CENTRAL/ 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | TBD | 20.87 | (1793.00, 1793.00) | OKGE/WERE |  | 45914000
Current Study | Steady State | 03 CENTRAL/ 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 514804 MIDLTNT4 138 532981 CRESWLN4 138 1 | TBD | 9.08 | (265.00, 265.00) | OKGE/WERE |  | 10896000
Current Study | Steady State | 03 CENTRAL/ 04 SOUTHEAST | DISIS-2024-001 | NRIS | Rebuild line 505492 SPRGFLD5 161 549970 CLAY 5 161 1 | TBD | 6.73 | (246.00, 246.00) | SPRM/SWPA |  | 10095000
Current Study | Steady State | 03 CENTRAL/ 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 505488 CARTHAG5 161 547485 CAR395 5 161 1 | TBD | 4.14 | (446.00, 446.00) | EMDE/SWPA |  | 6210000
Current Study | Steady State | 03 CENTRAL/ 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 510422 COFFEYT4 138 533002 DEARING4 138 1 | TBD | 5.02 | (717.00, 717.00) | AEPW/WERE |  | 6024000
Contingent | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030 | 900426 |  |  |  |  | 2372127948.71
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add line 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 P2 | TBD | 66.8 | (1011.00, 1176.00) | AEPW |  | 217080000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 508072 NWTXARK7 345 508359 WELSH 7 345 1 | TBD | 56.1 | (1793.00, 1793.00) | AEPW |  | 123420000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 334197 7ROCKYCRK% 345 783930 G24-232-TAP 345 1 | TBD | 45.65 | (1793.00, 1793.00) | AEPW/EES |  | 100430000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1 | TBD | 44.59 | (1793.00, 1793.00) | AEPW/OKGE |  | 98098000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 514934 DRAPER 7 345 515045 SEMINOL7 345 2 | TBD | 44.14 | (1793.00, 1793.00) | OKGE |  | 97108000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add line 515012 RVRVALY7 345 780360 G24-113-TAP 345 P2 | TBD | 23.28 | (1195.00, 1195.00) | OKGE |  | 82168000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 508359 WELSH 7 345 508841 WILKES 7 345 1 | TBD | 30.63 | (1793.00, 1793.00) | AEPW |  | 67386000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 514909 REDBUD 7 345 787290 G24-344-TAP 345 1 | TBD | 26.49 | (1793.00, 1793.00) | OKGE |  | 58278000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 508563 PIRKEY 7 345 508832 DIANA 7 345 1 | TBD | 24.75 | (1793.00, 1793.00) | AEPW |  | 54450000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | TBD | 21.38 | (1793.00, 1793.00) | AEPW/OKGE |  | 47036000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 3-winding transformer 515302 FTSMITH7 345 515305 FTSMITH8 500 515726 FTSMTH11 13 M2 | TBD |  | (660.00, 693.00) | OKGE |  | 47000000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 337376 7SAREPTA% 345 788340 G24-379-TAP 345 1 | TBD | 21.32 | (1793.00, 1793.00) | AEPW/EES |  | 46904000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 505600 TUPELO 4 138 505602 S BROWN4 138 1 | TBD | 36.9 | (211.00, 211.00) | SWPA |  | 44280000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 514715 WOODRNG7 345 515875 REDNGTN7 345 1 | TBD | 19.2 | (1793.00, 1793.00) | OKGE |  | 42240000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 508809 LONGWD 7 345 788340 G24-379-TAP 345 1 | TBD | 19.1 | (1793.00, 1793.00) | AEPW |  | 42020000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 507760 SW SHV 7 345 508809 LONGWD 7 345 1 | TBD | 19.02 | (1793.00, 1793.00) | AEPW |  | 41844000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | TBD | 18.75 | (519.00, 519.00) | AEPW |  | 35625000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | TBD | 15.27 | (1793.00, 1793.00) | AEPW |  | 33594000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | TBD | 14.6 | (1793.00, 1793.00) | AEPW |  | 32120000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 505552 GORE 5 161 505558 MUSKTAP5 161 1 | TBD | 16 | (246.00, 246.00) | SWPA |  | 24000000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 511541 DEMPSEYR POI 230 511557 CHISHOLM6 230 1 | TBD | 11.15 | (519.00, 519.00) | AEPW |  | 21185000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | NRIS | Rebuild line 509690 4PINELND 138 509691 4BROADUS 138 1 | TBD | 17 | (211.00, 211.00) | AEPW |  | 20400000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 3-winding transformer 515301 FTSMTHW5 161 515302 FTSMITH7 345 515728 FTSMTH51 13 M2 | TBD |  | (493.00, 493.00) | OKGE |  | 20300000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 787170 G24-340-TAP 345 787290 G24-344-TAP 345 1 | TBD | 8.4 | (1793.00, 1793.00) | OKGE |  | 18480000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 505522 VAN BUR5 161 505524 LIBERTY5 161 1 | TBD | 12.1 | (309.00, 309.00) | SWPA |  | 18150000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 3-winding transformer 508562 PIRKEY 4 138 508563 PIRKEY 7 345 508587 PIRKY1-1 13 M2 | TBD |  | (600.00, 600.00) | AEPW |  | 18100000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 3-winding transformer 508808 LONGWD 4 138 508809 LONGWD 7 345 508819 LONGW1-1 13 M2 | TBD |  | (580.00, 580.00) | AEPW |  | 18100000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | NRIS | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2 | TBD |  | (484.00, 515.00) | AEPW |  | 18100000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | NRIS | Add 3-winding transformer 514898 CIMARON4 138 514901 CIMARON7 345 515715 CIMARO21 13 M2 | TBD |  | (478.00, 478.00) | OKGE |  | 18100000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 3-winding transformer 514907 ARCADIA4 138 514908 ARCADIA7 345 515700 ARCADI41 13 M2 | TBD |  | (448.00, 448.00) | OKGE |  | 18100000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 3-winding transformer 515800 GRACMNT7 345 515801 GRCMNT11 13 515802 GRACMNT4 138 M2 | TBD |  | (478.00, 478.00) | OKGE |  | 18100000
Contingent | Steady State | 04 SOUTHEAST | DISIS-2024-001 | NRIS | 520_T.NO.4-46ST-TP-PPTAP_rebuild.idv : 2023 ITP, PID: 93019, NTC, ISD: 1/21/2027 | 93019 |  |  |  |  | 16346806
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 | TBD | 13.16 | (211.00, 211.00) | OKGE |  | 15792000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1 | TBD | 6.93 | (1793.00, 1793.00) | AEPW |  | 15246000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | NRIS | Rebuild line 511468 L.E.S.-7 345 764550 G20-087-TAP 345 1 | TBD | 6.89 | (1793.00, 1793.00) | AEPW |  | 15158000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | TBD | 14.95 | (329.00, 329.00) | AEPW/EES-EAI |  | 14950000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2 | TBD |  | (339.00, 330.00) | AEPW |  | 14000000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 508566 SABMINT4 138 508569 SEMRSHL4 138 1 | TBD | 10.52 | (395.00, 395.00) | AEPW |  | 12624000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 507727 FLOURNY4 138 508816 OAKPH 4 138 1 | TBD | 10.42 | (472.00, 472.00) | AEPW |  | 12504000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 3-winding transformer 512623 CATSAGD4 138 512638 CATSAGR5 161 512833 CATTER1 1 13 M2 | TBD |  | (150.00, 188.00) | GRDA |  | 12400000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 3-winding transformer 512636 CATSAGR4 138 512638 CATSAGR5 161 512834 CATTER2 1 13 M2 | TBD |  | (150.00, 188.00) | GRDA |  | 12400000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 508596 BRANDYBR4 138 509092 EASTON 4 138 1 | TBD | 9.88 | (717.00, 717.00) | AEPW |  | 11856000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | TBD | 5.3 | (1793.00, 1793.00) | AEPW |  | 11660000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | NRIS | Rebuild line 515227 5TRIBES2 69 516093 OKTAHA 2 69 1 | TBD | 13.49 | (140.00, 140.00) | OKGE |  | 11466500
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 508557 MARSHL-4 138 508562 PIRKEY 4 138 1 | TBD | 8.85 | (525.00, 525.00) | AEPW |  | 10620000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | NRIS | Carthage_Add_transformer_fixed.idv : | TBD |  |  |  |  | 10475000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | NRIS | Rebuild line 509691 4BROADUS 138 509692 4ETOIL 138 1 | TBD | 8.51 | (211.00, 211.00) | AEPW |  | 10212000
Contingent | Steady State | 04 SOUTHEAST | DISIS-2024-001 | NRIS | 524_SW134TP4-WESTMOR4_extendLine.idv : 2023 ITP, PID: 92996, NTC, ISD: 12/15/2025 (marked as in service) | 92996 |  |  |  |  | 9666986
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 508806 LIEBERM4 138 780630 G24-122-TAP 138 1 | TBD | 7.6 | (265.00, 265.00) | AEPW |  | 9120000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 508814 RODESSA2 69 783570 G24-220-TAP 69 1 | TBD | 10.34 | (69.00, 69.00) | AEPW |  | 8789000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 509083 ROKHILL4 138 509087 TATUM 4 138 1 | TBD | 6.5 | (472.00, 472.00) | AEPW |  | 7800000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 508804 HOSSTON2 69 508846 GODFREYRDTP2 69 1 | TBD | 8.6 | (69.00, 69.00) | AEPW |  | 7310000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 508567 SCOTTSV4 138 508569 SEMRSHL4 138 1 | TBD | 6.08 | (395.00, 395.00) | AEPW |  | 7296000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 507711 ARSHILL4 138 507749 RAINES 4 138 1 | TBD | 5.92 | (395.00, 395.00) | AEPW |  | 7104000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | NRIS | Rebuild line 514894 CZECHAL4 138 514898 CIMARON4 138 1 | TBD | 5.63 | (525.00, 525.00) | OKGE |  | 6756000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 515301 FTSMTHW5 161 515306 ARKOMA 5 161 1 | TBD | 4.48 | (446.00, 446.00) | OKGE |  | 6720000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 515055 MAUD 4 138 787770 G24-360-TAP 138 1 | TBD | 5.11 | (395.00, 395.00) | OKGE |  | 6132000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 509059 CHEROKE4 138 509087 TATUM 4 138 1 | TBD | 5.09 | (472.00, 472.00) | AEPW |  | 6108000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | NRIS | Rebuild line 515802 GRACMNT4 138 520814 ANADARK4 138 1 | TBD | 5.09 | (265.00, 265.00) | OKGE/WFEC |  | 6108000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild 3-winding transformer 515336 VBI 2 69 515339 VBI 5 161 515769 VBI 1 13 2 | TBD |  | (90.00, 90.00) | OKGE |  | 6075000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | NRIS | Rebuild 3-winding transformer 516092 OKTAHA 5 161 516093 OKTAHA 2 69 516095 OKTAHA71 13 7 | TBD |  | (186.00, 186.00) | OKGE |  | 6075000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 509770 LLAN WT4 138 509803 DAWSONT4 138 1 | TBD | 4.99 | (265.00, 265.00) | AEPW |  | 5988000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 509083 ROKHILL4 138 509102 NEWPROS4 138 1 | TBD | 4.82 | (395.00, 395.00) | AEPW |  | 5784000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 507774 NORAM 4 138 508808 LONGWD 4 138 1 | TBD | 4.8 | (395.00, 395.00) | AEPW |  | 5760000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | NRIS | Rebuild line 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | TBD | 4.8 | (395.00, 395.00) | OKGE |  | 5760000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 0.11 MVAR switched shunt at CHAMSPR7 345 kV | TBD |  |  | AEPW |  | 5300000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 0.4 MVAR switched shunt at TONTITN7 345 kV | TBD |  |  | AEPW |  | 5300000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 2 MVAR switched shunt at GEN-2017-140 345 kV | TBD |  |  | AEPW |  | 5300000
Contingent | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | 2023ITP PORTFOLIO - REPLACE TURK 138_115 KV CKT 1 XFMR.idv : 2023 ITP upgrade, PID : 92976, NTC, ISD : 4/25/2027 | 92976 |  |  |  |  | 5250000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 507732 GENMOTR4 138 507759 SW SHV 4 138 1 | TBD | 4.34 | (395.00, 395.00) | AEPW |  | 5208000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 | TBD | 3.89 | (265.00, 265.00) | OKGE |  | 4668000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 514804 MIDLTNT4 138 515381 PECKHMT4 138 1 | TBD | 3.49 | (265.00, 265.00) | OKGE |  | 4188000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 508548 KNOXLEE4 138 509059 CHEROKE4 138 1 | TBD | 3.35 | (472.00, 472.00) | AEPW |  | 4020000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 301402 5LOSTVALY 161 505502 TRUMAN 5 161 1 | TBD | 2.6 | (309.00, 309.00) | AECI/SWPA |  | 3900000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 508562 PIRKEY 4 138 508596 BRANDYBR4 138 1 | TBD | 3.14 | (717.00, 717.00) | AEPW |  | 3768000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 507711 ARSHILL4 138 507742 MCWILLI4 138 1 | TBD | 3.09 | (395.00, 395.00) | AEPW |  | 3708000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 515306 ARKOMA 5 161 515308 3RDST 5 161 1 | TBD | 2.44 | (364.00, 364.00) | OKGE |  | 3660000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 0.2 MVAR switched shunt at GROVE 5 161 kV | TBD |  |  | AEPW |  | 3250000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 40 MVAR switched shunt at INDEPCO5 161 kV | TBD |  |  | SWPA |  | 3250000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 515339 VBI 5 161 515406 ADABELL5 161 1 | TBD | 2.16 | (309.00, 309.00) | OKGE |  | 3240000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | TBD | 1.35 | (1793.00, 1793.00) | GRDA |  | 2970000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 509792 DAWSON-4 138 509803 DAWSONT4 138 1 | TBD | 2.41 | (265.00, 265.00) | AEPW |  | 2892000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 0.02 MVAR switched shunt at JAY 4 138 kV | TBD |  |  | AEPW |  | 2432500
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | NRIS | Add 11 MVAR switched shunt at WWRDEHV4 138 kV | TBD |  |  | OKGE |  | 2432500
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 13 MVAR switched shunt at RSS T1 4 138 kV | TBD |  |  | AEPW |  | 2432500
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 24 MVAR switched shunt at GROVE 4 138 kV | TBD |  |  | AEPW |  | 2432500
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 57 MVAR switched shunt at GUAVA 4 138 kV | TBD |  |  | AEPW |  | 2432500
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | TBD | 1 | (1793.00, 1793.00) | GRDA |  | 2200000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 508808 LONGWD 4 138 508816 OAKPH 4 138 1 | TBD | 1.8 | (472.00, 472.00) | AEPW |  | 2160000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1 | TBD | 1.8 | (472.00, 472.00) | AEPW |  | 2160000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 505602 S BROWN4 138 769060 G22-104-TAP 138 1 | TBD | 1.62 | (395.00, 395.00) | SWPA/WFEC |  | 1944000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | NRIS | Rebuild line 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | TBD | 1.6 | (211.00, 211.00) | AEPW |  | 1920000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 507727 FLOURNY4 138 507732 GENMOTR4 138 1 | TBD | 1.56 | (395.00, 395.00) | AEPW |  | 1872000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 | TBD | 1.46 | (265.00, 265.00) | OKGE |  | 1752000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | NRIS | Rebuild line 514893 XEROX 4 138 514894 CZECHAL4 138 1 | TBD | 1.17 | (472.00, 472.00) | OKGE |  | 1404000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 14 MVAR switched shunt at T.P.S.-2 69 kV | TBD |  |  | AEPW |  | 1380000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV | TBD |  |  | AEPW |  | 1380000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV | TBD |  |  | AEPW |  | 1380000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Add 3.6 MVAR switched shunt at HEDLEY 2 69 kV | TBD |  |  | AEPW |  | 1380000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | NRIS | Rebuild line 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | TBD | 0.93 | (211.00, 211.00) | AEPW |  | 1116000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 508562 PIRKEY 4 138 508566 SABMINT4 138 1 | TBD | 0.88 | (472.00, 472.00) | AEPW |  | 1056000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 508055 BLOOMBG2 69 783570 G24-220-TAP 69 1 | TBD | 1.23 | (69.00, 69.00) | AEPW |  | 1045500
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 508548 KNOXLEE4 138 509092 EASTON 4 138 1 | TBD | 0.69 | (717.00, 717.00) | AEPW |  | 828000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 514760 KILDARE4 138 514764 NWKRKAT4 138 1 | TBD | 0.58 | (265.00, 265.00) | OKGE |  | 696000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 515308 3RDST 5 161 515356 JSTREET5 161 1 | TBD | 0.45 | (246.00, 246.00) | OKGE |  | 675000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 509770 LLAN WT4 138 509804 E 11TH ST 4 138 1 | TBD | 0.48 | (265.00, 265.00) | AEPW |  | 576000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 508814 RODESSA2 69 508846 GODFREYRDTP2 69 1 | TBD | 0.28 | (69.00, 69.00) | AEPW |  | 238000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | TBD |  | (382.00, 382.00) | AEPW/GRDA |  | 120000
Current Study | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild line 509790 CATOOSA4 138 512636 CATSAGR4 138 Z1 | TBD |  | (307.00, 307.00) | AEPW/GRDA |  | 120000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | AES 5 161 kV Substation GEN-2024-286 Interconnection (Non-Shared NU) (OGE) | 171776 |  |  | OGE | 0 | 12000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | AES 5 161 kV Substation GEN-2024-286 Interconnection (TOIF) (OGE) | 171775 |  |  | OGE | 48 | 5000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | AES 5 345 kV Substation GEN-2024-299 Interconnection (Non-Shared NU) (OGE) | 171794 |  |  | OGE | 48 | 20000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | AES 5 345 kV Substation GEN-2024-299 Interconnection (TOIF) (OGE) | 171793 |  |  | OGE | 48 | 8000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Brown 138 kV Substation GEN-2024-204 Interconnection (Non-Shared NU) (OGE) | 171663 |  |  | OGE | 0 | 0
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Brown 138 kV Substation GEN-2024-204 Interconnection (TOIF) (OGE) | 171662 |  |  | OGE | 9 | 100000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Chigley - Oaklawn 138 kV Line GEN-2024-219 Interconnection (Non-Shared NU) (OGE) | 171687 |  |  | OGE | 36 | 7000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Chigley - Oaklawn 138 kV Line GEN-2024-219 Interconnection (TOIF) (OGE) | 171686 |  |  | OGE | 36 | 2000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Chisholm 345 kV Substation GEN-2024-154 Interconnection (Non-Shared NU) (AEP) | 171620 |  |  | AEP | 36 | 3900000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Chisholm 345 kV Substation GEN-2024-154 Interconnection (TOIF) (AEP) | 171619 |  |  | AEP | 36 | 5225000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Cimarron 345 kV Substation GEN-2024-239 Interconnection (Non-Shared NU) (OGE) | 171711 |  |  | OGE | 48 | 3000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Cimarron 345 kV Substation GEN-2024-239 Interconnection (TOIF) (OGE) | 171710 |  |  | OGE | 48 | 2500000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Cimmaron 345 kV Substation GEN-2024-252 Interconnection (Non-Shared NU) (OGE) | 171733 |  |  | OGE | 48 | 3000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Cimmaron 345 kV Substation GEN-2024-252 Interconnection (TOIF) (OGE) | 171732 |  |  | OGE | 48 | 2500000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Coffeyville Tap - North Bartlesville 138kV Line GEN-2024-117 Interconnection (Non-Shared NU) (AEP) | 171582 |  |  | AEP | 36 | 17175000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Coffeyville Tap - North Bartlesville 138kV Line GEN-2024-117 Interconnection (TOIF) (AEP) | 171581 |  |  | AEP | NA | 0
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Cow Creek - Morrison 138 kV line GEN-2024-056 Interconnection (Non-Shared NU) (OGE) | 171528 |  |  | OGE | 36 | 7000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Cow Creek - Morrison 138 kV line GEN-2024-056 Interconnection (TOIF) (OGE) | 171527 |  |  | OGE | 36 | 2000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Crockett - Rocky Creek 345 kV line GEN-2024-232 Interconnection (Non-Shared NU) (AEP) | 171703 |  |  | AEP | 42 | 28225000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Crockett - Rocky Creek 345 kV line GEN-2024-232 Interconnection (TOIF) (AEP) | 171702 |  |  | AEP | 42 | 5225000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Fitzhugh 161kV GEN-2024-003 Interconnection (Non-Shared NU) (AECC) | 171474 |  |  | AECC | 0 | 0
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Fitzhugh 161kV GEN-2024-003 Interconnection (TOIF) (AECC) | 171473 |  |  | AECC | 0 | 1750000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Gracemont - Lawton 345 kV Line GEN-2024-128 Interconnection (Non-Shared NU) (OGE) | 171596 |  |  | OGE | 36 | 18000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Gracemont - Lawton 345 kV Line GEN-2024-128 Interconnection (TOIF) (OGE) | 171595 |  |  | OGE | 36 | 3000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Hemphill 138 kV Substation GEN-2024-376 Interconnection (Non-Shared NU) (ETEC) | 171897 |  |  | ETEC | 0 | 0
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Hemphill 138 kV Substation GEN-2024-376 Interconnection (TOIF) (ETEC) | 171896 |  |  | ETEC | 0 | 0
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | ITC Hugo 7 345 kV Substation GEN-2024-323 Interconnection (Non-Shared NU) (ITCGP) | 171823 |  |  | ITCGP | 30 | 4630437
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | ITC Hugo 7 345 kV Substation GEN-2024-323 Interconnection (TOIF) (ITCGP) | 171822 |  |  | ITCGP | 30 | 1306438
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | JNS KAMO 138 kV Substation GEN-2024-120 Interconnection (Non-Shared NU) (OGE) | 171588 |  |  | OGE | 36 | 1500000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | JNS KAMO 138 kV Substation GEN-2024-120 Interconnection (TOIF) (OGE) | 171587 |  |  | OGE | 36 | 2000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Kelley Avenue 138 kV GEN-2024-333 Interconnection (Non-Shared NU) (OGE) | 171841 |  |  | OGE | 36 | 4500000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Kelley Avenue 138 kV GEN-2024-333 Interconnection (TOIF) (OGE) | 171840 |  |  | OGE | 36 | 2000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | LeBrock 345 kV Substation GEN-2024-343 Interconnection (Non-Shared NU) (AEP) | 171855 |  |  | AEP | 42 | 59500000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | LeBrock 345 kV Substation GEN-2024-343 Interconnection (TOIF) (AEP) | 171854 |  |  | AEP | 42 | 9700000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Leonard 138 kV Substation GEN-2024-362 Interconnection (Non-Shared NU) (AEP) | 171875 |  |  | AEP | 30 | 2800000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Leonard 138 kV SubstationGEN-2024-362 Interconnection (TOIF) (AEP) | 171874 |  |  | AEP | 30 | 3525000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Lieberman - IPC Jefferson 138 kV Line GEN-2024-122 Interconnection (Non-Shared NU) (AEP) | 171590 |  |  | AEP | NA | 0
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Lieberman - IPC Jefferson 138 kV Line GEN-2024-122 Interconnection (TOIF) (AEP) | 171589 |  |  | AEP | NA | 0
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Longwood - El Dorado 345 kV Line GEN-2024-379 Interconnection (Non-Shared NU) (AEP) | 171901 |  |  | AEP | 42 | 28225000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Longwood - El Dorado 345 kV Line GEN-2024-379 Interconnection (TOIF) (AEP) | 171900 |  |  | AEP | 42 | 5225000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Lydia - Welsh 345 kV Line GEN-2024-068 Interconnection (Non-Shared NU) (AEP) | 171540 |  |  | AEP | 42 | 28225000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Lydia - Welsh 345 kV Line GEN-2024-068 Interconnection (TOIF) (AEP) | 171539 |  |  | AEP | 42 | 5225000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Lydia 345 kV Substation GEN-2024-025 Interconnection (Non-Shared NU) (AEP) | 171495 |  |  | AEP | 36 | 3900000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Lydia 345 kV Substation GEN-2024-025 Interconnection (TOIF) (AEP) | 171494 |  |  | AEP | 36 | 5225000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Lydia 345 kV Substation GEN-2024-241 Interconnection (Non-Shared NU) (AEP) | 171715 |  |  | AEP | 0 | 0
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Lydia 345 kV Substation GEN-2024-241 Interconnection (TOIF) (AEP) | 171714 |  |  | AEP | 18 | 200000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Lynn Lane West Tap 138 kV Substation GEN-2024-118 Interconnection (Non-Shared NU) (AEP) | 171584 |  |  | AEP | 30 | 2800000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Lynn Lane West Tap 138 kV Substation GEN-2024-118 Interconnection (TOIF) (AEP) | 171583 |  |  | AEP | 30 | 3325000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Mathewson 345 kV Substation GEN-2024-254 Interconnection (Non-Shared NU) (OGE) | 171735 |  |  | OGE | 36 | 2000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Mathewson 345 kV Substation GEN-2024-254 Interconnection (TOIF) (OGE) | 171734 |  |  | OGE | 36 | 3000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Muskoge7 345 kV Substation GEN-2024-293 Interconnection (Non-Shared NU) (OGE) | 171784 |  |  | OGE | 36 | 5000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Muskoge7 345 kV Substation GEN-2024-293 Interconnection (TOIF) (OGE) | 171783 |  |  | OGE | 36 | 3000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Muskogee - Fort Smith 345 kV Line GEN-2024-268 Interconnection (Non-Shared NU) (OGE) | 171753 |  |  | OGE | 36 | 3000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Muskogee - Fort Smith 345 kV Line GEN-2024-268 Interconnection (TOIF) (OGE) | 171752 |  |  | OGE | 36 | 2000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Muskogee - Ft. Smith 345 kV Line GEN-2024-113 Interconnection (Non-Shared NU) (OGE) | 171578 |  |  | OGE | 36 | 18000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Muskogee - Ft. Smith 345 kV Line GEN-2024-113 Interconnection (TOIF) (OGE) | 171577 |  |  | OGE | 36 | 3000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Muskogee - Pittsburg 345 kV Line GEN-2024-296 Interconnection (TOIF) (OGE) | 171789 |  |  | OGE | 36 | 3000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Muskogee - Pittsburg 345 kV Line GEN-2024-296/297/298 Interconnection (Shared NU) (OGE) | 171792 |  |  | OGE | 36 | 18000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Muskogee - Pittsburg 345 kV Line GEN-2024-297 Interconnection (TOIF) (OGE) | 171790 |  |  | OGE | 36 | 3000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Neosho - Delaware 345 kV line GEN-2024-240 Interconnection (Non-Shared NU) (AEP) | 171713 |  |  | AEP | 42 | 28225000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Neosho - Delaware 345 kV line GEN-2024-240 Interconnection (TOIF) (AEP) | 171712 |  |  | AEP | 42 | 5225000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Norman Hills 345 kV GEN-2024-013 Interconnection (Non-Shared NU) (OGE) | 171478 |  |  | OGE | 36 | 2000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Norman Hills 345 kV GEN-2024-013 Interconnection (TOIF) (OGE) | 171477 |  |  | OGE | 36 | 3500000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | OMPA 345 kV Switchyard GEN-2024-334 Interconnection (Non-Shared NU) (OGE) | 171843 |  |  | OGE | 0 | 0
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | OMPA 345 kV Switchyard GEN-2024-334 Interconnection (TOIF) (OGE) | 171842 |  |  | OGE | 9 | 100000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Pirkey 138 kV Substation GEN-2024-178 Interconnection (Non-Shared NU) (AEP) | 171646 |  |  | AEP | 30 | 6300000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Pirkey 138 kV Substation GEN-2024-178 Interconnection (TOIF) (AEP) | 171645 |  |  | AEP | 30 | 3325000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Pirkey 345 kV Substation GEN-2024-377 Interconnection (Non-Shared NU) (AEP) | 171899 |  |  | AEP | 36 | 12750000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Pirkey 345 kV Substation GEN-2024-377 Interconnection (TOIF) (AEP) | 171898 |  |  | AEP | 36 | 5225000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Pittsburg - Johnston County 345 kV line GEN-2024-338 Interconnection (Non-Shared NU) (AEP) | 171849 |  |  | AEP | 42 | 28225000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Pittsburg - Johnston County 345 kV line GEN-2024-338 Interconnection (TOIF) (AEP) | 171848 |  |  | AEP | 42 | 5225000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Pittsburgh 345 kV Substation GEN-2024-341 Interconnection (Non-Shared NU) (AEP) | 171853 |  |  | AEP | 36 | 9250000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Pittsburgh 345 kV Substation GEN-2024-341 Interconnection (TOIF) (AEP) | 171852 |  |  | AEP | 36 | 5225000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Red Point 138 kV Substation GEN-2024-177 Interconnection (Non-Shared NU) (AEP) | 171644 |  |  | AEP | 30 | 2800000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Red Point 138 kV Substation GEN-2024-177 Interconnection (TOIF) (AEP) | 171643 |  |  | AEP | 30 | 3325000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Riverside – Redbud 345 kV line GEN-2024-340 Interconnection (Non-Shared NU) (AEP) | 171851 |  |  | AEP | 42 | 28225000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Riverside – Redbud 345 kV line GEN-2024-340 Interconnection (TOIF) (AEP) | 171850 |  |  | AEP | 42 | 5225000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Riverside - Redbud Switch 345 kV Line GEN-2024-344 Interconnection (Non-Shared NU) (AEP) | 171857 |  |  | AEP | 24 | 500000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Riverside - Redbud Switch 345 kV Line GEN-2024-344 Interconnection (Non-Shared NU) (OGE) | 171859 |  |  | OGE | 36 | 18000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Riverside - Redbud Switch 345 kV Line GEN-2024-344 Interconnection (TOIF) (AEP) | 171856 |  |  | AEP | 0 | 0
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Riverside - Redbud Switch 345 kV Line GEN-2024-344 Interconnection (TOIF) (OGE) | 171858 |  |  | OGE | 36 | 3000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rodessa - Bloomberg 69 kV Line GEN-2024-220 Interconnection (Non-Shared NU) (AEP) | 171689 |  |  | AEP | 36 | 16475000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rodessa - Bloomberg 69 kV Line GEN-2024-220 Interconnection (TOIF) (AEP) | 171688 |  |  | AEP | 36 | 3475000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Seminole - Maud 138 kV Line GEN-2024-360 Interconnection (Non-Shared NU) (OGE) | 171871 |  |  | OGE | 36 | 3000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Seminole - Maud 138 kV Line GEN-2024-360 Interconnection (TOIF) (OGE) | 171870 |  |  | OGE | 36 | 2000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Seminole - Muskogee 345 kV line GEN-2024-236 Interconnection (Non-Shared NU) (OGE) | 171709 |  |  | OGE | 36 | 18000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Seminole - Muskogee 345 kV line GEN-2024-236 Interconnection (TOIF) (OGE) | 171708 |  |  | OGE | 36 | 3000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Seminole 345 kV Substation GEN-2024-321 Interconnection (Non-Shared NU) (OGE) | 171819 |  |  | OGE | 36 | 5000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Seminole 345 kV Substation GEN-2024-321 Interconnection (TOIF) (OGE) | 171818 |  |  | OGE | 36 | 3000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Sooner - Wekiwa 345 kV line GEN-2024-235 Interconnection (Non-Shared NU) (AEP) | 171707 |  |  | AEP | 42 | 28225000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Sooner - Wekiwa 345 kV line GEN-2024-235 Interconnection (TOIF) (AEP) | 171706 |  |  | AEP | 42 | 5225000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Spring Creek 345 kV Substation GEN-2024-255 Interconnection (Non-Shared NU) (OGE) | 171737 |  |  | OGE | 36 | 7500000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Spring Creek 345 kV Substation GEN-2024-255 Interconnection (TOIF) (OGE) | 171736 |  |  | OGE | 36 | 2000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Spring Valley - Warwick 138 kV line GEN-2024-361 Interconnection (Non-Shared NU) (OGE) | 171873 |  |  | OGE | 36 | 7000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Spring Valley - Warwick 138 kV line GEN-2024-361 Interconnection (TOIF) (OGE) | 171872 |  |  | OGE | 36 | 2000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Tulsa North - American Airlines 138 kV Line GEN-2024-318 Interconnection (Non-Shared NU) (AEP) | 171815 |  |  | AEP | 36 | 17175000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Tulsa North - American Airlines 138 kV Line GEN-2024-318 Interconnection (TOIF) (AEP) | 171814 |  |  | AEP | 36 | 3325000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Tulsa North - GR Energy Center 345 kV Line GEN-2024-171 Interconnection (Non-Shared NU) (GRDA) | 171638 |  |  | GRDA | 36 | 14597250
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Tulsa North - GR Energy Center 345 kV Line GEN-2024-171 Interconnection (TOIF) (GRDA) | 171637 |  |  | GRDA | 36 | 3797463
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Tulsa North - Igloo Valley 345 kV line GEN-2024-294 Interconnection (Non-Shared NU) (GRDA) | 171786 |  |  | GRDA | 36 | 130000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Tulsa North - Igloo Valley 345 kV line GEN-2024-294 Interconnection (TOIF) (GRDA) | 171785 |  |  | GRDA | 0 | 0
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Unger - West Bank Tap 138 kV Line GEN-2024-052/373 Interconnection (Shared NU) (WFEC) | 171893 |  |  | WFEC | 60 | 7000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Unger - West Bank Tap 138 kV Line GEN-2024-373 Interconnection (TOIF) (WFEC) | 171892 |  |  | WFEC | 60 | 2000000
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | West Atlanta - Atlanta 69 kV Line GEN-2024-071 Interconnection (Non-Shared NU) (AEP) | 171542 |  |  | AEP | NA | 0
Interconnection | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | West Atlanta - Atlanta 69 kV Line GEN-2024-071 Interconnection (TOIF) (AEP) | 171541 |  |  | AEP | NA | 0
Contingent | Steady State | 04 SOUTHEAST/ 05 SOUTHWEST | DISIS-2024-001 | ERIS | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032 | 900427 |  |  |  |  | 1790026304.1702
Current Study | Steady State | 04 SOUTHEAST/ 05 SOUTHWEST | DISIS-2024-001 | ERIS | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | TBD | 57.98 | (1793.00, 1793.00) | AEPW/SPS |  | 127556000
Contingent | Steady State | 04 SOUTHEAST/ 05 SOUTHWEST | DISIS-2024-001 | ERIS | Apply contingent IDV 02_765_Phantom_Craw_1_DIS24_TC05ALL-26SP.idv Apply contingent IDV 02_765_Phantom_Craw_1_DIS24_TC05ALL-29SP.idv | TBD |  |  |  |  | 1366342009.82
Contingent | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Multi - Battle Axe - Wolfcamp Tap 115 kV DblCkt_Battle Axe - Ponderosa - Dollarhide 115 kV New Line.idv : PID : 900119, NTC, 2025 ITP, ISD: 6/1/2029 | 900119 |  |  |  |  | 224392680.0012
Contingent | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | 526_SPS_New_Branch_MooreCo_XIT_230kv.idv : 2024 ITP upgrade, PID : 220945, NTC, ISD : 12/15/2028 | 220945 |  |  |  |  | 71837623
Contingent | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028 | 94067 |  |  |  |  | 38846321
Contingent | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | 526_New_MooreCounty_2ndTransformer_230_115.idv : PID: 220817, 2024 ITP, NTC, ISD: 5/15/2029 | 220817 |  |  |  |  | 30028000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Add 3-winding transformer 523219 XIT_INTG TR1 13 523220 XIT_INTG 3 115 523221 XIT_INTG 6 230 M2 | TBD |  | (247.00, 284.00) | SPS |  | 13800000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Rebuild line 523959 POTTER_CO 6 230 524010 ROLLHILLS 6 230 1 | TBD | 6.23 | (637.00, 637.00) | SPS |  | 11837000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Rebuild line 527891 HOBBS_INT 3 115 784800 G24-261-TAP 115 1 | TBD | 11.57 | (217.00, 217.00) | SPS |  | 11570000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Rebuild line 523216 RB-HOGUE 3 115 523246 DALHART 3 115 1 | TBD | 11.44 | (115.00, 115.00) | SPS |  | 11440000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Rebuild line 528547 S_JAL 3 115 785400 G24-281-TAP 115 1 | TBD | 10.82 | (260.00, 260.00) | SPS |  | 10820000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Rebuild line 524875 OASIS 6 230 781740 G24-159-TAP 230 1 | TBD | 4.87 | (519.00, 519.00) | SPS |  | 9253000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Rebuild line 528526 TEAGUE 3 115 528596 CARDINAL 3 115 1 | TBD | 6.81 | (260.00, 260.00) | SPS |  | 6810000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | TBD | 3.02 | (1793.00, 1793.00) | SPS |  | 6644000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Add 23 MVAR switched shunt at FINNEY 7 345 kV | TBD |  |  | SPS |  | 5300000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | NRIS | Rebuild 2-winding transformer 528334 LE-NRTH_INT3 115 528618 LE-LOVINTON2 69 1 | TBD |  | (127.00, 127.00) | SPS |  | 4725000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | NRIS | Add 10 MVAR switched shunt at DEAFSMITH 6 230 kV | TBD |  |  | SPS |  | 3825000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Rebuild line 528547 S_JAL 3 115 528561 DOLLARHIDE 3 115 1 | TBD | 3.7 | (176.00, 176.00) | SPS |  | 3700000
Contingent | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | 22.DIS2001_ERIS_G00_Line_Uprate_Hobbs_to_Sidewinder_345kV_Line.idv : DISIS-2020-001 Upgrade | TBD |  |  |  |  | 2659649
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Rebuild line 528526 TEAGUE 3 115 785400 G24-281-TAP 115 1 | TBD | 2.6 | (260.00, 260.00) | SPS |  | 2600000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | NRIS | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV | TBD |  |  | SPS |  | 2300000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Add 69 MVAR switched shunt at SENDERO +3 115 kV | TBD |  |  | SPS |  | 2212500
Contingent | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | DIS2301-1_G03_ERIS_TurnOffReactors_Carpenter_Finney.idv : Switch out Carpenter 25 MVAR line reactor on the Carpenter to Hitchland 345 kV line | TBD |  |  |  |  | 1450000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV | TBD |  |  | SPS |  | 1380000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV | TBD |  |  | SPS |  | 1380000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Add 1.6 MVAR switched shunt at NP-BOOKER 2 69 kV | TBD |  |  | SPS |  | 1380000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Add 2.1 MVAR switched shunt at RB-TEXLINE 2 69 kV | TBD |  |  | SPS |  | 1380000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV | TBD |  |  | SPS |  | 1380000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Add 8 MVAR switched shunt at RB-N_SEDAN 2 69 kV | TBD |  |  | SPS |  | 1380000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Rebuild line 523220 XIT_INTG 3 115 523228 DALLAM 3 115 1 | TBD | 1.25 | (329.00, 329.00) | SPS |  | 1250000
Current Study | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Rebuild line 528333 LE-WEST_SUB3 115 528334 LE-NRTH_INT3 115 1 | TBD | 0.47 | (217.00, 217.00) | SPS |  | 470000
Contingent | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Apply contingent IDV 01_NewLine_Phantom_Crossroads_Potter_765_26SP.idv | TBD |  |  |  |  | 3275253469
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | 345 kV Crossroads - Eddy County 345 kV Line GEN-2024-221 Interconnection (Non-Shared NU) (SPS) | 171691 |  |  | SPS | 0 | 45536712.63
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | 345 kV Crossroads - Eddy County 345 kV Line GEN-2024-221 Interconnection (TOIF) (SPS) | 171690 |  |  | SPS | 0 | 4872126.25
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Andrews County 345 kV Substation GEN-2024-280 Interconnection (Non-Shared NU) (SPS) | 171765 |  |  | SPS | 0 | 8636936.73
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Andrews County 345 kV Substation GEN-2024-280 Interconnection (TOIF) (SPS) | 171764 |  |  | SPS | 0 | 4502736.58
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Crossroads - Tolk 345 kV Line GEN-2024-043 Interconnection (Non-Shared NU) (SPS) | 171516 |  |  | SPS | 0 | 29754372.46
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Crossroads - Tolk 345 kV Line GEN-2024-043 Interconnection (TOIF) (SPS) | 171515 |  |  | SPS | 0 | 4774296.21
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Crossroads 345 kV Substation GEN-2024-303 Interconnection (Non-Shared NU) (SPS) | 171796 |  |  | SPS | 0 | 8636936.73
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Crossroads 345 kV Substation GEN-2024-303 Interconnection (TOIF) (SPS) | 171795 |  |  | SPS | 0 | 4502736.58
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Crossroads 345 kV Substation GEN-2024-304 Interconnection (Non-Shared NU) (SPS) | 171798 |  |  | SPS | 0 | 8636936.73
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Crossroads 345 kV Substation GEN-2024-304 Interconnection (TOIF) (SPS) | 171797 |  |  | SPS | 0 | 4502736.58
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Dragon 345 kV Substation GEN-2024-317 Interconnection (Non-Shared NU) (SPS) | 171813 |  |  | SPS | 0 | 6564758.74
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Dragon 345 kV Substation GEN-2024-317 Interconnection (TOIF) (SPS) | 171812 |  |  | SPS | 0 | 2882135.29
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Eddy - Chaves 230 kV line GEN-2024-310 Interconnection (TOIF) (SPS) | 171805 |  |  | SPS | 0 | 4549755.92
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Eddy - Chaves 230 kV line GEN-2024-310/311 Interconnection (Shared NU) (SPS) | 171807 |  |  | SPS | 0 | 0
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Eddy - Chaves 230 kV line GEN-2024-311 Interconnection (TOIF) (SPS) | 171806 |  |  | SPS | 0 | 4549755.92
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Hobbs 115 kV Line GEN-2024-261 Interconnection (Non-Shared NU) (LCEC) | 171745 |  |  | LEA | 0 | 0
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Hobbs 115 kV Line GEN-2024-261 Interconnection (TOIF) (LCEC) | 171744 |  |  | LEA | 0 | 0
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Hobbs 115 kV Line GEN-2024-265 Interconnection (Non-Shared NU) (SPS) | 171747 |  |  | SPS | 0 | 15220699.21
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Hobbs 115 kV Line GEN-2024-265 Interconnection (TOIF) (SPS) | 171746 |  |  | SPS | 0 | 3262876.57
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Ink Basin 230 kV Substation GEN-2024-336 Interconnection (Non-Shared NU) (SPS) | 171845 |  |  | SPS | 0 | 6052126.09
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Ink Basin 230 kV Substation GEN-2024-336 Interconnection (TOIF) (SPS) | 171844 |  |  | SPS | 0 | 3955290.56
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Jal - Teague 115 kV Line GEN-2024-281 Interconnection (Non-Shared NU) (SPS) | 171767 |  |  | SPS | 0 | 22838049.8
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Jal - Teague 115 kV Line GEN-2024-281 Interconnection (TOIF) (SPS) | 171766 |  |  | SPS | 0 | 2804642.69
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Newhart 230 kV Substation GEN-2024-099 Interconnection (Non-Shared NU) (SPS) | 171572 |  |  | SPS | 0 | 1603584.62
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Newhart 230 kV Substation GEN-2024-099 Interconnection (TOIF) (SPS) | 171571 |  |  | SPS | 0 | 3214046.86
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Oasis - San Juan Mesa Wind 230 kV Line GEN-2024-159 Interconnection (Non-Shared NU) (SPS) | 171626 |  |  | SPS | 0 | 27237303
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Oasis - San Juan Mesa Wind 230 kV Line GEN-2024-159 Interconnection (TOIF) (SPS) | 171625 |  |  | SPS | 0 | 4119557
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | S Loving 115 kV Substation GEN-2024-295 Interconnection (Non-Shared NU) (SPS) | 171788 |  |  | SPS | 0 | 2172444.84
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | S Loving 115 kV Substation GEN-2024-295 Interconnection (TOIF) (SPS) | 171787 |  |  | SPS | 0 | 3362273.9
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Sundown-Amaco-Yoakum 230 kV Substation GEN-2024-015 Interconnection (Non-Shared NU) (SPS) | 171480 |  |  | SPS | 0 | 24794114
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Sundown-Amaco-Yoakum 230 kV Substation GEN-2024-015 Interconnection (TOIF) (SPS) | 171479 |  |  | SPS | 0 | 3766557
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Tolk - Crossroads 345 kV line GEN-2024-109 Interconnection (Non-Shared NU) (SPS) | 171576 |  |  | SPS | 0 | 27903630.08
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Tolk - Crossroads 345 kV line GEN-2024-109 Interconnection (TOIF) (SPS) | 171575 |  |  | SPS | 0 | 4671893.78
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Tuco - Whirlwind 345 kV line GEN-2024-041 Interconnection (TOIF) (SPS) | 171512 |  |  | SPS | 0 | 5024078.97
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Tuco - Whirlwind 345 kV line GEN-2024-041/042 Interconnection (Shared NU) (SPS) | 171514 |  |  | SPS | 0 | 27720322.3
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | Tuco - Whirlwind 345 kV line GEN-2024-042 Interconnection (TOIF) (SPS) | 171513 |  |  | SPS | 0 | 5024078.97
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | XIT Interchange 230 kV Substation GEN-2024-143 Interconnection (TOIF) (SPS) | 171612 |  |  | SPS | 0 | 4144145.19
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | XIT Interchange 230 kV Substation GEN-2024-143/145 Interconnection (Shared NU) (SPS) | 171616 |  |  | SPS | 0 | 2442046.04
Interconnection | Steady State | 05 SOUTHWEST | DISIS-2024-001 | ERIS | XIT Interchange 230 kV Substation GEN-2024-145 Interconnection (TOIF) (SPS) | 171615 |  |  | SPS | 0 | 4144145.19
JTIQ Expanded Scope Analysis | Steady State | 01 NORTH | DISIS-2024-001 | ERIS | Rebuild the SOURIS 7 to MALLARD7 115kV Line 1 | TBD | 5.3 | (125, 125) | XEL |  | 4088950
JTIQ Expanded Scope Analysis | Steady State | 03 CENTRAL | DISIS-2024-001 | ERIS | Rebuild the 5MCBAINE to 5OVERTON 2 115kV Line 1 | TBD | 11.98 | (557, 557) | AMMO |  | 16766010
JTIQ Expanded Scope Analysis | Steady State | 04 SOUTHEAST | DISIS-2024-001 | ERIS | Rebuild the 3MINDEN_LA! to 3SAREPTA! 115kV Line 1 | TBD | 21.84 | (228, 228) | EES |  | 16849560

## All Thermal
SOLUTIONTYPE | Group | Scenario | Season | Mitigation Iteration | Source | Direction | MONTCOMMONNAME | Rating Type | Rating (MVA) | TDF | TC Loading % | CONTNAME | Constraint Violation Criteria | Upgrade Name
Non-Converged | WECC | 0 | 26SP | WECC | N/A | '' | None |  |  |  |  | None |  | None
Non-Converged | WECC | 0 | 31WP | WECC | N/A | '' | None |  |  |  |  | None |  | None
Non-Converged | WECC | 0 | 31SP | WECC | N/A | '' | None |  |  |  |  | None |  | None
Thermal | WECC | 1 | 26SP | WECC | N/A | '' | None |  |  |  |  | None |  | None
Thermal | WECC | 1 | 31WP | WECC | N/A | '' | None |  |  |  |  | None |  | None
Thermal | WECC | 1 | 31SP | WECC | N/A | '' | None |  |  |  |  | None |  | None
Thermal | 00ALL | 1 | 29SP | T0 | ASGI-2024-001 | FROM->TO | 337909 8ANO% 500 515305 FTSMITH8 500 1 | B | 1299 | 0.085219 | 102.9598 | P52:345:AEPW:NR4PITTSB-7:::: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 05ALL | 1 | 29SP | T0 | ASGI-2024-002 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.057894 | 100.0488 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | ASGI-2024-002 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.059621 | 103.9266 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | ASGI-2024-002 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.059404 | 104.7552 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | ASGI-2024-002 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.059404 | 104.888 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | ASGI-2024-002 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.061086 | 107.2243 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | ASGI-2024-002 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.061086 | 107.2951 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | ASGI-2024-002 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.059256 | 115.0541 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | ASGI-2024-002 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.060772 | 118.9427 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | ASGI-2024-002 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.060772 | 119.313 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 00NR | 1 | 29SP | T0 | ASGI-2024-003 | FROM->TO | 531481 HUGOTON3 115 531483 GRANTTP3 115 1 | B | 230.3 | 0.2804 | 100.7245 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | Rebuild line 531481 HUGOTON3 115 531483 GRANTTP3 115 1
Thermal | 00NR | 1 | 29SP | T0 | ASGI-2024-003 | FROM->TO | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | B | 165.1 | 0.12226 | 100.9381 | P42:345:SPS:FINNEY_OR70:::EHV: | TDF Impact | Rebuild line 531405 WALKMYR3 115 539654 CIM-PLT3 115 1
Thermal | 00NR | 1 | 26SP | T0 | ASGI-2024-003 | FROM->TO | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | B | 165.1 | 0.12193 | 102.6446 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Rebuild line 531405 WALKMYR3 115 539654 CIM-PLT3 115 1
Thermal | 00NR | 1 | 26SP | T0 | ASGI-2024-003 | FROM->TO | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | B | 165.1 | 0.12225 | 104.371 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Rebuild line 531405 WALKMYR3 115 539654 CIM-PLT3 115 1
Thermal | 00NR | 1 | 26SP | T0 | ASGI-2024-003 | FROM->TO | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | B | 165.1 | 0.12225 | 104.371 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | TDF Impact | Rebuild line 531405 WALKMYR3 115 539654 CIM-PLT3 115 1
Thermal | 00NR | 1 | 26SP | T0 | ASGI-2024-003 | FROM->TO | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | B | 165.1 | 0.12225 | 104.371 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | Rebuild line 531405 WALKMYR3 115 539654 CIM-PLT3 115 1
Thermal | 00NR | 1 | 29SP | T0 | ASGI-2024-003 | FROM->TO | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | B | 165.1 | 0.1219 | 106.0206 | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | Rebuild line 531405 WALKMYR3 115 539654 CIM-PLT3 115 1
Thermal | 00NR | 1 | 29SP | T0 | ASGI-2024-003 | FROM->TO | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | B | 165.1 | 0.12226 | 108.7275 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | TDF Impact | Rebuild line 531405 WALKMYR3 115 539654 CIM-PLT3 115 1
Thermal | 00NR | 1 | 29SP | T0 | ASGI-2024-003 | FROM->TO | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | B | 165.1 | 0.12226 | 108.7275 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | TDF Impact | Rebuild line 531405 WALKMYR3 115 539654 CIM-PLT3 115 1
Thermal | 00NR | 1 | 29SP | T0 | ASGI-2024-003 | FROM->TO | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | B | 165.1 | 0.12226 | 108.7275 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | TDF Impact | Rebuild line 531405 WALKMYR3 115 539654 CIM-PLT3 115 1
Thermal | 00NR | 1 | 26SP | T0 | ASGI-2024-003 | FROM->TO | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | B | 165.1 | 0.11888 | 111.0123 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | Rebuild line 531405 WALKMYR3 115 539654 CIM-PLT3 115 1
Thermal | 00NR | 1 | 29SP | T0 | ASGI-2024-003 | FROM->TO | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | B | 165.1 | 0.11912 | 118.9406 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | Rebuild line 531405 WALKMYR3 115 539654 CIM-PLT3 115 1
Thermal | 00NR | 1 | 29SP | T0 | ASGI-2024-006 | FROM->TO | 531481 HUGOTON3 115 531483 GRANTTP3 115 1 | B | 230.3 | 0.044216 | 100.7245 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | Rebuild line 531481 HUGOTON3 115 531483 GRANTTP3 115 1
Thermal | 00ALL | 1 | 29SP | T0 | ASGI-2024-007 | FROM->TO | 337909 8ANO% 500 515305 FTSMITH8 500 1 | B | 1299 | 0.067849 | 102.9598 | P52:345:AEPW:NR4PITTSB-7:::: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | ASGI-2024-008 | FROM->TO | 337909 8ANO% 500 515305 FTSMITH8 500 1 | B | 1299 | 0.067849 | 102.9598 | P52:345:AEPW:NR4PITTSB-7:::: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | ASGI-2024-020 | FROM->TO | 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 | B | 956 | 0.050453 | 100.5447 | P42:345:NPPD:BKR-MOR-3306:::: | Cumulative Impact | Rebuild line 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | ASGI-2024-020 | FROM->TO | 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 | B | 956 | 0.050611 | 102.9523 | P42:345:NPPD:BKR-MOR-3306:::: | Cumulative Impact | Rebuild line 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | ASGI-2024-020 | FROM->TO | 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 | B | 956 | 0.058546 | 108.5368 | P42:345:NPPD:BKR-MOR-3310:::: | Cumulative Impact | Rebuild line 640277 MOORE 3 345 650189 103&ROKEBY3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | ASGI-2024-020 | FROM->TO | 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 | B | 956 | 0.058546 | 108.5368 | P42:345:NPPD:L3502A.MOORE.MCCOOL.CB3310:::: | Cumulative Impact | Rebuild line 640277 MOORE 3 345 650189 103&ROKEBY3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | ASGI-2024-020 | FROM->TO | 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 | B | 956 | 0.053205 | 115.201 | P42:345:NPPD:BKR-MOR-3306:::: | Cumulative Impact | Rebuild line 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1
Thermal | 04ALL | 1 | 26SP | T0 | ASGI-2024-023 | FROM->TO | 507456 TURK 3 115 3WXFMR 520:TURK 2 138 1 | B | 177 | 0.99985 | 103.2017 | Single 338874 3LEWISVILLE# 115 338875 3PATMOS.W# 115 1 | TDF Impact | 2023ITP PORTFOLIO - REPLACE TURK 138_115 KV CKT 1 XFMR.idv : 2023 ITP upgrade, PID : 92976, NTC, ISD : 4/25/2027
Thermal | 04ALL | 1 | 26SP | T0 | ASGI-2024-023 | FROM->TO | 507456 TURK 3 115 3WXFMR 520:TURK 2 138 1 | B | 177 | 0.99985 | 105.218 | P12:115:EES-EAI-AEPW:3COUCH:FULTON3::: | TDF Impact | 2023ITP PORTFOLIO - REPLACE TURK 138_115 KV CKT 1 XFMR.idv : 2023 ITP upgrade, PID : 92976, NTC, ISD : 4/25/2027
Thermal | 04ALL | 1 | 26SP | T0 | ASGI-2024-023 | FROM->TO | 507456 TURK 3 115 3WXFMR 520:TURK 2 138 1 | B | 177 | 0.99985 | 105.218 | P12:115:EES-EAI:COUCH:LEWISV:1 | TDF Impact | 2023ITP PORTFOLIO - REPLACE TURK 138_115 KV CKT 1 XFMR.idv : 2023 ITP upgrade, PID : 92976, NTC, ISD : 4/25/2027
Thermal | 04ALL | 1 | 26SP | T0 | ASGI-2024-023 | FROM->TO | 507456 TURK 3 115 3WXFMR 520:TURK 2 138 1 | B | 177 | 0.99985 | 105.218 | P12:115:EES:3COUCH%:FULTON 3:1:HV: | TDF Impact | 2023ITP PORTFOLIO - REPLACE TURK 138_115 KV CKT 1 XFMR.idv : 2023 ITP upgrade, PID : 92976, NTC, ISD : 4/25/2027
Thermal | 04ALL | 1 | 26SP | T0 | ASGI-2024-023 | FROM->TO | 507456 TURK 3 115 3WXFMR 520:TURK 2 138 1 | B | 177 | 0.99985 | 105.2371 | Single 338875 3PATMOS.W# 115 503912 FULTON3 115 1 | TDF Impact | 2023ITP PORTFOLIO - REPLACE TURK 138_115 KV CKT 1 XFMR.idv : 2023 ITP upgrade, PID : 92976, NTC, ISD : 4/25/2027
Thermal | 04ALL | 1 | 26SP | T0 | ASGI-2024-023 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | B | 1000 | 0.11059 | 116.8554 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | Cumulative Impact | Rebuild line 508359 WELSH 7 345 508841 WILKES 7 345 1
Thermal | 03ALL | 1 | 29SP | T0 | ASGI-2024-024 | FROM->TO | 541251 MARYVLE5 161 635038 BRADDYVILLE5 161 1 | A | 161 | 0.031419 | 100.2848 | System Intact | TDF Impact | Rebuild line 541251 MARYVLE5 161 635038 BRADDYVILLE5 161 1
Thermal | 03ALL | 1 | 29SP | T0 | ASGI-2024-024 | FROM->TO | 541253 ST JOE 5 161 541394 AVENUECTY 5 161 1 | A | 161 | 0.059213 | 100.5556 | System Intact | TDF Impact | Rebuild line 541253 ST JOE 5 161 541394 AVENUECTY 5 161 1
Thermal | 03ALL | 1 | 29WP | T0 | ASGI-2024-024 | FROM->TO | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.060149 | 104.394 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 26SP | T0 | ASGI-2024-024 | FROM->TO | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.069113 | 111.8275 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-003 | FROM->TO | 508298 LYDIA 7 345 510911 VALIANT7 345 1 | B | 1176 | 0.050943 | 102.11 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB:::: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-003 | FROM->TO | 508298 LYDIA 7 345 510911 VALIANT7 345 1 | B | 1176 | 0.051526 | 102.3256 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB:::: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-003 | FROM->TO | 508298 LYDIA 7 345 510911 VALIANT7 345 1 | B | 1176 | 0.051624 | 102.7311 | Single 508072 NWTXARK7 345 764520 G20-020-TAP 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-003 | FROM->TO | 508298 LYDIA 7 345 510911 VALIANT7 345 1 | B | 1176 | 0.051624 | 103.2181 | Single 510911 VALIANT7 345 764520 G20-020-TAP 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-003 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.060433 | 103.8575 | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-003 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.061617 | 104.6172 | P23:345:AEPW:PITTSBURG CB 3433A NBTB:::: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-003 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.059629 | 105.6255 | Single 510907 PITTSB-7 345 787110 G24-338-TAP 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-003 | FROM->TO | 515339 VBI 5 161 3WXFMR 524:524:VBI2 161 2 | A | 76 | 0.032857 | 108.2991 | System Intact | TDF Impact | Rebuild 3-winding transformer 515336 VBI 2 69 515339 VBI 5 161 515769 VBI 1 13 2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-003 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.062358 | 110.0508 | P22:345:EES:MUSKOGE7!:::EHV: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-003 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.062724 | 110.6242 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-003 | FROM->TO | 505552 GORE 5 161 505558 MUSKTAP5 161 1 | B | 201 | 0.09875 | 111.1438 | P22:345:EES:MUSKOGE7!:::EHV: | Cumulative Impact | Rebuild line 505552 GORE 5 161 505558 MUSKTAP5 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-003 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.062046 | 111.1525 | Single 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-003 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.059629 | 111.5464 | Single 514809 JOHNCO7 345 787110 G24-338-TAP 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-003 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.059629 | 111.595 | P42:345:OKGE:SB_JOCO7311:::EHV: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-003 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.062046 | 111.7065 | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-003 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.062435 | 115.5426 | Single 514809 JOHNCO7 345 787110 G24-338-TAP 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-003 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.062435 | 115.6069 | P42:345:OKGE:SB_JOCO7311:::EHV: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-003 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.070061 | 117.3852 | P22:345:EES:MUSKOGE7!:::EHV: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-003 | FROM->TO | 505522 VAN BUR5 161 505524 LIBERTY5 161 1 | B | 222 | 0.13509 | 117.409 | P22:345:EES:MUSKOGE7!:::EHV: | Cumulative Impact | Rebuild line 505522 VAN BUR5 161 505524 LIBERTY5 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-003 | FROM->TO | 515339 VBI 5 161 3WXFMR 524:524:VBI2 161 2 | A | 76 | 0.034842 | 117.4893 | System Intact | TDF Impact | Rebuild 3-winding transformer 515336 VBI 2 69 515339 VBI 5 161 515769 VBI 1 13 2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-003 | FROM->TO | 505552 GORE 5 161 505558 MUSKTAP5 161 1 | B | 201 | 0.10074 | 117.908 | P22:345:EES:MUSKOGE7!:::EHV: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-013 | FROM->TO | 514887 WESTMOR4 138 514925 PENN 4 138 1 | B | 287 | 0.037954 | 100.0254 | P12:138:OKGE:BKRBKR1482:::HV: | TDF Impact | 524_SW134TP4-WESTMOR4_extendLine.idv : 2023 ITP, PID: 92996, NTC, ISD: 12/15/2025 (marked as in service)
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-013 | FROM->TO | 514887 WESTMOR4 138 514925 PENN 4 138 1 | B | 287 | 0.034196 | 102.6127 | Single 514955 MOORE4 138 515380 INDIANH4 138 1 | TDF Impact | 524_SW134TP4-WESTMOR4_extendLine.idv : 2023 ITP, PID: 92996, NTC, ISD: 12/15/2025 (marked as in service)
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-013 | FROM->TO | 514887 WESTMOR4 138 514925 PENN 4 138 1 | B | 287 | 0.034196 | 104.5692 | Single 514954 INDNHIL4 138 515380 INDIANH4 138 1 | TDF Impact | 524_SW134TP4-WESTMOR4_extendLine.idv : 2023 ITP, PID: 92996, NTC, ISD: 12/15/2025 (marked as in service)
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-013 | FROM->TO | 514887 WESTMOR4 138 514925 PENN 4 138 1 | B | 287 | 0.034196 | 105.2997 | Single 514953 HOLLYWD4 138 514954 INDNHIL4 138 1 | TDF Impact | 524_SW134TP4-WESTMOR4_extendLine.idv : 2023 ITP, PID: 92996, NTC, ISD: 12/15/2025 (marked as in service)
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-015 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.07111 | 100.0488 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-015 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.062562 | 100.533 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-015 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.074481 | 103.9266 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-015 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.074292 | 104.7552 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-015 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.074292 | 104.888 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-015 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.077605 | 107.2243 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-015 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063503 | 107.2793 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-015 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063503 | 107.2794 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-015 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.077605 | 107.2951 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-015 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063503 | 107.3093 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-015 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063503 | 107.7557 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-015 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063503 | 108.2747 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-015 | FROM->TO | 523961 POTTER_CO 7 345 3WXFMR 526:WAUK 90343-A 230 1 | B | 559 | 0.074012 | 108.8994 | P42:345:SPS:HITCHLAND-1R15:::EHV: | Cumulative Impact | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-015 | FROM->TO | 523961 POTTER_CO 7 345 3WXFMR 526:WAUK 90343-A 230 1 | B | 559 | 0.074012 | 108.9122 | Single 523097 HITCHLAND7 345 523961 POTTER_CO7 345 1 | Cumulative Impact | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-015 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063503 | 111.3621 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-015 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.072215 | 115.0541 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-015 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.075415 | 118.9427 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-015 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.075415 | 119.313 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-017 | FROM->TO | 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 | B | 956 | 0.30051 | 100.5447 | P42:345:NPPD:BKR-MOR-3306:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-017 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.049637 | 100.5915 | P23:345:MEC:HIGHLAND:903::EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-017 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.049637 | 100.6154 | P23:345:MEC:HIGHLAND:902::EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-017 | FROM->TO | 645454 S3454 3 345 645455 S3455 3 345 1 | B | 1195 | 0.083779 | 100.6765 | P12:345:OPPD:S3455-S3740:::EHV: | Cumulative Impact | Rebuild line 645454 S3454 3 345 645455 S3455 3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-017 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.047493 | 100.6843 | P12:230.0:UMZ:# N-1 #:: LINE TWIN CH4-SIOUXCY4-1 :HV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-017 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.049637 | 101.5782 | Single 635368 OBRIEN3 345 635400 HIGHLAND3 345 1 | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-017 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.049637 | 101.5782 | P12:345:MEC:OBRIEN:HIGHLAND:1REACTOR:EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-017 | FROM->TO | 640278 SHELDON7 115 650242 FOLSM&PHIL7 115 1 | B | 300 | 0.077878 | 101.775 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Rebuild line 640278 SHELDON7 115 650242 FOLSM&PHIL7 115 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-017 | FROM->TO | 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 | B | 956 | 0.29921 | 102.9523 | P42:345:NPPD:BKR-MOR-3306:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-017 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.050323 | 103.0767 | P23:345:MEC:OBRIEN:903::EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-017 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.050509 | 104.0624 | P23:345:MEC:OBRIEN:906::EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-017 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.036935 | 106.6762 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-017 | FROM->TO | 640125 COLMB.E3 345 3WXFMR 640:COL.EAST T4 345 1 | B | 336 | 0.055374 | 108.1049 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | TDF Impact | Add 3-winding transformer 640125 COLMB.E3 345 640127 COLMB.E7 115 640129 COLMB.T9 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-017 | FROM->TO | 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 | B | 956 | 0.3442 | 108.5368 | P42:345:NPPD:BKR-MOR-3310:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 650189 103&ROKEBY3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-017 | FROM->TO | 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 | B | 956 | 0.3442 | 108.5368 | P42:345:NPPD:L3502A.MOORE.MCCOOL.CB3310:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 650189 103&ROKEBY3 345 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-017 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.037085 | 108.9935 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-017 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.037085 | 109.0153 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-017 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.036941 | 109.4444 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-017 | FROM->TO | 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1 | B | 240 | 0.067945 | 111.0462 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Rebuild line 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-017 | FROM->TO | 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1 | B | 240 | 0.071936 | 111.1518 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Rebuild line 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-017 | FROM->TO | 640125 COLMB.E3 345 3WXFMR 640:COL.EAST T4 345 1 | B | 336 | 0.053886 | 111.4413 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | TDF Impact | Add 3-winding transformer 640125 COLMB.E3 345 640127 COLMB.E7 115 640129 COLMB.T9 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-017 | FROM->TO | 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 | B | 956 | 0.29986 | 115.201 | P42:345:NPPD:BKR-MOR-3306:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-017 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.037506 | 118.0094 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-017 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.036511 | 119.5678 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-017 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.03666 | 121.2729 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-017 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.03666 | 121.3014 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-017 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.036496 | 121.5027 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-017 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.14359 | 124.4543 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-017 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.14359 | 124.4543 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-017 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.14254 | 124.734 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-017 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.14254 | 124.734 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-017 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.14397 | 129.5673 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-017 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.14397 | 129.5673 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-017 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.14292 | 130.1714 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-017 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.14292 | 130.1714 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-017 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.037142 | 130.4818 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-017 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.036362 | 146.377 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-017 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.036527 | 148.5944 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-017 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.036527 | 148.6147 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-017 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.036368 | 148.9728 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-017 | FROM->TO | 771999 G23-222-POI 345 3WXFMR 640:BPS_345_115 T1 345 1 | B | 417 | 0.11523 | 159.9374 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-017 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.037063 | 159.9633 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-017 | FROM->TO | 771999 G23-222-POI 345 3WXFMR 640:BPS_345_115 T1 345 1 | B | 417 | 0.11516 | 161.1357 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-017 | FROM->TO | 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1 | B | 240 | 0.10523 | 161.4982 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Rebuild line 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-017 | FROM->TO | 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1 | B | 240 | 0.10503 | 166.5845 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Rebuild line 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-017 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.21062 | 180.6221 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | TDF Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-017 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.21062 | 180.6221 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | TDF Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-017 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.21045 | 183.9678 | P42:345:NPPD:BKR-MOR-3308:::: | TDF Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-017 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.21045 | 183.9678 | P42:345:NPPD:BKR-MOR-3308:::: | TDF Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-017 | FROM->TO | 640278 SHELDON7 115 3WXFMR 640:MOORE T1 345 1 | B | 400 | 0.22823 | 185.3265 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | TDF Impact | Add 3-winding transformer 640277 MOORE 3 345 640278 SHELDON7 115 640280 MOORE 9 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-017 | FROM->TO | 640278 SHELDON7 115 3WXFMR 640:MOORE T1 345 1 | B | 400 | 0.22746 | 195.4671 | P42:345:NPPD:BKR-MOR-3308:::: | TDF Impact | Add 3-winding transformer 640277 MOORE 3 345 640278 SHELDON7 115 640280 MOORE 9 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | FROM->TO | 771999 G23-222-POI 345 3WXFMR 640:BPS_345_115 T1 345 1 | B | 417 | 0.16295 | 100.483 | P42:345:NPPD:L3502A.MOORE.MCCOOL.CB3310:::: | Cumulative Impact | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | FROM->TO | 771999 G23-222-POI 345 3WXFMR 640:BPS_345_115 T1 345 1 | B | 417 | 0.16295 | 100.483 | P42:345:NPPD:BKR-MOR-3310:::: | Cumulative Impact | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | FROM->TO | 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 | B | 956 | 0.28128 | 100.5447 | P42:345:NPPD:BKR-MOR-3306:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-018 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.047677 | 100.5915 | P23:345:MEC:HIGHLAND:903::EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-018 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.047677 | 100.6154 | P23:345:MEC:HIGHLAND:902::EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-018 | FROM->TO | 645454 S3454 3 345 645455 S3455 3 345 1 | B | 1195 | 0.07637 | 100.6765 | P12:345:OPPD:S3455-S3740:::EHV: | Cumulative Impact | Rebuild line 645454 S3454 3 345 645455 S3455 3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-018 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.045853 | 100.6843 | P12:230.0:UMZ:# N-1 #:: LINE TWIN CH4-SIOUXCY4-1 :HV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-018 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.047677 | 101.5782 | Single 635368 OBRIEN3 345 635400 HIGHLAND3 345 1 | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-018 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.047677 | 101.5782 | P12:345:MEC:OBRIEN:HIGHLAND:1REACTOR:EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | FROM->TO | 640278 SHELDON7 115 650242 FOLSM&PHIL7 115 1 | B | 300 | 0.08 | 101.775 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Rebuild line 640278 SHELDON7 115 650242 FOLSM&PHIL7 115 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-018 | FROM->TO | 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 | B | 956 | 0.26113 | 102.9523 | P42:345:NPPD:BKR-MOR-3306:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-018 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.048353 | 103.0767 | P23:345:MEC:OBRIEN:903::EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-018 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.04855 | 104.0624 | P23:345:MEC:OBRIEN:906::EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-018 | FROM->TO | 771999 G23-222-POI 345 3WXFMR 640:BPS_345_115 T1 345 1 | B | 417 | 0.22042 | 105.8248 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | TDF Impact | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-018 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.034913 | 106.6762 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-018 | FROM->TO | 640125 COLMB.E3 345 3WXFMR 640:COL.EAST T4 345 1 | B | 336 | 0.050004 | 108.1049 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | TDF Impact | Add 3-winding transformer 640125 COLMB.E3 345 640127 COLMB.E7 115 640129 COLMB.T9 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-018 | FROM->TO | 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 | B | 956 | 0.30242 | 108.5368 | P42:345:NPPD:BKR-MOR-3310:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 650189 103&ROKEBY3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-018 | FROM->TO | 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 | B | 956 | 0.30242 | 108.5368 | P42:345:NPPD:L3502A.MOORE.MCCOOL.CB3310:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 650189 103&ROKEBY3 345 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-018 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.03505 | 108.9935 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-018 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.03505 | 109.0153 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-018 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.034923 | 109.4444 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-018 | FROM->TO | 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1 | B | 240 | 0.054249 | 111.1518 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Rebuild line 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-018 | FROM->TO | 640125 COLMB.E3 345 3WXFMR 640:COL.EAST T4 345 1 | B | 336 | 0.048521 | 111.4413 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | TDF Impact | Add 3-winding transformer 640125 COLMB.E3 345 640127 COLMB.E7 115 640129 COLMB.T9 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-018 | FROM->TO | 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 | B | 956 | 0.26198 | 115.201 | P42:345:NPPD:BKR-MOR-3306:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-018 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.035431 | 118.0094 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-018 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.034552 | 119.5678 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-018 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.034689 | 121.2729 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-018 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.034689 | 121.3014 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-018 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.034542 | 121.5027 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-018 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.066519 | 124.4543 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-018 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.066519 | 124.4543 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-018 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.064932 | 124.734 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-018 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.064932 | 124.734 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-018 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.066824 | 129.5673 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-018 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.066823 | 129.5673 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-018 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.065231 | 130.1714 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-018 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.065232 | 130.1714 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-018 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.035134 | 130.4818 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | A | 99 | 0.038079 | 131.9721 | System Intact | TDF Impact | DIS2301_P2_G00_ERIS_2_640_NPPD_TO_1000_DAYKIN_345KV_SUB.idv : DISIS_2023 Identified Upgrade
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | A | 99 | 0.038079 | 131.9721 | System Intact | TDF Impact | DIS2301_P2_G00_ERIS_3_640_NPPD_TO_2000_add_BPS_345_Lines_Rev34.idv : DISIS_2023 Identified Upgrade
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | FROM->TO | 640235 HUMBOLT7 115 3WXFMR 640:HUMBOLDT T2 161 1 | B | 126 | 0.11827 | 137.8984 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | Cumulative Impact | Add 3-winding transformer 640234 HUMBOLT5 161 640235 HUMBOLT7 115 643087 HUMBOLDT T29 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-018 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.034372 | 146.377 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-018 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.034525 | 148.5944 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-018 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.034525 | 148.6147 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-018 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.034382 | 148.9728 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | FROM->TO | 640076 BEATRCE7 115 640361 STEINER7 115 1 | B | 121 | 0.11827 | 154.0683 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | Cumulative Impact | Rebuild line 640076 BEATRCE7 115 640361 STEINER7 115 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | FROM->TO | 640169 FAIRBRY7 115 640218 HEBRN N7 115 1 | B | 99 | 0.087347 | 155.7041 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | Cumulative Impact | Rebuild line 640169 FAIRBRY7 115 640218 HEBRN N7 115 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | FROM->TO | 771999 G23-222-POI 345 3WXFMR 640:BPS_345_115 T1 345 1 | B | 417 | 0.23297 | 159.9374 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | TDF Impact | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-018 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.035021 | 159.9633 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | FROM->TO | 771999 G23-222-POI 345 3WXFMR 640:BPS_345_115 T1 345 1 | B | 417 | 0.23284 | 161.1357 | P42:345:NPPD:BKR-MOR-3308:::: | TDF Impact | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | FROM->TO | 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1 | B | 240 | 0.10464 | 161.4982 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Rebuild line 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | FROM->TO | 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1 | B | 240 | 0.1042 | 166.5845 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Rebuild line 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | B | 99 | 0.050016 | 167.9201 | P42:345:NPPD:BKR-MOR-3312:::: | Cumulative Impact | DIS2301_P2_G00_ERIS_2_640_NPPD_TO_1000_DAYKIN_345KV_SUB.idv : DISIS_2023 Identified Upgrade
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | B | 99 | 0.050016 | 167.9201 | P42:345:NPPD:BKR-MOR-3312:::: | Cumulative Impact | DIS2301_P2_G00_ERIS_3_640_NPPD_TO_2000_add_BPS_345_Lines_Rev34.idv : DISIS_2023 Identified Upgrade
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.16766 | 180.6221 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.16766 | 180.6221 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.16729 | 183.9678 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.16729 | 183.9678 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | FROM->TO | 640278 SHELDON7 115 3WXFMR 640:MOORE T1 345 1 | B | 400 | 0.23142 | 185.3265 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | TDF Impact | Add 3-winding transformer 640277 MOORE 3 345 640278 SHELDON7 115 640280 MOORE 9 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | FROM->TO | 640278 SHELDON7 115 3WXFMR 640:MOORE T1 345 1 | B | 400 | 0.22973 | 195.4671 | P42:345:NPPD:BKR-MOR-3308:::: | TDF Impact | Add 3-winding transformer 640277 MOORE 3 345 640278 SHELDON7 115 640280 MOORE 9 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | B | 99 | 0.063813 | 222.8106 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | DIS2301_P2_G00_ERIS_2_640_NPPD_TO_1000_DAYKIN_345KV_SUB.idv : DISIS_2023 Identified Upgrade
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | B | 99 | 0.063813 | 222.8106 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | DIS2301_P2_G00_ERIS_3_640_NPPD_TO_2000_add_BPS_345_Lines_Rev34.idv : DISIS_2023 Identified Upgrade
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | B | 99 | 0.06375 | 225.1739 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | DIS2301_P2_G00_ERIS_2_640_NPPD_TO_1000_DAYKIN_345KV_SUB.idv : DISIS_2023 Identified Upgrade
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | B | 99 | 0.06375 | 225.1739 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | DIS2301_P2_G00_ERIS_3_640_NPPD_TO_2000_add_BPS_345_Lines_Rev34.idv : DISIS_2023 Identified Upgrade
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | B | 193 | 0.40312 | 336.4692 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | TDF Impact | Add line 640088 BPS SUB7 115 640278 SHELDON7 115 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | B | 99 | 0.16673 | 337.5032 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | Cumulative Impact | DIS2301_P2_G00_ERIS_2_640_NPPD_TO_1000_DAYKIN_345KV_SUB.idv : DISIS_2023 Identified Upgrade
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | B | 99 | 0.16673 | 337.5032 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | Cumulative Impact | DIS2301_P2_G00_ERIS_3_640_NPPD_TO_2000_add_BPS_345_Lines_Rev34.idv : DISIS_2023 Identified Upgrade
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | B | 140 | 0.31188 | 348.4283 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | TDF Impact | Rebuild line 640111 CLATONA7 115 640278 SHELDON7 115 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | B | 140 | 0.31188 | 354.8766 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | TDF Impact | Rebuild line 640088 BPS SUB7 115 640111 CLATONA7 115 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | FROM->TO | 771999 G23-222-POI 345 3WXFMR 640:BPS_345_115 T1 345 1 | B | 417 | 1 | 393.5711 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | TDF Impact | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | FROM->TO | 771999 G23-222-POI 345 3WXFMR 640:BPS_345_115 T1 345 1 | B | 417 | 0.16295 | 100.483 | P42:345:NPPD:L3502A.MOORE.MCCOOL.CB3310:::: | Cumulative Impact | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | FROM->TO | 771999 G23-222-POI 345 3WXFMR 640:BPS_345_115 T1 345 1 | B | 417 | 0.16295 | 100.483 | P42:345:NPPD:BKR-MOR-3310:::: | Cumulative Impact | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | FROM->TO | 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 | B | 956 | 0.28128 | 100.5447 | P42:345:NPPD:BKR-MOR-3306:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-019 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.047677 | 100.5915 | P23:345:MEC:HIGHLAND:903::EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-019 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.047677 | 100.6154 | P23:345:MEC:HIGHLAND:902::EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-019 | FROM->TO | 645454 S3454 3 345 645455 S3455 3 345 1 | B | 1195 | 0.07637 | 100.6765 | P12:345:OPPD:S3455-S3740:::EHV: | Cumulative Impact | Rebuild line 645454 S3454 3 345 645455 S3455 3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-019 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.045853 | 100.6843 | P12:230.0:UMZ:# N-1 #:: LINE TWIN CH4-SIOUXCY4-1 :HV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-019 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.047677 | 101.5782 | Single 635368 OBRIEN3 345 635400 HIGHLAND3 345 1 | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-019 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.047677 | 101.5782 | P12:345:MEC:OBRIEN:HIGHLAND:1REACTOR:EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | FROM->TO | 640278 SHELDON7 115 650242 FOLSM&PHIL7 115 1 | B | 300 | 0.08 | 101.775 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Rebuild line 640278 SHELDON7 115 650242 FOLSM&PHIL7 115 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-019 | FROM->TO | 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 | B | 956 | 0.26113 | 102.9523 | P42:345:NPPD:BKR-MOR-3306:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-019 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.048353 | 103.0767 | P23:345:MEC:OBRIEN:903::EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-019 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.04855 | 104.0624 | P23:345:MEC:OBRIEN:906::EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-019 | FROM->TO | 771999 G23-222-POI 345 3WXFMR 640:BPS_345_115 T1 345 1 | B | 417 | 0.22042 | 105.8248 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | TDF Impact | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-019 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.034913 | 106.6762 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-019 | FROM->TO | 640125 COLMB.E3 345 3WXFMR 640:COL.EAST T4 345 1 | B | 336 | 0.050004 | 108.1049 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | TDF Impact | Add 3-winding transformer 640125 COLMB.E3 345 640127 COLMB.E7 115 640129 COLMB.T9 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-019 | FROM->TO | 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 | B | 956 | 0.30242 | 108.5368 | P42:345:NPPD:BKR-MOR-3310:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 650189 103&ROKEBY3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-019 | FROM->TO | 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 | B | 956 | 0.30242 | 108.5368 | P42:345:NPPD:L3502A.MOORE.MCCOOL.CB3310:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 650189 103&ROKEBY3 345 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-019 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.03505 | 108.9935 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-019 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.03505 | 109.0153 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-019 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.034923 | 109.4444 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-019 | FROM->TO | 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1 | B | 240 | 0.054249 | 111.1518 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Rebuild line 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-019 | FROM->TO | 640125 COLMB.E3 345 3WXFMR 640:COL.EAST T4 345 1 | B | 336 | 0.048521 | 111.4413 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | TDF Impact | Add 3-winding transformer 640125 COLMB.E3 345 640127 COLMB.E7 115 640129 COLMB.T9 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-019 | FROM->TO | 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 | B | 956 | 0.26198 | 115.201 | P42:345:NPPD:BKR-MOR-3306:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-019 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.035431 | 118.0094 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-019 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.034552 | 119.5678 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-019 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.034689 | 121.2729 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-019 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.034689 | 121.3014 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-019 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.034542 | 121.5027 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-019 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.066519 | 124.4543 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-019 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.066519 | 124.4543 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-019 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.064932 | 124.734 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-019 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.064932 | 124.734 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-019 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.066824 | 129.5673 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-019 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.066823 | 129.5673 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-019 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.065231 | 130.1714 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-019 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.065232 | 130.1714 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-019 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.035134 | 130.4818 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | A | 99 | 0.038079 | 131.9721 | System Intact | TDF Impact | DIS2301_P2_G00_ERIS_2_640_NPPD_TO_1000_DAYKIN_345KV_SUB.idv : DISIS_2023 Identified Upgrade
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | A | 99 | 0.038079 | 131.9721 | System Intact | TDF Impact | DIS2301_P2_G00_ERIS_3_640_NPPD_TO_2000_add_BPS_345_Lines_Rev34.idv : DISIS_2023 Identified Upgrade
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | FROM->TO | 640235 HUMBOLT7 115 3WXFMR 640:HUMBOLDT T2 161 1 | B | 126 | 0.11827 | 137.8984 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | Cumulative Impact | Add 3-winding transformer 640234 HUMBOLT5 161 640235 HUMBOLT7 115 643087 HUMBOLDT T29 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-019 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.034372 | 146.377 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-019 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.034525 | 148.5944 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-019 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.034525 | 148.6147 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-019 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.034382 | 148.9728 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | FROM->TO | 640076 BEATRCE7 115 640361 STEINER7 115 1 | B | 121 | 0.11827 | 154.0683 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | Cumulative Impact | Rebuild line 640076 BEATRCE7 115 640361 STEINER7 115 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | FROM->TO | 640169 FAIRBRY7 115 640218 HEBRN N7 115 1 | B | 99 | 0.087347 | 155.7041 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | Cumulative Impact | Rebuild line 640169 FAIRBRY7 115 640218 HEBRN N7 115 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | FROM->TO | 771999 G23-222-POI 345 3WXFMR 640:BPS_345_115 T1 345 1 | B | 417 | 0.23297 | 159.9374 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | TDF Impact | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-019 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.035021 | 159.9633 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | FROM->TO | 771999 G23-222-POI 345 3WXFMR 640:BPS_345_115 T1 345 1 | B | 417 | 0.23284 | 161.1357 | P42:345:NPPD:BKR-MOR-3308:::: | TDF Impact | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | FROM->TO | 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1 | B | 240 | 0.10464 | 161.4982 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Rebuild line 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | FROM->TO | 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1 | B | 240 | 0.1042 | 166.5845 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Rebuild line 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | B | 99 | 0.050016 | 167.9201 | P42:345:NPPD:BKR-MOR-3312:::: | Cumulative Impact | DIS2301_P2_G00_ERIS_2_640_NPPD_TO_1000_DAYKIN_345KV_SUB.idv : DISIS_2023 Identified Upgrade
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | B | 99 | 0.050016 | 167.9201 | P42:345:NPPD:BKR-MOR-3312:::: | Cumulative Impact | DIS2301_P2_G00_ERIS_3_640_NPPD_TO_2000_add_BPS_345_Lines_Rev34.idv : DISIS_2023 Identified Upgrade
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.16766 | 180.6221 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.16766 | 180.6221 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.16729 | 183.9678 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.16729 | 183.9678 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | FROM->TO | 640278 SHELDON7 115 3WXFMR 640:MOORE T1 345 1 | B | 400 | 0.23142 | 185.3265 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | TDF Impact | Add 3-winding transformer 640277 MOORE 3 345 640278 SHELDON7 115 640280 MOORE 9 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | FROM->TO | 640278 SHELDON7 115 3WXFMR 640:MOORE T1 345 1 | B | 400 | 0.22973 | 195.4671 | P42:345:NPPD:BKR-MOR-3308:::: | TDF Impact | Add 3-winding transformer 640277 MOORE 3 345 640278 SHELDON7 115 640280 MOORE 9 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | B | 99 | 0.063813 | 222.8106 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | DIS2301_P2_G00_ERIS_2_640_NPPD_TO_1000_DAYKIN_345KV_SUB.idv : DISIS_2023 Identified Upgrade
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | B | 99 | 0.063813 | 222.8106 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | DIS2301_P2_G00_ERIS_3_640_NPPD_TO_2000_add_BPS_345_Lines_Rev34.idv : DISIS_2023 Identified Upgrade
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | B | 99 | 0.06375 | 225.1739 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | DIS2301_P2_G00_ERIS_2_640_NPPD_TO_1000_DAYKIN_345KV_SUB.idv : DISIS_2023 Identified Upgrade
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | B | 99 | 0.06375 | 225.1739 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | DIS2301_P2_G00_ERIS_3_640_NPPD_TO_2000_add_BPS_345_Lines_Rev34.idv : DISIS_2023 Identified Upgrade
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | B | 193 | 0.40312 | 336.4692 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | TDF Impact | Add line 640088 BPS SUB7 115 640278 SHELDON7 115 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | B | 99 | 0.16673 | 337.5032 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | Cumulative Impact | DIS2301_P2_G00_ERIS_2_640_NPPD_TO_1000_DAYKIN_345KV_SUB.idv : DISIS_2023 Identified Upgrade
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | B | 99 | 0.16673 | 337.5032 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | Cumulative Impact | DIS2301_P2_G00_ERIS_3_640_NPPD_TO_2000_add_BPS_345_Lines_Rev34.idv : DISIS_2023 Identified Upgrade
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | B | 140 | 0.31188 | 348.4283 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | TDF Impact | Rebuild line 640111 CLATONA7 115 640278 SHELDON7 115 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | B | 140 | 0.31188 | 354.8766 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | TDF Impact | Rebuild line 640088 BPS SUB7 115 640111 CLATONA7 115 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | FROM->TO | 771999 G23-222-POI 345 3WXFMR 640:BPS_345_115 T1 345 1 | B | 417 | 1 | 393.5711 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | TDF Impact | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-020 | FROM->TO | 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 | B | 956 | 0.30051 | 100.5447 | P42:345:NPPD:BKR-MOR-3306:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-020 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.049637 | 100.5915 | P23:345:MEC:HIGHLAND:903::EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-020 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.049637 | 100.6154 | P23:345:MEC:HIGHLAND:902::EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-020 | FROM->TO | 645454 S3454 3 345 645455 S3455 3 345 1 | B | 1195 | 0.083779 | 100.6765 | P12:345:OPPD:S3455-S3740:::EHV: | Cumulative Impact | Rebuild line 645454 S3454 3 345 645455 S3455 3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-020 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.047493 | 100.6843 | P12:230.0:UMZ:# N-1 #:: LINE TWIN CH4-SIOUXCY4-1 :HV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-020 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.049637 | 101.5782 | Single 635368 OBRIEN3 345 635400 HIGHLAND3 345 1 | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-020 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.049637 | 101.5782 | P12:345:MEC:OBRIEN:HIGHLAND:1REACTOR:EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-020 | FROM->TO | 640278 SHELDON7 115 650242 FOLSM&PHIL7 115 1 | B | 300 | 0.077878 | 101.775 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Rebuild line 640278 SHELDON7 115 650242 FOLSM&PHIL7 115 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-020 | FROM->TO | 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 | B | 956 | 0.29921 | 102.9523 | P42:345:NPPD:BKR-MOR-3306:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-020 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.050323 | 103.0767 | P23:345:MEC:OBRIEN:903::EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-020 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.050509 | 104.0624 | P23:345:MEC:OBRIEN:906::EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-020 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.036935 | 106.6762 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-020 | FROM->TO | 640125 COLMB.E3 345 3WXFMR 640:COL.EAST T4 345 1 | B | 336 | 0.055374 | 108.1049 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | TDF Impact | Add 3-winding transformer 640125 COLMB.E3 345 640127 COLMB.E7 115 640129 COLMB.T9 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-020 | FROM->TO | 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 | B | 956 | 0.3442 | 108.5368 | P42:345:NPPD:BKR-MOR-3310:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 650189 103&ROKEBY3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-020 | FROM->TO | 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 | B | 956 | 0.3442 | 108.5368 | P42:345:NPPD:L3502A.MOORE.MCCOOL.CB3310:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 650189 103&ROKEBY3 345 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-020 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.037085 | 108.9935 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-020 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.037085 | 109.0153 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-020 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.036941 | 109.4444 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-020 | FROM->TO | 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1 | B | 240 | 0.067945 | 111.0462 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Rebuild line 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-020 | FROM->TO | 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1 | B | 240 | 0.071936 | 111.1518 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Rebuild line 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-020 | FROM->TO | 640125 COLMB.E3 345 3WXFMR 640:COL.EAST T4 345 1 | B | 336 | 0.053886 | 111.4413 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | TDF Impact | Add 3-winding transformer 640125 COLMB.E3 345 640127 COLMB.E7 115 640129 COLMB.T9 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-020 | FROM->TO | 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 | B | 956 | 0.29986 | 115.201 | P42:345:NPPD:BKR-MOR-3306:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-020 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.037506 | 118.0094 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-020 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.036511 | 119.5678 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-020 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.03666 | 121.2729 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-020 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.03666 | 121.3014 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-020 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.036496 | 121.5027 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-020 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.14359 | 124.4543 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-020 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.14359 | 124.4543 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-020 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.14254 | 124.734 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-020 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.14254 | 124.734 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-020 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.14397 | 129.5673 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-020 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.14397 | 129.5673 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-020 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.14292 | 130.1714 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-020 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.14292 | 130.1714 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-020 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.037142 | 130.4818 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-020 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.036362 | 146.377 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-020 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.036527 | 148.5944 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-020 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.036527 | 148.6147 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-020 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.036368 | 148.9728 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-020 | FROM->TO | 771999 G23-222-POI 345 3WXFMR 640:BPS_345_115 T1 345 1 | B | 417 | 0.11523 | 159.9374 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-020 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.037063 | 159.9633 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-020 | FROM->TO | 771999 G23-222-POI 345 3WXFMR 640:BPS_345_115 T1 345 1 | B | 417 | 0.11516 | 161.1357 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-020 | FROM->TO | 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1 | B | 240 | 0.10523 | 161.4982 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Rebuild line 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-020 | FROM->TO | 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1 | B | 240 | 0.10503 | 166.5845 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Rebuild line 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-020 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.21062 | 180.6221 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | TDF Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-020 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.21062 | 180.6221 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | TDF Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-020 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.21045 | 183.9678 | P42:345:NPPD:BKR-MOR-3308:::: | TDF Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-020 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.21045 | 183.9678 | P42:345:NPPD:BKR-MOR-3308:::: | TDF Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-020 | FROM->TO | 640278 SHELDON7 115 3WXFMR 640:MOORE T1 345 1 | B | 400 | 0.22823 | 185.3265 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | TDF Impact | Add 3-winding transformer 640277 MOORE 3 345 640278 SHELDON7 115 640280 MOORE 9 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-020 | FROM->TO | 640278 SHELDON7 115 3WXFMR 640:MOORE T1 345 1 | B | 400 | 0.22746 | 195.4671 | P42:345:NPPD:BKR-MOR-3308:::: | TDF Impact | Add 3-winding transformer 640277 MOORE 3 345 640278 SHELDON7 115 640280 MOORE 9 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-021 | FROM->TO | 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 | B | 956 | 0.30051 | 100.5447 | P42:345:NPPD:BKR-MOR-3306:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-021 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.049637 | 100.5915 | P23:345:MEC:HIGHLAND:903::EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-021 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.049637 | 100.6154 | P23:345:MEC:HIGHLAND:902::EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-021 | FROM->TO | 645454 S3454 3 345 645455 S3455 3 345 1 | B | 1195 | 0.083779 | 100.6765 | P12:345:OPPD:S3455-S3740:::EHV: | Cumulative Impact | Rebuild line 645454 S3454 3 345 645455 S3455 3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-021 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.047493 | 100.6843 | P12:230.0:UMZ:# N-1 #:: LINE TWIN CH4-SIOUXCY4-1 :HV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-021 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.049637 | 101.5782 | Single 635368 OBRIEN3 345 635400 HIGHLAND3 345 1 | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-021 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.049637 | 101.5782 | P12:345:MEC:OBRIEN:HIGHLAND:1REACTOR:EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-021 | FROM->TO | 640278 SHELDON7 115 650242 FOLSM&PHIL7 115 1 | B | 300 | 0.077878 | 101.775 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Rebuild line 640278 SHELDON7 115 650242 FOLSM&PHIL7 115 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-021 | FROM->TO | 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 | B | 956 | 0.29921 | 102.9523 | P42:345:NPPD:BKR-MOR-3306:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-021 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.050323 | 103.0767 | P23:345:MEC:OBRIEN:903::EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-021 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.050509 | 104.0624 | P23:345:MEC:OBRIEN:906::EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-021 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.036935 | 106.6762 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-021 | FROM->TO | 640125 COLMB.E3 345 3WXFMR 640:COL.EAST T4 345 1 | B | 336 | 0.055374 | 108.1049 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | TDF Impact | Add 3-winding transformer 640125 COLMB.E3 345 640127 COLMB.E7 115 640129 COLMB.T9 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-021 | FROM->TO | 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 | B | 956 | 0.3442 | 108.5368 | P42:345:NPPD:BKR-MOR-3310:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 650189 103&ROKEBY3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-021 | FROM->TO | 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 | B | 956 | 0.3442 | 108.5368 | P42:345:NPPD:L3502A.MOORE.MCCOOL.CB3310:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 650189 103&ROKEBY3 345 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-021 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.037085 | 108.9935 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-021 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.037085 | 109.0153 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-021 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.036941 | 109.4444 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-021 | FROM->TO | 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1 | B | 240 | 0.067945 | 111.0462 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Rebuild line 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-021 | FROM->TO | 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1 | B | 240 | 0.071936 | 111.1518 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Rebuild line 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-021 | FROM->TO | 640125 COLMB.E3 345 3WXFMR 640:COL.EAST T4 345 1 | B | 336 | 0.053886 | 111.4413 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | TDF Impact | Add 3-winding transformer 640125 COLMB.E3 345 640127 COLMB.E7 115 640129 COLMB.T9 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-021 | FROM->TO | 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 | B | 956 | 0.29986 | 115.201 | P42:345:NPPD:BKR-MOR-3306:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-021 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.037506 | 118.0094 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-021 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.036511 | 119.5678 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-021 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.03666 | 121.2729 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-021 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.03666 | 121.3014 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-021 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.036496 | 121.5027 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-021 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.14359 | 124.4543 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-021 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.14359 | 124.4543 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-021 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.14254 | 124.734 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-021 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.14254 | 124.734 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-021 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.14397 | 129.5673 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-021 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.14397 | 129.5673 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-021 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.14292 | 130.1714 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-021 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.14292 | 130.1714 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-021 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.037142 | 130.4818 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-021 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.036362 | 146.377 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-021 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.036527 | 148.5944 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-021 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.036527 | 148.6147 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-021 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.036368 | 148.9728 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-021 | FROM->TO | 771999 G23-222-POI 345 3WXFMR 640:BPS_345_115 T1 345 1 | B | 417 | 0.11523 | 159.9374 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-021 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.037063 | 159.9633 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-021 | FROM->TO | 771999 G23-222-POI 345 3WXFMR 640:BPS_345_115 T1 345 1 | B | 417 | 0.11516 | 161.1357 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-021 | FROM->TO | 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1 | B | 240 | 0.10523 | 161.4982 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Rebuild line 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-021 | FROM->TO | 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1 | B | 240 | 0.10503 | 166.5845 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Rebuild line 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-021 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.21062 | 180.6221 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | TDF Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-021 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.21062 | 180.6221 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | TDF Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-021 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.21045 | 183.9678 | P42:345:NPPD:BKR-MOR-3308:::: | TDF Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-021 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.21045 | 183.9678 | P42:345:NPPD:BKR-MOR-3308:::: | TDF Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-021 | FROM->TO | 640278 SHELDON7 115 3WXFMR 640:MOORE T1 345 1 | B | 400 | 0.22823 | 185.3265 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | TDF Impact | Add 3-winding transformer 640277 MOORE 3 345 640278 SHELDON7 115 640280 MOORE 9 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-021 | FROM->TO | 640278 SHELDON7 115 3WXFMR 640:MOORE T1 345 1 | B | 400 | 0.22746 | 195.4671 | P42:345:NPPD:BKR-MOR-3308:::: | TDF Impact | Add 3-winding transformer 640277 MOORE 3 345 640278 SHELDON7 115 640280 MOORE 9 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | FROM->TO | 771999 G23-222-POI 345 3WXFMR 640:BPS_345_115 T1 345 1 | B | 417 | 0.16295 | 100.483 | P42:345:NPPD:L3502A.MOORE.MCCOOL.CB3310:::: | Cumulative Impact | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | FROM->TO | 771999 G23-222-POI 345 3WXFMR 640:BPS_345_115 T1 345 1 | B | 417 | 0.16295 | 100.483 | P42:345:NPPD:BKR-MOR-3310:::: | Cumulative Impact | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | FROM->TO | 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 | B | 956 | 0.28128 | 100.5447 | P42:345:NPPD:BKR-MOR-3306:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-022 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.047677 | 100.5915 | P23:345:MEC:HIGHLAND:903::EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-022 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.047677 | 100.6154 | P23:345:MEC:HIGHLAND:902::EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-022 | FROM->TO | 645454 S3454 3 345 645455 S3455 3 345 1 | B | 1195 | 0.07637 | 100.6765 | P12:345:OPPD:S3455-S3740:::EHV: | Cumulative Impact | Rebuild line 645454 S3454 3 345 645455 S3455 3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-022 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.045853 | 100.6843 | P12:230.0:UMZ:# N-1 #:: LINE TWIN CH4-SIOUXCY4-1 :HV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-022 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.047677 | 101.5782 | Single 635368 OBRIEN3 345 635400 HIGHLAND3 345 1 | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-022 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.047677 | 101.5782 | P12:345:MEC:OBRIEN:HIGHLAND:1REACTOR:EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | FROM->TO | 640278 SHELDON7 115 650242 FOLSM&PHIL7 115 1 | B | 300 | 0.08 | 101.775 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Rebuild line 640278 SHELDON7 115 650242 FOLSM&PHIL7 115 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-022 | FROM->TO | 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 | B | 956 | 0.26113 | 102.9523 | P42:345:NPPD:BKR-MOR-3306:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-022 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.048353 | 103.0767 | P23:345:MEC:OBRIEN:903::EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-022 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.04855 | 104.0624 | P23:345:MEC:OBRIEN:906::EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-022 | FROM->TO | 771999 G23-222-POI 345 3WXFMR 640:BPS_345_115 T1 345 1 | B | 417 | 0.22042 | 105.8248 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | TDF Impact | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-022 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.034913 | 106.6762 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-022 | FROM->TO | 640125 COLMB.E3 345 3WXFMR 640:COL.EAST T4 345 1 | B | 336 | 0.050004 | 108.1049 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | TDF Impact | Add 3-winding transformer 640125 COLMB.E3 345 640127 COLMB.E7 115 640129 COLMB.T9 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-022 | FROM->TO | 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 | B | 956 | 0.30242 | 108.5368 | P42:345:NPPD:BKR-MOR-3310:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 650189 103&ROKEBY3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-022 | FROM->TO | 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 | B | 956 | 0.30242 | 108.5368 | P42:345:NPPD:L3502A.MOORE.MCCOOL.CB3310:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 650189 103&ROKEBY3 345 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-022 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.03505 | 108.9935 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-022 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.03505 | 109.0153 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-022 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.034923 | 109.4444 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-022 | FROM->TO | 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1 | B | 240 | 0.054249 | 111.1518 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Rebuild line 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-022 | FROM->TO | 640125 COLMB.E3 345 3WXFMR 640:COL.EAST T4 345 1 | B | 336 | 0.048521 | 111.4413 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | TDF Impact | Add 3-winding transformer 640125 COLMB.E3 345 640127 COLMB.E7 115 640129 COLMB.T9 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-022 | FROM->TO | 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 | B | 956 | 0.26198 | 115.201 | P42:345:NPPD:BKR-MOR-3306:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-022 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.035431 | 118.0094 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-022 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.034552 | 119.5678 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-022 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.034689 | 121.2729 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-022 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.034689 | 121.3014 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-022 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.034542 | 121.5027 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-022 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.066519 | 124.4543 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-022 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.066519 | 124.4543 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-022 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.064932 | 124.734 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-022 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.064932 | 124.734 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-022 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.066824 | 129.5673 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-022 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.066823 | 129.5673 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-022 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.065231 | 130.1714 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-022 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.065232 | 130.1714 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-022 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.035134 | 130.4818 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | A | 99 | 0.038079 | 131.9721 | System Intact | TDF Impact | DIS2301_P2_G00_ERIS_2_640_NPPD_TO_1000_DAYKIN_345KV_SUB.idv : DISIS_2023 Identified Upgrade
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | A | 99 | 0.038079 | 131.9721 | System Intact | TDF Impact | DIS2301_P2_G00_ERIS_3_640_NPPD_TO_2000_add_BPS_345_Lines_Rev34.idv : DISIS_2023 Identified Upgrade
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | FROM->TO | 640235 HUMBOLT7 115 3WXFMR 640:HUMBOLDT T2 161 1 | B | 126 | 0.11827 | 137.8984 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | Cumulative Impact | Add 3-winding transformer 640234 HUMBOLT5 161 640235 HUMBOLT7 115 643087 HUMBOLDT T29 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-022 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.034372 | 146.377 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-022 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.034525 | 148.5944 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-022 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.034525 | 148.6147 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-022 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.034382 | 148.9728 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | FROM->TO | 640076 BEATRCE7 115 640361 STEINER7 115 1 | B | 121 | 0.11827 | 154.0683 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | Cumulative Impact | Rebuild line 640076 BEATRCE7 115 640361 STEINER7 115 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | FROM->TO | 640169 FAIRBRY7 115 640218 HEBRN N7 115 1 | B | 99 | 0.087347 | 155.7041 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | Cumulative Impact | Rebuild line 640169 FAIRBRY7 115 640218 HEBRN N7 115 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | FROM->TO | 771999 G23-222-POI 345 3WXFMR 640:BPS_345_115 T1 345 1 | B | 417 | 0.23297 | 159.9374 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | TDF Impact | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-022 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.035021 | 159.9633 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | FROM->TO | 771999 G23-222-POI 345 3WXFMR 640:BPS_345_115 T1 345 1 | B | 417 | 0.23284 | 161.1357 | P42:345:NPPD:BKR-MOR-3308:::: | TDF Impact | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | FROM->TO | 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1 | B | 240 | 0.10464 | 161.4982 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Rebuild line 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | FROM->TO | 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1 | B | 240 | 0.1042 | 166.5845 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Rebuild line 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | B | 99 | 0.050016 | 167.9201 | P42:345:NPPD:BKR-MOR-3312:::: | Cumulative Impact | DIS2301_P2_G00_ERIS_2_640_NPPD_TO_1000_DAYKIN_345KV_SUB.idv : DISIS_2023 Identified Upgrade
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | B | 99 | 0.050016 | 167.9201 | P42:345:NPPD:BKR-MOR-3312:::: | Cumulative Impact | DIS2301_P2_G00_ERIS_3_640_NPPD_TO_2000_add_BPS_345_Lines_Rev34.idv : DISIS_2023 Identified Upgrade
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.16766 | 180.6221 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.16766 | 180.6221 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.16729 | 183.9678 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.16729 | 183.9678 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | FROM->TO | 640278 SHELDON7 115 3WXFMR 640:MOORE T1 345 1 | B | 400 | 0.23142 | 185.3265 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | TDF Impact | Add 3-winding transformer 640277 MOORE 3 345 640278 SHELDON7 115 640280 MOORE 9 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | FROM->TO | 640278 SHELDON7 115 3WXFMR 640:MOORE T1 345 1 | B | 400 | 0.22973 | 195.4671 | P42:345:NPPD:BKR-MOR-3308:::: | TDF Impact | Add 3-winding transformer 640277 MOORE 3 345 640278 SHELDON7 115 640280 MOORE 9 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | B | 99 | 0.063813 | 222.8106 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | DIS2301_P2_G00_ERIS_2_640_NPPD_TO_1000_DAYKIN_345KV_SUB.idv : DISIS_2023 Identified Upgrade
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | B | 99 | 0.063813 | 222.8106 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | DIS2301_P2_G00_ERIS_3_640_NPPD_TO_2000_add_BPS_345_Lines_Rev34.idv : DISIS_2023 Identified Upgrade
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | B | 99 | 0.06375 | 225.1739 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | DIS2301_P2_G00_ERIS_2_640_NPPD_TO_1000_DAYKIN_345KV_SUB.idv : DISIS_2023 Identified Upgrade
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | B | 99 | 0.06375 | 225.1739 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | DIS2301_P2_G00_ERIS_3_640_NPPD_TO_2000_add_BPS_345_Lines_Rev34.idv : DISIS_2023 Identified Upgrade
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | B | 193 | 0.40312 | 336.4692 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | TDF Impact | Add line 640088 BPS SUB7 115 640278 SHELDON7 115 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | B | 99 | 0.16673 | 337.5032 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | Cumulative Impact | DIS2301_P2_G00_ERIS_2_640_NPPD_TO_1000_DAYKIN_345KV_SUB.idv : DISIS_2023 Identified Upgrade
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | B | 99 | 0.16673 | 337.5032 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | Cumulative Impact | DIS2301_P2_G00_ERIS_3_640_NPPD_TO_2000_add_BPS_345_Lines_Rev34.idv : DISIS_2023 Identified Upgrade
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | B | 140 | 0.31188 | 348.4283 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | TDF Impact | Rebuild line 640111 CLATONA7 115 640278 SHELDON7 115 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | B | 140 | 0.31188 | 354.8766 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | TDF Impact | Rebuild line 640088 BPS SUB7 115 640111 CLATONA7 115 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | FROM->TO | 771999 G23-222-POI 345 3WXFMR 640:BPS_345_115 T1 345 1 | B | 417 | 1 | 393.5711 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | TDF Impact | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | FROM->TO | 771999 G23-222-POI 345 3WXFMR 640:BPS_345_115 T1 345 1 | B | 417 | 0.16295 | 100.483 | P42:345:NPPD:L3502A.MOORE.MCCOOL.CB3310:::: | Cumulative Impact | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | FROM->TO | 771999 G23-222-POI 345 3WXFMR 640:BPS_345_115 T1 345 1 | B | 417 | 0.16295 | 100.483 | P42:345:NPPD:BKR-MOR-3310:::: | Cumulative Impact | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | FROM->TO | 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 | B | 956 | 0.28128 | 100.5447 | P42:345:NPPD:BKR-MOR-3306:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-023 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.047677 | 100.5915 | P23:345:MEC:HIGHLAND:903::EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-023 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.047677 | 100.6154 | P23:345:MEC:HIGHLAND:902::EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-023 | FROM->TO | 645454 S3454 3 345 645455 S3455 3 345 1 | B | 1195 | 0.07637 | 100.6765 | P12:345:OPPD:S3455-S3740:::EHV: | Cumulative Impact | Rebuild line 645454 S3454 3 345 645455 S3455 3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-023 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.045853 | 100.6843 | P12:230.0:UMZ:# N-1 #:: LINE TWIN CH4-SIOUXCY4-1 :HV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-023 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.047677 | 101.5782 | Single 635368 OBRIEN3 345 635400 HIGHLAND3 345 1 | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-023 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.047677 | 101.5782 | P12:345:MEC:OBRIEN:HIGHLAND:1REACTOR:EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | FROM->TO | 640278 SHELDON7 115 650242 FOLSM&PHIL7 115 1 | B | 300 | 0.08 | 101.775 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Rebuild line 640278 SHELDON7 115 650242 FOLSM&PHIL7 115 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-023 | FROM->TO | 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 | B | 956 | 0.26113 | 102.9523 | P42:345:NPPD:BKR-MOR-3306:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-023 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.048353 | 103.0767 | P23:345:MEC:OBRIEN:903::EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-023 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.04855 | 104.0624 | P23:345:MEC:OBRIEN:906::EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-023 | FROM->TO | 771999 G23-222-POI 345 3WXFMR 640:BPS_345_115 T1 345 1 | B | 417 | 0.22042 | 105.8248 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | TDF Impact | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-023 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.034913 | 106.6762 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-023 | FROM->TO | 640125 COLMB.E3 345 3WXFMR 640:COL.EAST T4 345 1 | B | 336 | 0.050004 | 108.1049 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | TDF Impact | Add 3-winding transformer 640125 COLMB.E3 345 640127 COLMB.E7 115 640129 COLMB.T9 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-023 | FROM->TO | 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 | B | 956 | 0.30242 | 108.5368 | P42:345:NPPD:BKR-MOR-3310:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 650189 103&ROKEBY3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-023 | FROM->TO | 640277 MOORE 3 345 650189 103&ROKEBY3 345 1 | B | 956 | 0.30242 | 108.5368 | P42:345:NPPD:L3502A.MOORE.MCCOOL.CB3310:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 650189 103&ROKEBY3 345 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-023 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.03505 | 108.9935 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-023 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.03505 | 109.0153 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-023 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.034923 | 109.4444 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-023 | FROM->TO | 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1 | B | 240 | 0.054249 | 111.1518 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Rebuild line 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-023 | FROM->TO | 640125 COLMB.E3 345 3WXFMR 640:COL.EAST T4 345 1 | B | 336 | 0.048521 | 111.4413 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | TDF Impact | Add 3-winding transformer 640125 COLMB.E3 345 640127 COLMB.E7 115 640129 COLMB.T9 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-023 | FROM->TO | 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1 | B | 956 | 0.26198 | 115.201 | P42:345:NPPD:BKR-MOR-3306:::: | TDF Impact | Rebuild line 640277 MOORE 3 345 650114 NW68HOLDRG3 345 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-023 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.035431 | 118.0094 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-023 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.034552 | 119.5678 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-023 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.034689 | 121.2729 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-023 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.034689 | 121.3014 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-023 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.034542 | 121.5027 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-023 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.066519 | 124.4543 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-023 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.066519 | 124.4543 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-023 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.064932 | 124.734 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-023 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.064932 | 124.734 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-023 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.066824 | 129.5673 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-023 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.066823 | 129.5673 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-023 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.065231 | 130.1714 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-023 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.065232 | 130.1714 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-023 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.035134 | 130.4818 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | A | 99 | 0.038079 | 131.9721 | System Intact | TDF Impact | DIS2301_P2_G00_ERIS_2_640_NPPD_TO_1000_DAYKIN_345KV_SUB.idv : DISIS_2023 Identified Upgrade
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | A | 99 | 0.038079 | 131.9721 | System Intact | TDF Impact | DIS2301_P2_G00_ERIS_3_640_NPPD_TO_2000_add_BPS_345_Lines_Rev34.idv : DISIS_2023 Identified Upgrade
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | FROM->TO | 640235 HUMBOLT7 115 3WXFMR 640:HUMBOLDT T2 161 1 | B | 126 | 0.11827 | 137.8984 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | Cumulative Impact | Add 3-winding transformer 640234 HUMBOLT5 161 640235 HUMBOLT7 115 643087 HUMBOLDT T29 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-023 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.034372 | 146.377 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-023 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.034525 | 148.5944 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-023 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.034525 | 148.6147 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-023 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.034382 | 148.9728 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | FROM->TO | 640076 BEATRCE7 115 640361 STEINER7 115 1 | B | 121 | 0.11827 | 154.0683 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | Cumulative Impact | Rebuild line 640076 BEATRCE7 115 640361 STEINER7 115 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | FROM->TO | 640169 FAIRBRY7 115 640218 HEBRN N7 115 1 | B | 99 | 0.087347 | 155.7041 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | Cumulative Impact | Rebuild line 640169 FAIRBRY7 115 640218 HEBRN N7 115 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | FROM->TO | 771999 G23-222-POI 345 3WXFMR 640:BPS_345_115 T1 345 1 | B | 417 | 0.23297 | 159.9374 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | TDF Impact | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-023 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.035021 | 159.9633 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | FROM->TO | 771999 G23-222-POI 345 3WXFMR 640:BPS_345_115 T1 345 1 | B | 417 | 0.23284 | 161.1357 | P42:345:NPPD:BKR-MOR-3308:::: | TDF Impact | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | FROM->TO | 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1 | B | 240 | 0.10464 | 161.4982 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Rebuild line 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | FROM->TO | 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1 | B | 240 | 0.1042 | 166.5845 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Rebuild line 640591 OLIVECREEK 7 115 650246 SW7&BENNET7 115 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | B | 99 | 0.050016 | 167.9201 | P42:345:NPPD:BKR-MOR-3312:::: | Cumulative Impact | DIS2301_P2_G00_ERIS_2_640_NPPD_TO_1000_DAYKIN_345KV_SUB.idv : DISIS_2023 Identified Upgrade
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | B | 99 | 0.050016 | 167.9201 | P42:345:NPPD:BKR-MOR-3312:::: | Cumulative Impact | DIS2301_P2_G00_ERIS_3_640_NPPD_TO_2000_add_BPS_345_Lines_Rev34.idv : DISIS_2023 Identified Upgrade
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.16766 | 180.6221 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.16766 | 180.6221 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.16729 | 183.9678 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | FROM->TO | 640590 OLIVECREEK 3 345 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.16729 | 183.9678 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | FROM->TO | 640278 SHELDON7 115 3WXFMR 640:MOORE T1 345 1 | B | 400 | 0.23142 | 185.3265 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | TDF Impact | Add 3-winding transformer 640277 MOORE 3 345 640278 SHELDON7 115 640280 MOORE 9 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | FROM->TO | 640278 SHELDON7 115 3WXFMR 640:MOORE T1 345 1 | B | 400 | 0.22973 | 195.4671 | P42:345:NPPD:BKR-MOR-3308:::: | TDF Impact | Add 3-winding transformer 640277 MOORE 3 345 640278 SHELDON7 115 640280 MOORE 9 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | B | 99 | 0.063813 | 222.8106 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | DIS2301_P2_G00_ERIS_2_640_NPPD_TO_1000_DAYKIN_345KV_SUB.idv : DISIS_2023 Identified Upgrade
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | B | 99 | 0.063813 | 222.8106 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | DIS2301_P2_G00_ERIS_3_640_NPPD_TO_2000_add_BPS_345_Lines_Rev34.idv : DISIS_2023 Identified Upgrade
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | B | 99 | 0.06375 | 225.1739 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | DIS2301_P2_G00_ERIS_2_640_NPPD_TO_1000_DAYKIN_345KV_SUB.idv : DISIS_2023 Identified Upgrade
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | B | 99 | 0.06375 | 225.1739 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | DIS2301_P2_G00_ERIS_3_640_NPPD_TO_2000_add_BPS_345_Lines_Rev34.idv : DISIS_2023 Identified Upgrade
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | FROM->TO | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | B | 193 | 0.40312 | 336.4692 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | TDF Impact | Add line 640088 BPS SUB7 115 640278 SHELDON7 115 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | B | 99 | 0.16673 | 337.5032 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | Cumulative Impact | DIS2301_P2_G00_ERIS_2_640_NPPD_TO_1000_DAYKIN_345KV_SUB.idv : DISIS_2023 Identified Upgrade
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | FROM->TO | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | B | 99 | 0.16673 | 337.5032 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | Cumulative Impact | DIS2301_P2_G00_ERIS_3_640_NPPD_TO_2000_add_BPS_345_Lines_Rev34.idv : DISIS_2023 Identified Upgrade
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | FROM->TO | 640111 CLATONA7 115 640278 SHELDON7 115 1 | B | 140 | 0.31188 | 348.4283 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | TDF Impact | Rebuild line 640111 CLATONA7 115 640278 SHELDON7 115 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | FROM->TO | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | B | 140 | 0.31188 | 354.8766 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | TDF Impact | Rebuild line 640088 BPS SUB7 115 640111 CLATONA7 115 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | FROM->TO | 771999 G23-222-POI 345 3WXFMR 640:BPS_345_115 T1 345 1 | B | 417 | 1 | 393.5711 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | TDF Impact | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-025 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | B | 1220 | 0.26302 | 105.5159 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | Rebuild line 508359 WELSH 7 345 508841 WILKES 7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-025 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | B | 1000 | 0.26264 | 116.8554 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | Rebuild line 508359 WELSH 7 345 508841 WILKES 7 345 1
Thermal | 01ALL | 1 | 26SP | T0 | GEN-2024-035 | FROM->TO | 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1 | B | 119 | 0.13093 | 109.0564 | P12:345.0:UMZ:# N-1 #:: LINE GROTON__-BE3-CROCKER_-BE3-1 :EHV: | Cumulative Impact | Rebuild line 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1
Thermal | 01ALL | 1 | 26SP | T0 | GEN-2024-035 | FROM->TO | 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1 | B | 119 | 0.13093 | 110.6095 | P23:345:UMZB:# 7110 #:: CKE IN SD. CKE BREAKER FAULT (192):EHV: | Cumulative Impact | Rebuild line 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1
Thermal | 01ALL | 1 | 29SP | T0 | GEN-2024-035 | FROM->TO | 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1 | B | 119 | 0.13097 | 111.8115 | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-CROCKER_-BE3-1 :EHV: | Cumulative Impact | Rebuild line 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1
Thermal | 01ALL | 1 | 26SP | T0 | GEN-2024-035 | FROM->TO | 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1 | B | 119 | 0.13093 | 123.7796 | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-CROCKER_-BE3-1 :EHV: | Cumulative Impact | Rebuild line 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-035 | FROM->TO | 652512 GROTON 7 115 660001 ABR SIEBRCHT 115 1 | B | 180.3 | 0.043007 | 133.08 | P12:230:MDU:ELLENDALE:ELLENDALE345:Z: | TDF Impact | Rebuild line 652512 GROTON 7 115 660001 ABR SIEBRCHT 115 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-035 | FROM->TO | 652512 GROTON 7 115 660001 ABR SIEBRCHT 115 1 | B | 180.3 | 0.043395 | 133.41 | P12:230:MDU:ELLENDALE:ELLENDALE345:Z: | TDF Impact | Rebuild line 652512 GROTON 7 115 660001 ABR SIEBRCHT 115 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-035 | FROM->TO | 652512 GROTON 7 115 660001 ABR SIEBRCHT 115 1 | B | 180.3 | 0.042649 | 134.04 | P12:230:MDU:ELLENDALE:ELLENDALE345:Z: | TDF Impact | Rebuild line 652512 GROTON 7 115 660001 ABR SIEBRCHT 115 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-041 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063539 | 100.0488 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-041 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.06007 | 100.533 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-041 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.06472 | 103.9266 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-041 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.06719 | 104.7552 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-041 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.06719 | 104.888 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-041 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.068321 | 107.2243 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-041 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.061064 | 107.2793 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-041 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.061064 | 107.2794 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-041 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.068321 | 107.2951 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-041 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.061064 | 107.3093 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-041 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.061064 | 107.7557 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-041 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.061064 | 108.2747 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-041 | FROM->TO | 523961 POTTER_CO 7 345 3WXFMR 526:WAUK 90343-A 230 1 | B | 559 | 0.058962 | 108.8994 | P42:345:SPS:HITCHLAND-1R15:::EHV: | Cumulative Impact | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-041 | FROM->TO | 523961 POTTER_CO 7 345 3WXFMR 526:WAUK 90343-A 230 1 | B | 559 | 0.058962 | 108.9122 | Single 523097 HITCHLAND7 345 523961 POTTER_CO7 345 1 | Cumulative Impact | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-041 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.061064 | 111.3621 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-041 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.064672 | 115.0541 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-041 | FROM->TO | 511468 L.E.S.-7 345 3WXFMR 520:LES 5 345 2 | B | 515 | 0.030947 | 115.3782 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | TDF Impact | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-041 | FROM->TO | 511468 L.E.S.-7 345 3WXFMR 520:LES 5 345 2 | B | 515 | 0.03192 | 116.8526 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | TDF Impact | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-041 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.068348 | 118.9427 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-041 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.068348 | 119.313 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-042 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063539 | 100.0488 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-042 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.06007 | 100.533 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-042 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.06472 | 103.9266 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-042 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.06719 | 104.7552 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-042 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.06719 | 104.888 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-042 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.068321 | 107.2243 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-042 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.061064 | 107.2793 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-042 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.061064 | 107.2794 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-042 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.068321 | 107.2951 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-042 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.061064 | 107.3093 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-042 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.061064 | 107.7557 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-042 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.061064 | 108.2747 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-042 | FROM->TO | 523961 POTTER_CO 7 345 3WXFMR 526:WAUK 90343-A 230 1 | B | 559 | 0.058962 | 108.8994 | P42:345:SPS:HITCHLAND-1R15:::EHV: | Cumulative Impact | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-042 | FROM->TO | 523961 POTTER_CO 7 345 3WXFMR 526:WAUK 90343-A 230 1 | B | 559 | 0.058962 | 108.9122 | Single 523097 HITCHLAND7 345 523961 POTTER_CO7 345 1 | Cumulative Impact | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-042 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.061064 | 111.3621 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-042 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.064672 | 115.0541 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-042 | FROM->TO | 511468 L.E.S.-7 345 3WXFMR 520:LES 5 345 2 | B | 515 | 0.030947 | 115.3782 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | TDF Impact | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-042 | FROM->TO | 511468 L.E.S.-7 345 3WXFMR 520:LES 5 345 2 | B | 515 | 0.03192 | 116.8526 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | TDF Impact | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-042 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.068348 | 118.9427 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-042 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.068348 | 119.313 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-043 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.073998 | 100.0488 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29L | T0 | GEN-2024-043 | FROM->TO | 511541 DEMPSEYR POI 230 511557 CHISHOLM6 230 1 | B | 439 | 0.068189 | 100.3116 | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | Cumulative Impact | Rebuild line 511541 DEMPSEYR POI 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-043 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063318 | 100.533 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-043 | FROM->TO | 523959 POTTER_CO 6 230 524010 ROLLHILLS 6 230 1 | B | 548 | 0.057735 | 103.4659 | MULTIGEN523979 | Cumulative Impact | Rebuild line 523959 POTTER_CO 6 230 524010 ROLLHILLS 6 230 1
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-043 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.078508 | 103.9266 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-043 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.076983 | 104.7552 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-043 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.076983 | 104.888 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-043 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.081431 | 107.2243 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-043 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.06414 | 107.2793 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-043 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.06414 | 107.2794 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-043 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.081431 | 107.2951 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-043 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.06414 | 107.3093 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-043 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.06414 | 107.7557 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-043 | FROM->TO | 531512 HARBNGR7 345 3WXFMR 534:HARBGR345 345 1 | B | 385 | 0.050062 | 107.8261 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Add 3-winding transformer 531510 HARBNGR3 115 531511 HARBNGR-1 13 531512 HARBNGR7 345 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-043 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.06414 | 108.2747 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-043 | FROM->TO | 523961 POTTER_CO 7 345 3WXFMR 526:WAUK 90343-A 230 1 | B | 559 | 0.14831 | 108.8994 | P42:345:SPS:HITCHLAND-1R15:::EHV: | Cumulative Impact | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-043 | FROM->TO | 523961 POTTER_CO 7 345 3WXFMR 526:WAUK 90343-A 230 1 | B | 559 | 0.14831 | 108.9122 | Single 523097 HITCHLAND7 345 523961 POTTER_CO7 345 1 | Cumulative Impact | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-043 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.06414 | 111.3621 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-043 | FROM->TO | 523959 POTTER_CO 6 230 524010 ROLLHILLS 6 230 1 | B | 548 | 0.052204 | 114.0984 | MULTIGEN523978 | Cumulative Impact | Rebuild line 523959 POTTER_CO 6 230 524010 ROLLHILLS 6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-043 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.075003 | 115.0541 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-043 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.078004 | 118.9427 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-043 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.078004 | 119.313 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-051 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.055105 | 100.5915 | P23:345:MEC:HIGHLAND:903::EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-051 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.055105 | 100.6154 | P23:345:MEC:HIGHLAND:902::EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-051 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.051775 | 100.6843 | P12:230.0:UMZ:# N-1 #:: LINE TWIN CH4-SIOUXCY4-1 :HV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-051 | FROM->TO | 652564 SIOUXCY3 345 3WXFMR 652:652: SC2 KU1B 230 1 | B | 750 | 0.033131 | 100.7724 | P23:345:XEL:396 BKR SPK:::EHV: | TDF Impact | Add 3-winding transformer 652305 SIOUXC29 13 652552 SIOUXCY2 230 652564 SIOUXCY3 345 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-051 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.055105 | 101.5782 | Single 635368 OBRIEN3 345 635400 HIGHLAND3 345 1 | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-051 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.055105 | 101.5782 | P12:345:MEC:OBRIEN:HIGHLAND:1REACTOR:EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-051 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.10434 | 101.6704 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-051 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.055813 | 103.0767 | P23:345:MEC:OBRIEN:903::EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-051 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.055976 | 104.0624 | P23:345:MEC:OBRIEN:906::EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-051 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | A | 110 | 0.10605 | 105.8619 | System Intact | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-051 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.11043 | 106.3207 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-051 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.12476 | 106.6762 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-051 | FROM->TO | 640125 COLMB.E3 345 3WXFMR 640:COL.EAST T4 345 1 | B | 336 | 0.044935 | 108.1049 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | TDF Impact | Add 3-winding transformer 640125 COLMB.E3 345 640127 COLMB.E7 115 640129 COLMB.T9 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-051 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.12495 | 108.9935 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-051 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.12495 | 109.0153 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-051 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.12585 | 109.4444 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-051 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.10747 | 110.3426 | P42:345:LES:L1485::NW68&HOLDREGE.WAGENER.CB3006:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-051 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.1063 | 111.0459 | P13:161-345:OPPD:TX01::S3454.CKT1:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-051 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.1063 | 111.0459 | P13:161-345:OPPD:S1254 T1:::HV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-051 | FROM->TO | 640125 COLMB.E3 345 3WXFMR 640:COL.EAST T4 345 1 | B | 336 | 0.043428 | 111.4413 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | TDF Impact | Add 3-winding transformer 640125 COLMB.E3 345 640127 COLMB.E7 115 640129 COLMB.T9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-051 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.10985 | 117.1294 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-051 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.12508 | 118.0094 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-051 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.12425 | 119.5678 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-051 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.12443 | 121.2729 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-051 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.12443 | 121.3014 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-051 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.1253 | 121.5027 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-051 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.10445 | 125.7992 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-051 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.12462 | 130.4818 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-051 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.12414 | 146.377 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-051 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.10992 | 148.4763 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-051 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.12434 | 148.5944 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-051 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.12434 | 148.6147 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-051 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.12522 | 148.9728 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-051 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.12459 | 159.9633 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-054 | FROM->TO | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.05078 | 111.8275 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-055 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | B | 756 | 0.09042 | 101.463 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild line 541200 PHILL 7 345 541201 SIBLEY 7 345 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-055 | FROM->TO | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.06118 | 111.8275 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-055 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | B | 756 | 0.092518 | 117.5821 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild line 541200 PHILL 7 345 541201 SIBLEY 7 345 1
Thermal | 04ALL | 1 | 29SP | T1 | GEN-2024-056 | FROM->TO | 532768 EMPEC 7 345 776400 G23-221-TAP 345 1 | A | 1076 | 0.030791 | 100.907 | System Intact | TDF Impact | Rebuild line 532768 EMPEC 7 345 776400 G23-221-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T1 | GEN-2024-056 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.03266 | 103.0993 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T1 | GEN-2024-056 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.035766 | 103.3038 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-056 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | A | 1187 | 0.048972 | 103.8656 | System Intact | TDF Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-056 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.053877 | 104.9177 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-056 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.064228 | 106.1409 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-056 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.053587 | 106.3238 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-056 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.0559 | 106.5158 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-056 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.06357 | 107.841 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-056 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.0559 | 108.059 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-056 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.06357 | 109.5335 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-056 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.06357 | 109.534 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-056 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.06357 | 112.0538 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-056 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.078816 | 114.5102 | System Intact | TDF Impact | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-056 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.073426 | 114.6214 | System Intact | TDF Impact | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-056 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.06357 | 116.5975 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-056 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.040973 | 119.3706 | System Intact | TDF Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-056 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.040973 | 119.3706 | System Intact | TDF Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-056 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.040973 | 119.3706 | System Intact | TDF Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-056 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.037713 | 119.5141 | System Intact | TDF Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-056 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.037713 | 119.5141 | System Intact | TDF Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-056 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.037713 | 119.5141 | System Intact | TDF Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-056 | FROM->TO | 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 | A | 194 | 0.040966 | 124.6163 | System Intact | TDF Impact | Rebuild line 514759 NEWKIRK4 138 515381 PECKHMT4 138 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-056 | FROM->TO | 514759 NEWKIRK4 138 515381 PECKHMT4 138 1 | A | 194 | 0.041195 | 124.7711 | System Intact | TDF Impact | Rebuild line 514759 NEWKIRK4 138 515381 PECKHMT4 138 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-056 | FROM->TO | 514760 KILDARE4 138 514764 NWKRKAT4 138 1 | A | 194 | 0.040966 | 131.4149 | System Intact | TDF Impact | Rebuild line 514760 KILDARE4 138 514764 NWKRKAT4 138 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-056 | FROM->TO | 514760 KILDARE4 138 514764 NWKRKAT4 138 1 | A | 194 | 0.041195 | 131.5644 | System Intact | TDF Impact | Rebuild line 514760 KILDARE4 138 514764 NWKRKAT4 138 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-056 | FROM->TO | 514804 MIDLTNT4 138 532981 CRESWLN4 138 1 | A | 194 | 0.041195 | 132.7096 | System Intact | TDF Impact | Rebuild line 514804 MIDLTNT4 138 532981 CRESWLN4 138 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-056 | FROM->TO | 514804 MIDLTNT4 138 532981 CRESWLN4 138 1 | A | 194 | 0.040966 | 132.8517 | System Intact | TDF Impact | Rebuild line 514804 MIDLTNT4 138 532981 CRESWLN4 138 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-056 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.053785 | 140.3415 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-056 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.053785 | 140.3415 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-056 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.053785 | 140.3415 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-056 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.053252 | 142.6431 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-056 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.053252 | 142.6431 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-056 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.053252 | 142.6431 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-056 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.053252 | 145.1309 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-056 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.053252 | 145.1309 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-056 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.053252 | 145.1309 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-056 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.053252 | 145.1356 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-056 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.053252 | 145.1356 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-056 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.053252 | 145.1356 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-056 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.053252 | 148.805 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-056 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.053252 | 148.805 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-056 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.053252 | 148.805 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-056 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.053252 | 155.6146 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-056 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.053252 | 155.6146 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-056 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.053252 | 155.6146 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 02ALL | 1 | 29SP | T0 | GEN-2024-065 | FROM->TO | 640173 FREMONT7 115 3WXFMR 640:FREMONT T4 115 1 | B | 56 | 0.18159 | 100.0935 | GEN647418 8 | Cumulative Impact | Fremont_Add_transformer_fixed.idv :
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-065 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.044682 | 100.5915 | P23:345:MEC:HIGHLAND:903::EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-065 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.044682 | 100.6154 | P23:345:MEC:HIGHLAND:902::EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-065 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.061367 | 100.6843 | P12:230.0:UMZ:# N-1 #:: LINE TWIN CH4-SIOUXCY4-1 :HV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 02ALL | 1 | 29WP | T0 | GEN-2024-065 | FROM->TO | 640173 FREMONT7 115 3WXFMR 640:FREMONT T4 115 1 | B | 56 | 0.18146 | 101.175 | P13:069:OPPD:FREM 8G:::HV: | Cumulative Impact | Fremont_Add_transformer_fixed.idv :
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-065 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.044682 | 101.5782 | Single 635368 OBRIEN3 345 635400 HIGHLAND3 345 1 | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-065 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.044682 | 101.5782 | P12:345:MEC:OBRIEN:HIGHLAND:1REACTOR:EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 02ALL | 1 | 29SP | T0 | GEN-2024-065 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | B | 320 | 0.06839 | 101.6588 | Single 635200 RAUN3 345 635214 J279NEAL4G 24 1 | Cumulative Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 02ALL | 1 | 29SP | T0 | GEN-2024-065 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | B | 320 | 0.06839 | 101.6588 | P11:345:MEC:NEAL:4 | Cumulative Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 02ALL | 1 | 26SP | T0 | GEN-2024-065 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | B | 320 | 0.070982 | 101.7487 | P13:345-230.0:UMZ:# N-1 #:: 3WND SIOUXCY3-SIOUXCY2-SIOUXC29-1 652_ SC2 KU1B_:EHV: | Cumulative Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 02ALL | 1 | 29SP | T0 | GEN-2024-065 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | B | 320 | 0.066233 | 101.8142 | Single 640226 HOSKINS3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 02ALL | 1 | 29SP | T0 | GEN-2024-065 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | B | 320 | 0.066233 | 101.8163 | Single 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 02ALL | 1 | 29SP | T0 | GEN-2024-065 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | B | 320 | 0.068389 | 103.0404 | P55:345:XEL:PRI1 | Cumulative Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-065 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.045296 | 103.0767 | P23:345:MEC:OBRIEN:903::EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 02ALL | 1 | 29SP | T0 | GEN-2024-065 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | B | 320 | 0.06839 | 103.4776 | Single 640425 S.SIOUXCITY8 69 640424 S.SIOUXCITY7 115 643170 'S.SIOUXCYT19' 13 1 | Cumulative Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 02ALL | 1 | 29WP | T0 | GEN-2024-065 | FROM->TO | 640173 FREMONT7 115 3WXFMR 640:FREMONT T4 115 1 | B | 56 | 0.18146 | 103.7079 | GEN647418 8 | Cumulative Impact | Fremont_Add_transformer_fixed.idv :
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-065 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.045117 | 104.0624 | P23:345:MEC:OBRIEN:906::EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 02ALL | 1 | 29SP | T0 | GEN-2024-065 | FROM->TO | 640173 FREMONT7 115 3WXFMR 640:FREMONT T1 115 1 | B | 63 | 0.1998 | 104.265 | GEN647418 8 | Cumulative Impact | Fremont_Add_transformer_fixed.idv :
Thermal | 02ALL | 1 | 29WP | T0 | GEN-2024-065 | FROM->TO | 640173 FREMONT7 115 3WXFMR 640:FREMONT T1 115 1 | B | 63 | 0.19966 | 104.7388 | P13:069:OPPD:FREM 8G:::HV: | Cumulative Impact | Fremont_Add_transformer_fixed.idv :
Thermal | 02ALL | 1 | 29SP | T0 | GEN-2024-065 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | B | 320 | 0.06385 | 105.8279 | P13:345-230.0:UMZ:# N-1 #:: 3WND SIOUXCY3-SIOUXCY2-SIOUXC29-1 652_ SC2 KU1B_:EHV: | Cumulative Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 02ALL | 1 | 29WP | T0 | GEN-2024-065 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | A | 320 | 0.068106 | 107.0771 | System Intact | TDF Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 02ALL | 1 | 29WP | T0 | GEN-2024-065 | FROM->TO | 640173 FREMONT7 115 3WXFMR 640:FREMONT T1 115 1 | B | 63 | 0.19966 | 107.5489 | GEN647418 8 | Cumulative Impact | Fremont_Add_transformer_fixed.idv :
Thermal | 02ALL | 1 | 26SP | T0 | GEN-2024-065 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | B | 320 | 0.091417 | 109.1304 | Single 635200 RAUN3 345 640226 HOSKINS3 345 1 | Cumulative Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 02ALL | 1 | 26SP | T0 | GEN-2024-065 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | B | 320 | 0.079371 | 109.5852 | P12:345.0:UMZ:# N-1 #:: LINE RAUN 3-SIOUXCY3-1 :EHV: | Cumulative Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 02ALL | 1 | 29WP | T0 | GEN-2024-065 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | B | 320 | 0.065919 | 113.5344 | Single 640226 HOSKINS3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 02ALL | 1 | 29WP | T0 | GEN-2024-065 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | B | 320 | 0.065919 | 113.5475 | Single 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 02ALL | 1 | 29WP | T0 | GEN-2024-065 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | B | 320 | 0.06867 | 114.1774 | P55:345:MEC:ORIENT | Cumulative Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 02ALL | 1 | 29WP | T0 | GEN-2024-065 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | B | 320 | 0.069961 | 114.4083 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOMP3-FTTHOM2-LNX3-Z :EHV: | Cumulative Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 02ALL | 1 | 29WP | T0 | GEN-2024-065 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | B | 320 | 0.069961 | 114.4096 | P12:345.0:UMZ:# N-1 #:: LINE GR PRAIRIE 3-GRPRAR2-LNX3-Z :EHV: | Cumulative Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 02ALL | 1 | 29WP | T0 | GEN-2024-065 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | B | 320 | 0.069961 | 114.4098 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOM2-LNX3-GRPRAR2-LNX3-1 :EHV: | Cumulative Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 02ALL | 1 | 29WP | T0 | GEN-2024-065 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | B | 320 | 0.068105 | 114.4544 | P55:345:XEL:PRI1 | Cumulative Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 02ALL | 1 | 29WP | T0 | GEN-2024-065 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | B | 320 | 0.068106 | 115.3828 | Single 640425 S.SIOUXCITY8 69 640424 S.SIOUXCITY7 115 643170 'S.SIOUXCYT19' 13 1 | Cumulative Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 02ALL | 1 | 29SP | T0 | GEN-2024-065 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | B | 320 | 0.076043 | 116.5719 | Single 635200 RAUN3 345 640226 HOSKINS3 345 1 | Cumulative Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 02ALL | 1 | 29SP | T0 | GEN-2024-065 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | B | 320 | 0.071115 | 116.7129 | P12:345.0:UMZ:# N-1 #:: LINE RAUN 3-SIOUXCY3-1 :EHV: | Cumulative Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 02ALL | 1 | 29WP | T0 | GEN-2024-065 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | B | 320 | 0.07075 | 118.405 | P12:345.0:UMZ:# N-1 #:: LINE RAUN 3-SIOUXCY3-1 :EHV: | Cumulative Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 02ALL | 1 | 26SP | T0 | GEN-2024-065 | FROM->TO | 640173 FREMONT7 115 3WXFMR 640:FREMONT T1 115 1 | B | 63 | 0.32848 | 126.4086 | P13:069-115:NPPD:FREMONT T4:::HV: | TDF Impact | Fremont_Add_transformer_fixed.idv :
Thermal | 02ALL | 1 | 29SP | T0 | GEN-2024-065 | FROM->TO | 640173 FREMONT7 115 3WXFMR 640:FREMONT T1 115 1 | B | 63 | 0.3266 | 129.3815 | P13:069-115:NPPD:FREMONT T4:::HV: | TDF Impact | Fremont_Add_transformer_fixed.idv :
Thermal | 02ALL | 1 | 29WP | T0 | GEN-2024-065 | FROM->TO | 640173 FREMONT7 115 3WXFMR 640:FREMONT T1 115 1 | B | 63 | 0.32642 | 132.5504 | P13:069-115:NPPD:FREMONT T4:::HV: | TDF Impact | Fremont_Add_transformer_fixed.idv :
Thermal | 02ALL | 1 | 26SP | T0 | GEN-2024-065 | FROM->TO | 640173 FREMONT7 115 3WXFMR 640:FREMONT T4 115 1 | B | 56 | 0.31874 | 133.698 | Single 647976 S9768 69 640173 FREMONT7 115 643058 'FREMONT T1 9' 13 1 | TDF Impact | Fremont_Add_transformer_fixed.idv :
Thermal | 02ALL | 1 | 29WP | T0 | GEN-2024-065 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | B | 320 | 0.075602 | 136.3055 | Single 635200 RAUN3 345 640226 HOSKINS3 345 1 | Cumulative Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 02ALL | 1 | 29SP | T0 | GEN-2024-065 | FROM->TO | 640173 FREMONT7 115 3WXFMR 640:FREMONT T4 115 1 | B | 56 | 0.3169 | 136.8298 | Single 647976 S9768 69 640173 FREMONT7 115 643058 'FREMONT T1 9' 13 1 | TDF Impact | Fremont_Add_transformer_fixed.idv :
Thermal | 02ALL | 1 | 29WP | T0 | GEN-2024-065 | FROM->TO | 640173 FREMONT7 115 3WXFMR 640:FREMONT T4 115 1 | B | 56 | 0.31672 | 140.8163 | Single 647976 S9768 69 640173 FREMONT7 115 643058 'FREMONT T1 9' 13 1 | TDF Impact | Fremont_Add_transformer_fixed.idv :
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-067 | FROM->TO | 539658 CONCRD6 230 3WXFMR 534:CONCORD6 230 1 | B | 225.5 | 0.088333 | 107.4002 | Single 539805 ELMCREEK7 345 640600 DAYKIN3 345 1 | Cumulative Impact | Add 3-winding transformer 539657 CONCORD3 115 539658 CONCRD6 230 539904 CONCOD-1 13 M2
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-067 | FROM->TO | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.059009 | 111.8275 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-068 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | B | 1220 | 0.29089 | 105.5159 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | Rebuild line 508359 WELSH 7 345 508841 WILKES 7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-068 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | B | 1000 | 0.29061 | 116.8554 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | Rebuild line 508359 WELSH 7 345 508841 WILKES 7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-071 | FROM->TO | 508814 RODESSA2 69 508846 GODFREYRDTP2 69 1 | B | 53 | 0.10928 | 100.2066 | P42:345:AEPW:WILKES CB 1W10 NBTB+FAULT:::: | Cumulative Impact | Rebuild line 508814 RODESSA2 69 508846 GODFREYRDTP2 69 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-071 | FROM->TO | 508814 RODESSA2 69 508846 GODFREYRDTP2 69 1 | B | 53 | 0.10844 | 100.31 | P12:345:AEPW:LONGWD7:WILKES7::: | Cumulative Impact | Rebuild line 508814 RODESSA2 69 508846 GODFREYRDTP2 69 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-071 | FROM->TO | 508814 RODESSA2 69 508846 GODFREYRDTP2 69 1 | B | 65 | 0.40372 | 100.3955 | P12:69:AEPW:WATLANT2:LINDEN 2::: | TDF Impact | Rebuild line 508814 RODESSA2 69 508846 GODFREYRDTP2 69 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-071 | FROM->TO | 508814 RODESSA2 69 508846 GODFREYRDTP2 69 1 | B | 53 | 0.10877 | 100.487 | P23:345:AEPW:LONGWOOD CB 1N60 NBTB:::: | Cumulative Impact | Rebuild line 508814 RODESSA2 69 508846 GODFREYRDTP2 69 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-071 | FROM->TO | 508814 RODESSA2 69 508846 GODFREYRDTP2 69 1 | B | 53 | 0.40377 | 101.3242 | Single 508089 WATLANT2 69 779100 G24-071-TAP 69 1 | TDF Impact | Rebuild line 508814 RODESSA2 69 508846 GODFREYRDTP2 69 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-071 | FROM->TO | 508814 RODESSA2 69 508846 GODFREYRDTP2 69 1 | B | 53 | 0.40382 | 101.8575 | P12:69:AEPW:WATLANT2:LINDEN 2::: | TDF Impact | Rebuild line 508814 RODESSA2 69 508846 GODFREYRDTP2 69 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-071 | FROM->TO | 508814 RODESSA2 69 508846 GODFREYRDTP2 69 1 | B | 53 | 0.10508 | 108.3659 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | Cumulative Impact | Rebuild line 508814 RODESSA2 69 508846 GODFREYRDTP2 69 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-071 | FROM->TO | 508814 RODESSA2 69 508846 GODFREYRDTP2 69 1 | B | 53 | 0.40274 | 112.6016 | Single 508089 WATLANT2 69 779100 G24-071-TAP 69 1 | TDF Impact | Rebuild line 508814 RODESSA2 69 508846 GODFREYRDTP2 69 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-071 | FROM->TO | 508814 RODESSA2 69 508846 GODFREYRDTP2 69 1 | B | 53 | 0.40279 | 113.2563 | P12:69:AEPW:WATLANT2:LINDEN 2::: | TDF Impact | Rebuild line 508814 RODESSA2 69 508846 GODFREYRDTP2 69 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-074 | FROM->TO | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.068106 | 104.394 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-074 | FROM->TO | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.075589 | 111.8275 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-076 | FROM->TO | 532793 NEOSHO 7 345 3WXFMR 536:N345 TX-2 161 2 | B | 550 | 0.077001 | 101.4582 | Single 533021 NEOSHO4 138 533023 N34534 138 1 | TDF Impact | Add 3-winding transformer 532793 NEOSHO 7 345 532825 N345 2 1 13 532939 N345 4 5 161 M2
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-076 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | B | 756 | 0.076767 | 101.463 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild line 541200 PHILL 7 345 541201 SIBLEY 7 345 1
Thermal | 00NR | 1 | 29WP | T1 | GEN-2024-076 | FROM->TO | 532937 NEOSHO 5 161 764310 G20-079-TAP 161 1 | B | 533 | 0.053249 | 101.6771 | P23:345:AECI:7BLACKBERRY:653::: | TDF Impact | Rebuild line 532937 NEOSHO 5 161 764310 G20-079-TAP 161 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-076 | FROM->TO | 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | B | 956 | 0.086204 | 101.9427 | P23:345:AECI:7BLACKBERRY:6_2::: | Cumulative Impact | Rebuild line 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-076 | FROM->TO | 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | B | 956 | 0.086204 | 101.9438 | P23:345:AECI:7BLACKBERRY:6_3::: | Cumulative Impact | Rebuild line 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-076 | FROM->TO | 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | B | 956 | 0.078709 | 103.0407 | Single 300739 7BLACKBERRY 345 785580 G24-287-TAP 345 1 | Cumulative Impact | Rebuild line 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-076 | FROM->TO | 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | B | 956 | 0.080345 | 103.5013 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Rebuild line 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-076 | FROM->TO | 532793 NEOSHO 7 345 3WXFMR 536:N345 TX-2 161 2 | B | 550 | 0.082919 | 103.5308 | Single 533021 NEOSHO4 138 533023 N34534 138 1 | TDF Impact | Add 3-winding transformer 532793 NEOSHO 7 345 532825 N345 2 1 13 532939 N345 4 5 161 M2
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-076 | FROM->TO | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.21651 | 104.394 | P23:345:AECI:7BLACKBERRY:653::: | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-076 | FROM->TO | 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | B | 956 | 0.083394 | 105.9563 | P23:345:AECI:7BLACKBERRY:6_2::: | Cumulative Impact | Rebuild line 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-076 | FROM->TO | 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | B | 956 | 0.083394 | 105.9589 | P23:345:AECI:7BLACKBERRY:6_3::: | Cumulative Impact | Rebuild line 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-076 | FROM->TO | 532793 NEOSHO 7 345 3WXFMR 536:N345 TX-2 161 2 | B | 550 | 0.082767 | 111.3295 | Single 533021 NEOSHO4 138 533023 N34534 138 1 | TDF Impact | Add 3-winding transformer 532793 NEOSHO 7 345 532825 N345 2 1 13 532939 N345 4 5 161 M2
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-076 | FROM->TO | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.19043 | 111.8275 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-076 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | B | 756 | 0.077955 | 117.5821 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild line 541200 PHILL 7 345 541201 SIBLEY 7 345 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-081 | FROM->TO | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z | B | 506 | 0.26895 | 100.5821 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Rebuild line 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | A | 600 | 0.20744 | 100.9191 | System Intact | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | A | 600 | 0.20744 | 100.9191 | System Intact | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | A | 600 | 0.20744 | 100.9191 | System Intact | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.2042 | 101.5268 | 259421 | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.2042 | 101.5268 | 259421 | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.2042 | 101.5268 | 259421 | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.2042 | 101.9222 | 259422 | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.2042 | 101.9222 | 259698 | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.2042 | 101.9222 | 259422 | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.2042 | 101.9222 | 259698 | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.2042 | 101.9222 | 259422 | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.2042 | 101.9222 | 259698 | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.2042 | 101.9222 | P12:230:SASK:230KV-G1P-FUT:::HV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.2042 | 101.9222 | P12:230:SASK:230KV-G1P-FUT:::HV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.2042 | 101.9222 | P12:230:SASK:230KV-G1P-FUT:::HV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.2042 | 101.937 | P11:13.8:SASK:CHNK #1 GT:::HV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.2042 | 101.937 | P11:13.8:SASK:CHNK #1 GT:::HV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.2042 | 101.937 | P11:13.8:SASK:CHNK #1 GT:::HV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.32319 | 102.1082 | 279736 | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.32319 | 102.1082 | 279736 | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.32319 | 102.1082 | 279736 | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | FROM->TO | 337909 8ANO% 500 515305 FTSMITH8 500 1 | B | 1299 | 0.077604 | 102.9598 | P52:345:AEPW:NR4PITTSB-7:::: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | FROM->TO | 659330 SPRNGBRK-BE3 345 659333 JUDSON__-BE3 345 1 | B | 1087 | 0.84338 | 103.9514 | P23:345:UMZB:# 7148 #:: TND IN ND. BREAKER FAULT (296):EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | FROM->TO | 659330 SPRNGBRK-BE3 345 659333 JUDSON__-BE3 345 1 | B | 1087 | 0.84338 | 103.9514 | P23:345:UMZB:# 7148 #:: TND IN ND. BREAKER FAULT (296):EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | FROM->TO | 659330 SPRNGBRK-BE3 345 659333 JUDSON__-BE3 345 1 | B | 1087 | 0.84338 | 103.9514 | P23:345:UMZB:# 7148 #:: TND IN ND. BREAKER FAULT (296):EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | FROM->TO | 659330 SPRNGBRK-BE3 345 659333 JUDSON__-BE3 345 1 | B | 1087 | 0.84355 | 104.5233 | P23:345:UMZB:# 7149 #:: TND IN ND. BREAKER FAULT (292):EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | FROM->TO | 659330 SPRNGBRK-BE3 345 659333 JUDSON__-BE3 345 1 | B | 1087 | 0.84355 | 104.5233 | P23:345:UMZB:# 7149 #:: TND IN ND. BREAKER FAULT (292):EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | FROM->TO | 659330 SPRNGBRK-BE3 345 659333 JUDSON__-BE3 345 1 | B | 1087 | 0.84355 | 104.5233 | P23:345:UMZB:# 7149 #:: TND IN ND. BREAKER FAULT (292):EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | FROM->TO | 659333 JUDSON__-BE3 345 3WXFMR 659:JUDSON KU3A 230 1 | B | 717 | 0.12894 | 104.5457 | Single 659333 JUDSON__-BE3 345 659334 JUDSON__-BE4 230 659329 'JDS.KUXA-BE9' 13 1 | Cumulative Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | FROM->TO | 659333 JUDSON__-BE3 345 3WXFMR 659:JUDSON KU3A 230 1 | B | 717 | 0.12894 | 104.5457 | Single 659333 JUDSON__-BE3 345 659334 JUDSON__-BE4 230 659329 'JDS.KUXA-BE9' 13 1 | Cumulative Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | FROM->TO | 659333 JUDSON__-BE3 345 3WXFMR 659:JUDSON KU3A 230 1 | B | 717 | 0.12894 | 104.5457 | Single 659333 JUDSON__-BE3 345 659334 JUDSON__-BE4 230 659329 'JDS.KUXA-BE9' 13 1 | Cumulative Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | FROM->TO | 659333 JUDSON__-BE3 345 3WXFMR 659:652: JUDSON KUXA 230 1 | B | 717 | 0.12894 | 104.5457 | P13:345-230.0:UMZ:# N-1 #:: 3WND JUDSON__-BE3-JUDSON__-BE4-JDS.KU6A-BE9-1 JUDSON KU3A:EHV: | Cumulative Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | FROM->TO | 659333 JUDSON__-BE3 345 3WXFMR 659:652: JUDSON KUXA 230 1 | B | 717 | 0.12894 | 104.5457 | P13:345-230.0:UMZ:# N-1 #:: 3WND JUDSON__-BE3-JUDSON__-BE4-JDS.KU6A-BE9-1 JUDSON KU3A:EHV: | Cumulative Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | FROM->TO | 659333 JUDSON__-BE3 345 3WXFMR 659:652: JUDSON KUXA 230 1 | B | 717 | 0.12894 | 104.5457 | P13:345-230.0:UMZ:# N-1 #:: 3WND JUDSON__-BE3-JUDSON__-BE4-JDS.KU6A-BE9-1 JUDSON KU3A:EHV: | Cumulative Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | FROM->TO | 659330 SPRNGBRK-BE3 345 659333 JUDSON__-BE3 345 1 | B | 1087 | 0.84266 | 104.7813 | Single 659427 TN.LS-JD-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | FROM->TO | 659330 SPRNGBRK-BE3 345 659333 JUDSON__-BE3 345 1 | B | 1087 | 0.84266 | 104.7813 | Single 659427 TN.LS-JD-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | FROM->TO | 659330 SPRNGBRK-BE3 345 659333 JUDSON__-BE3 345 1 | B | 1087 | 0.84266 | 104.7813 | Single 659427 TN.LS-JD-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | FROM->TO | 659330 SPRNGBRK-BE3 345 659333 JUDSON__-BE3 345 1 | B | 1087 | 0.84266 | 104.9387 | P12:345.0:UMZ:# N-1 #:: LINE TANDE___-BE3-TN.LS-JD-BE3-Z :EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | FROM->TO | 659330 SPRNGBRK-BE3 345 659333 JUDSON__-BE3 345 1 | B | 1087 | 0.84266 | 104.9387 | P12:345.0:UMZ:# N-1 #:: LINE TANDE___-BE3-TN.LS-JD-BE3-Z :EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | FROM->TO | 659330 SPRNGBRK-BE3 345 659333 JUDSON__-BE3 345 1 | B | 1087 | 0.84266 | 104.9387 | P12:345.0:UMZ:# N-1 #:: LINE TANDE___-BE3-TN.LS-JD-BE3-Z :EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.22643 | 105.0534 | P13:345-115.0:UMZ:# N-1 #:: 3WND SPRNGBRK-BE3-SPRNGBRK-BE7-SPRNGBRK-BE9-1 652_ SPRNGBRK KUXA_:EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.22643 | 105.0534 | P13:345-115.0:UMZ:# N-1 #:: 3WND SPRNGBRK-BE3-SPRNGBRK-BE7-SPRNGBRK-BE9-1 652_ SPRNGBRK KUXA_:EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.22643 | 105.0534 | P13:345-115.0:UMZ:# N-1 #:: 3WND SPRNGBRK-BE3-SPRNGBRK-BE7-SPRNGBRK-BE9-1 652_ SPRNGBRK KUXA_:EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.22643 | 105.0536 | P12:115.0:UMZ:# N-1 #:: LINE EASTFORK-MW7-SPRNGBRK-BE7-1 :HV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.22643 | 105.0536 | P12:115.0:UMZ:# N-1 #:: LINE EASTFORK-MW7-SPRNGBRK-BE7-1 :HV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.22643 | 105.0536 | P12:115.0:UMZ:# N-1 #:: LINE EASTFORK-MW7-SPRNGBRK-BE7-1 :HV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | A | 600 | 0.2042 | 107.4023 | System Intact | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | A | 600 | 0.2042 | 107.4023 | System Intact | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | A | 600 | 0.2042 | 107.4023 | System Intact | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.24707 | 108.9361 | P12:230.0:UMZ:# N-1 #:: LINE WILISTN4-JUDSON__-BE4-1 :HV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.24707 | 108.9361 | P12:230.0:UMZ:# N-1 #:: LINE WILISTN4-JUDSON__-BE4-1 :HV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.24707 | 108.9361 | P12:230.0:UMZ:# N-1 #:: LINE WILISTN4-JUDSON__-BE4-1 :HV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | FROM->TO | 659330 SPRNGBRK-BE3 345 659333 JUDSON__-BE3 345 1 | B | 1087 | 0.84379 | 110.354 | P23:345:UMZB:# 7148 #:: TND IN ND. BREAKER FAULT (296):EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | FROM->TO | 659330 SPRNGBRK-BE3 345 659333 JUDSON__-BE3 345 1 | B | 1087 | 0.84379 | 110.354 | P23:345:UMZB:# 7148 #:: TND IN ND. BREAKER FAULT (296):EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | FROM->TO | 659330 SPRNGBRK-BE3 345 659333 JUDSON__-BE3 345 1 | B | 1087 | 0.84379 | 110.354 | P23:345:UMZB:# 7148 #:: TND IN ND. BREAKER FAULT (296):EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | FROM->TO | 652400 WILISTN4 230 659334 JUDSON__-BE4 230 1 | B | 482 | 0.21575 | 110.6312 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | FROM->TO | 652400 WILISTN4 230 659334 JUDSON__-BE4 230 1 | B | 482 | 0.21575 | 110.6312 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | FROM->TO | 652400 WILISTN4 230 659334 JUDSON__-BE4 230 1 | B | 482 | 0.21575 | 110.6312 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | FROM->TO | 659330 SPRNGBRK-BE3 345 659333 JUDSON__-BE3 345 1 | B | 1087 | 0.84397 | 110.8651 | P23:345:UMZB:# 7149 #:: TND IN ND. BREAKER FAULT (292):EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | FROM->TO | 659330 SPRNGBRK-BE3 345 659333 JUDSON__-BE3 345 1 | B | 1087 | 0.84397 | 110.8651 | P23:345:UMZB:# 7149 #:: TND IN ND. BREAKER FAULT (292):EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | FROM->TO | 659330 SPRNGBRK-BE3 345 659333 JUDSON__-BE3 345 1 | B | 1087 | 0.84397 | 110.8651 | P23:345:UMZB:# 7149 #:: TND IN ND. BREAKER FAULT (292):EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | FROM->TO | 659330 SPRNGBRK-BE3 345 659333 JUDSON__-BE3 345 1 | B | 1087 | 0.84301 | 110.9083 | P12:345.0:UMZ:# N-1 #:: LINE TANDE___-BE3-TN.LS-JD-BE3-Z :EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | FROM->TO | 659330 SPRNGBRK-BE3 345 659333 JUDSON__-BE3 345 1 | B | 1087 | 0.84301 | 110.9083 | P12:345.0:UMZ:# N-1 #:: LINE TANDE___-BE3-TN.LS-JD-BE3-Z :EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | FROM->TO | 659330 SPRNGBRK-BE3 345 659333 JUDSON__-BE3 345 1 | B | 1087 | 0.84301 | 110.9083 | P12:345.0:UMZ:# N-1 #:: LINE TANDE___-BE3-TN.LS-JD-BE3-Z :EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | FROM->TO | 659330 SPRNGBRK-BE3 345 659333 JUDSON__-BE3 345 1 | B | 1087 | 0.84301 | 111.0855 | Single 659427 TN.LS-JD-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | FROM->TO | 659330 SPRNGBRK-BE3 345 659333 JUDSON__-BE3 345 1 | B | 1087 | 0.84301 | 111.0855 | Single 659427 TN.LS-JD-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | FROM->TO | 659330 SPRNGBRK-BE3 345 659333 JUDSON__-BE3 345 1 | B | 1087 | 0.84301 | 111.0855 | Single 659427 TN.LS-JD-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.22311 | 112.1833 | P13:345-115.0:UMZ:# N-1 #:: 3WND SPRNGBRK-BE3-SPRNGBRK-BE7-SPRNGBRK-BE9-1 652_ SPRNGBRK KUXA_:EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.22311 | 112.1833 | P13:345-115.0:UMZ:# N-1 #:: 3WND SPRNGBRK-BE3-SPRNGBRK-BE7-SPRNGBRK-BE9-1 652_ SPRNGBRK KUXA_:EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.22311 | 112.1833 | P13:345-115.0:UMZ:# N-1 #:: 3WND SPRNGBRK-BE3-SPRNGBRK-BE7-SPRNGBRK-BE9-1 652_ SPRNGBRK KUXA_:EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.22311 | 112.1836 | P12:115.0:UMZ:# N-1 #:: LINE EASTFORK-MW7-SPRNGBRK-BE7-1 :HV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.22311 | 112.1836 | P12:115.0:UMZ:# N-1 #:: LINE EASTFORK-MW7-SPRNGBRK-BE7-1 :HV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.22311 | 112.1836 | P12:115.0:UMZ:# N-1 #:: LINE EASTFORK-MW7-SPRNGBRK-BE7-1 :HV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29SP | T2 | GEN-2024-081 | FROM->TO | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z | B | 509 | 0.29741 | 112.6519 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Rebuild line 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | FROM->TO | 652391 WILLISTON27 115 652421 WILISTN7 115 Z1 | B | 201 | 0.087059 | 112.6538 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | Cumulative Impact | Rebuild line 652391 WILLISTON27 115 652421 WILISTN7 115 Z1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | FROM->TO | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z | B | 526 | 0.32968 | 113.8448 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | FROM->TO | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z | B | 526 | 0.32968 | 113.8448 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | FROM->TO | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z | B | 526 | 0.32968 | 113.8448 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29WP | T2 | GEN-2024-081 | FROM->TO | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z | B | 509 | 0.2974 | 113.8469 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Rebuild line 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.40604 | 115.1422 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.40604 | 115.1422 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.40604 | 115.1422 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.24286 | 116.8154 | P12:230.0:UMZ:# N-1 #:: LINE WILISTN4-JUDSON__-BE4-1 :HV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.24286 | 116.8154 | P12:230.0:UMZ:# N-1 #:: LINE WILISTN4-JUDSON__-BE4-1 :HV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.24286 | 116.8154 | P12:230.0:UMZ:# N-1 #:: LINE WILISTN4-JUDSON__-BE4-1 :HV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | FROM->TO | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z | B | 506 | 0.32553 | 121.1448 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | FROM->TO | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z | B | 506 | 0.32553 | 121.1448 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | FROM->TO | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z | B | 506 | 0.32553 | 121.1448 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | FROM->TO | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z | B | 506 | 0.36814 | 122.2033 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | FROM->TO | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z | B | 506 | 0.36814 | 122.2033 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | FROM->TO | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z | B | 506 | 0.36814 | 122.2033 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | FROM->TO | 652391 WILLISTON27 115 652421 WILISTN7 115 Z1 | B | 201 | 0.10176 | 127.8644 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | Cumulative Impact | Rebuild line 652391 WILLISTON27 115 652421 WILISTN7 115 Z1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | FROM->TO | 659330 SPRNGBRK-BE3 345 3WXFMR 659:652: SPRNGBRK KUXA 115 1 | B | 416 | 0.25008 | 130.276 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | FROM->TO | 659330 SPRNGBRK-BE3 345 3WXFMR 659:652: SPRNGBRK KUXA 115 1 | B | 416 | 0.25008 | 130.276 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | FROM->TO | 659330 SPRNGBRK-BE3 345 3WXFMR 659:652: SPRNGBRK KUXA 115 1 | B | 416 | 0.25008 | 130.276 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | FROM->TO | 659330 SPRNGBRK-BE3 345 3WXFMR 659:652: SPRNGBRK KUXA 115 1 | B | 416 | 0.24415 | 132.3291 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | FROM->TO | 659330 SPRNGBRK-BE3 345 3WXFMR 659:652: SPRNGBRK KUXA 115 1 | B | 416 | 0.24415 | 132.3291 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | FROM->TO | 659330 SPRNGBRK-BE3 345 3WXFMR 659:652: SPRNGBRK KUXA 115 1 | B | 416 | 0.24415 | 132.3291 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-081 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.36634 | 132.5403 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Add 3-winding transformer 659336 TANDE___-BE3 345 659337 TANDE___-BE4 230 659338 TND.KU3A-BE9 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | FROM->TO | 659330 SPRNGBRK-BE3 345 3WXFMR 659:652: SPRNGBRK KUXA 115 1 | B | 416 | 0.25434 | 134.7044 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | FROM->TO | 659330 SPRNGBRK-BE3 345 3WXFMR 659:652: SPRNGBRK KUXA 115 1 | B | 416 | 0.25434 | 134.7044 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | FROM->TO | 659330 SPRNGBRK-BE3 345 3WXFMR 659:652: SPRNGBRK KUXA 115 1 | B | 416 | 0.25434 | 134.7044 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-081 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.36527 | 138.2005 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Add 3-winding transformer 659336 TANDE___-BE3 345 659337 TANDE___-BE4 230 659338 TND.KU3A-BE9 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.42458 | 147.6215 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.42458 | 147.6215 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.42458 | 147.6215 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.42753 | 150.1034 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.42753 | 150.1034 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.42753 | 150.1034 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.58394 | 172.61 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.58394 | 172.61 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.58394 | 172.61 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | FROM->TO | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z | B | 526 | 0.46953 | 177.0036 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | FROM->TO | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z | B | 526 | 0.46953 | 177.0036 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | FROM->TO | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z | B | 526 | 0.46953 | 177.0036 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | FROM->TO | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z | B | 506 | 0.46317 | 184.5908 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | FROM->TO | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z | B | 506 | 0.46317 | 184.5908 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | FROM->TO | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z | B | 506 | 0.46317 | 184.5908 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | FROM->TO | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z | B | 506 | 0.51666 | 190.6179 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | FROM->TO | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z | B | 506 | 0.51666 | 190.6179 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | FROM->TO | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z | B | 506 | 0.51666 | 190.6179 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.60807 | 204.6432 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.60807 | 204.6432 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.60807 | 204.6432 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.61416 | 208.6129 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.61416 | 208.6129 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.61416 | 208.6129 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-082 | FROM->TO | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z | B | 506 | 0.26895 | 100.5821 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Rebuild line 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | A | 600 | 0.20744 | 100.9191 | System Intact | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | A | 600 | 0.20744 | 100.9191 | System Intact | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | A | 600 | 0.20744 | 100.9191 | System Intact | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.2042 | 101.5268 | 259421 | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.2042 | 101.5268 | 259421 | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.2042 | 101.5268 | 259421 | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.2042 | 101.9222 | 259422 | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.2042 | 101.9222 | 259698 | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.2042 | 101.9222 | 259422 | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.2042 | 101.9222 | 259698 | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.2042 | 101.9222 | 259422 | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.2042 | 101.9222 | 259698 | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.2042 | 101.9222 | P12:230:SASK:230KV-G1P-FUT:::HV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.2042 | 101.9222 | P12:230:SASK:230KV-G1P-FUT:::HV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.2042 | 101.9222 | P12:230:SASK:230KV-G1P-FUT:::HV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.2042 | 101.937 | P11:13.8:SASK:CHNK #1 GT:::HV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.2042 | 101.937 | P11:13.8:SASK:CHNK #1 GT:::HV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.2042 | 101.937 | P11:13.8:SASK:CHNK #1 GT:::HV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.32319 | 102.1082 | 279736 | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.32319 | 102.1082 | 279736 | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.32319 | 102.1082 | 279736 | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | FROM->TO | 337909 8ANO% 500 515305 FTSMITH8 500 1 | B | 1299 | 0.077604 | 102.9598 | P52:345:AEPW:NR4PITTSB-7:::: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | FROM->TO | 659330 SPRNGBRK-BE3 345 659333 JUDSON__-BE3 345 1 | B | 1087 | 0.84338 | 103.9514 | P23:345:UMZB:# 7148 #:: TND IN ND. BREAKER FAULT (296):EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | FROM->TO | 659330 SPRNGBRK-BE3 345 659333 JUDSON__-BE3 345 1 | B | 1087 | 0.84338 | 103.9514 | P23:345:UMZB:# 7148 #:: TND IN ND. BREAKER FAULT (296):EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | FROM->TO | 659330 SPRNGBRK-BE3 345 659333 JUDSON__-BE3 345 1 | B | 1087 | 0.84338 | 103.9514 | P23:345:UMZB:# 7148 #:: TND IN ND. BREAKER FAULT (296):EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | FROM->TO | 659330 SPRNGBRK-BE3 345 659333 JUDSON__-BE3 345 1 | B | 1087 | 0.84355 | 104.5233 | P23:345:UMZB:# 7149 #:: TND IN ND. BREAKER FAULT (292):EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | FROM->TO | 659330 SPRNGBRK-BE3 345 659333 JUDSON__-BE3 345 1 | B | 1087 | 0.84355 | 104.5233 | P23:345:UMZB:# 7149 #:: TND IN ND. BREAKER FAULT (292):EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | FROM->TO | 659330 SPRNGBRK-BE3 345 659333 JUDSON__-BE3 345 1 | B | 1087 | 0.84355 | 104.5233 | P23:345:UMZB:# 7149 #:: TND IN ND. BREAKER FAULT (292):EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | FROM->TO | 659333 JUDSON__-BE3 345 3WXFMR 659:JUDSON KU3A 230 1 | B | 717 | 0.12894 | 104.5457 | Single 659333 JUDSON__-BE3 345 659334 JUDSON__-BE4 230 659329 'JDS.KUXA-BE9' 13 1 | Cumulative Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | FROM->TO | 659333 JUDSON__-BE3 345 3WXFMR 659:JUDSON KU3A 230 1 | B | 717 | 0.12894 | 104.5457 | Single 659333 JUDSON__-BE3 345 659334 JUDSON__-BE4 230 659329 'JDS.KUXA-BE9' 13 1 | Cumulative Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | FROM->TO | 659333 JUDSON__-BE3 345 3WXFMR 659:JUDSON KU3A 230 1 | B | 717 | 0.12894 | 104.5457 | Single 659333 JUDSON__-BE3 345 659334 JUDSON__-BE4 230 659329 'JDS.KUXA-BE9' 13 1 | Cumulative Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | FROM->TO | 659333 JUDSON__-BE3 345 3WXFMR 659:652: JUDSON KUXA 230 1 | B | 717 | 0.12894 | 104.5457 | P13:345-230.0:UMZ:# N-1 #:: 3WND JUDSON__-BE3-JUDSON__-BE4-JDS.KU6A-BE9-1 JUDSON KU3A:EHV: | Cumulative Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | FROM->TO | 659333 JUDSON__-BE3 345 3WXFMR 659:652: JUDSON KUXA 230 1 | B | 717 | 0.12894 | 104.5457 | P13:345-230.0:UMZ:# N-1 #:: 3WND JUDSON__-BE3-JUDSON__-BE4-JDS.KU6A-BE9-1 JUDSON KU3A:EHV: | Cumulative Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | FROM->TO | 659333 JUDSON__-BE3 345 3WXFMR 659:652: JUDSON KUXA 230 1 | B | 717 | 0.12894 | 104.5457 | P13:345-230.0:UMZ:# N-1 #:: 3WND JUDSON__-BE3-JUDSON__-BE4-JDS.KU6A-BE9-1 JUDSON KU3A:EHV: | Cumulative Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | FROM->TO | 659330 SPRNGBRK-BE3 345 659333 JUDSON__-BE3 345 1 | B | 1087 | 0.84266 | 104.7813 | Single 659427 TN.LS-JD-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | FROM->TO | 659330 SPRNGBRK-BE3 345 659333 JUDSON__-BE3 345 1 | B | 1087 | 0.84266 | 104.7813 | Single 659427 TN.LS-JD-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | FROM->TO | 659330 SPRNGBRK-BE3 345 659333 JUDSON__-BE3 345 1 | B | 1087 | 0.84266 | 104.7813 | Single 659427 TN.LS-JD-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | FROM->TO | 659330 SPRNGBRK-BE3 345 659333 JUDSON__-BE3 345 1 | B | 1087 | 0.84266 | 104.9387 | P12:345.0:UMZ:# N-1 #:: LINE TANDE___-BE3-TN.LS-JD-BE3-Z :EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | FROM->TO | 659330 SPRNGBRK-BE3 345 659333 JUDSON__-BE3 345 1 | B | 1087 | 0.84266 | 104.9387 | P12:345.0:UMZ:# N-1 #:: LINE TANDE___-BE3-TN.LS-JD-BE3-Z :EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | FROM->TO | 659330 SPRNGBRK-BE3 345 659333 JUDSON__-BE3 345 1 | B | 1087 | 0.84266 | 104.9387 | P12:345.0:UMZ:# N-1 #:: LINE TANDE___-BE3-TN.LS-JD-BE3-Z :EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.22643 | 105.0534 | P13:345-115.0:UMZ:# N-1 #:: 3WND SPRNGBRK-BE3-SPRNGBRK-BE7-SPRNGBRK-BE9-1 652_ SPRNGBRK KUXA_:EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.22643 | 105.0534 | P13:345-115.0:UMZ:# N-1 #:: 3WND SPRNGBRK-BE3-SPRNGBRK-BE7-SPRNGBRK-BE9-1 652_ SPRNGBRK KUXA_:EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.22643 | 105.0534 | P13:345-115.0:UMZ:# N-1 #:: 3WND SPRNGBRK-BE3-SPRNGBRK-BE7-SPRNGBRK-BE9-1 652_ SPRNGBRK KUXA_:EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.22643 | 105.0536 | P12:115.0:UMZ:# N-1 #:: LINE EASTFORK-MW7-SPRNGBRK-BE7-1 :HV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.22643 | 105.0536 | P12:115.0:UMZ:# N-1 #:: LINE EASTFORK-MW7-SPRNGBRK-BE7-1 :HV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.22643 | 105.0536 | P12:115.0:UMZ:# N-1 #:: LINE EASTFORK-MW7-SPRNGBRK-BE7-1 :HV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | A | 600 | 0.2042 | 107.4023 | System Intact | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | A | 600 | 0.2042 | 107.4023 | System Intact | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | A | 600 | 0.2042 | 107.4023 | System Intact | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.24707 | 108.9361 | P12:230.0:UMZ:# N-1 #:: LINE WILISTN4-JUDSON__-BE4-1 :HV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.24707 | 108.9361 | P12:230.0:UMZ:# N-1 #:: LINE WILISTN4-JUDSON__-BE4-1 :HV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.24707 | 108.9361 | P12:230.0:UMZ:# N-1 #:: LINE WILISTN4-JUDSON__-BE4-1 :HV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | FROM->TO | 659330 SPRNGBRK-BE3 345 659333 JUDSON__-BE3 345 1 | B | 1087 | 0.84379 | 110.354 | P23:345:UMZB:# 7148 #:: TND IN ND. BREAKER FAULT (296):EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | FROM->TO | 659330 SPRNGBRK-BE3 345 659333 JUDSON__-BE3 345 1 | B | 1087 | 0.84379 | 110.354 | P23:345:UMZB:# 7148 #:: TND IN ND. BREAKER FAULT (296):EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | FROM->TO | 659330 SPRNGBRK-BE3 345 659333 JUDSON__-BE3 345 1 | B | 1087 | 0.84379 | 110.354 | P23:345:UMZB:# 7148 #:: TND IN ND. BREAKER FAULT (296):EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | FROM->TO | 652400 WILISTN4 230 659334 JUDSON__-BE4 230 1 | B | 482 | 0.21575 | 110.6312 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | FROM->TO | 652400 WILISTN4 230 659334 JUDSON__-BE4 230 1 | B | 482 | 0.21575 | 110.6312 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | FROM->TO | 652400 WILISTN4 230 659334 JUDSON__-BE4 230 1 | B | 482 | 0.21575 | 110.6312 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | FROM->TO | 659330 SPRNGBRK-BE3 345 659333 JUDSON__-BE3 345 1 | B | 1087 | 0.84397 | 110.8651 | P23:345:UMZB:# 7149 #:: TND IN ND. BREAKER FAULT (292):EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | FROM->TO | 659330 SPRNGBRK-BE3 345 659333 JUDSON__-BE3 345 1 | B | 1087 | 0.84397 | 110.8651 | P23:345:UMZB:# 7149 #:: TND IN ND. BREAKER FAULT (292):EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | FROM->TO | 659330 SPRNGBRK-BE3 345 659333 JUDSON__-BE3 345 1 | B | 1087 | 0.84397 | 110.8651 | P23:345:UMZB:# 7149 #:: TND IN ND. BREAKER FAULT (292):EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | FROM->TO | 659330 SPRNGBRK-BE3 345 659333 JUDSON__-BE3 345 1 | B | 1087 | 0.84301 | 110.9083 | P12:345.0:UMZ:# N-1 #:: LINE TANDE___-BE3-TN.LS-JD-BE3-Z :EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | FROM->TO | 659330 SPRNGBRK-BE3 345 659333 JUDSON__-BE3 345 1 | B | 1087 | 0.84301 | 110.9083 | P12:345.0:UMZ:# N-1 #:: LINE TANDE___-BE3-TN.LS-JD-BE3-Z :EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | FROM->TO | 659330 SPRNGBRK-BE3 345 659333 JUDSON__-BE3 345 1 | B | 1087 | 0.84301 | 110.9083 | P12:345.0:UMZ:# N-1 #:: LINE TANDE___-BE3-TN.LS-JD-BE3-Z :EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | FROM->TO | 659330 SPRNGBRK-BE3 345 659333 JUDSON__-BE3 345 1 | B | 1087 | 0.84301 | 111.0855 | Single 659427 TN.LS-JD-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | FROM->TO | 659330 SPRNGBRK-BE3 345 659333 JUDSON__-BE3 345 1 | B | 1087 | 0.84301 | 111.0855 | Single 659427 TN.LS-JD-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | FROM->TO | 659330 SPRNGBRK-BE3 345 659333 JUDSON__-BE3 345 1 | B | 1087 | 0.84301 | 111.0855 | Single 659427 TN.LS-JD-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.22311 | 112.1833 | P13:345-115.0:UMZ:# N-1 #:: 3WND SPRNGBRK-BE3-SPRNGBRK-BE7-SPRNGBRK-BE9-1 652_ SPRNGBRK KUXA_:EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.22311 | 112.1833 | P13:345-115.0:UMZ:# N-1 #:: 3WND SPRNGBRK-BE3-SPRNGBRK-BE7-SPRNGBRK-BE9-1 652_ SPRNGBRK KUXA_:EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.22311 | 112.1833 | P13:345-115.0:UMZ:# N-1 #:: 3WND SPRNGBRK-BE3-SPRNGBRK-BE7-SPRNGBRK-BE9-1 652_ SPRNGBRK KUXA_:EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.22311 | 112.1836 | P12:115.0:UMZ:# N-1 #:: LINE EASTFORK-MW7-SPRNGBRK-BE7-1 :HV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.22311 | 112.1836 | P12:115.0:UMZ:# N-1 #:: LINE EASTFORK-MW7-SPRNGBRK-BE7-1 :HV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.22311 | 112.1836 | P12:115.0:UMZ:# N-1 #:: LINE EASTFORK-MW7-SPRNGBRK-BE7-1 :HV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29SP | T2 | GEN-2024-082 | FROM->TO | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z | B | 509 | 0.29741 | 112.6519 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Rebuild line 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | FROM->TO | 652391 WILLISTON27 115 652421 WILISTN7 115 Z1 | B | 201 | 0.087059 | 112.6538 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | Cumulative Impact | Rebuild line 652391 WILLISTON27 115 652421 WILISTN7 115 Z1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | FROM->TO | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z | B | 526 | 0.32968 | 113.8448 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | FROM->TO | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z | B | 526 | 0.32968 | 113.8448 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | FROM->TO | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z | B | 526 | 0.32968 | 113.8448 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29WP | T2 | GEN-2024-082 | FROM->TO | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z | B | 509 | 0.2974 | 113.8469 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Rebuild line 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.40604 | 115.1422 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.40604 | 115.1422 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.40604 | 115.1422 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.24286 | 116.8154 | P12:230.0:UMZ:# N-1 #:: LINE WILISTN4-JUDSON__-BE4-1 :HV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.24286 | 116.8154 | P12:230.0:UMZ:# N-1 #:: LINE WILISTN4-JUDSON__-BE4-1 :HV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.24286 | 116.8154 | P12:230.0:UMZ:# N-1 #:: LINE WILISTN4-JUDSON__-BE4-1 :HV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | FROM->TO | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z | B | 506 | 0.32553 | 121.1448 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | FROM->TO | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z | B | 506 | 0.32553 | 121.1448 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | FROM->TO | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z | B | 506 | 0.32553 | 121.1448 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | FROM->TO | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z | B | 506 | 0.36814 | 122.2033 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | FROM->TO | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z | B | 506 | 0.36814 | 122.2033 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | FROM->TO | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z | B | 506 | 0.36814 | 122.2033 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | FROM->TO | 652391 WILLISTON27 115 652421 WILISTN7 115 Z1 | B | 201 | 0.10176 | 127.8644 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | Cumulative Impact | Rebuild line 652391 WILLISTON27 115 652421 WILISTN7 115 Z1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | FROM->TO | 659330 SPRNGBRK-BE3 345 3WXFMR 659:652: SPRNGBRK KUXA 115 1 | B | 416 | 0.25008 | 130.276 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | FROM->TO | 659330 SPRNGBRK-BE3 345 3WXFMR 659:652: SPRNGBRK KUXA 115 1 | B | 416 | 0.25008 | 130.276 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | FROM->TO | 659330 SPRNGBRK-BE3 345 3WXFMR 659:652: SPRNGBRK KUXA 115 1 | B | 416 | 0.25008 | 130.276 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | FROM->TO | 659330 SPRNGBRK-BE3 345 3WXFMR 659:652: SPRNGBRK KUXA 115 1 | B | 416 | 0.24415 | 132.3291 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | FROM->TO | 659330 SPRNGBRK-BE3 345 3WXFMR 659:652: SPRNGBRK KUXA 115 1 | B | 416 | 0.24415 | 132.3291 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | FROM->TO | 659330 SPRNGBRK-BE3 345 3WXFMR 659:652: SPRNGBRK KUXA 115 1 | B | 416 | 0.24415 | 132.3291 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-082 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.36634 | 132.5403 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Add 3-winding transformer 659336 TANDE___-BE3 345 659337 TANDE___-BE4 230 659338 TND.KU3A-BE9 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | FROM->TO | 659330 SPRNGBRK-BE3 345 3WXFMR 659:652: SPRNGBRK KUXA 115 1 | B | 416 | 0.25434 | 134.7044 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | FROM->TO | 659330 SPRNGBRK-BE3 345 3WXFMR 659:652: SPRNGBRK KUXA 115 1 | B | 416 | 0.25434 | 134.7044 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | FROM->TO | 659330 SPRNGBRK-BE3 345 3WXFMR 659:652: SPRNGBRK KUXA 115 1 | B | 416 | 0.25434 | 134.7044 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-082 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.36527 | 138.2005 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Add 3-winding transformer 659336 TANDE___-BE3 345 659337 TANDE___-BE4 230 659338 TND.KU3A-BE9 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.42458 | 147.6215 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.42458 | 147.6215 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.42458 | 147.6215 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.42753 | 150.1034 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.42753 | 150.1034 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.42753 | 150.1034 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.58394 | 172.61 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.58394 | 172.61 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.58394 | 172.61 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | FROM->TO | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z | B | 526 | 0.46953 | 177.0036 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | FROM->TO | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z | B | 526 | 0.46953 | 177.0036 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | FROM->TO | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z | B | 526 | 0.46953 | 177.0036 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | FROM->TO | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z | B | 506 | 0.46317 | 184.5908 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | FROM->TO | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z | B | 506 | 0.46317 | 184.5908 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | FROM->TO | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z | B | 506 | 0.46317 | 184.5908 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | FROM->TO | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z | B | 506 | 0.51666 | 190.6179 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | FROM->TO | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z | B | 506 | 0.51666 | 190.6179 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | FROM->TO | 659138 NESET___-BE4 230 661084 TIOGA4 4 230 Z | B | 506 | 0.51666 | 190.6179 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.60807 | 204.6432 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.60807 | 204.6432 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.60807 | 204.6432 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.61416 | 208.6129 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.61416 | 208.6129 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | FROM->TO | 659336 TANDE___-BE3 345 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.61416 | 208.6129 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-090 | FROM->TO | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.067484 | 104.394 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-090 | FROM->TO | 541204 SMTHVL 5 161 541221 PLTCTY 5 161 1 | B | 297 | 1 | 109.8349 | Single 541203 NASHUA5 161 541204 SMTHVL5 161 1 | TDF Impact | Rebuild line 541204 SMTHVL 5 161 541221 PLTCTY 5 161 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-090 | FROM->TO | 541214 TWA 5 161 541318 NCONGRS5 161 1 | B | 193 | 0.50058 | 109.9324 | Single 541203 NASHUA5 161 541204 SMTHVL5 161 1 | TDF Impact | Rebuild line 541214 TWA 5 161 541318 NCONGRS5 161 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-090 | FROM->TO | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.075433 | 111.8275 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-090 | FROM->TO | 541204 SMTHVL 5 161 541221 PLTCTY 5 161 1 | B | 261 | 1 | 123.916 | Single 541203 NASHUA5 161 541204 SMTHVL5 161 1 | TDF Impact | Rebuild line 541204 SMTHVL 5 161 541221 PLTCTY 5 161 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-090 | FROM->TO | 541204 SMTHVL 5 161 541221 PLTCTY 5 161 1 | B | 261 | 1 | 124.0382 | Single 541203 NASHUA5 161 541204 SMTHVL5 161 1 | TDF Impact | Rebuild line 541204 SMTHVL 5 161 541221 PLTCTY 5 161 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-099 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.075865 | 100.0488 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-099 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.064964 | 100.533 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-099 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.079762 | 103.9266 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-099 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.078863 | 104.7552 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-099 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.078863 | 104.888 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-099 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.082699 | 107.2243 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-099 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.066147 | 107.2793 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-099 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.066147 | 107.2794 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-099 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.082699 | 107.2951 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-099 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.066147 | 107.3093 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-099 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.066147 | 107.7557 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-099 | FROM->TO | 531512 HARBNGR7 345 3WXFMR 534:HARBGR345 345 1 | B | 385 | 0.050125 | 107.8261 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Add 3-winding transformer 531510 HARBNGR3 115 531511 HARBNGR-1 13 531512 HARBNGR7 345 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-099 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.066147 | 108.2747 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-099 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.066147 | 111.3621 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-099 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.077147 | 115.0541 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-099 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.080164 | 118.9427 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-099 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.080164 | 119.313 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-109 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.074578 | 100.0488 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29L | T0 | GEN-2024-109 | FROM->TO | 511541 DEMPSEYR POI 230 511557 CHISHOLM6 230 1 | B | 439 | 0.071011 | 100.3116 | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | Cumulative Impact | Rebuild line 511541 DEMPSEYR POI 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-109 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063727 | 100.533 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-109 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.079085 | 103.9266 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-109 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.077559 | 104.7552 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-109 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.077559 | 104.888 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-109 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.082004 | 107.2243 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-109 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.064596 | 107.2793 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-109 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.064596 | 107.2794 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-109 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.082004 | 107.2951 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-109 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.064596 | 107.3093 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-109 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.064596 | 107.7557 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-109 | FROM->TO | 531512 HARBNGR7 345 3WXFMR 534:HARBGR345 345 1 | B | 385 | 0.050234 | 107.8261 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Add 3-winding transformer 531510 HARBNGR3 115 531511 HARBNGR-1 13 531512 HARBNGR7 345 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-109 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.064596 | 108.2747 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-109 | FROM->TO | 523961 POTTER_CO 7 345 3WXFMR 526:WAUK 90343-A 230 1 | B | 559 | 0.11281 | 108.8994 | P42:345:SPS:HITCHLAND-1R15:::EHV: | Cumulative Impact | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-109 | FROM->TO | 523961 POTTER_CO 7 345 3WXFMR 526:WAUK 90343-A 230 1 | B | 559 | 0.11281 | 108.9122 | Single 523097 HITCHLAND7 345 523961 POTTER_CO7 345 1 | Cumulative Impact | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-109 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.064596 | 111.3621 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-109 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.07562 | 115.0541 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-109 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.078618 | 118.9427 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-109 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.078618 | 119.313 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 04ALL | 1 | 29SP | T1 | GEN-2024-113 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.035131 | 103.3038 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-113 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | A | 1187 | 0.062342 | 103.8656 | System Intact | TDF Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-113 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.069672 | 104.9177 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-113 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.066451 | 106.1409 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-113 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.068019 | 106.3238 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-113 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.06163 | 106.5158 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-113 | FROM->TO | 515302 FTSMITH7 345 3WXFMR 524:524:FTSMITH1 500 1 | B | 693 | 0.33292 | 107.4747 | P12:161:EES:FTSMTHW5%:FTSMITH7%:FTSMTH511:HV: | TDF Impact | Add 3-winding transformer 515302 FTSMITH7 345 515305 FTSMITH8 500 515726 FTSMTH11 13 M2
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-113 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.065793 | 107.841 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-113 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.06163 | 108.059 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-113 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.065793 | 109.5335 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-113 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.065793 | 109.534 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-113 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.065793 | 112.0538 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-113 | FROM->TO | 515302 FTSMITH7 345 3WXFMR 524:524:FTSMITH1 500 1 | B | 693 | 0.22329 | 114.2948 | Single 515302 FTSMITH7 345 515305 FTSMITH8 500 519010 'FTSMITH71 ' 13 2 | TDF Impact | Add 3-winding transformer 515302 FTSMITH7 345 515305 FTSMITH8 500 515726 FTSMTH11 13 M2
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-113 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.065793 | 116.5975 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-113 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.048447 | 119.3706 | System Intact | TDF Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-113 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.048447 | 119.3706 | System Intact | TDF Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-113 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.048447 | 119.3706 | System Intact | TDF Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-113 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.043381 | 119.5141 | System Intact | TDF Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-113 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.043381 | 119.5141 | System Intact | TDF Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-113 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.043381 | 119.5141 | System Intact | TDF Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-113 | FROM->TO | 515302 FTSMITH7 345 3WXFMR 524:524:FTSMITH5 345 5 | B | 493 | 0.20353 | 120.3942 | P42:500:OKGE:SB_FTTH8585:::EHV: | TDF Impact | Add 3-winding transformer 515301 FTSMTHW5 161 515302 FTSMITH7 345 515728 FTSMTH51 13 M2
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-113 | FROM->TO | 515302 FTSMITH7 345 3WXFMR 524:524:FTSMITH5 345 5 | B | 493 | 0.26036 | 126.769 | P12:345:EES:FTSMITH7%:FTSMITH8%:FTSMTH111:EHV: | TDF Impact | Add 3-winding transformer 515301 FTSMTHW5 161 515302 FTSMITH7 345 515728 FTSMTH51 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-113 | FROM->TO | 516092 OKTAHA 5 161 3WXFMR OKTAHA 5 69 7 | B | 112 | 0.036806 | 128.9125 | P22:345:EES:MUSKOGE7!:::EHV: | TDF Impact | Rebuild 3-winding transformer 516092 OKTAHA 5 161 516093 OKTAHA 2 69 516095 OKTAHA71 13 7
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-113 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.052349 | 136.9237 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-113 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.052349 | 136.9237 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-113 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.052349 | 136.9237 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-113 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.052493 | 140.3415 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-113 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.052493 | 140.3415 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-113 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.052493 | 140.3415 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-113 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.056476 | 141.6076 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-113 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.056476 | 141.6076 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-113 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.056476 | 141.6076 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-113 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.053786 | 142.5086 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-113 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.053786 | 142.5086 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-113 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.053786 | 142.5086 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-113 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.05196 | 142.6431 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-113 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.05196 | 142.6431 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-113 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.05196 | 142.6431 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-113 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051059 | 142.7223 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-113 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051059 | 142.7223 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-113 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051059 | 142.7223 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-113 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.05196 | 145.1309 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-113 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.05196 | 145.1309 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-113 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.05196 | 145.1309 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-113 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.05196 | 145.1356 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-113 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.05196 | 145.1356 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-113 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.05196 | 145.1356 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-113 | FROM->TO | 516092 OKTAHA 5 161 3WXFMR OKTAHA 5 69 7 | B | 112 | 0.035995 | 147.7196 | P22:345:EES:MUSKOGE7!:::EHV: | TDF Impact | Rebuild 3-winding transformer 516092 OKTAHA 5 161 516093 OKTAHA 2 69 516095 OKTAHA71 13 7
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-113 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.05196 | 148.805 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-113 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.05196 | 148.805 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-113 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.05196 | 148.805 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-113 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.05196 | 155.6146 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-113 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.05196 | 155.6146 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-113 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.05196 | 155.6146 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-113 | FROM->TO | 516092 OKTAHA 5 161 3WXFMR OKTAHA 5 69 7 | B | 112 | 0.037495 | 165.8816 | P22:345:EES:MUSKOGE7!:::EHV: | TDF Impact | Rebuild 3-winding transformer 516092 OKTAHA 5 161 516093 OKTAHA 2 69 516095 OKTAHA71 13 7
Thermal | 00NR | 1 | 29WP | T1 | GEN-2024-117 | FROM->TO | 532937 NEOSHO 5 161 764310 G20-079-TAP 161 1 | B | 533 | 0.03625 | 101.6771 | P23:345:AECI:7BLACKBERRY:653::: | TDF Impact | Rebuild line 532937 NEOSHO 5 161 764310 G20-079-TAP 161 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-117 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | A | 717 | 0.035261 | 102.1682 | System Intact | TDF Impact | Rebuild line 541198 PECULR 7 345 541200 PHILL 7 345 1
Thermal | 04ALL | 1 | 26SP | T1 | GEN-2024-117 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.036243 | 103.0993 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T1 | GEN-2024-117 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.041125 | 103.3038 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-117 | FROM->TO | 510422 COFFEYT4 138 533002 DEARING4 138 1 | B | 478 | 0.31576 | 104.1226 | Single 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | TDF Impact | Rebuild line 510422 COFFEYT4 138 533002 DEARING4 138 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-117 | FROM->TO | 510422 COFFEYT4 138 533002 DEARING4 138 1 | B | 478 | 0.31366 | 105.2003 | Single 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | TDF Impact | Rebuild line 510422 COFFEYT4 138 533002 DEARING4 138 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-117 | FROM->TO | 510422 COFFEYT4 138 533002 DEARING4 138 1 | B | 478 | 0.31576 | 109.147 | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | Rebuild line 510422 COFFEYT4 138 533002 DEARING4 138 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-117 | FROM->TO | 510422 COFFEYT4 138 533002 DEARING4 138 1 | B | 478 | 0.31366 | 110.1546 | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | Rebuild line 510422 COFFEYT4 138 533002 DEARING4 138 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-117 | FROM->TO | 510422 COFFEYT4 138 533002 DEARING4 138 1 | B | 478 | 0.31319 | 114.9546 | P23:345:WERE:N345-345-20:EHV: | TDF Impact | Rebuild line 510422 COFFEYT4 138 533002 DEARING4 138 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-117 | FROM->TO | 510422 COFFEYT4 138 533002 DEARING4 138 1 | B | 478 | 0.31118 | 115.247 | P23:345:WERE:N345-345-20:EHV: | TDF Impact | Rebuild line 510422 COFFEYT4 138 533002 DEARING4 138 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-117 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.073834 | 119.3706 | System Intact | TDF Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-117 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.073834 | 119.3706 | System Intact | TDF Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-117 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.073834 | 119.3706 | System Intact | TDF Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-117 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.068666 | 119.5141 | System Intact | TDF Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-117 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.068666 | 119.5141 | System Intact | TDF Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-117 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.068666 | 119.5141 | System Intact | TDF Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-117 | FROM->TO | 533020 NEOSHOS4 138 3WXFMR 536:NEOSHO TX-5 138 1 | B | 165 | 0.030993 | 124.761 | Single 532937 NEOSHO5 161 532939 N34545 161 1 | TDF Impact | Add 3-winding transformer 532937 NEOSHO 5 161 532959 NEOSH5 1 13 533020 NEOSHOS4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-117 | FROM->TO | 533020 NEOSHOS4 138 3WXFMR 536:NEOSHO TX-5 138 1 | B | 165 | 0.030993 | 124.7681 | Single 532793 NEOSHO7 345 532939 N34545 161 532825 'N345 2 1 ' 13 2 | TDF Impact | Add 3-winding transformer 532937 NEOSHO 5 161 532959 NEOSH5 1 13 533020 NEOSHOS4 138 M2
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-117 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.076237 | 136.5828 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-117 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.076237 | 136.5828 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-117 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.076237 | 136.5828 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-117 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.18923 | 136.8919 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-117 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.18923 | 136.8919 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-117 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.18923 | 136.8919 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-117 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.19321 | 136.9237 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-117 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.19321 | 136.9237 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-117 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.19321 | 136.9237 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-117 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.069906 | 139.3736 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-117 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.069906 | 139.3736 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-117 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.069906 | 139.3736 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-117 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.074655 | 140.3415 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-117 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.074655 | 140.3415 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-117 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.074655 | 140.3415 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-117 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.06846 | 140.6152 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-117 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.06846 | 140.6152 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-117 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.06846 | 140.6152 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-117 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.07674 | 141.6076 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-117 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.07674 | 141.6076 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-117 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.07674 | 141.6076 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-117 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.072144 | 142.5086 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-117 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.072144 | 142.5086 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-117 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.072144 | 142.5086 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-117 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.074122 | 142.6431 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-117 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.074122 | 142.6431 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-117 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.074122 | 142.6431 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-117 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.070851 | 142.7223 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-117 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.070851 | 142.7223 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-117 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.070851 | 142.7223 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-117 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.067871 | 143.2233 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-117 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.067871 | 143.2233 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-117 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.067871 | 143.2233 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-117 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.066428 | 143.8401 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-117 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.066428 | 143.8401 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-117 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.066428 | 143.8401 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-117 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.074122 | 145.1309 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-117 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.074122 | 145.1309 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-117 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.074122 | 145.1309 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-117 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.074122 | 145.1356 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-117 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.074122 | 145.1356 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-117 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.074122 | 145.1356 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-117 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.067871 | 145.7578 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-117 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.067871 | 145.7578 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-117 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.067871 | 145.7578 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-117 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.067871 | 145.7646 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-117 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.067871 | 145.7646 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-117 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.067871 | 145.7646 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-117 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.074122 | 148.805 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-117 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.074122 | 148.805 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-117 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.074122 | 148.805 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-117 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.067871 | 149.8057 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-117 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.067871 | 149.8057 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-117 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.067871 | 149.8057 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-117 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.074122 | 155.6146 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-117 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.074122 | 155.6146 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-117 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.074122 | 155.6146 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-117 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.067871 | 157.3662 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-117 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.067871 | 157.3662 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-117 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.067871 | 157.3662 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T1 | GEN-2024-118 | FROM->TO | 509790 CATOOSA4 138 512636 CATSAGR4 138 Z1 | B | 272 | 0.19523 | 100.1562 | Single 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | Cumulative Impact | Rebuild line 509790 CATOOSA4 138 512636 CATSAGR4 138 Z1
Thermal | 04ALL | 1 | 26SP | T1 | GEN-2024-118 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.051711 | 103.0993 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T1 | GEN-2024-118 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.056424 | 103.3038 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-118 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | A | 1187 | 0.10023 | 103.8656 | System Intact | TDF Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-118 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.11545 | 104.9177 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-118 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.10627 | 106.1409 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-118 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.11341 | 106.3238 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-118 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.10128 | 106.5158 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-118 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.10562 | 107.841 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-118 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.10128 | 108.059 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-118 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.10562 | 109.5335 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-118 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.10562 | 109.534 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | FROM->TO | 509790 CATOOSA4 138 512636 CATSAGR4 138 Z1 | B | 218 | 0.16779 | 110.4083 | Single 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | Cumulative Impact | Rebuild line 509790 CATOOSA4 138 512636 CATSAGR4 138 Z1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-118 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.10562 | 112.0538 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T1 | GEN-2024-118 | FROM->TO | 509790 CATOOSA4 138 512636 CATSAGR4 138 Z1 | B | 272 | 0.1944 | 112.6598 | Single 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | Cumulative Impact | Rebuild line 509790 CATOOSA4 138 512636 CATSAGR4 138 Z1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | FROM->TO | 512623 CATSAGD4 138 3WXFMR 523:CATAUTO1 138 1 | B | 188 | 0.17417 | 114.3439 | P13:138-161:GRDA:CATAUTO2:::HV: | Cumulative Impact | Add 3-winding transformer 512623 CATSAGD4 138 512638 CATSAGR5 161 512833 CATTER1 1 13 M2
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | FROM->TO | 512623 CATSAGD4 138 3WXFMR 523:CATAUTO1 138 1 | B | 188 | 0.17417 | 114.3439 | Single 509790 CATOOSA4 138 512636 CATSAGR4 138 Z1 | Cumulative Impact | Add 3-winding transformer 512623 CATSAGD4 138 512638 CATSAGR5 161 512833 CATTER1 1 13 M2
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | FROM->TO | 512636 CATSAGR4 138 3WXFMR 523:CATAUTO2 138 2 | B | 188 | 0.17469 | 114.6833 | P13:138-161:GRDA:CATAUTO1:::HV: | Cumulative Impact | Add 3-winding transformer 512636 CATSAGR4 138 512638 CATSAGR5 161 512834 CATTER2 1 13 M2
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | FROM->TO | 512636 CATSAGR4 138 3WXFMR 523:CATAUTO2 138 2 | B | 188 | 0.17469 | 114.6833 | Single 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | Cumulative Impact | Add 3-winding transformer 512636 CATSAGR4 138 512638 CATSAGR5 161 512834 CATTER2 1 13 M2
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | FROM->TO | 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | B | 188 | 0.17417 | 115.0684 | P13:138-161:GRDA:CATAUTO2:::HV: | Cumulative Impact | Rebuild line 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | FROM->TO | 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | B | 188 | 0.17417 | 115.0684 | Single 509790 CATOOSA4 138 512636 CATSAGR4 138 Z1 | Cumulative Impact | Rebuild line 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-118 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.10562 | 116.5975 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.078865 | 119.3706 | System Intact | TDF Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.078865 | 119.3706 | System Intact | TDF Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.078865 | 119.3706 | System Intact | TDF Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.074405 | 119.5141 | System Intact | TDF Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.074405 | 119.5141 | System Intact | TDF Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.074405 | 119.5141 | System Intact | TDF Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-118 | FROM->TO | 509790 CATOOSA4 138 512636 CATSAGR4 138 Z1 | B | 218 | 0.16643 | 124.6315 | Single 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | Cumulative Impact | Rebuild line 509790 CATOOSA4 138 512636 CATSAGR4 138 Z1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | FROM->TO | 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | B | 188 | 0.14113 | 126.4273 | Single 300795 4OOLOGAHKAMO 138 513124 OOLOGAH4 138 Z1 | Cumulative Impact | Rebuild line 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | FROM->TO | 509770 LLAN WT4 138 509803 DAWSONT4 138 1 | B | 187 | 0.50238 | 127.2777 | Single 509790 CATOOSA4 138 509804 E11THST4 138 1 | TDF Impact | Rebuild line 509770 LLAN WT4 138 509803 DAWSONT4 138 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | FROM->TO | 512636 CATSAGR4 138 3WXFMR 523:CATAUTO2 138 2 | B | 188 | 0.16779 | 127.8636 | Single 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | Cumulative Impact | Add 3-winding transformer 512636 CATSAGR4 138 512638 CATSAGR5 161 512834 CATTER2 1 13 M2
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | FROM->TO | 509770 LLAN WT4 138 509803 DAWSONT4 138 1 | B | 187 | 0.49617 | 129.7618 | Single 509790 CATOOSA4 138 509804 E11THST4 138 1 | TDF Impact | Rebuild line 509770 LLAN WT4 138 509803 DAWSONT4 138 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | FROM->TO | 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | A | 150 | 0.13925 | 132.7121 | System Intact | TDF Impact | Rebuild line 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.080167 | 136.5828 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.080167 | 136.5828 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.080167 | 136.5828 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.086024 | 136.8919 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.086024 | 136.8919 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.086024 | 136.8919 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.09002 | 136.9237 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.09002 | 136.9237 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.09002 | 136.9237 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.074726 | 139.3736 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.074726 | 139.3736 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.074726 | 139.3736 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | FROM->TO | 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | B | 188 | 0.14395 | 139.5037 | P22:345:EES:CLARKSV7!:::EHV: | Cumulative Impact | Rebuild line 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.084708 | 140.3415 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.084708 | 140.3415 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.084708 | 140.3415 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.079403 | 140.6152 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.079403 | 140.6152 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.079403 | 140.6152 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.095081 | 141.6076 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.095081 | 141.6076 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.095081 | 141.6076 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.091685 | 142.5086 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.091685 | 142.5086 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.091685 | 142.5086 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.084175 | 142.6431 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.084175 | 142.6431 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.084175 | 142.6431 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.089969 | 142.7223 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.089969 | 142.7223 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.089969 | 142.7223 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-118 | FROM->TO | 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | B | 188 | 0.13981 | 143.0169 | Single 300795 4OOLOGAHKAMO 138 513124 OOLOGAH4 138 Z1 | Cumulative Impact | Rebuild line 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.078814 | 143.2233 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.078814 | 143.2233 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.078814 | 143.2233 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-118 | FROM->TO | 512636 CATSAGR4 138 3WXFMR 523:CATAUTO2 138 2 | B | 188 | 0.16643 | 143.4156 | Single 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | Cumulative Impact | Add 3-winding transformer 512636 CATSAGR4 138 512638 CATSAGR5 161 512834 CATTER2 1 13 M2
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.086693 | 143.8401 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.086693 | 143.8401 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.086693 | 143.8401 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.084175 | 145.1309 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.084175 | 145.1309 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.084175 | 145.1309 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.084175 | 145.1356 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.084175 | 145.1356 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.084175 | 145.1356 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.078814 | 145.7578 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.078814 | 145.7578 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.078814 | 145.7578 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.078814 | 145.7646 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.078814 | 145.7646 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.078814 | 145.7646 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.084175 | 148.805 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.084175 | 148.805 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.084175 | 148.805 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | FROM->TO | 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | B | 188 | 0.19662 | 149.5687 | Single 509790 CATOOSA4 138 512636 CATSAGR4 138 Z1 | Cumulative Impact | Rebuild line 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | FROM->TO | 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | B | 188 | 0.19662 | 149.5687 | P13:138-161:GRDA:CATAUTO2:::HV: | Cumulative Impact | Rebuild line 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.078814 | 149.8057 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.078814 | 149.8057 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.078814 | 149.8057 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-118 | FROM->TO | 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | A | 150 | 0.13817 | 149.9079 | System Intact | TDF Impact | Rebuild line 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | FROM->TO | 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | B | 188 | 0.14059 | 150.3111 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | Cumulative Impact | Rebuild line 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | FROM->TO | 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | B | 188 | 0.13947 | 152.0562 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB:::: | Cumulative Impact | Rebuild line 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | FROM->TO | 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | B | 188 | 0.13948 | 152.2091 | P12:345:EES:CHAMSPR7!:CLARKSV7!:1:EHV: | Cumulative Impact | Rebuild line 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.084175 | 155.6146 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.084175 | 155.6146 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.084175 | 155.6146 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-118 | FROM->TO | 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | B | 188 | 0.14231 | 155.7771 | P22:345:EES:CLARKSV7!:::EHV: | Cumulative Impact | Rebuild line 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.078814 | 157.3662 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.078814 | 157.3662 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.078814 | 157.3662 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | FROM->TO | 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | B | 188 | 0.14059 | 160.386 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Cumulative Impact | Rebuild line 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-118 | FROM->TO | 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | B | 188 | 0.13819 | 161.2104 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB:::: | Cumulative Impact | Rebuild line 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-118 | FROM->TO | 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | B | 188 | 0.1382 | 161.3969 | P12:345:EES:CHAMSPR7!:CLARKSV7!:1:EHV: | Cumulative Impact | Rebuild line 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-118 | FROM->TO | 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | B | 188 | 0.13894 | 165.4608 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | Cumulative Impact | Rebuild line 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-118 | FROM->TO | 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | B | 188 | 0.19508 | 168.9167 | Single 509790 CATOOSA4 138 512636 CATSAGR4 138 Z1 | Cumulative Impact | Rebuild line 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-118 | FROM->TO | 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | B | 188 | 0.19508 | 168.9167 | P13:138-161:GRDA:CATAUTO2:::HV: | Cumulative Impact | Rebuild line 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-118 | FROM->TO | 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | B | 188 | 0.13894 | 175.1417 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Cumulative Impact | Rebuild line 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | FROM->TO | 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | B | 188 | 0.14059 | 180.2339 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | Cumulative Impact | Rebuild line 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | FROM->TO | 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | B | 188 | 0.14059 | 190.5992 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Rebuild line 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-118 | FROM->TO | 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | B | 188 | 0.13894 | 194.2647 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | Cumulative Impact | Rebuild line 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-118 | FROM->TO | 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | B | 188 | 0.13894 | 203.1414 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Rebuild line 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1
Thermal | 04ALL | 1 | 26SP | T1 | GEN-2024-120 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.031912 | 103.0993 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T1 | GEN-2024-120 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.034341 | 103.3038 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-120 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | A | 1187 | 0.048288 | 103.8656 | System Intact | TDF Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-120 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.053244 | 104.9177 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-120 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.057392 | 106.1409 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-120 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.052764 | 106.3238 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-120 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.052849 | 106.5158 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-120 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.056734 | 107.841 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-120 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.052849 | 108.059 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-120 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.056734 | 109.5335 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-120 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.056734 | 109.534 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-120 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.056734 | 112.0538 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-120 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.062041 | 114.5102 | System Intact | TDF Impact | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-120 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.055135 | 114.6214 | System Intact | TDF Impact | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-120 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.056734 | 116.5975 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-120 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.040064 | 119.3706 | System Intact | TDF Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-120 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.040064 | 119.3706 | System Intact | TDF Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-120 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.040064 | 119.3706 | System Intact | TDF Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-120 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.038013 | 119.5141 | System Intact | TDF Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-120 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.038013 | 119.5141 | System Intact | TDF Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-120 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.038013 | 119.5141 | System Intact | TDF Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-125 | FROM->TO | 532793 NEOSHO 7 345 3WXFMR 536:N345 TX-2 161 2 | B | 550 | 0.063411 | 101.4582 | Single 533021 NEOSHO4 138 533023 N34534 138 1 | TDF Impact | Add 3-winding transformer 532793 NEOSHO 7 345 532825 N345 2 1 13 532939 N345 4 5 161 M2
Thermal | 00NR | 1 | 29WP | T1 | GEN-2024-125 | FROM->TO | 532937 NEOSHO 5 161 764310 G20-079-TAP 161 1 | B | 533 | 0.046393 | 101.6771 | P23:345:AECI:7BLACKBERRY:653::: | TDF Impact | Rebuild line 532937 NEOSHO 5 161 764310 G20-079-TAP 161 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-125 | FROM->TO | 532793 NEOSHO 7 345 3WXFMR 536:N345 TX-2 161 2 | B | 550 | 0.06975 | 103.5308 | Single 533021 NEOSHO4 138 533023 N34534 138 1 | TDF Impact | Add 3-winding transformer 532793 NEOSHO 7 345 532825 N345 2 1 13 532939 N345 4 5 161 M2
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-125 | FROM->TO | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.17309 | 104.394 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-125 | FROM->TO | 532793 NEOSHO 7 345 3WXFMR 536:N345 TX-2 161 2 | B | 550 | 0.070113 | 111.3295 | Single 533021 NEOSHO4 138 533023 N34534 138 1 | TDF Impact | Add 3-winding transformer 532793 NEOSHO 7 345 532825 N345 2 1 13 532939 N345 4 5 161 M2
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-125 | FROM->TO | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.15494 | 111.8275 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-125 | FROM->TO | 532777 NRSS7 345 532793 NEOSHO 7 345 1 | B | 1159 | 0.99044 | 115.0851 | P12:345:WERE:CANR-LATH-345:EHV: | TDF Impact | Rebuild line 532777 NRSS7 345 532793 NEOSHO 7 345 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-125 | FROM->TO | 532777 NRSS7 345 532793 NEOSHO 7 345 1 | B | 1159 | 0.99043 | 115.0927 | P23:345:WERE:LATH-BKRS:EHV: | TDF Impact | Rebuild line 532777 NRSS7 345 532793 NEOSHO 7 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-125 | FROM->TO | 532777 NRSS7 345 532793 NEOSHO 7 345 1 | B | 1159 | 0.99089 | 115.1543 | P12:345:WERE:CANR-LATH-345:EHV: | TDF Impact | Rebuild line 532777 NRSS7 345 532793 NEOSHO 7 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-125 | FROM->TO | 532777 NRSS7 345 532793 NEOSHO 7 345 1 | B | 1159 | 0.99088 | 115.1609 | P23:345:WERE:LATH-BKRS:EHV: | TDF Impact | Rebuild line 532777 NRSS7 345 532793 NEOSHO 7 345 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-125 | FROM->TO | 532777 NRSS7 345 532793 NEOSHO 7 345 1 | B | 1159 | 0.99044 | 115.269 | Single 532780 CANEYRV7 345 780720 G24-125-TAP 345 1 | TDF Impact | Rebuild line 532777 NRSS7 345 532793 NEOSHO 7 345 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-125 | FROM->TO | 532777 NRSS7 345 532793 NEOSHO 7 345 1 | B | 1159 | 0.99044 | 115.2716 | P23:345:WERE:CANR-BKRS:EHV: | TDF Impact | Rebuild line 532777 NRSS7 345 532793 NEOSHO 7 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-125 | FROM->TO | 532777 NRSS7 345 532793 NEOSHO 7 345 1 | B | 1159 | 0.99089 | 115.3106 | Single 532780 CANEYRV7 345 780720 G24-125-TAP 345 1 | TDF Impact | Rebuild line 532777 NRSS7 345 532793 NEOSHO 7 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-125 | FROM->TO | 532777 NRSS7 345 532793 NEOSHO 7 345 1 | B | 1159 | 0.99089 | 115.3137 | P23:345:WERE:CANR-BKRS:EHV: | TDF Impact | Rebuild line 532777 NRSS7 345 532793 NEOSHO 7 345 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-125 | FROM->TO | 532777 NRSS7 345 532793 NEOSHO 7 345 1 | B | 1159 | 0.98908 | 115.6655 | P12:345:WERE:LATH-ROSE-345:EHV: | TDF Impact | Rebuild line 532777 NRSS7 345 532793 NEOSHO 7 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-125 | FROM->TO | 532777 NRSS7 345 532793 NEOSHO 7 345 1 | B | 1159 | 0.98944 | 115.8195 | P12:345:WERE:LATH-ROSE-345:EHV: | TDF Impact | Rebuild line 532777 NRSS7 345 532793 NEOSHO 7 345 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-125 | FROM->TO | 532777 NRSS7 345 532793 NEOSHO 7 345 1 | B | 1159 | 0.97949 | 119.277 | Single 532780 CANEYRV7 345 780720 G24-125-TAP 345 1 | TDF Impact | Rebuild line 532777 NRSS7 345 532793 NEOSHO 7 345 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-125 | FROM->TO | 532777 NRSS7 345 532793 NEOSHO 7 345 1 | B | 1159 | 0.97949 | 119.2875 | P23:345:WERE:CANR-BKRS:EHV: | TDF Impact | Rebuild line 532777 NRSS7 345 532793 NEOSHO 7 345 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-125 | FROM->TO | 532777 NRSS7 345 532793 NEOSHO 7 345 1 | B | 1159 | 0.97949 | 121.1165 | P12:345:WERE:CANR-LATH-345:EHV: | TDF Impact | Rebuild line 532777 NRSS7 345 532793 NEOSHO 7 345 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-125 | FROM->TO | 532777 NRSS7 345 532793 NEOSHO 7 345 1 | B | 1159 | 0.97943 | 121.1263 | P23:345:WERE:LATH-BKRS:EHV: | TDF Impact | Rebuild line 532777 NRSS7 345 532793 NEOSHO 7 345 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-125 | FROM->TO | 532777 NRSS7 345 532793 NEOSHO 7 345 1 | B | 1159 | 0.97668 | 122.1748 | P12:345:WERE:LATH-ROSE-345:EHV: | TDF Impact | Rebuild line 532777 NRSS7 345 532793 NEOSHO 7 345 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-128 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | B | 234 | 0.088369 | 100.0952 | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | Rebuild line 515802 GRACMNT4 138 520814 ANADARK4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-128 | FROM->TO | 511468 L.E.S.-7 345 3WXFMR 520:LES 5 345 2 | B | 515 | 0.19605 | 101.4646 | P42:345:OKGE:SB_GRNT7313:::EHV: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-128 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | B | 173 | 0.071283 | 101.8021 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Rebuild line 511467 L.E.S.-4 138 511494 COMMTAP4 138 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-128 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | B | 173 | 0.071859 | 102.1634 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | TDF Impact | Rebuild line 511467 L.E.S.-4 138 511494 COMMTAP4 138 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-128 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | B | 234 | 0.088369 | 102.6013 | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | Rebuild line 515802 GRACMNT4 138 520814 ANADARK4 138 1
Thermal | 00NR | 1 | 29SP | T1 | GEN-2024-128 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | B | 211 | 0.070093 | 104.2208 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Rebuild line 511494 COMMTAP4 138 529304 OMDUNCN4 138 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-128 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | B | 173 | 0.072003 | 104.3322 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Rebuild line 511467 L.E.S.-4 138 511494 COMMTAP4 138 1
Thermal | 00NR | 1 | 29SP | T1 | GEN-2024-128 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | B | 211 | 0.070572 | 104.4644 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | TDF Impact | Rebuild line 511494 COMMTAP4 138 529304 OMDUNCN4 138 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-128 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | B | 173 | 0.072582 | 104.979 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | TDF Impact | Rebuild line 511467 L.E.S.-4 138 511494 COMMTAP4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-128 | FROM->TO | 515800 GRACMNT7 345 3WXFMR 524:524:GRACMNT3 345 3 | B | 478 | 0.36629 | 105.3618 | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | Add 3-winding transformer 515800 GRACMNT7 345 515801 GRCMNT11 13 515802 GRACMNT4 138 M2
Thermal | 00NR | 1 | 26SP | T1 | GEN-2024-128 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | B | 211 | 0.07028 | 105.818 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Rebuild line 511494 COMMTAP4 138 529304 OMDUNCN4 138 1
Thermal | 00NR | 1 | 26SP | T1 | GEN-2024-128 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | B | 211 | 0.070763 | 106.2948 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | TDF Impact | Rebuild line 511494 COMMTAP4 138 529304 OMDUNCN4 138 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-128 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | B | 234 | 0.1237 | 110.8778 | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | Rebuild line 515802 GRACMNT4 138 520814 ANADARK4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-128 | FROM->TO | 515800 GRACMNT7 345 3WXFMR 524:524:GRACMNT3 345 3 | B | 478 | 0.36401 | 111.6521 | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | Add 3-winding transformer 515800 GRACMNT7 345 515801 GRCMNT11 13 515802 GRACMNT4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-128 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | B | 171 | 0.061956 | 111.9556 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Rebuild line 511494 COMMTAP4 138 529304 OMDUNCN4 138 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-128 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | B | 171 | 0.062292 | 112.1038 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | TDF Impact | Rebuild line 511494 COMMTAP4 138 529304 OMDUNCN4 138 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-128 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | B | 171 | 0.062115 | 113.7961 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Rebuild line 511494 COMMTAP4 138 529304 OMDUNCN4 138 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-128 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | B | 171 | 0.06245 | 114.1433 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | TDF Impact | Rebuild line 511494 COMMTAP4 138 529304 OMDUNCN4 138 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-128 | FROM->TO | 511468 L.E.S.-7 345 3WXFMR 520:LES 5 345 2 | B | 515 | 0.20582 | 114.3077 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-128 | FROM->TO | 511468 L.E.S.-7 345 3WXFMR 520:LES 5 345 2 | B | 515 | 0.20715 | 114.3448 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-128 | FROM->TO | 511468 L.E.S.-7 345 3WXFMR 520:LES 5 345 2 | B | 515 | 0.21237 | 115.3782 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | TDF Impact | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-128 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | B | 106 | 0.046806 | 115.7772 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Line - Duncan - Duncan Tap - Duncan Eastside - Rush Springs Tap - Marlow 138 kV Rebuild.idv : 2025 ITP, PID: 900298, NTC, ISD: Unknown
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-128 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | B | 106 | 0.047152 | 116.0225 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | TDF Impact | Line - Duncan - Duncan Tap - Duncan Eastside - Rush Springs Tap - Marlow 138 kV Rebuild.idv : 2025 ITP, PID: 900298, NTC, ISD: Unknown
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-128 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | B | 106 | 0.046897 | 116.8055 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Line - Duncan - Duncan Tap - Duncan Eastside - Rush Springs Tap - Marlow 138 kV Rebuild.idv : 2025 ITP, PID: 900298, NTC, ISD: Unknown
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-128 | FROM->TO | 511468 L.E.S.-7 345 3WXFMR 520:LES 5 345 2 | B | 515 | 0.21381 | 116.8526 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | TDF Impact | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-128 | FROM->TO | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | B | 106 | 0.047245 | 117.3847 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | TDF Impact | Line - Duncan - Duncan Tap - Duncan Eastside - Rush Springs Tap - Marlow 138 kV Rebuild.idv : 2025 ITP, PID: 900298, NTC, ISD: Unknown
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-128 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | B | 106 | 0.046806 | 131.9717 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Rebuild line 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-128 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | B | 106 | 0.047152 | 132.2092 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | TDF Impact | Rebuild line 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-128 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | B | 106 | 0.046897 | 133.0547 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Rebuild line 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-128 | FROM->TO | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | B | 106 | 0.047245 | 133.612 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | TDF Impact | Rebuild line 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-129 | FROM->TO | 532780 CANEYRV7 345 532800 LATHAMS7 345 1 | B | 1159 | 0.97252 | 100.8022 | P12:345:WERE:NRSS-N345-345:EHV: | TDF Impact | Rebuild line 532780 CANEYRV7 345 532800 LATHAMS7 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-129 | FROM->TO | 532780 CANEYRV7 345 532800 LATHAMS7 345 1 | B | 1159 | 0.97252 | 100.8309 | P23:345:WERE:N345-345-20:EHV: | TDF Impact | Rebuild line 532780 CANEYRV7 345 532800 LATHAMS7 345 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-129 | FROM->TO | 532793 NEOSHO 7 345 3WXFMR 536:N345 TX-2 161 2 | B | 550 | 0.092767 | 101.4582 | Single 533021 NEOSHO4 138 533023 N34534 138 1 | TDF Impact | Add 3-winding transformer 532793 NEOSHO 7 345 532825 N345 2 1 13 532939 N345 4 5 161 M2
Thermal | 00NR | 1 | 29WP | T1 | GEN-2024-129 | FROM->TO | 532937 NEOSHO 5 161 764310 G20-079-TAP 161 1 | B | 533 | 0.063219 | 101.6771 | P23:345:AECI:7BLACKBERRY:653::: | TDF Impact | Rebuild line 532937 NEOSHO 5 161 764310 G20-079-TAP 161 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-129 | FROM->TO | 532793 NEOSHO 7 345 3WXFMR 536:N345 TX-2 161 2 | B | 550 | 0.09931 | 103.5308 | Single 533021 NEOSHO4 138 533023 N34534 138 1 | TDF Impact | Add 3-winding transformer 532793 NEOSHO 7 345 532825 N345 2 1 13 532939 N345 4 5 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-129 | FROM->TO | 532793 NEOSHO 7 345 3WXFMR 536:N345 TX-1 138 1 | B | 400 | 0.095642 | 105.5559 | Single 532937 NEOSHO5 161 532939 N34545 161 1 | Cumulative Impact | Add 3-winding transformer 532793 NEOSHO 7 345 532824 N345 1 1 13 533023 N345 3 4 138 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-129 | FROM->TO | 532793 NEOSHO 7 345 3WXFMR 536:N345 TX-1 138 1 | B | 400 | 0.095642 | 105.5635 | Single 532793 NEOSHO7 345 532939 N34545 161 532825 'N345 2 1 ' 13 2 | Cumulative Impact | Add 3-winding transformer 532793 NEOSHO 7 345 532824 N345 1 1 13 533023 N345 3 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-129 | FROM->TO | 532793 NEOSHO 7 345 3WXFMR 536:N345 TX-2 161 2 | B | 550 | 0.099768 | 111.3295 | Single 533021 NEOSHO4 138 533023 N34534 138 1 | TDF Impact | Add 3-winding transformer 532793 NEOSHO 7 345 532825 N345 2 1 13 532939 N345 4 5 161 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-129 | FROM->TO | 533020 NEOSHOS4 138 3WXFMR 536:NEOSHO TX-5 138 1 | B | 165 | 0.03672 | 113.4155 | Single 532937 NEOSHO5 161 532939 N34545 161 1 | TDF Impact | Add 3-winding transformer 532937 NEOSHO 5 161 532959 NEOSH5 1 13 533020 NEOSHOS4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-129 | FROM->TO | 533020 NEOSHOS4 138 3WXFMR 536:NEOSHO TX-5 138 1 | B | 165 | 0.03672 | 113.4225 | Single 532793 NEOSHO7 345 532939 N34545 161 532825 'N345 2 1 ' 13 2 | TDF Impact | Add 3-winding transformer 532937 NEOSHO 5 161 532959 NEOSH5 1 13 533020 NEOSHOS4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-129 | FROM->TO | 532777 NRSS7 345 532793 NEOSHO 7 345 1 | B | 1159 | 0.99044 | 115.0851 | P12:345:WERE:CANR-LATH-345:EHV: | TDF Impact | Rebuild line 532777 NRSS7 345 532793 NEOSHO 7 345 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-129 | FROM->TO | 532777 NRSS7 345 532793 NEOSHO 7 345 1 | B | 1159 | 0.99043 | 115.0927 | P23:345:WERE:LATH-BKRS:EHV: | TDF Impact | Rebuild line 532777 NRSS7 345 532793 NEOSHO 7 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-129 | FROM->TO | 532777 NRSS7 345 532793 NEOSHO 7 345 1 | B | 1159 | 0.99089 | 115.1543 | P12:345:WERE:CANR-LATH-345:EHV: | TDF Impact | Rebuild line 532777 NRSS7 345 532793 NEOSHO 7 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-129 | FROM->TO | 532777 NRSS7 345 532793 NEOSHO 7 345 1 | B | 1159 | 0.99088 | 115.1609 | P23:345:WERE:LATH-BKRS:EHV: | TDF Impact | Rebuild line 532777 NRSS7 345 532793 NEOSHO 7 345 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-129 | FROM->TO | 532777 NRSS7 345 532793 NEOSHO 7 345 1 | B | 1159 | 0.99044 | 115.269 | Single 532780 CANEYRV7 345 780720 G24-125-TAP 345 1 | TDF Impact | Rebuild line 532777 NRSS7 345 532793 NEOSHO 7 345 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-129 | FROM->TO | 532777 NRSS7 345 532793 NEOSHO 7 345 1 | B | 1159 | 0.99044 | 115.2716 | P23:345:WERE:CANR-BKRS:EHV: | TDF Impact | Rebuild line 532777 NRSS7 345 532793 NEOSHO 7 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-129 | FROM->TO | 532777 NRSS7 345 532793 NEOSHO 7 345 1 | B | 1159 | 0.99089 | 115.3106 | Single 532780 CANEYRV7 345 780720 G24-125-TAP 345 1 | TDF Impact | Rebuild line 532777 NRSS7 345 532793 NEOSHO 7 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-129 | FROM->TO | 532777 NRSS7 345 532793 NEOSHO 7 345 1 | B | 1159 | 0.99089 | 115.3137 | P23:345:WERE:CANR-BKRS:EHV: | TDF Impact | Rebuild line 532777 NRSS7 345 532793 NEOSHO 7 345 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-129 | FROM->TO | 532777 NRSS7 345 532793 NEOSHO 7 345 1 | B | 1159 | 0.98908 | 115.6655 | P12:345:WERE:LATH-ROSE-345:EHV: | TDF Impact | Rebuild line 532777 NRSS7 345 532793 NEOSHO 7 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-129 | FROM->TO | 532777 NRSS7 345 532793 NEOSHO 7 345 1 | B | 1159 | 0.98944 | 115.8195 | P12:345:WERE:LATH-ROSE-345:EHV: | TDF Impact | Rebuild line 532777 NRSS7 345 532793 NEOSHO 7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-129 | FROM->TO | 532793 NEOSHO 7 345 3WXFMR 536:N345 TX-1 138 1 | B | 400 | 0.095013 | 117.1576 | Single 532937 NEOSHO5 161 532939 N34545 161 1 | Cumulative Impact | Add 3-winding transformer 532793 NEOSHO 7 345 532824 N345 1 1 13 533023 N345 3 4 138 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-129 | FROM->TO | 532793 NEOSHO 7 345 3WXFMR 536:N345 TX-1 138 1 | B | 400 | 0.095013 | 117.1612 | Single 532793 NEOSHO7 345 532939 N34545 161 532825 'N345 2 1 ' 13 2 | Cumulative Impact | Add 3-winding transformer 532793 NEOSHO 7 345 532824 N345 1 1 13 533023 N345 3 4 138 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-129 | FROM->TO | 532777 NRSS7 345 532793 NEOSHO 7 345 1 | B | 1159 | 0.97949 | 119.277 | Single 532780 CANEYRV7 345 780720 G24-125-TAP 345 1 | TDF Impact | Rebuild line 532777 NRSS7 345 532793 NEOSHO 7 345 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-129 | FROM->TO | 532777 NRSS7 345 532793 NEOSHO 7 345 1 | B | 1159 | 0.97949 | 119.2875 | P23:345:WERE:CANR-BKRS:EHV: | TDF Impact | Rebuild line 532777 NRSS7 345 532793 NEOSHO 7 345 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-129 | FROM->TO | 532777 NRSS7 345 532793 NEOSHO 7 345 1 | B | 1159 | 0.97949 | 121.1165 | P12:345:WERE:CANR-LATH-345:EHV: | TDF Impact | Rebuild line 532777 NRSS7 345 532793 NEOSHO 7 345 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-129 | FROM->TO | 532777 NRSS7 345 532793 NEOSHO 7 345 1 | B | 1159 | 0.97943 | 121.1263 | P23:345:WERE:LATH-BKRS:EHV: | TDF Impact | Rebuild line 532777 NRSS7 345 532793 NEOSHO 7 345 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-129 | FROM->TO | 532777 NRSS7 345 532793 NEOSHO 7 345 1 | B | 1159 | 0.97668 | 122.1748 | P12:345:WERE:LATH-ROSE-345:EHV: | TDF Impact | Rebuild line 532777 NRSS7 345 532793 NEOSHO 7 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-129 | FROM->TO | 532793 NEOSHO 7 345 3WXFMR 536:N345 TX-1 138 1 | B | 400 | 0.098814 | 123.3043 | Single 532937 NEOSHO5 161 532939 N34545 161 1 | Cumulative Impact | Add 3-winding transformer 532793 NEOSHO 7 345 532824 N345 1 1 13 533023 N345 3 4 138 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-129 | FROM->TO | 532793 NEOSHO 7 345 3WXFMR 536:N345 TX-1 138 1 | B | 400 | 0.098814 | 123.3093 | Single 532793 NEOSHO7 345 532939 N34545 161 532825 'N345 2 1 ' 13 2 | Cumulative Impact | Add 3-winding transformer 532793 NEOSHO 7 345 532824 N345 1 1 13 533023 N345 3 4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-129 | FROM->TO | 533020 NEOSHOS4 138 3WXFMR 536:NEOSHO TX-5 138 1 | B | 165 | 0.037516 | 124.761 | Single 532937 NEOSHO5 161 532939 N34545 161 1 | TDF Impact | Add 3-winding transformer 532937 NEOSHO 5 161 532959 NEOSH5 1 13 533020 NEOSHOS4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-129 | FROM->TO | 533020 NEOSHOS4 138 3WXFMR 536:NEOSHO TX-5 138 1 | B | 165 | 0.037516 | 124.7681 | Single 532793 NEOSHO7 345 532939 N34545 161 532825 'N345 2 1 ' 13 2 | TDF Impact | Add 3-winding transformer 532937 NEOSHO 5 161 532959 NEOSH5 1 13 533020 NEOSHOS4 138 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-129 | FROM->TO | 533020 NEOSHOS4 138 3WXFMR 536:NEOSHO TX-5 138 1 | B | 165 | 0.033451 | 129.6064 | Single 532793 NEOSHO7 345 532939 N34545 161 532825 'N345 2 1 ' 13 2 | TDF Impact | Add 3-winding transformer 532937 NEOSHO 5 161 532959 NEOSH5 1 13 533020 NEOSHOS4 138 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-129 | FROM->TO | 533020 NEOSHOS4 138 3WXFMR 536:NEOSHO TX-5 138 1 | B | 165 | 0.033451 | 129.6104 | Single 532937 NEOSHO5 161 532939 N34545 161 1 | TDF Impact | Add 3-winding transformer 532937 NEOSHO 5 161 532959 NEOSH5 1 13 533020 NEOSHOS4 138 M2
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-139 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | B | 756 | 0.0616 | 101.463 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild line 541200 PHILL 7 345 541201 SIBLEY 7 345 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-139 | FROM->TO | 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | B | 956 | 0.46631 | 101.9427 | P23:345:AECI:7BLACKBERRY:6_2::: | TDF Impact | Rebuild line 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-139 | FROM->TO | 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | B | 956 | 0.46631 | 101.9438 | P23:345:AECI:7BLACKBERRY:6_3::: | TDF Impact | Rebuild line 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-139 | FROM->TO | 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | B | 956 | 0.46655 | 103.0407 | Single 300739 7BLACKBERRY 345 785580 G24-287-TAP 345 1 | TDF Impact | Rebuild line 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-139 | FROM->TO | 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | B | 956 | 0.46729 | 103.5013 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | TDF Impact | Rebuild line 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-139 | FROM->TO | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.11794 | 104.394 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-139 | FROM->TO | 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | B | 956 | 0.46826 | 105.9563 | P23:345:AECI:7BLACKBERRY:6_2::: | TDF Impact | Rebuild line 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-139 | FROM->TO | 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | B | 956 | 0.46826 | 105.9589 | P23:345:AECI:7BLACKBERRY:6_3::: | TDF Impact | Rebuild line 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-139 | FROM->TO | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.11416 | 111.8275 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-139 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | B | 756 | 0.062532 | 117.5821 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild line 541200 PHILL 7 345 541201 SIBLEY 7 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-140 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.045572 | 100.5915 | P23:345:MEC:HIGHLAND:903::EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-140 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.045572 | 100.6154 | P23:345:MEC:HIGHLAND:902::EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-140 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.061572 | 100.6843 | P12:230.0:UMZ:# N-1 #:: LINE TWIN CH4-SIOUXCY4-1 :HV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 02ALL | 1 | 26SP | T0 | GEN-2024-140 | FROM->TO | 640113 CLRWATR7 115 640305 ONEILL 7 115 1 | B | 120 | 0.1712 | 101.1484 | P42:345:NPPD:BKR-HOS-3308:::: | Cumulative Impact | 640_NPPD_NewBranch_Holt-Antilope3_345.idv : 2024 ITP, PID: 94842, NTC, ISD: 12/31/2029
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-140 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.045572 | 101.5782 | Single 635368 OBRIEN3 345 635400 HIGHLAND3 345 1 | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-140 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.045572 | 101.5782 | P12:345:MEC:OBRIEN:HIGHLAND:1REACTOR:EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 02ALL | 1 | 29SP | T0 | GEN-2024-140 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | B | 320 | 0.067686 | 101.6588 | Single 635200 RAUN3 345 635214 J279NEAL4G 24 1 | Cumulative Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 02ALL | 1 | 29SP | T0 | GEN-2024-140 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | B | 320 | 0.067686 | 101.6588 | P11:345:MEC:NEAL:4 | Cumulative Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 02ALL | 1 | 29SP | T0 | GEN-2024-140 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | B | 320 | 0.070557 | 101.7336 | Single 640163 EMERSON7 115 640387 TWINCH7 115 1 | Cumulative Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 02ALL | 1 | 26SP | T0 | GEN-2024-140 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | B | 320 | 0.093205 | 101.7487 | P13:345-230.0:UMZ:# N-1 #:: 3WND SIOUXCY3-SIOUXCY2-SIOUXC29-1 652_ SC2 KU1B_:EHV: | Cumulative Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 02ALL | 1 | 29SP | T0 | GEN-2024-140 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | B | 320 | 0.086395 | 101.8142 | Single 640226 HOSKINS3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 02ALL | 1 | 29SP | T0 | GEN-2024-140 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | B | 320 | 0.086395 | 101.8163 | Single 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 02ALL | 1 | 26SP | T0 | GEN-2024-140 | FROM->TO | 640072 BATTLCR7 115 640296 NORFK.N7 115 1 | B | 193 | 0.39194 | 102.5395 | Single 640226 HOSKINS3 345 763443 G18-131-TAP 345 1 | TDF Impact | 640_NPPD_NewBranch_Holt-Antilope3_345.idv : 2024 ITP, PID: 94842, NTC, ISD: 12/31/2029
Thermal | 02ALL | 1 | 29SP | T0 | GEN-2024-140 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | B | 320 | 0.067685 | 103.0404 | P55:345:XEL:PRI1 | Cumulative Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-140 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.045872 | 103.0767 | P23:345:MEC:OBRIEN:903::EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-140 | FROM->TO | 640227 HOSKINS4 230 3WXFMR 640:HOSKINS T1 230 1 | B | 187 | 0.031401 | 103.3209 | P13:115-345:NPPD:HOSKINS3:T4::: | TDF Impact | Add 3-winding transformer 640227 HOSKINS4 230 640228 HOSKINS7 115 643083 HOSKINS T1 9 13 M2
Thermal | 02ALL | 1 | 29SP | T0 | GEN-2024-140 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | B | 320 | 0.067686 | 103.4776 | Single 640425 S.SIOUXCITY8 69 640424 S.SIOUXCITY7 115 643170 'S.SIOUXCYT19' 13 1 | Cumulative Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-140 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.045485 | 104.0624 | P23:345:MEC:OBRIEN:906::EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 02ALL | 1 | 29SP | T0 | GEN-2024-140 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | B | 320 | 0.064257 | 105.8279 | P13:345-230.0:UMZ:# N-1 #:: 3WND SIOUXCY3-SIOUXCY2-SIOUXC29-1 652_ SC2 KU1B_:EHV: | Cumulative Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 02ALL | 1 | 29WP | T0 | GEN-2024-140 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | A | 320 | 0.067399 | 107.0771 | System Intact | TDF Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 02ALL | 1 | 26SP | T0 | GEN-2024-140 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | B | 320 | 0.19149 | 109.1304 | Single 635200 RAUN3 345 640226 HOSKINS3 345 1 | Cumulative Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 02ALL | 1 | 26SP | T0 | GEN-2024-140 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | B | 320 | 0.10276 | 109.5852 | P12:345.0:UMZ:# N-1 #:: LINE RAUN 3-SIOUXCY3-1 :EHV: | Cumulative Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 02ALL | 1 | 29WP | T0 | GEN-2024-140 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | B | 320 | 0.086176 | 113.5344 | Single 640226 HOSKINS3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 02ALL | 1 | 29WP | T0 | GEN-2024-140 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | B | 320 | 0.086176 | 113.5475 | Single 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 02ALL | 1 | 29WP | T0 | GEN-2024-140 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | B | 320 | 0.067414 | 114.1774 | P55:345:MEC:ORIENT | Cumulative Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 02ALL | 1 | 29WP | T0 | GEN-2024-140 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | B | 320 | 0.074179 | 114.4083 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOMP3-FTTHOM2-LNX3-Z :EHV: | Cumulative Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 02ALL | 1 | 29WP | T0 | GEN-2024-140 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | B | 320 | 0.074179 | 114.4096 | P12:345.0:UMZ:# N-1 #:: LINE GR PRAIRIE 3-GRPRAR2-LNX3-Z :EHV: | Cumulative Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 02ALL | 1 | 29WP | T0 | GEN-2024-140 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | B | 320 | 0.074179 | 114.4098 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOM2-LNX3-GRPRAR2-LNX3-1 :EHV: | Cumulative Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 02ALL | 1 | 29WP | T0 | GEN-2024-140 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | B | 320 | 0.067398 | 114.4544 | P55:345:XEL:PRI1 | Cumulative Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 02ALL | 1 | 29WP | T0 | GEN-2024-140 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | B | 320 | 0.067399 | 115.3828 | Single 640425 S.SIOUXCITY8 69 640424 S.SIOUXCITY7 115 643170 'S.SIOUXCYT19' 13 1 | Cumulative Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 02ALL | 1 | 29SP | T0 | GEN-2024-140 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | B | 320 | 0.12323 | 116.5719 | Single 635200 RAUN3 345 640226 HOSKINS3 345 1 | Cumulative Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 02ALL | 1 | 29SP | T0 | GEN-2024-140 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | B | 320 | 0.070545 | 116.7129 | P12:345.0:UMZ:# N-1 #:: LINE RAUN 3-SIOUXCY3-1 :EHV: | Cumulative Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 02ALL | 1 | 29WP | T0 | GEN-2024-140 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | B | 320 | 0.070186 | 118.405 | P12:345.0:UMZ:# N-1 #:: LINE RAUN 3-SIOUXCY3-1 :EHV: | Cumulative Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 02ALL | 1 | 29WP | T0 | GEN-2024-140 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | B | 320 | 0.1225 | 136.3055 | Single 635200 RAUN3 345 640226 HOSKINS3 345 1 | Cumulative Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-143 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.075571 | 100.0488 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29L | T0 | GEN-2024-143 | FROM->TO | 511541 DEMPSEYR POI 230 511557 CHISHOLM6 230 1 | B | 439 | 0.092264 | 100.3116 | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | Cumulative Impact | Rebuild line 511541 DEMPSEYR POI 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-143 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.06169 | 100.533 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-143 | FROM->TO | 523221 XIT_INTG 6 230 3WXFMR 526:SIEM_T126401 115 1 | B | 284 | 0.17256 | 101.4148 | Single 523309 MOORE_CNTY6 230 523308 MOORE_E3 115 523302 'MOORE_TR1 1' 13 1 | Cumulative Impact | Add 3-winding transformer 523219 XIT_INTG TR1 13 523220 XIT_INTG 3 115 523221 XIT_INTG 6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-143 | FROM->TO | 523959 POTTER_CO 6 230 524010 ROLLHILLS 6 230 1 | B | 548 | 0.071051 | 103.4659 | MULTIGEN523979 | Cumulative Impact | Rebuild line 523959 POTTER_CO 6 230 524010 ROLLHILLS 6 230 1
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-143 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.079609 | 103.9266 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-143 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.077927 | 104.7552 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-143 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.077927 | 104.888 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-143 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.081907 | 107.2243 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-143 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063077 | 107.2793 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-143 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063077 | 107.2794 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-143 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.081907 | 107.2951 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-143 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063077 | 107.3093 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T1 | GEN-2024-143 | FROM->TO | 523220 XIT_INTG 3 115 523228 DALLAM 3 115 1 | B | 297 | 0.40682 | 107.6799 | Single 523221 XIT_INTG6 230 523309 MOORE_CNTY6 230 1 | TDF Impact | Rebuild line 523220 XIT_INTG 3 115 523228 DALLAM 3 115 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-143 | FROM->TO | 523220 XIT_INTG 3 115 523228 DALLAM 3 115 1 | B | 271 | 0.37348 | 107.7522 | Single 523221 XIT_INTG6 230 523309 MOORE_CNTY6 230 1 | TDF Impact | Rebuild line 523220 XIT_INTG 3 115 523228 DALLAM 3 115 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-143 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063077 | 107.7557 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-143 | FROM->TO | 531512 HARBNGR7 345 3WXFMR 534:HARBGR345 345 1 | B | 385 | 0.057704 | 107.8261 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Add 3-winding transformer 531510 HARBNGR3 115 531511 HARBNGR-1 13 531512 HARBNGR7 345 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-143 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063077 | 108.2747 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-143 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063077 | 111.3621 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-143 | FROM->TO | 523221 XIT_INTG 6 230 3WXFMR 526:SIEM_T126401 115 1 | B | 284 | 0.37348 | 113.4078 | Single 523221 XIT_INTG6 230 523309 MOORE_CNTY6 230 1 | TDF Impact | Add 3-winding transformer 523219 XIT_INTG TR1 13 523220 XIT_INTG 3 115 523221 XIT_INTG 6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-143 | FROM->TO | 523959 POTTER_CO 6 230 524010 ROLLHILLS 6 230 1 | B | 548 | 0.065737 | 114.0984 | MULTIGEN523978 | Cumulative Impact | Rebuild line 523959 POTTER_CO 6 230 524010 ROLLHILLS 6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-143 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.077008 | 115.0541 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-143 | FROM->TO | 523309 MOORE_CNTY 6 230 3WXFMR 526:ENRCO 136402 115 1 | B | 239 | 0.12016 | 115.4027 | P12:115:SPS:W80.1.XIT.DALM:::HV: | Cumulative Impact | 526_New_MooreCounty_2ndTransformer_230_115.idv : PID: 220817, 2024 ITP, NTC, ISD: 5/15/2029
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-143 | FROM->TO | 523309 MOORE_CNTY 6 230 3WXFMR 526:ENRCO 136402 115 1 | B | 239 | 0.12016 | 115.4027 | Single 523220 XIT_INTG3 115 523228 DALLAM3 115 1 | Cumulative Impact | 526_New_MooreCounty_2ndTransformer_230_115.idv : PID: 220817, 2024 ITP, NTC, ISD: 5/15/2029
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-143 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.079378 | 118.9427 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-143 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.079378 | 119.313 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-143 | FROM->TO | 523309 MOORE_CNTY 6 230 3WXFMR 526:ENRCO 136402 115 1 | B | 239 | 0.12016 | 121.0708 | Single 523221 XIT_INTG6 230 523220 XIT_INTG3 115 523219 'XIT_INTG TR1' 13 1 | Cumulative Impact | 526_New_MooreCounty_2ndTransformer_230_115.idv : PID: 220817, 2024 ITP, NTC, ISD: 5/15/2029
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-143 | FROM->TO | 523309 MOORE_CNTY 6 230 3WXFMR 526:ENRCO 136402 115 1 | B | 239 | 0.19816 | 126.5251 | P12:230:SPS:K98:1:XITINTG_CHAN+TASCOS___:HV: | Cumulative Impact | 526_New_MooreCounty_2ndTransformer_230_115.idv : PID: 220817, 2024 ITP, NTC, ISD: 5/15/2029
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-145 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.075571 | 100.0488 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29L | T0 | GEN-2024-145 | FROM->TO | 511541 DEMPSEYR POI 230 511557 CHISHOLM6 230 1 | B | 439 | 0.092264 | 100.3116 | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | Cumulative Impact | Rebuild line 511541 DEMPSEYR POI 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-145 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.06169 | 100.533 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-145 | FROM->TO | 523221 XIT_INTG 6 230 3WXFMR 526:SIEM_T126401 115 1 | B | 284 | 0.17256 | 101.4148 | Single 523309 MOORE_CNTY6 230 523308 MOORE_E3 115 523302 'MOORE_TR1 1' 13 1 | Cumulative Impact | Add 3-winding transformer 523219 XIT_INTG TR1 13 523220 XIT_INTG 3 115 523221 XIT_INTG 6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-145 | FROM->TO | 523959 POTTER_CO 6 230 524010 ROLLHILLS 6 230 1 | B | 548 | 0.071051 | 103.4659 | MULTIGEN523979 | Cumulative Impact | Rebuild line 523959 POTTER_CO 6 230 524010 ROLLHILLS 6 230 1
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-145 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.079609 | 103.9266 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-145 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.077927 | 104.7552 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-145 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.077927 | 104.888 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-145 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.081907 | 107.2243 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-145 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063077 | 107.2793 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-145 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063077 | 107.2794 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-145 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.081907 | 107.2951 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-145 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063077 | 107.3093 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T1 | GEN-2024-145 | FROM->TO | 523220 XIT_INTG 3 115 523228 DALLAM 3 115 1 | B | 297 | 0.40682 | 107.6799 | Single 523221 XIT_INTG6 230 523309 MOORE_CNTY6 230 1 | TDF Impact | Rebuild line 523220 XIT_INTG 3 115 523228 DALLAM 3 115 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-145 | FROM->TO | 523220 XIT_INTG 3 115 523228 DALLAM 3 115 1 | B | 271 | 0.37348 | 107.7522 | Single 523221 XIT_INTG6 230 523309 MOORE_CNTY6 230 1 | TDF Impact | Rebuild line 523220 XIT_INTG 3 115 523228 DALLAM 3 115 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-145 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063077 | 107.7557 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-145 | FROM->TO | 531512 HARBNGR7 345 3WXFMR 534:HARBGR345 345 1 | B | 385 | 0.057704 | 107.8261 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Add 3-winding transformer 531510 HARBNGR3 115 531511 HARBNGR-1 13 531512 HARBNGR7 345 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-145 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063077 | 108.2747 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-145 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063077 | 111.3621 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-145 | FROM->TO | 523221 XIT_INTG 6 230 3WXFMR 526:SIEM_T126401 115 1 | B | 284 | 0.37348 | 113.4078 | Single 523221 XIT_INTG6 230 523309 MOORE_CNTY6 230 1 | TDF Impact | Add 3-winding transformer 523219 XIT_INTG TR1 13 523220 XIT_INTG 3 115 523221 XIT_INTG 6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-145 | FROM->TO | 523959 POTTER_CO 6 230 524010 ROLLHILLS 6 230 1 | B | 548 | 0.065737 | 114.0984 | MULTIGEN523978 | Cumulative Impact | Rebuild line 523959 POTTER_CO 6 230 524010 ROLLHILLS 6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-145 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.077008 | 115.0541 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-145 | FROM->TO | 523309 MOORE_CNTY 6 230 3WXFMR 526:ENRCO 136402 115 1 | B | 239 | 0.12016 | 115.4027 | P12:115:SPS:W80.1.XIT.DALM:::HV: | Cumulative Impact | 526_New_MooreCounty_2ndTransformer_230_115.idv : PID: 220817, 2024 ITP, NTC, ISD: 5/15/2029
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-145 | FROM->TO | 523309 MOORE_CNTY 6 230 3WXFMR 526:ENRCO 136402 115 1 | B | 239 | 0.12016 | 115.4027 | Single 523220 XIT_INTG3 115 523228 DALLAM3 115 1 | Cumulative Impact | 526_New_MooreCounty_2ndTransformer_230_115.idv : PID: 220817, 2024 ITP, NTC, ISD: 5/15/2029
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-145 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.079378 | 118.9427 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-145 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.079378 | 119.313 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-145 | FROM->TO | 523309 MOORE_CNTY 6 230 3WXFMR 526:ENRCO 136402 115 1 | B | 239 | 0.12016 | 121.0708 | Single 523221 XIT_INTG6 230 523220 XIT_INTG3 115 523219 'XIT_INTG TR1' 13 1 | Cumulative Impact | 526_New_MooreCounty_2ndTransformer_230_115.idv : PID: 220817, 2024 ITP, NTC, ISD: 5/15/2029
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-145 | FROM->TO | 523309 MOORE_CNTY 6 230 3WXFMR 526:ENRCO 136402 115 1 | B | 239 | 0.19816 | 126.5251 | P12:230:SPS:K98:1:XITINTG_CHAN+TASCOS___:HV: | Cumulative Impact | 526_New_MooreCounty_2ndTransformer_230_115.idv : PID: 220817, 2024 ITP, NTC, ISD: 5/15/2029
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-154 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | B | 234 | 0.03427 | 100.0952 | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | Rebuild line 515802 GRACMNT4 138 520814 ANADARK4 138 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-154 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | B | 234 | 0.03427 | 102.6013 | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | Rebuild line 515802 GRACMNT4 138 520814 ANADARK4 138 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-159 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.073955 | 100.0488 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-159 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063708 | 100.533 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-159 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.077999 | 103.9266 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-159 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.076993 | 104.7552 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-159 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.076993 | 104.888 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-159 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.080976 | 107.2243 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-159 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.064675 | 107.2793 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-159 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.064675 | 107.2794 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-159 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.080976 | 107.2951 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-159 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.064675 | 107.3093 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-159 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.064675 | 107.7557 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-159 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.064675 | 108.2747 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-159 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.064675 | 111.3621 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-159 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.075075 | 115.0541 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-159 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.07813 | 118.9427 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-159 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.07813 | 119.313 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-162 | FROM->TO | 640080 BELDEN 7 115 640212 HARTGTN7 115 1 | B | 123 | 0.032294 | 100.1109 | P13:230-115.0:UMZ:# N-1 #:: 3WND UTICAJC4-UTICAJC7-UTICAJC9-1 652_ UJ KV3A_:HV: | TDF Impact | Rebuild line 640080 BELDEN 7 115 640212 HARTGTN7 115 1
Thermal | 00NR | 1 | 29SP | T1 | GEN-2024-162 | FROM->TO | 652552 SIOUXCY2 230 659900 EAGLE___-NI4 230 1 | B | 386 | 0.066472 | 100.2184 | P23:345:XEL:396 BKR SPK:::EHV: | TDF Impact | Rebuild line 652552 SIOUXCY2 230 659900 EAGLE___-NI4 230 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-162 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.058957 | 100.6843 | P12:230.0:UMZ:# N-1 #:: LINE TWIN CH4-SIOUXCY4-1 :HV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 02ALL | 1 | 29SP | T0 | GEN-2024-162 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | B | 320 | 0.60552 | 101.6588 | Single 635200 RAUN3 345 635214 J279NEAL4G 24 1 | TDF Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 02ALL | 1 | 29SP | T0 | GEN-2024-162 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | B | 320 | 0.60552 | 101.6588 | P11:345:MEC:NEAL:4 | TDF Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 02ALL | 1 | 29SP | T0 | GEN-2024-162 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | B | 320 | 0.6446 | 101.7336 | Single 640163 EMERSON7 115 640387 TWINCH7 115 1 | TDF Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 02ALL | 1 | 26SP | T0 | GEN-2024-162 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | B | 320 | 0.55612 | 101.7487 | P13:345-230.0:UMZ:# N-1 #:: 3WND SIOUXCY3-SIOUXCY2-SIOUXC29-1 652_ SC2 KU1B_:EHV: | TDF Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 02ALL | 1 | 29SP | T0 | GEN-2024-162 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | B | 320 | 0.61656 | 101.8142 | Single 640226 HOSKINS3 345 763982 G19-069TAP 345 1 | TDF Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 02ALL | 1 | 29SP | T0 | GEN-2024-162 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | B | 320 | 0.61656 | 101.8163 | Single 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | TDF Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-162 | FROM->TO | 652552 SIOUXCY2 230 659900 EAGLE___-NI4 230 1 | B | 370 | 0.065966 | 101.858 | P23:345:XEL:396 BKR SPK:::EHV: | TDF Impact | Rebuild line 652552 SIOUXCY2 230 659900 EAGLE___-NI4 230 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-162 | FROM->TO | 640080 BELDEN 7 115 640212 HARTGTN7 115 1 | B | 123 | 0.091441 | 102.727 | P12:230.0:UMZ:# N-1 #:: LINE TWIN CH4-SIOUXCY4-1 :HV: | TDF Impact | Rebuild line 640080 BELDEN 7 115 640212 HARTGTN7 115 1
Thermal | 02ALL | 1 | 29SP | T0 | GEN-2024-162 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | B | 320 | 0.60552 | 103.0404 | P55:345:XEL:PRI1 | TDF Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-162 | FROM->TO | 640080 BELDEN 7 115 640212 HARTGTN7 115 1 | B | 132 | 0.093497 | 103.2444 | P12:230.0:UMZ:# N-1 #:: LINE TWIN CH4-SIOUXCY4-1 :HV: | TDF Impact | Rebuild line 640080 BELDEN 7 115 640212 HARTGTN7 115 1
Thermal | 02ALL | 1 | 29SP | T0 | GEN-2024-162 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | B | 320 | 0.60552 | 103.4776 | Single 640425 S.SIOUXCITY8 69 640424 S.SIOUXCITY7 115 643170 'S.SIOUXCYT19' 13 1 | TDF Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 02ALL | 1 | 29SP | T0 | GEN-2024-162 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | B | 320 | 0.54615 | 105.8279 | P13:345-230.0:UMZ:# N-1 #:: 3WND SIOUXCY3-SIOUXCY2-SIOUXC29-1 652_ SC2 KU1B_:EHV: | TDF Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-162 | FROM->TO | 640080 BELDEN 7 115 640212 HARTGTN7 115 1 | B | 123 | 0.035047 | 106.1714 | P12:230.0:UMZ:# N-1 #:: LINE SIOUXCY4-RASMUSN-ER4-1 :HV: | TDF Impact | Rebuild line 640080 BELDEN 7 115 640212 HARTGTN7 115 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-162 | FROM->TO | 640080 BELDEN 7 115 640212 HARTGTN7 115 1 | B | 123 | 0.030111 | 106.3318 | P12:115.0:UMZ:# N-1 #:: LINE BLMFLD 7-GAVINS 7-1 :HV: | TDF Impact | Rebuild line 640080 BELDEN 7 115 640212 HARTGTN7 115 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-162 | FROM->TO | 640080 BELDEN 7 115 640212 HARTGTN7 115 1 | B | 123 | 0.037682 | 106.6574 | Single 640520 ANTELOPE3 345 763443 G18-131-TAP 345 1 | TDF Impact | Rebuild line 640080 BELDEN 7 115 640212 HARTGTN7 115 1
Thermal | 02ALL | 1 | 29WP | T0 | GEN-2024-162 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | A | 320 | 0.60564 | 107.0771 | System Intact | TDF Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-162 | FROM->TO | 640080 BELDEN 7 115 640212 HARTGTN7 115 1 | B | 123 | 0.032797 | 107.647 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOM2-LNX3-GRPRAR2-LNX3-1 :EHV: | TDF Impact | Rebuild line 640080 BELDEN 7 115 640212 HARTGTN7 115 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-162 | FROM->TO | 640080 BELDEN 7 115 640212 HARTGTN7 115 1 | B | 123 | 0.032797 | 107.649 | P12:345.0:UMZ:# N-1 #:: LINE GR PRAIRIE 3-GRPRAR2-LNX3-Z :EHV: | TDF Impact | Rebuild line 640080 BELDEN 7 115 640212 HARTGTN7 115 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-162 | FROM->TO | 640080 BELDEN 7 115 640212 HARTGTN7 115 1 | B | 123 | 0.032797 | 107.6498 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOMP3-FTTHOM2-LNX3-Z :EHV: | TDF Impact | Rebuild line 640080 BELDEN 7 115 640212 HARTGTN7 115 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-162 | FROM->TO | 640080 BELDEN 7 115 640212 HARTGTN7 115 1 | B | 123 | 0.032709 | 108.9827 | P13:230-115.0:UMZ:# N-1 #:: 3WND UTICAJC4-UTICAJC7-UTICAJC9-1 652_ UJ KV3A_:HV: | TDF Impact | Rebuild line 640080 BELDEN 7 115 640212 HARTGTN7 115 1
Thermal | 02ALL | 1 | 26SP | T0 | GEN-2024-162 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | B | 320 | 0.62987 | 109.1304 | Single 635200 RAUN3 345 640226 HOSKINS3 345 1 | TDF Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 02ALL | 1 | 26SP | T0 | GEN-2024-162 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | B | 320 | 0.58011 | 109.5852 | P12:345.0:UMZ:# N-1 #:: LINE RAUN 3-SIOUXCY3-1 :EHV: | TDF Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-162 | FROM->TO | 640080 BELDEN 7 115 640212 HARTGTN7 115 1 | B | 132 | 0.031058 | 109.87 | Single 640149 CREITON7 115 640521 ANTELOPE7 115 1 | TDF Impact | Rebuild line 640080 BELDEN 7 115 640212 HARTGTN7 115 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-162 | FROM->TO | 640080 BELDEN 7 115 640212 HARTGTN7 115 1 | B | 123 | 0.030111 | 112.7976 | Single 640084 BLMFLD7 115 640149 CREITON7 115 1 | TDF Impact | Rebuild line 640080 BELDEN 7 115 640212 HARTGTN7 115 1
Thermal | 02ALL | 1 | 29WP | T0 | GEN-2024-162 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | B | 320 | 0.61666 | 113.5344 | Single 640226 HOSKINS3 345 763982 G19-069TAP 345 1 | TDF Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 02ALL | 1 | 29WP | T0 | GEN-2024-162 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | B | 320 | 0.61666 | 113.5475 | Single 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | TDF Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-162 | FROM->TO | 640080 BELDEN 7 115 640212 HARTGTN7 115 1 | B | 123 | 0.092685 | 114.0081 | P12:230.0:UMZ:# N-1 #:: LINE TWIN CH4-SIOUXCY4-1 :HV: | TDF Impact | Rebuild line 640080 BELDEN 7 115 640212 HARTGTN7 115 1
Thermal | 02ALL | 1 | 29WP | T0 | GEN-2024-162 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | B | 320 | 0.60504 | 114.1774 | P55:345:MEC:ORIENT | TDF Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 02ALL | 1 | 29WP | T0 | GEN-2024-162 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | B | 320 | 0.60613 | 114.4083 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOMP3-FTTHOM2-LNX3-Z :EHV: | TDF Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 02ALL | 1 | 29WP | T0 | GEN-2024-162 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | B | 320 | 0.60613 | 114.4096 | P12:345.0:UMZ:# N-1 #:: LINE GR PRAIRIE 3-GRPRAR2-LNX3-Z :EHV: | TDF Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 02ALL | 1 | 29WP | T0 | GEN-2024-162 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | B | 320 | 0.60613 | 114.4098 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOM2-LNX3-GRPRAR2-LNX3-1 :EHV: | TDF Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 02ALL | 1 | 29WP | T0 | GEN-2024-162 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | B | 320 | 0.60564 | 114.4544 | P55:345:XEL:PRI1 | TDF Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 02ALL | 1 | 29WP | T0 | GEN-2024-162 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | B | 320 | 0.60564 | 115.3828 | Single 640425 S.SIOUXCITY8 69 640424 S.SIOUXCITY7 115 643170 'S.SIOUXCYT19' 13 1 | TDF Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 02ALL | 1 | 29SP | T0 | GEN-2024-162 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | B | 320 | 0.60755 | 116.5719 | Single 635200 RAUN3 345 640226 HOSKINS3 345 1 | TDF Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 02ALL | 1 | 29SP | T0 | GEN-2024-162 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | B | 320 | 0.56913 | 116.7129 | P12:345.0:UMZ:# N-1 #:: LINE RAUN 3-SIOUXCY3-1 :EHV: | TDF Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 02ALL | 1 | 29WP | T0 | GEN-2024-162 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | B | 320 | 0.56941 | 118.405 | P12:345.0:UMZ:# N-1 #:: LINE RAUN 3-SIOUXCY3-1 :EHV: | TDF Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-162 | FROM->TO | 640080 BELDEN 7 115 640212 HARTGTN7 115 1 | B | 123 | 0.030111 | 129.7178 | Single 640149 CREITON7 115 640521 ANTELOPE7 115 1 | TDF Impact | Rebuild line 640080 BELDEN 7 115 640212 HARTGTN7 115 1
Thermal | 02ALL | 1 | 29WP | T0 | GEN-2024-162 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | B | 320 | 0.60776 | 136.3055 | Single 635200 RAUN3 345 640226 HOSKINS3 345 1 | TDF Impact | Rebuild line 640386 TWIN CH4 230 652565 SIOUXCY4 230 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-168 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.040766 | 100.5915 | P23:345:MEC:HIGHLAND:903::EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-168 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.040766 | 100.6154 | P23:345:MEC:HIGHLAND:902::EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-168 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.041506 | 100.6843 | P12:230.0:UMZ:# N-1 #:: LINE TWIN CH4-SIOUXCY4-1 :HV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-168 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.040766 | 101.5782 | Single 635368 OBRIEN3 345 635400 HIGHLAND3 345 1 | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-168 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.040766 | 101.5782 | P12:345:MEC:OBRIEN:HIGHLAND:1REACTOR:EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-168 | FROM->TO | 640272 MCCOOL 7 115 640413 YORK SW7 115 1 | B | 160 | 0.085419 | 102.859 | P12:115:NPPD:1156:NW68HOLDRG7:SEWARD 7 BTB | TDF Impact | Rebuild line 640272 MCCOOL 7 115 640413 YORK SW7 115 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-168 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.041336 | 103.0767 | P23:345:MEC:OBRIEN:903::EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-168 | FROM->TO | 640272 MCCOOL 7 115 640413 YORK SW7 115 1 | B | 160 | 0.11694 | 103.0964 | P23:345:UMZW:# 2427 #:: GI IN NE. GI 1392 BKR FAULT:EHV: | TDF Impact | Rebuild line 640272 MCCOOL 7 115 640413 YORK SW7 115 1
Thermal | 02ALL | 1 | 26SP | T0 | GEN-2024-168 | FROM->TO | 640316 PAWNEEL7 115 650214 NW68HOLDRG7 115 1 | B | 154 | 0.052583 | 103.1035 | P42:345:NPPD:L3502A.MOORE.MCCOOL.CB3310:::: | Cumulative Impact | Rebuild line 640316 PAWNEEL7 115 650214 NW68HOLDRG7 115 1
Thermal | 02ALL | 1 | 26SP | T0 | GEN-2024-168 | FROM->TO | 640316 PAWNEEL7 115 650214 NW68HOLDRG7 115 1 | B | 154 | 0.052583 | 103.1035 | P42:345:NPPD:BKR-MOR-3310:::: | Cumulative Impact | Rebuild line 640316 PAWNEEL7 115 650214 NW68HOLDRG7 115 1
Thermal | 02ALL | 1 | 26SP | T0 | GEN-2024-168 | FROM->TO | 640316 PAWNEEL7 115 650214 NW68HOLDRG7 115 1 | B | 154 | 0.052753 | 103.4371 | P42:345:NPPD:BKR-MOR-3306:::: | Cumulative Impact | Rebuild line 640316 PAWNEEL7 115 650214 NW68HOLDRG7 115 1
Thermal | 02ALL | 1 | 26SP | T0 | GEN-2024-168 | FROM->TO | 640316 PAWNEEL7 115 650214 NW68HOLDRG7 115 1 | B | 154 | 0.052437 | 103.4454 | P12:345:NPPD:LN004::MOORE.MCCOOL.CKT1:: | Cumulative Impact | Rebuild line 640316 PAWNEEL7 115 650214 NW68HOLDRG7 115 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-168 | FROM->TO | 640272 MCCOOL 7 115 640413 YORK SW7 115 1 | B | 160 | 0.085419 | 103.4875 | Single 640316 PAWNEEL7 115 640340 SEWARD7 115 1 | TDF Impact | Rebuild line 640272 MCCOOL 7 115 640413 YORK SW7 115 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-168 | FROM->TO | 640178 GENEVA 7 115 640272 MCCOOL 7 115 1 | B | 160 | 0.44536 | 103.8416 | P12:345:NPPD:LN004::MOORE.MCCOOL.CKT1:: | TDF Impact | Rebuild line 640178 GENEVA 7 115 640272 MCCOOL 7 115 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-168 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.041436 | 104.0624 | P23:345:MEC:OBRIEN:906::EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 02ALL | 1 | 26SP | T0 | GEN-2024-168 | FROM->TO | 640316 PAWNEEL7 115 650214 NW68HOLDRG7 115 1 | A | 140 | 0.03301 | 104.8453 | System Intact | TDF Impact | Rebuild line 640316 PAWNEEL7 115 650214 NW68HOLDRG7 115 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-168 | FROM->TO | 640178 GENEVA 7 115 640272 MCCOOL 7 115 1 | B | 160 | 0.44813 | 105.582 | P12:345:NPPD:LN004::MOORE.MCCOOL.CKT1:: | TDF Impact | Rebuild line 640178 GENEVA 7 115 640272 MCCOOL 7 115 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-168 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.033007 | 106.6762 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-168 | FROM->TO | 640272 MCCOOL 7 115 640413 YORK SW7 115 1 | B | 160 | 0.11659 | 108.3007 | P23:345:UMZW:# 2427 #:: GI IN NE. GI 1392 BKR FAULT:EHV: | TDF Impact | Rebuild line 640272 MCCOOL 7 115 640413 YORK SW7 115 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-168 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.033039 | 108.9935 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-168 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.033039 | 109.0153 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-168 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.032839 | 109.4444 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-168 | FROM->TO | 640178 GENEVA 7 115 640272 MCCOOL 7 115 1 | B | 160 | 0.44675 | 109.5547 | P42:345:NPPD:BKR-MOR-3306:::: | TDF Impact | Rebuild line 640178 GENEVA 7 115 640272 MCCOOL 7 115 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-168 | FROM->TO | 640178 GENEVA 7 115 640272 MCCOOL 7 115 1 | B | 160 | 0.44951 | 110.6689 | P42:345:NPPD:BKR-MOR-3306:::: | TDF Impact | Rebuild line 640178 GENEVA 7 115 640272 MCCOOL 7 115 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-168 | FROM->TO | 640178 GENEVA 7 115 640272 MCCOOL 7 115 1 | B | 160 | 0.44603 | 112.3173 | P42:345:NPPD:BKR-MOR-3310:::: | TDF Impact | Rebuild line 640178 GENEVA 7 115 640272 MCCOOL 7 115 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-168 | FROM->TO | 640178 GENEVA 7 115 640272 MCCOOL 7 115 1 | B | 160 | 0.44603 | 112.3173 | P42:345:NPPD:L3502A.MOORE.MCCOOL.CB3310:::: | TDF Impact | Rebuild line 640178 GENEVA 7 115 640272 MCCOOL 7 115 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-168 | FROM->TO | 640178 GENEVA 7 115 640272 MCCOOL 7 115 1 | B | 160 | 0.44879 | 113.2969 | P42:345:NPPD:L3502A.MOORE.MCCOOL.CB3310:::: | TDF Impact | Rebuild line 640178 GENEVA 7 115 640272 MCCOOL 7 115 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-168 | FROM->TO | 640178 GENEVA 7 115 640272 MCCOOL 7 115 1 | B | 160 | 0.44879 | 113.2969 | P42:345:NPPD:BKR-MOR-3310:::: | TDF Impact | Rebuild line 640178 GENEVA 7 115 640272 MCCOOL 7 115 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-168 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.033217 | 118.0094 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-168 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.032868 | 119.5678 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-168 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.032905 | 121.2729 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-168 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.032905 | 121.3014 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-168 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.032686 | 121.5027 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-168 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.033152 | 130.4818 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-168 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.032571 | 146.377 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-168 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.032621 | 148.5944 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-168 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.03262 | 148.6147 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-168 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.032404 | 148.9728 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-168 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.032916 | 159.9633 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-170 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | B | 756 | 0.34283 | 101.463 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | Rebuild line 541200 PHILL 7 345 541201 SIBLEY 7 345 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-170 | FROM->TO | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.077608 | 104.394 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-170 | FROM->TO | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.08303 | 111.8275 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-170 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | B | 756 | 0.34561 | 117.5821 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | Rebuild line 541200 PHILL 7 345 541201 SIBLEY 7 345 1
Thermal | 04ALL | 1 | 26SP | T1 | GEN-2024-171 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.078478 | 103.0993 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T1 | GEN-2024-171 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.079741 | 103.3038 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-171 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | A | 1187 | 0.14128 | 103.8656 | System Intact | TDF Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-171 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.15509 | 104.9177 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-171 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.14969 | 106.1409 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-171 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.15321 | 106.3238 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-171 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.17148 | 106.5158 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-171 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.14903 | 107.841 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-171 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.17148 | 108.059 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-171 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.14903 | 109.5335 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-171 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.14903 | 109.534 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-171 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.14903 | 112.0538 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-171 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.14903 | 116.5975 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-171 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.10388 | 119.3706 | System Intact | TDF Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-171 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.10388 | 119.3706 | System Intact | TDF Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-171 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.10388 | 119.3706 | System Intact | TDF Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-171 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.1027 | 119.5141 | System Intact | TDF Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-171 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.1027 | 119.5141 | System Intact | TDF Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-171 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.1027 | 119.5141 | System Intact | TDF Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-171 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.12687 | 136.5828 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-171 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.12687 | 136.5828 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-171 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.12687 | 136.5828 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-171 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.11082 | 136.8919 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-171 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.11082 | 136.8919 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-171 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.11082 | 136.8919 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-171 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.11281 | 136.9237 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-171 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.11281 | 136.9237 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-171 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.11281 | 136.9237 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-171 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.12747 | 139.3736 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-171 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.12747 | 139.3736 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-171 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.12747 | 139.3736 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-171 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.11172 | 140.3415 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-171 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.11172 | 140.3415 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-171 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.11172 | 140.3415 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-171 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.10994 | 140.6152 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-171 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.10994 | 140.6152 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-171 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.10994 | 140.6152 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-171 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.11857 | 141.6076 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-171 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.11857 | 141.6076 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-171 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.11857 | 141.6076 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-171 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.11539 | 142.5086 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-171 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.11539 | 142.5086 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-171 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.11539 | 142.5086 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-171 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.11118 | 142.6431 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-171 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.11118 | 142.6431 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-171 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.11118 | 142.6431 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-171 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.11679 | 142.7223 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-171 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.11679 | 142.7223 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-171 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.11679 | 142.7223 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-171 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.10935 | 143.2233 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-171 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.10935 | 143.2233 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-171 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.10935 | 143.2233 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-171 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.11376 | 143.8401 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-171 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.11376 | 143.8401 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-171 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.11376 | 143.8401 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-171 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.11118 | 145.1309 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-171 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.11118 | 145.1309 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-171 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.11118 | 145.1309 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-171 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.11118 | 145.1356 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-171 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.11118 | 145.1356 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-171 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.11118 | 145.1356 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-171 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.10935 | 145.7578 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-171 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.10935 | 145.7578 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-171 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.10935 | 145.7578 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-171 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.10935 | 145.7646 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-171 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.10935 | 145.7646 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-171 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.10935 | 145.7646 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-171 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.11118 | 148.805 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-171 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.11118 | 148.805 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-171 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.11118 | 148.805 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-171 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.10935 | 149.8057 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-171 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.10935 | 149.8057 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-171 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.10935 | 149.8057 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-171 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.11118 | 155.6146 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-171 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.11118 | 155.6146 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-171 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.11118 | 155.6146 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-171 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.10935 | 157.3662 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-171 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.10935 | 157.3662 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-171 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.10935 | 157.3662 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-173 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.049884 | 100.5915 | P23:345:MEC:HIGHLAND:903::EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-173 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.049884 | 100.6154 | P23:345:MEC:HIGHLAND:902::EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-173 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.048996 | 100.6843 | P12:230.0:UMZ:# N-1 #:: LINE TWIN CH4-SIOUXCY4-1 :HV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-173 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.049884 | 101.5782 | Single 635368 OBRIEN3 345 635400 HIGHLAND3 345 1 | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-173 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.049884 | 101.5782 | P12:345:MEC:OBRIEN:HIGHLAND:1REACTOR:EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-173 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.058593 | 101.6704 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 02ALL | 1 | 29WP | T0 | GEN-2024-173 | FROM->TO | 640316 PAWNEEL7 115 650214 NW68HOLDRG7 115 1 | B | 174 | 1 | 102.4601 | Single 640316 PAWNEEL7 115 640340 SEWARD7 115 1 | TDF Impact | Rebuild line 640316 PAWNEEL7 115 650214 NW68HOLDRG7 115 1
Thermal | 02ALL | 1 | 26SP | T0 | GEN-2024-173 | FROM->TO | 640316 PAWNEEL7 115 650214 NW68HOLDRG7 115 1 | B | 154 | 0.78401 | 102.7396 | P42:345:LES:L1485::NW68&HOLDREGE.WAGENER.CB3006:: | TDF Impact | Rebuild line 640316 PAWNEEL7 115 650214 NW68HOLDRG7 115 1
Thermal | 02ALL | 1 | 26SP | T0 | GEN-2024-173 | FROM->TO | 640316 PAWNEEL7 115 650214 NW68HOLDRG7 115 1 | B | 154 | 0.78537 | 102.8126 | P12:345:NPPD:L3521::NW68&HOLDREGE.COLUMBUSEAST.CKT1:: | TDF Impact | Rebuild line 640316 PAWNEEL7 115 650214 NW68HOLDRG7 115 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-173 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.050532 | 103.0767 | P23:345:MEC:OBRIEN:903::EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 02ALL | 1 | 26SP | T0 | GEN-2024-173 | FROM->TO | 640316 PAWNEEL7 115 650214 NW68HOLDRG7 115 1 | B | 154 | 0.78495 | 103.1035 | P42:345:NPPD:L3502A.MOORE.MCCOOL.CB3310:::: | TDF Impact | Rebuild line 640316 PAWNEEL7 115 650214 NW68HOLDRG7 115 1
Thermal | 02ALL | 1 | 26SP | T0 | GEN-2024-173 | FROM->TO | 640316 PAWNEEL7 115 650214 NW68HOLDRG7 115 1 | B | 154 | 0.78495 | 103.1035 | P42:345:NPPD:BKR-MOR-3310:::: | TDF Impact | Rebuild line 640316 PAWNEEL7 115 650214 NW68HOLDRG7 115 1
Thermal | 02ALL | 1 | 26SP | T0 | GEN-2024-173 | FROM->TO | 640316 PAWNEEL7 115 650214 NW68HOLDRG7 115 1 | B | 154 | 0.87005 | 103.4296 | Single 640340 SEWARD7 115 640375 TAMORA7 115 1 | TDF Impact | Rebuild line 640316 PAWNEEL7 115 650214 NW68HOLDRG7 115 1
Thermal | 02ALL | 1 | 26SP | T0 | GEN-2024-173 | FROM->TO | 640316 PAWNEEL7 115 650214 NW68HOLDRG7 115 1 | B | 154 | 0.87005 | 103.4338 | P12:115:NPPD:1155:YORK 7:SEWARD 7 BTB | TDF Impact | Rebuild line 640316 PAWNEEL7 115 650214 NW68HOLDRG7 115 1
Thermal | 02ALL | 1 | 26SP | T0 | GEN-2024-173 | FROM->TO | 640316 PAWNEEL7 115 650214 NW68HOLDRG7 115 1 | B | 154 | 0.78668 | 103.4371 | P42:345:NPPD:BKR-MOR-3306:::: | TDF Impact | Rebuild line 640316 PAWNEEL7 115 650214 NW68HOLDRG7 115 1
Thermal | 02ALL | 1 | 26SP | T0 | GEN-2024-173 | FROM->TO | 640316 PAWNEEL7 115 650214 NW68HOLDRG7 115 1 | B | 154 | 0.78666 | 103.4454 | P12:345:NPPD:LN004::MOORE.MCCOOL.CKT1:: | TDF Impact | Rebuild line 640316 PAWNEEL7 115 650214 NW68HOLDRG7 115 1
Thermal | 02ALL | 1 | 26SP | T0 | GEN-2024-173 | FROM->TO | 640316 PAWNEEL7 115 650214 NW68HOLDRG7 115 1 | B | 154 | 0.7792 | 103.9486 | P42:345:LES:L3516::NW68&HOLDREGE.MOORE.CB3005:: | TDF Impact | Rebuild line 640316 PAWNEEL7 115 650214 NW68HOLDRG7 115 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-173 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.050642 | 104.0624 | P23:345:MEC:OBRIEN:906::EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 02ALL | 1 | 26SP | T0 | GEN-2024-173 | FROM->TO | 640316 PAWNEEL7 115 650214 NW68HOLDRG7 115 1 | A | 140 | 0.7893 | 104.8453 | System Intact | TDF Impact | Rebuild line 640316 PAWNEEL7 115 650214 NW68HOLDRG7 115 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-173 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | A | 110 | 0.059859 | 105.8619 | System Intact | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-173 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.064764 | 106.3207 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-173 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.076201 | 106.6762 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-173 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.0763 | 108.9935 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-173 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.0763 | 109.0153 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-173 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.075908 | 109.4444 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-173 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.062894 | 110.3426 | P42:345:LES:L1485::NW68&HOLDREGE.WAGENER.CB3006:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-173 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.060535 | 111.0459 | P13:161-345:OPPD:TX01::S3454.CKT1:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-173 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.060535 | 111.0459 | P13:161-345:OPPD:S1254 T1:::HV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-173 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.064329 | 117.1294 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-173 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.076455 | 118.0094 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 02ALL | 1 | 29SP | T0 | GEN-2024-173 | FROM->TO | 640316 PAWNEEL7 115 650214 NW68HOLDRG7 115 1 | B | 154 | 1 | 118.7703 | Single 640316 PAWNEEL7 115 640340 SEWARD7 115 1 | TDF Impact | Rebuild line 640316 PAWNEEL7 115 650214 NW68HOLDRG7 115 1
Thermal | 02ALL | 1 | 26SP | T0 | GEN-2024-173 | FROM->TO | 640316 PAWNEEL7 115 650214 NW68HOLDRG7 115 1 | B | 154 | 1 | 119.0273 | Single 640316 PAWNEEL7 115 640340 SEWARD7 115 1 | TDF Impact | Rebuild line 640316 PAWNEEL7 115 650214 NW68HOLDRG7 115 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-173 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.075817 | 119.5678 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-173 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.075914 | 121.2729 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-173 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.075914 | 121.3014 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-173 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.075503 | 121.5027 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-173 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.058631 | 125.7992 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 02ALL | 1 | 29WP | T0 | GEN-2024-173 | FROM->TO | 640316 PAWNEEL7 115 640340 SEWARD 7 115 1 | B | 140 | 1 | 127.5755 | P12:115:NPPD:L1156B::NW68&HOLDREGE.PAWNEELAKE.CKT1:: | TDF Impact | Rebuild line 640316 PAWNEEL7 115 640340 SEWARD 7 115 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-173 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.076126 | 130.4818 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 02ALL | 1 | 29SP | T0 | GEN-2024-173 | FROM->TO | 640316 PAWNEEL7 115 640340 SEWARD 7 115 1 | B | 140 | 1 | 130.7053 | P12:115:NPPD:L1156B::NW68&HOLDREGE.PAWNEELAKE.CKT1:: | TDF Impact | Rebuild line 640316 PAWNEEL7 115 640340 SEWARD 7 115 1
Thermal | 02ALL | 1 | 26SP | T0 | GEN-2024-173 | FROM->TO | 640316 PAWNEEL7 115 640340 SEWARD 7 115 1 | B | 140 | 1 | 130.8993 | P12:115:NPPD:L1156B::NW68&HOLDREGE.PAWNEELAKE.CKT1:: | TDF Impact | Rebuild line 640316 PAWNEEL7 115 640340 SEWARD 7 115 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-173 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.075616 | 146.377 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-173 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.064296 | 148.4763 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-173 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.075731 | 148.5944 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-173 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.075731 | 148.6147 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-173 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.075325 | 148.9728 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-173 | FROM->TO | 650269 70&BLUFF 7 115 3WXFMR 650:T691 161 1 | B | 120 | 0.075999 | 159.9633 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-181 | FROM->TO | 505492 SPRGFLD5 161 549970 CLAY 5 161 1 | B | 223 | 0.080712 | 102.2021 | P12:345:AECI:HUBEN:MORGAN_345:1:: | TDF Impact | Rebuild line 505492 SPRGFLD5 161 549970 CLAY 5 161 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-181 | FROM->TO | 505492 SPRGFLD5 161 549970 CLAY 5 161 1 | B | 223 | 0.076351 | 102.2853 | P23:345:AECI:7HUBEN:1312::: | TDF Impact | Rebuild line 505492 SPRGFLD5 161 549970 CLAY 5 161 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-204 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | A | 1187 | 0.04257 | 103.8656 | System Intact | TDF Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-204 | FROM->TO | 511468 L.E.S.-7 345 3WXFMR 520:LES 5 345 2 | B | 515 | 0.03699 | 114.3077 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-204 | FROM->TO | 511468 L.E.S.-7 345 3WXFMR 520:LES 5 345 2 | B | 515 | 0.037462 | 114.3448 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-204 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.041393 | 114.5102 | System Intact | TDF Impact | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-204 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.035245 | 114.6214 | System Intact | TDF Impact | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-204 | FROM->TO | 511468 L.E.S.-7 345 3WXFMR 520:LES 5 345 2 | B | 515 | 0.035346 | 115.3782 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | TDF Impact | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-204 | FROM->TO | 511468 L.E.S.-7 345 3WXFMR 520:LES 5 345 2 | B | 515 | 0.035969 | 116.8526 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | TDF Impact | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-204 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | B | 1000 | 0.082939 | 116.8554 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | Cumulative Impact | Rebuild line 508359 WELSH 7 345 508841 WILKES 7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-204 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.035378 | 119.3706 | System Intact | TDF Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-204 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.035378 | 119.3706 | System Intact | TDF Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-204 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.035378 | 119.3706 | System Intact | TDF Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-204 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.031824 | 119.5141 | System Intact | TDF Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-204 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.031824 | 119.5141 | System Intact | TDF Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-204 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.031824 | 119.5141 | System Intact | TDF Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 00NR | 1 | 29SP | T1 | GEN-2024-205 | FROM->TO | 530679 SEWRDMW3 115 3WXFMR 531:SEWARD T1 69 1 | B | 53 | 0.23451 | 101.4947 | Single 539666 GBENDTP3 115 539692 SEWARD3 115 1 | TDF Impact | Rebuild 3-winding transformer 530565 SEWARD 2 69 530631 SWRD1 1 12 530679 SEWRDMW3 115 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-205 | FROM->TO | 530679 SEWRDMW3 115 3WXFMR 531:SEWARD T1 69 1 | B | 44.79 | 0.23265 | 105.8778 | Single 539666 GBENDTP3 115 539692 SEWARD3 115 1 | TDF Impact | Rebuild 3-winding transformer 530565 SEWARD 2 69 530631 SWRD1 1 12 530679 SEWRDMW3 115 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-205 | FROM->TO | 530679 SEWRDMW3 115 3WXFMR 531:SEWARD T1 69 1 | B | 44.79 | 0.23312 | 106.4389 | Single 539666 GBENDTP3 115 539692 SEWARD3 115 1 | TDF Impact | Rebuild 3-winding transformer 530565 SEWARD 2 69 530631 SWRD1 1 12 530679 SEWRDMW3 115 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-205 | FROM->TO | 530679 SEWRDMW3 115 3WXFMR 531:SEWARD T1 69 1 | B | 44.79 | 0.23274 | 117.8065 | Single 539666 GBENDTP3 115 539692 SEWARD3 115 1 | TDF Impact | Rebuild 3-winding transformer 530565 SEWARD 2 69 530631 SWRD1 1 12 530679 SEWRDMW3 115 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | FROM->TO | 542988 GRAND W5 161 542990 CROSTWN5 161 1 | B | 259 | 0.065124 | 102.5286 | Single 542990 CROSTWN5 161 543133 CHARLOT5 161 1 | Cumulative Impact | Line - Crosstown - Blue Valley Station 161 kV New Line.idv : 2025 ITP upgrade, PID : 900341, NO NTC
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | FROM->TO | 542987 GRAND 5 161 542989 NAVY 5 161 1 | B | 259 | 0.089345 | 104.143 | P12:161:KCPL:NORTHEAST-GRANDAVEW-NAV:::HV: | Cumulative Impact | Line - Crosstown - Blue Valley Station 161 kV New Line.idv : 2025 ITP upgrade, PID : 900341, NO NTC
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | FROM->TO | 542987 GRAND 5 161 542989 NAVY 5 161 1 | B | 259 | 0.0895 | 104.5841 | P12:161:KCPL:NRTHST-GRANDAVE-NTHEASTCAP:::HV: | Cumulative Impact | Line - Crosstown - Blue Valley Station 161 kV New Line.idv : 2025 ITP upgrade, PID : 900341, NO NTC
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | FROM->TO | 542987 GRAND 5 161 542989 NAVY 5 161 1 | B | 259 | 0.0895 | 104.6104 | Single 542985 NEASTS5 161 542988 GRANDW5 161 1 | Cumulative Impact | Line - Crosstown - Blue Valley Station 161 kV New Line.idv : 2025 ITP upgrade, PID : 900341, NO NTC
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | FROM->TO | 542988 GRAND W5 161 542990 CROSTWN5 161 1 | B | 259 | 0.063131 | 104.6173 | Single 542985 NEASTS5 161 543133 CHARLOT5 161 1 | Cumulative Impact | Line - Crosstown - Blue Valley Station 161 kV New Line.idv : 2025 ITP upgrade, PID : 900341, NO NTC
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.38442 | 107.0069 | Single 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.38442 | 107.0069 | P12:161:INDN:BLUVLY-ECKLES:::HV: | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.3843 | 107.0434 | Single 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.3843 | 107.0434 | P12:161:INDN:BLUVLY-ECKLES:::HV: | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.38366 | 110.7788 | Single 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.38366 | 110.7789 | P12:161:INDN:BLUVLY-ECKLES:::HV: | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | FROM->TO | 542988 GRAND W5 161 542990 CROSTWN5 161 1 | B | 259 | 0.065124 | 112.18 | Single 542985 NEASTS5 161 543133 CHARLOT5 161 1 | Cumulative Impact | Line - Crosstown - Blue Valley Station 161 kV New Line.idv : 2025 ITP upgrade, PID : 900341, NO NTC
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | A | 334 | 0.3906 | 146.2073 | System Intact | TDF Impact | Add line 543004 BLUMILS5 161 548808 ECKLES-161 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 334 | 0.3906 | 149.0227 | Single 541235 DUNCAN5 161 779191 GEN-2024-074 161 1 | TDF Impact | Add line 543004 BLUMILS5 161 548808 ECKLES-161 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 334 | 0.3906 | 149.0228 | Single 779191 GEN-2024-074 161 779192 G24-074XFMR1 34 779207 'G24-074TER1 ' 13 1 | TDF Impact | Add line 543004 BLUMILS5 161 548808 ECKLES-161 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 334 | 0.3906 | 149.0249 | GEN-2024-074_POI_541235_Generator_outage | TDF Impact | Add line 543004 BLUMILS5 161 548808 ECKLES-161 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 334 | 0.39627 | 149.2345 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | TDF Impact | Add line 543004 BLUMILS5 161 548808 ECKLES-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 309 | 0.39197 | 149.2794 | Single 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | TDF Impact | Add line 543004 BLUMILS5 161 548808 ECKLES-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 309 | 0.39038 | 149.4313 | Single 300076 5FAIRPTB2 161 301559 5FAIRPTXF3 161 1 | TDF Impact | Add line 543004 BLUMILS5 161 548808 ECKLES-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 309 | 0.39038 | 149.4313 | Single 301559 5FAIRPTXF3 161 300039 7FAIRPT 345 3 | TDF Impact | Add line 543004 BLUMILS5 161 548808 ECKLES-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 309 | 0.36617 | 149.9448 | Single 541202 SIBLEY5 161 541250 SIBLEYPL 161 1 | TDF Impact | Add line 543004 BLUMILS5 161 548808 ECKLES-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 309 | 0.36617 | 149.9465 | Single 541201 SIBLEY7 345 541202 SIBLEY5 161 541360 'SIBLEY T ' 13 11 | TDF Impact | Add line 543004 BLUMILS5 161 548808 ECKLES-161 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 309 | 0.3911 | 151.47 | P12:345:NPPD:3517:COOPER 3:ST JOE 3 BTB | TDF Impact | Add line 543004 BLUMILS5 161 548808 ECKLES-161 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 309 | 0.3911 | 151.47 | P12:345:AECI-KCPL:FRPRT:STJ:CPR:: | TDF Impact | Add line 543004 BLUMILS5 161 548808 ECKLES-161 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 309 | 0.3922 | 151.4824 | Single 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | TDF Impact | Add line 543004 BLUMILS5 161 548808 ECKLES-161 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 309 | 0.39065 | 151.5249 | Single 300076 5FAIRPTB2 161 301559 5FAIRPTXF3 161 1 | TDF Impact | Add line 543004 BLUMILS5 161 548808 ECKLES-161 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 309 | 0.39065 | 151.5249 | Single 301559 5FAIRPTXF3 161 300039 7FAIRPT 345 3 | TDF Impact | Add line 543004 BLUMILS5 161 548808 ECKLES-161 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 334 | 0.39138 | 151.8529 | Single 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | TDF Impact | Add line 543004 BLUMILS5 161 548808 ECKLES-161 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 334 | 0.40122 | 152.2333 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | TDF Impact | Add line 543004 BLUMILS5 161 548808 ECKLES-161 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 334 | 0.40163 | 152.4626 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | TDF Impact | Add line 543004 BLUMILS5 161 548808 ECKLES-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 309 | 0.40184 | 153.5823 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | TDF Impact | Add line 543004 BLUMILS5 161 548808 ECKLES-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 309 | 0.40224 | 153.8821 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | TDF Impact | Add line 543004 BLUMILS5 161 548808 ECKLES-161 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 309 | 0.40204 | 155.9308 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | TDF Impact | Add line 543004 BLUMILS5 161 548808 ECKLES-161 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 309 | 0.40244 | 156.2304 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | TDF Impact | Add line 543004 BLUMILS5 161 548808 ECKLES-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | A | 281 | 0.3912 | 160.1528 | System Intact | TDF Impact | Add line 543004 BLUMILS5 161 548808 ECKLES-161 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | A | 335 | 0.50104 | 162.6504 | System Intact | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | A | 281 | 0.39142 | 162.7364 | System Intact | TDF Impact | Add line 543004 BLUMILS5 161 548808 ECKLES-161 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | A | 335 | 0.50266 | 162.9321 | System Intact | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | A | 335 | 0.50256 | 165.1095 | System Intact | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.50244 | 167.9798 | GEN542951 5 | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.50761 | 168.5157 | P12:161:AECI-INDN:ECKLES-5LEVASY:::HV: | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.51294 | 168.7946 | Single 300098 5MOCITYB2 161 301563 5MOCITYB1 161 Z1 | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.51123 | 170.3569 | Single 300098 5MOCITYB2 161 301563 5MOCITYB1 161 Z1 | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.5023 | 170.3704 | GEN542951 5 | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.51114 | 170.7374 | Single 541205 BLSPE5 161 541235 DUNCAN5 161 1 | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.50957 | 171.3971 | Single 541205 BLSPE5 161 541235 DUNCAN5 161 1 | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.51275 | 172.5676 | Single 300098 5MOCITYB2 161 301563 5MOCITYB1 161 Z1 | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.51116 | 173.9617 | Single 541205 BLSPE5 161 541235 DUNCAN5 161 1 | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.52489 | 174.5798 | P12:161:AECI-INDN:ECKLES-5MOCITYB1:::HV: | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.52359 | 175.4958 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.52445 | 175.9838 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.52672 | 177.4037 | P12:161:AECI-INDN:ECKLES-5MOCITYB1:::HV: | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.52654 | 178.1949 | P12:161:AECI-INDN:ECKLES-5MOCITYB1:::HV: | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.52494 | 178.286 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.52578 | 178.8645 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.58011 | 180.2478 | P12:161:INDN-KCPL:ECKLES-SIBLEYPL:::HV: | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.52481 | 180.4445 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.52564 | 181.0228 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.57807 | 181.4652 | P12:161:INDN-KCPL:ECKLES-SIBLEYPL:::HV: | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.57985 | 181.8986 | P12:161:INDN-KCPL:ECKLES-SIBLEYPL:::HV: | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.82191 | 230.54 | P12:161:INDN:BLUVLY-ECKLES:::HV: | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.82191 | 230.7546 | Single 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.82141 | 230.8847 | P12:161:INDN:BLUVLY-ECKLES:::HV: | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.82141 | 231.0999 | Single 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.81815 | 237.7831 | P12:161:INDN:BLUVLY-ECKLES:::HV: | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.81815 | 237.9841 | Single 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 334 | 0.72207 | 250.6404 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | TDF Impact | Add line 543004 BLUMILS5 161 548808 ECKLES-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 309 | 0.72597 | 253.0481 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | TDF Impact | Add line 543004 BLUMILS5 161 548808 ECKLES-161 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 334 | 0.72646 | 257.5868 | P12:161:INDN:BLUVLY-SUB M:::HV: | TDF Impact | Add line 543004 BLUMILS5 161 548808 ECKLES-161 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 309 | 0.72583 | 257.8738 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | TDF Impact | Add line 543004 BLUMILS5 161 548808 ECKLES-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 309 | 0.73205 | 268.7302 | P12:161:INDN:BLUVLY-SUB M:::HV: | TDF Impact | Add line 543004 BLUMILS5 161 548808 ECKLES-161 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 309 | 0.73241 | 269.5505 | P12:161:INDN:BLUVLY-SUB M:::HV: | TDF Impact | Add line 543004 BLUMILS5 161 548808 ECKLES-161 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.82191 | 276.0338 | Single 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.82141 | 276.5048 | Single 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.81815 | 282.9433 | Single 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | FROM->TO | 542988 GRAND W5 161 542990 CROSTWN5 161 1 | B | 259 | 0.064707 | 102.5286 | Single 542990 CROSTWN5 161 543133 CHARLOT5 161 1 | Cumulative Impact | Line - Crosstown - Blue Valley Station 161 kV New Line.idv : 2025 ITP upgrade, PID : 900341, NO NTC
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | FROM->TO | 542987 GRAND 5 161 542989 NAVY 5 161 1 | B | 259 | 0.088827 | 104.143 | P12:161:KCPL:NORTHEAST-GRANDAVEW-NAV:::HV: | Cumulative Impact | Line - Crosstown - Blue Valley Station 161 kV New Line.idv : 2025 ITP upgrade, PID : 900341, NO NTC
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | FROM->TO | 542987 GRAND 5 161 542989 NAVY 5 161 1 | B | 259 | 0.088981 | 104.5841 | P12:161:KCPL:NRTHST-GRANDAVE-NTHEASTCAP:::HV: | Cumulative Impact | Line - Crosstown - Blue Valley Station 161 kV New Line.idv : 2025 ITP upgrade, PID : 900341, NO NTC
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | FROM->TO | 542987 GRAND 5 161 542989 NAVY 5 161 1 | B | 259 | 0.088981 | 104.6104 | Single 542985 NEASTS5 161 542988 GRANDW5 161 1 | Cumulative Impact | Line - Crosstown - Blue Valley Station 161 kV New Line.idv : 2025 ITP upgrade, PID : 900341, NO NTC
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | FROM->TO | 542988 GRAND W5 161 542990 CROSTWN5 161 1 | B | 259 | 0.062712 | 104.6173 | Single 542985 NEASTS5 161 543133 CHARLOT5 161 1 | Cumulative Impact | Line - Crosstown - Blue Valley Station 161 kV New Line.idv : 2025 ITP upgrade, PID : 900341, NO NTC
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.38442 | 107.0069 | Single 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.38442 | 107.0069 | P12:161:INDN:BLUVLY-ECKLES:::HV: | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.3843 | 107.0434 | Single 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.3843 | 107.0434 | P12:161:INDN:BLUVLY-ECKLES:::HV: | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.38366 | 110.7788 | Single 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.38366 | 110.7789 | P12:161:INDN:BLUVLY-ECKLES:::HV: | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | FROM->TO | 542988 GRAND W5 161 542990 CROSTWN5 161 1 | B | 259 | 0.064707 | 112.18 | Single 542985 NEASTS5 161 543133 CHARLOT5 161 1 | Cumulative Impact | Line - Crosstown - Blue Valley Station 161 kV New Line.idv : 2025 ITP upgrade, PID : 900341, NO NTC
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | A | 334 | 0.39837 | 146.2073 | System Intact | TDF Impact | Add line 543004 BLUMILS5 161 548808 ECKLES-161 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 334 | 0.39837 | 149.0227 | Single 541235 DUNCAN5 161 779191 GEN-2024-074 161 1 | TDF Impact | Add line 543004 BLUMILS5 161 548808 ECKLES-161 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 334 | 0.39837 | 149.0228 | Single 779191 GEN-2024-074 161 779192 G24-074XFMR1 34 779207 'G24-074TER1 ' 13 1 | TDF Impact | Add line 543004 BLUMILS5 161 548808 ECKLES-161 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 334 | 0.39837 | 149.0249 | GEN-2024-074_POI_541235_Generator_outage | TDF Impact | Add line 543004 BLUMILS5 161 548808 ECKLES-161 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 334 | 0.40379 | 149.2345 | P23:345:GMO-KCPL:SIBLEY_R8-10::SIBLEY-HAWTHORN-PHILL_1 | TDF Impact | Add line 543004 BLUMILS5 161 548808 ECKLES-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 309 | 0.39971 | 149.2794 | Single 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | TDF Impact | Add line 543004 BLUMILS5 161 548808 ECKLES-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 309 | 0.39813 | 149.4313 | Single 300076 5FAIRPTB2 161 301559 5FAIRPTXF3 161 1 | TDF Impact | Add line 543004 BLUMILS5 161 548808 ECKLES-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 309 | 0.39813 | 149.4313 | Single 301559 5FAIRPTXF3 161 300039 7FAIRPT 345 3 | TDF Impact | Add line 543004 BLUMILS5 161 548808 ECKLES-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 309 | 0.37356 | 149.9448 | Single 541202 SIBLEY5 161 541250 SIBLEYPL 161 1 | TDF Impact | Add line 543004 BLUMILS5 161 548808 ECKLES-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 309 | 0.37356 | 149.9465 | Single 541201 SIBLEY7 345 541202 SIBLEY5 161 541360 'SIBLEY T ' 13 11 | TDF Impact | Add line 543004 BLUMILS5 161 548808 ECKLES-161 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 309 | 0.39885 | 151.47 | P12:345:NPPD:3517:COOPER 3:ST JOE 3 BTB | TDF Impact | Add line 543004 BLUMILS5 161 548808 ECKLES-161 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 309 | 0.39885 | 151.47 | P12:345:AECI-KCPL:FRPRT:STJ:CPR:: | TDF Impact | Add line 543004 BLUMILS5 161 548808 ECKLES-161 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 309 | 0.39994 | 151.4824 | Single 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | TDF Impact | Add line 543004 BLUMILS5 161 548808 ECKLES-161 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 309 | 0.3984 | 151.5249 | Single 300076 5FAIRPTB2 161 301559 5FAIRPTXF3 161 1 | TDF Impact | Add line 543004 BLUMILS5 161 548808 ECKLES-161 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 309 | 0.3984 | 151.5249 | Single 301559 5FAIRPTXF3 161 300039 7FAIRPT 345 3 | TDF Impact | Add line 543004 BLUMILS5 161 548808 ECKLES-161 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 334 | 0.39914 | 151.8529 | Single 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | TDF Impact | Add line 543004 BLUMILS5 161 548808 ECKLES-161 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 334 | 0.40885 | 152.2333 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | TDF Impact | Add line 543004 BLUMILS5 161 548808 ECKLES-161 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 334 | 0.40925 | 152.4626 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | TDF Impact | Add line 543004 BLUMILS5 161 548808 ECKLES-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 309 | 0.40945 | 153.5823 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | TDF Impact | Add line 543004 BLUMILS5 161 548808 ECKLES-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 309 | 0.40985 | 153.8821 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | TDF Impact | Add line 543004 BLUMILS5 161 548808 ECKLES-161 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 309 | 0.40966 | 155.9308 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | TDF Impact | Add line 543004 BLUMILS5 161 548808 ECKLES-161 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 309 | 0.41005 | 156.2304 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | TDF Impact | Add line 543004 BLUMILS5 161 548808 ECKLES-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | A | 281 | 0.39896 | 160.1528 | System Intact | TDF Impact | Add line 543004 BLUMILS5 161 548808 ECKLES-161 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | A | 335 | 0.49473 | 162.6504 | System Intact | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | A | 281 | 0.39918 | 162.7364 | System Intact | TDF Impact | Add line 543004 BLUMILS5 161 548808 ECKLES-161 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | A | 335 | 0.49633 | 162.9321 | System Intact | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | A | 335 | 0.49624 | 165.1095 | System Intact | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.49611 | 167.9798 | GEN542951 5 | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.50138 | 168.5157 | P12:161:AECI-INDN:ECKLES-5LEVASY:::HV: | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.50705 | 168.7946 | Single 300098 5MOCITYB2 161 301563 5MOCITYB1 161 Z1 | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.50537 | 170.3569 | Single 300098 5MOCITYB2 161 301563 5MOCITYB1 161 Z1 | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.49597 | 170.3704 | GEN542951 5 | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.50491 | 170.7374 | Single 541205 BLSPE5 161 541235 DUNCAN5 161 1 | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.50336 | 171.3971 | Single 541205 BLSPE5 161 541235 DUNCAN5 161 1 | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.50687 | 172.5676 | Single 300098 5MOCITYB2 161 301563 5MOCITYB1 161 Z1 | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.50494 | 173.9617 | Single 541205 BLSPE5 161 541235 DUNCAN5 161 1 | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.5192 | 174.5798 | P12:161:AECI-INDN:ECKLES-5MOCITYB1:::HV: | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.51698 | 175.4958 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.51782 | 175.9838 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.52101 | 177.4037 | P12:161:AECI-INDN:ECKLES-5MOCITYB1:::HV: | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.52083 | 178.1949 | P12:161:AECI-INDN:ECKLES-5MOCITYB1:::HV: | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.51831 | 178.286 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.51914 | 178.8645 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.57524 | 180.2478 | P12:161:INDN-KCPL:ECKLES-SIBLEYPL:::HV: | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.51818 | 180.4445 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.51901 | 181.0228 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.57322 | 181.4652 | P12:161:INDN-KCPL:ECKLES-SIBLEYPL:::HV: | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.57499 | 181.8986 | P12:161:INDN-KCPL:ECKLES-SIBLEYPL:::HV: | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.82191 | 230.54 | P12:161:INDN:BLUVLY-ECKLES:::HV: | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.82191 | 230.7546 | Single 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.82141 | 230.8847 | P12:161:INDN:BLUVLY-ECKLES:::HV: | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.82141 | 231.0999 | Single 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.81815 | 237.7831 | P12:161:INDN:BLUVLY-ECKLES:::HV: | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.81815 | 237.9841 | Single 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 334 | 0.7257 | 250.6404 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | TDF Impact | Add line 543004 BLUMILS5 161 548808 ECKLES-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 309 | 0.72955 | 253.0481 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | TDF Impact | Add line 543004 BLUMILS5 161 548808 ECKLES-161 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 334 | 0.73 | 257.5868 | P12:161:INDN:BLUVLY-SUB M:::HV: | TDF Impact | Add line 543004 BLUMILS5 161 548808 ECKLES-161 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 309 | 0.72941 | 257.8738 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | TDF Impact | Add line 543004 BLUMILS5 161 548808 ECKLES-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 309 | 0.73552 | 268.7302 | P12:161:INDN:BLUVLY-SUB M:::HV: | TDF Impact | Add line 543004 BLUMILS5 161 548808 ECKLES-161 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 309 | 0.73587 | 269.5505 | P12:161:INDN:BLUVLY-SUB M:::HV: | TDF Impact | Add line 543004 BLUMILS5 161 548808 ECKLES-161 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.82191 | 276.0338 | Single 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.82141 | 276.5048 | Single 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 334 | 1 | 279.2988 | Single 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | TDF Impact | Add line 543004 BLUMILS5 161 548808 ECKLES-161 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | FROM->TO | 548807 BLUVLY-161 161 548814 SUB M-161 161 1 | B | 335 | 0.81815 | 282.9433 | Single 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | TDF Impact | Add line and rebuild line 548807 BLUVLY-161 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 309 | 1 | 302.3771 | Single 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | TDF Impact | Add line 543004 BLUMILS5 161 548808 ECKLES-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | FROM->TO | 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | B | 309 | 1 | 302.4555 | Single 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | TDF Impact | Add line 543004 BLUMILS5 161 548808 ECKLES-161 161 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-211 | FROM->TO | 645454 S3454 3 345 645455 S3455 3 345 1 | B | 1195 | 0.17418 | 100.6765 | P12:345:OPPD:S3455-S3740:::EHV: | Cumulative Impact | Rebuild line 645454 S3454 3 345 645455 S3455 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-211 | FROM->TO | 337909 8ANO% 500 515305 FTSMITH8 500 1 | B | 1299 | 0.055695 | 102.9598 | P52:345:AEPW:NR4PITTSB-7:::: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-211 | FROM->TO | 646221 S1221 5 161 646231 S1231 5 161 1 | B | 217 | 0.051754 | 103.3851 | P23:345:OPPD:S3456-S3455&CB:::EHV: | Cumulative Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-211 | FROM->TO | 646221 S1221 5 161 646231 S1231 5 161 1 | B | 217 | 0.053847 | 103.9783 | P12:345:OPPD:S3455-S3456:::EHV: | Cumulative Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-211 | FROM->TO | 646221 S1221 5 161 646231 S1231 5 161 1 | B | 217 | 0.051922 | 105.1121 | P23:345:OPPD:S3456-S3455&CB:::EHV: | Cumulative Impact | Rebuild line 646221 S1221 5 161 646231 S1231 5 161 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-211 | FROM->TO | 646221 S1221 5 161 646231 S1231 5 161 1 | B | 217 | 0.054035 | 105.8605 | P12:345:OPPD:S3455-S3456:::EHV: | Cumulative Impact | Rebuild line 646221 S1221 5 161 646231 S1231 5 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-211 | FROM->TO | 646259 S1259 5 161 646278 S1278 5 161 1 | B | 215 | 0.053204 | 106.7879 | P23:345:OPPD:FUTURE 56-55&56-58:::EHV: | Cumulative Impact | Rebuild line 646259 S1259 5 161 646278 S1278 5 161 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-211 | FROM->TO | 646221 S1221 5 161 646231 S1231 5 161 1 | B | 217 | 0.058653 | 117.252 | P23:345:OPPD:FUTURE 56-55&56-58:::EHV: | Cumulative Impact | Rebuild line 646221 S1221 5 161 646231 S1231 5 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-211 | FROM->TO | 646221 S1221 5 161 646231 S1231 5 161 1 | B | 217 | 0.068037 | 119.4065 | P23:345:OPPD:FUTURE 56-55&56-58:::EHV: | Cumulative Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-211 | FROM->TO | 646221 S1221 5 161 646231 S1231 5 161 1 | B | 217 | 0.0595 | 127.9376 | P23:345:OPPD:FUTURE 56-55&56-58:::EHV: | Cumulative Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-211 | FROM->TO | 646221 S1221 5 161 646231 S1231 5 161 1 | B | 217 | 0.05978 | 129.6986 | P23:345:OPPD:FUTURE 56-55&56-58:::EHV: | Cumulative Impact | Rebuild line 646221 S1221 5 161 646231 S1231 5 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-211 | FROM->TO | 646221 S1221 5 161 646231 S1231 5 161 1 | B | 217 | 0.059483 | 145.0025 | P23:345:OPPD:FUTURE 56-55&56-58:::EHV: | Cumulative Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-211 | FROM->TO | 646221 S1221 5 161 646231 S1231 5 161 1 | B | 217 | 0.059743 | 147.401 | P23:345:OPPD:FUTURE 56-55&56-58:::EHV: | Cumulative Impact | Rebuild line 646221 S1221 5 161 646231 S1231 5 161 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-212 | FROM->TO | 645454 S3454 3 345 645455 S3455 3 345 1 | B | 1195 | 0.17418 | 100.6765 | P12:345:OPPD:S3455-S3740:::EHV: | Cumulative Impact | Rebuild line 645454 S3454 3 345 645455 S3455 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-212 | FROM->TO | 337909 8ANO% 500 515305 FTSMITH8 500 1 | B | 1299 | 0.055695 | 102.9598 | P52:345:AEPW:NR4PITTSB-7:::: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-212 | FROM->TO | 646221 S1221 5 161 646231 S1231 5 161 1 | B | 217 | 0.051754 | 103.3851 | P23:345:OPPD:S3456-S3455&CB:::EHV: | Cumulative Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-212 | FROM->TO | 646221 S1221 5 161 646231 S1231 5 161 1 | B | 217 | 0.053847 | 103.9783 | P12:345:OPPD:S3455-S3456:::EHV: | Cumulative Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-212 | FROM->TO | 646221 S1221 5 161 646231 S1231 5 161 1 | B | 217 | 0.051922 | 105.1121 | P23:345:OPPD:S3456-S3455&CB:::EHV: | Cumulative Impact | Rebuild line 646221 S1221 5 161 646231 S1231 5 161 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-212 | FROM->TO | 646221 S1221 5 161 646231 S1231 5 161 1 | B | 217 | 0.054035 | 105.8605 | P12:345:OPPD:S3455-S3456:::EHV: | Cumulative Impact | Rebuild line 646221 S1221 5 161 646231 S1231 5 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-212 | FROM->TO | 646259 S1259 5 161 646278 S1278 5 161 1 | B | 215 | 0.053204 | 106.7879 | P23:345:OPPD:FUTURE 56-55&56-58:::EHV: | Cumulative Impact | Rebuild line 646259 S1259 5 161 646278 S1278 5 161 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-212 | FROM->TO | 646221 S1221 5 161 646231 S1231 5 161 1 | B | 217 | 0.058653 | 117.252 | P23:345:OPPD:FUTURE 56-55&56-58:::EHV: | Cumulative Impact | Rebuild line 646221 S1221 5 161 646231 S1231 5 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-212 | FROM->TO | 646221 S1221 5 161 646231 S1231 5 161 1 | B | 217 | 0.068037 | 119.4065 | P23:345:OPPD:FUTURE 56-55&56-58:::EHV: | Cumulative Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-212 | FROM->TO | 646221 S1221 5 161 646231 S1231 5 161 1 | B | 217 | 0.0595 | 127.9376 | P23:345:OPPD:FUTURE 56-55&56-58:::EHV: | Cumulative Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-212 | FROM->TO | 646221 S1221 5 161 646231 S1231 5 161 1 | B | 217 | 0.05978 | 129.6986 | P23:345:OPPD:FUTURE 56-55&56-58:::EHV: | Cumulative Impact | Rebuild line 646221 S1221 5 161 646231 S1231 5 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-212 | FROM->TO | 646221 S1221 5 161 646231 S1231 5 161 1 | B | 217 | 0.059483 | 145.0025 | P23:345:OPPD:FUTURE 56-55&56-58:::EHV: | Cumulative Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-212 | FROM->TO | 646221 S1221 5 161 646231 S1231 5 161 1 | B | 217 | 0.059743 | 147.401 | P23:345:OPPD:FUTURE 56-55&56-58:::EHV: | Cumulative Impact | Rebuild line 646221 S1221 5 161 646231 S1231 5 161 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-213 | FROM->TO | 645454 S3454 3 345 645455 S3455 3 345 1 | B | 1195 | 0.17418 | 100.6765 | P12:345:OPPD:S3455-S3740:::EHV: | Cumulative Impact | Rebuild line 645454 S3454 3 345 645455 S3455 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-213 | FROM->TO | 337909 8ANO% 500 515305 FTSMITH8 500 1 | B | 1299 | 0.055695 | 102.9598 | P52:345:AEPW:NR4PITTSB-7:::: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-213 | FROM->TO | 646221 S1221 5 161 646231 S1231 5 161 1 | B | 217 | 0.051754 | 103.3851 | P23:345:OPPD:S3456-S3455&CB:::EHV: | Cumulative Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-213 | FROM->TO | 646221 S1221 5 161 646231 S1231 5 161 1 | B | 217 | 0.053847 | 103.9783 | P12:345:OPPD:S3455-S3456:::EHV: | Cumulative Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-213 | FROM->TO | 646221 S1221 5 161 646231 S1231 5 161 1 | B | 217 | 0.051922 | 105.1121 | P23:345:OPPD:S3456-S3455&CB:::EHV: | Cumulative Impact | Rebuild line 646221 S1221 5 161 646231 S1231 5 161 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-213 | FROM->TO | 646221 S1221 5 161 646231 S1231 5 161 1 | B | 217 | 0.054035 | 105.8605 | P12:345:OPPD:S3455-S3456:::EHV: | Cumulative Impact | Rebuild line 646221 S1221 5 161 646231 S1231 5 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-213 | FROM->TO | 646259 S1259 5 161 646278 S1278 5 161 1 | B | 215 | 0.053204 | 106.7879 | P23:345:OPPD:FUTURE 56-55&56-58:::EHV: | Cumulative Impact | Rebuild line 646259 S1259 5 161 646278 S1278 5 161 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-213 | FROM->TO | 646221 S1221 5 161 646231 S1231 5 161 1 | B | 217 | 0.058653 | 117.252 | P23:345:OPPD:FUTURE 56-55&56-58:::EHV: | Cumulative Impact | Rebuild line 646221 S1221 5 161 646231 S1231 5 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-213 | FROM->TO | 646221 S1221 5 161 646231 S1231 5 161 1 | B | 217 | 0.068037 | 119.4065 | P23:345:OPPD:FUTURE 56-55&56-58:::EHV: | Cumulative Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-213 | FROM->TO | 646221 S1221 5 161 646231 S1231 5 161 1 | B | 217 | 0.0595 | 127.9376 | P23:345:OPPD:FUTURE 56-55&56-58:::EHV: | Cumulative Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-213 | FROM->TO | 646221 S1221 5 161 646231 S1231 5 161 1 | B | 217 | 0.05978 | 129.6986 | P23:345:OPPD:FUTURE 56-55&56-58:::EHV: | Cumulative Impact | Rebuild line 646221 S1221 5 161 646231 S1231 5 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-213 | FROM->TO | 646221 S1221 5 161 646231 S1231 5 161 1 | B | 217 | 0.059483 | 145.0025 | P23:345:OPPD:FUTURE 56-55&56-58:::EHV: | Cumulative Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-213 | FROM->TO | 646221 S1221 5 161 646231 S1231 5 161 1 | B | 217 | 0.059743 | 147.401 | P23:345:OPPD:FUTURE 56-55&56-58:::EHV: | Cumulative Impact | Rebuild line 646221 S1221 5 161 646231 S1231 5 161 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-215 | FROM->TO | 539658 CONCRD6 230 3WXFMR 534:CONCORD6 230 1 | B | 225.5 | 0.096151 | 107.4002 | Single 539805 ELMCREEK7 345 640600 DAYKIN3 345 1 | Cumulative Impact | Add 3-winding transformer 539657 CONCORD3 115 539658 CONCRD6 230 539904 CONCOD-1 13 M2
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-215 | FROM->TO | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.05882 | 111.8275 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T1 | GEN-2024-219 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.030504 | 103.3038 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-219 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | A | 1187 | 0.044236 | 103.8656 | System Intact | TDF Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-219 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.051055 | 106.1409 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-219 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.050398 | 107.841 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-219 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.050398 | 109.5335 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-219 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.050398 | 109.534 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-219 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.050398 | 112.0538 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-219 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.047345 | 114.5102 | System Intact | TDF Impact | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-219 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.041238 | 114.6214 | System Intact | TDF Impact | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-219 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.050398 | 116.5975 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-219 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | B | 1000 | 0.061155 | 116.8554 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | Cumulative Impact | Rebuild line 508359 WELSH 7 345 508841 WILKES 7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-219 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.036807 | 119.3706 | System Intact | TDF Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-219 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.036807 | 119.3706 | System Intact | TDF Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-219 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.036807 | 119.3706 | System Intact | TDF Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-219 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.033568 | 119.5141 | System Intact | TDF Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-219 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.033568 | 119.5141 | System Intact | TDF Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-219 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.033568 | 119.5141 | System Intact | TDF Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-220 | FROM->TO | 508814 RODESSA2 69 508846 GODFREYRDTP2 69 1 | B | 53 | 0.29071 | 100.2066 | P42:345:AEPW:WILKES CB 1W10 NBTB+FAULT:::: | TDF Impact | Rebuild line 508814 RODESSA2 69 508846 GODFREYRDTP2 69 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-220 | FROM->TO | 508814 RODESSA2 69 508846 GODFREYRDTP2 69 1 | B | 53 | 0.29024 | 100.31 | P12:345:AEPW:LONGWD7:WILKES7::: | TDF Impact | Rebuild line 508814 RODESSA2 69 508846 GODFREYRDTP2 69 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-220 | FROM->TO | 508814 RODESSA2 69 508846 GODFREYRDTP2 69 1 | B | 65 | 0.42724 | 100.3955 | P12:69:AEPW:WATLANT2:LINDEN 2::: | TDF Impact | Rebuild line 508814 RODESSA2 69 508846 GODFREYRDTP2 69 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-220 | FROM->TO | 508814 RODESSA2 69 508846 GODFREYRDTP2 69 1 | B | 53 | 0.29048 | 100.487 | P23:345:AEPW:LONGWOOD CB 1N60 NBTB:::: | TDF Impact | Rebuild line 508814 RODESSA2 69 508846 GODFREYRDTP2 69 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-220 | FROM->TO | 508814 RODESSA2 69 508846 GODFREYRDTP2 69 1 | B | 53 | 0.4273 | 101.3242 | Single 508089 WATLANT2 69 779100 G24-071-TAP 69 1 | TDF Impact | Rebuild line 508814 RODESSA2 69 508846 GODFREYRDTP2 69 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-220 | FROM->TO | 508814 RODESSA2 69 508846 GODFREYRDTP2 69 1 | B | 53 | 0.42735 | 101.8575 | P12:69:AEPW:WATLANT2:LINDEN 2::: | TDF Impact | Rebuild line 508814 RODESSA2 69 508846 GODFREYRDTP2 69 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-220 | FROM->TO | 508814 RODESSA2 69 508846 GODFREYRDTP2 69 1 | B | 53 | 0.28824 | 108.3659 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | Rebuild line 508814 RODESSA2 69 508846 GODFREYRDTP2 69 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-220 | FROM->TO | 508814 RODESSA2 69 508846 GODFREYRDTP2 69 1 | B | 53 | 0.42622 | 112.6016 | Single 508089 WATLANT2 69 779100 G24-071-TAP 69 1 | TDF Impact | Rebuild line 508814 RODESSA2 69 508846 GODFREYRDTP2 69 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-220 | FROM->TO | 508814 RODESSA2 69 508846 GODFREYRDTP2 69 1 | B | 53 | 0.42627 | 113.2563 | P12:69:AEPW:WATLANT2:LINDEN 2::: | TDF Impact | Rebuild line 508814 RODESSA2 69 508846 GODFREYRDTP2 69 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-221 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.073449 | 100.0488 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29L | T0 | GEN-2024-221 | FROM->TO | 511541 DEMPSEYR POI 230 511557 CHISHOLM6 230 1 | B | 439 | 0.066904 | 100.3116 | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | Cumulative Impact | Rebuild line 511541 DEMPSEYR POI 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-221 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063087 | 100.533 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-221 | FROM->TO | 523959 POTTER_CO 6 230 524010 ROLLHILLS 6 230 1 | B | 548 | 0.056222 | 103.4659 | MULTIGEN523979 | Cumulative Impact | Rebuild line 523959 POTTER_CO 6 230 524010 ROLLHILLS 6 230 1
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-221 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.0778 | 103.9266 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-221 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.076457 | 104.7552 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-221 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.076457 | 104.888 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-221 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.080747 | 107.2243 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-221 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063915 | 107.2793 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-221 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063915 | 107.2794 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-221 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.080747 | 107.2951 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-221 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063915 | 107.3093 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-221 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063915 | 107.7557 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-221 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063915 | 108.2747 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-221 | FROM->TO | 523961 POTTER_CO 7 345 3WXFMR 526:WAUK 90343-A 230 1 | B | 559 | 0.14621 | 108.8994 | P42:345:SPS:HITCHLAND-1R15:::EHV: | Cumulative Impact | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-221 | FROM->TO | 523961 POTTER_CO 7 345 3WXFMR 526:WAUK 90343-A 230 1 | B | 559 | 0.14621 | 108.9122 | Single 523097 HITCHLAND7 345 523961 POTTER_CO7 345 1 | Cumulative Impact | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-221 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063915 | 111.3621 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-221 | FROM->TO | 523959 POTTER_CO 6 230 524010 ROLLHILLS 6 230 1 | B | 548 | 0.050823 | 114.0984 | MULTIGEN523978 | Cumulative Impact | Rebuild line 523959 POTTER_CO 6 230 524010 ROLLHILLS 6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-221 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.074461 | 115.0541 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-221 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.077486 | 118.9427 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-221 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.077486 | 119.313 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 00NR | 1 | 29SP | T1 | GEN-2024-234 | FROM->TO | 652552 SIOUXCY2 230 659900 EAGLE___-NI4 230 1 | B | 386 | 0.03655 | 100.2184 | P23:345:XEL:396 BKR SPK:::EHV: | TDF Impact | Rebuild line 652552 SIOUXCY2 230 659900 EAGLE___-NI4 230 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-234 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.081023 | 100.5915 | P23:345:MEC:HIGHLAND:903::EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-234 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.081023 | 100.6154 | P23:345:MEC:HIGHLAND:902::EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-234 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.069584 | 100.6843 | P12:230.0:UMZ:# N-1 #:: LINE TWIN CH4-SIOUXCY4-1 :HV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-234 | FROM->TO | 652564 SIOUXCY3 345 3WXFMR 652:652: SC2 KU1B 230 1 | B | 750 | 0.034756 | 100.7724 | P23:345:XEL:396 BKR SPK:::EHV: | TDF Impact | Add 3-winding transformer 652305 SIOUXC29 13 652552 SIOUXCY2 230 652564 SIOUXCY3 345 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-234 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.081023 | 101.5782 | Single 635368 OBRIEN3 345 635400 HIGHLAND3 345 1 | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-234 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.081023 | 101.5782 | P12:345:MEC:OBRIEN:HIGHLAND:1REACTOR:EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-234 | FROM->TO | 652552 SIOUXCY2 230 659900 EAGLE___-NI4 230 1 | B | 370 | 0.035564 | 101.858 | P23:345:XEL:396 BKR SPK:::EHV: | TDF Impact | Rebuild line 652552 SIOUXCY2 230 659900 EAGLE___-NI4 230 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-234 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.08172 | 103.0767 | P23:345:MEC:OBRIEN:903::EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-234 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.081319 | 104.0624 | P23:345:MEC:OBRIEN:906::EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 04ALL | 1 | 26SP | T1 | GEN-2024-235 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.044986 | 103.0993 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T1 | GEN-2024-235 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.047583 | 103.3038 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-235 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | A | 1187 | 0.076477 | 103.8656 | System Intact | TDF Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-235 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.083201 | 104.9177 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-235 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.097904 | 106.1409 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-235 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.082547 | 106.3238 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-235 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.087323 | 106.5158 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-235 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.097247 | 107.841 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-235 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.087323 | 108.059 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-235 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.097247 | 109.5335 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-235 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.097247 | 109.534 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-235 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.097247 | 112.0538 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.05617 | 114.5102 | System Intact | TDF Impact | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.050465 | 114.6214 | System Intact | TDF Impact | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-235 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.097247 | 116.5975 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.058301 | 119.3706 | System Intact | TDF Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.058301 | 119.3706 | System Intact | TDF Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.058301 | 119.3706 | System Intact | TDF Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.055608 | 119.5141 | System Intact | TDF Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.055608 | 119.5141 | System Intact | TDF Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.055608 | 119.5141 | System Intact | TDF Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.066858 | 136.5828 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.066858 | 136.5828 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.066858 | 136.5828 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.060555 | 136.8919 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.060555 | 136.8919 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.060555 | 136.8919 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.06367 | 136.9237 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.06367 | 136.9237 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.06367 | 136.9237 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.06461 | 139.3736 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.06461 | 139.3736 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.06461 | 139.3736 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.076315 | 140.3415 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.076315 | 140.3415 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.076315 | 140.3415 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.073049 | 140.6152 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.073049 | 140.6152 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.073049 | 140.6152 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.065546 | 141.6076 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.065546 | 141.6076 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.065546 | 141.6076 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.064477 | 142.5086 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.064477 | 142.5086 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.064477 | 142.5086 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.075782 | 142.6431 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.075782 | 142.6431 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.075782 | 142.6431 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.062258 | 142.7223 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.062258 | 142.7223 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.062258 | 142.7223 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.07246 | 143.2233 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.07246 | 143.2233 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.07246 | 143.2233 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.061346 | 143.8401 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.061346 | 143.8401 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.061346 | 143.8401 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.075782 | 145.1309 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.075782 | 145.1309 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.075782 | 145.1309 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.075782 | 145.1356 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.075782 | 145.1356 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.075782 | 145.1356 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.07246 | 145.7578 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.07246 | 145.7578 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.07246 | 145.7578 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.07246 | 145.7646 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.07246 | 145.7646 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.07246 | 145.7646 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.075782 | 148.805 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.075782 | 148.805 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.075782 | 148.805 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.07246 | 149.8057 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.07246 | 149.8057 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.07246 | 149.8057 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.075782 | 155.6146 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.075782 | 155.6146 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.075782 | 155.6146 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.07246 | 157.3662 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.07246 | 157.3662 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.07246 | 157.3662 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T1 | GEN-2024-236 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.032631 | 103.0993 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T1 | GEN-2024-236 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.03528 | 103.3038 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-236 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | A | 1187 | 0.057556 | 103.8656 | System Intact | TDF Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-236 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.063785 | 104.9177 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-236 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.064302 | 106.1409 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-236 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.062814 | 106.3238 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-236 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.059799 | 106.5158 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-236 | FROM->TO | 515302 FTSMITH7 345 3WXFMR 524:524:FTSMITH1 500 1 | B | 693 | 0.07105 | 107.4747 | P12:161:EES:FTSMTHW5%:FTSMITH7%:FTSMTH511:HV: | Cumulative Impact | Add 3-winding transformer 515302 FTSMITH7 345 515305 FTSMITH8 500 515726 FTSMTH11 13 M2
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-236 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.063644 | 107.841 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-236 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.059799 | 108.059 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-236 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.063644 | 109.5335 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-236 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.063644 | 109.534 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-236 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.063644 | 112.0538 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-236 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.043807 | 114.5102 | System Intact | TDF Impact | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-236 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.037957 | 114.6214 | System Intact | TDF Impact | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-236 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.063644 | 116.5975 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-236 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.045977 | 119.3706 | System Intact | TDF Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-236 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.045977 | 119.3706 | System Intact | TDF Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-236 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.045977 | 119.3706 | System Intact | TDF Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-236 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.043758 | 119.5141 | System Intact | TDF Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-236 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.043758 | 119.5141 | System Intact | TDF Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-236 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.043758 | 119.5141 | System Intact | TDF Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-236 | FROM->TO | 515302 FTSMITH7 345 3WXFMR 524:524:FTSMITH5 345 5 | B | 493 | 0.054263 | 126.769 | P12:345:EES:FTSMITH7%:FTSMITH8%:FTSMTH111:EHV: | Cumulative Impact | Add 3-winding transformer 515301 FTSMTHW5 161 515302 FTSMITH7 345 515728 FTSMTH51 13 M2
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-236 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051996 | 140.3415 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-236 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051996 | 140.3415 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-236 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051996 | 140.3415 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-236 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.052767 | 141.6076 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-236 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.052767 | 141.6076 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-236 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.052767 | 141.6076 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-236 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051241 | 142.5086 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-236 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051241 | 142.5086 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-236 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051241 | 142.5086 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-236 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051463 | 142.6431 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-236 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051463 | 142.6431 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-236 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051463 | 142.6431 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-236 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.050166 | 142.7223 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-236 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.050166 | 142.7223 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-236 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.050166 | 142.7223 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-236 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051463 | 145.1309 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-236 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051463 | 145.1309 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-236 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051463 | 145.1309 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-236 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051463 | 145.1356 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-236 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051463 | 145.1356 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-236 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051463 | 145.1356 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-236 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051463 | 148.805 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-236 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051463 | 148.805 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-236 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051463 | 148.805 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-236 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051463 | 155.6146 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-236 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051463 | 155.6146 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-236 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051463 | 155.6146 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-239 | FROM->TO | 514901 CIMARON7 345 3WXFMR 524:524:CIMARON2 345 2 | B | 478 | 0.067544 | 101.8584 | P13:138:OKGE:BKRBKR_3W020:::HV: | TDF Impact | Add 3-winding transformer 514898 CIMARON4 138 514901 CIMARON7 345 515715 CIMARO21 13 M2
Thermal | 04ALL | 1 | 29SP | T1 | GEN-2024-239 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.030327 | 103.3038 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-239 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | A | 1187 | 0.038358 | 103.8656 | System Intact | TDF Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-239 | FROM->TO | 514901 CIMARON7 345 3WXFMR 524:524:CIMARON2 345 2 | B | 478 | 0.070638 | 105.6405 | P13:138:OKGE:BKRBKR_3W020:::HV: | TDF Impact | Add 3-winding transformer 514898 CIMARON4 138 514901 CIMARON7 345 515715 CIMARO21 13 M2
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-239 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.067317 | 114.5102 | System Intact | TDF Impact | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-239 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.062464 | 114.6214 | System Intact | TDF Impact | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-239 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.033193 | 119.3706 | System Intact | TDF Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-239 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.033193 | 119.3706 | System Intact | TDF Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-239 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.033193 | 119.3706 | System Intact | TDF Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-240 | FROM->TO | 532793 NEOSHO 7 345 3WXFMR 536:N345 TX-2 161 2 | B | 550 | 0.052242 | 101.4582 | Single 533021 NEOSHO4 138 533023 N34534 138 1 | TDF Impact | Add 3-winding transformer 532793 NEOSHO 7 345 532825 N345 2 1 13 532939 N345 4 5 161 M2
Thermal | 00NR | 1 | 29WP | T1 | GEN-2024-240 | FROM->TO | 532937 NEOSHO 5 161 764310 G20-079-TAP 161 1 | B | 533 | 0.046061 | 101.6771 | P23:345:AECI:7BLACKBERRY:653::: | TDF Impact | Rebuild line 532937 NEOSHO 5 161 764310 G20-079-TAP 161 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-240 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | A | 717 | 0.039879 | 102.1682 | System Intact | TDF Impact | Rebuild line 541198 PECULR 7 345 541200 PHILL 7 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-240 | FROM->TO | 532793 NEOSHO 7 345 3WXFMR 536:N345 TX-2 161 2 | B | 550 | 0.061457 | 103.5308 | Single 533021 NEOSHO4 138 533023 N34534 138 1 | TDF Impact | Add 3-winding transformer 532793 NEOSHO 7 345 532825 N345 2 1 13 532939 N345 4 5 161 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-240 | FROM->TO | 532793 NEOSHO 7 345 3WXFMR 536:N345 TX-2 161 2 | B | 550 | 0.062944 | 111.3295 | Single 533021 NEOSHO4 138 533023 N34534 138 1 | TDF Impact | Add 3-winding transformer 532793 NEOSHO 7 345 532825 N345 2 1 13 532939 N345 4 5 161 M2
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-241 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | B | 1220 | 0.26302 | 105.5159 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | Rebuild line 508359 WELSH 7 345 508841 WILKES 7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-241 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | B | 1000 | 0.26264 | 116.8554 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | Rebuild line 508359 WELSH 7 345 508841 WILKES 7 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-252 | FROM->TO | 514901 CIMARON7 345 3WXFMR 524:524:CIMARON2 345 2 | B | 478 | 0.067544 | 101.8584 | P13:138:OKGE:BKRBKR_3W020:::HV: | TDF Impact | Add 3-winding transformer 514898 CIMARON4 138 514901 CIMARON7 345 515715 CIMARO21 13 M2
Thermal | 04ALL | 1 | 29SP | T1 | GEN-2024-252 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.030327 | 103.3038 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-252 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | A | 1187 | 0.038358 | 103.8656 | System Intact | TDF Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-252 | FROM->TO | 514901 CIMARON7 345 3WXFMR 524:524:CIMARON2 345 2 | B | 478 | 0.070638 | 105.6405 | P13:138:OKGE:BKRBKR_3W020:::HV: | TDF Impact | Add 3-winding transformer 514898 CIMARON4 138 514901 CIMARON7 345 515715 CIMARO21 13 M2
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-252 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.067317 | 114.5102 | System Intact | TDF Impact | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-252 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.062464 | 114.6214 | System Intact | TDF Impact | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-252 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.033193 | 119.3706 | System Intact | TDF Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-252 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.033193 | 119.3706 | System Intact | TDF Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-252 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.033193 | 119.3706 | System Intact | TDF Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-253 | FROM->TO | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.073602 | 104.394 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-253 | FROM->TO | 533243 JAGGARD3 115 533261 PENTAGN3 115 1 | B | 201 | 0.057858 | 107.2439 | Single 532775 87TH7 345 784560 G24-253-TAP 345 1 | Cumulative Impact | Rebuild line 533243 JAGGARD3 115 533261 PENTAGN3 115 1
Thermal | 03ALL | 1 | 29WP | T1 | GEN-2024-253 | FROM->TO | 533243 JAGGARD3 115 533261 PENTAGN3 115 1 | B | 260 | 0.057119 | 108.9944 | Single 532775 87TH7 345 784560 G24-253-TAP 345 1 | Cumulative Impact | Rebuild line 533243 JAGGARD3 115 533261 PENTAGN3 115 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-253 | FROM->TO | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.080162 | 111.8275 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-254 | FROM->TO | 514901 CIMARON7 345 3WXFMR 524:524:CIMARON2 345 2 | B | 478 | 0.042947 | 101.8584 | P13:138:OKGE:BKRBKR_3W020:::HV: | TDF Impact | Add 3-winding transformer 514898 CIMARON4 138 514901 CIMARON7 345 515715 CIMARO21 13 M2
Thermal | 04ALL | 1 | 29SP | T1 | GEN-2024-254 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.030037 | 103.3038 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-254 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | A | 1187 | 0.036671 | 103.8656 | System Intact | TDF Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-254 | FROM->TO | 514901 CIMARON7 345 3WXFMR 524:524:CIMARON2 345 2 | B | 478 | 0.048347 | 105.6405 | P13:138:OKGE:BKRBKR_3W020:::HV: | TDF Impact | Add 3-winding transformer 514898 CIMARON4 138 514901 CIMARON7 345 515715 CIMARO21 13 M2
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-254 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.07251 | 114.5102 | System Intact | TDF Impact | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-254 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.068241 | 114.6214 | System Intact | TDF Impact | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-254 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.03208 | 119.3706 | System Intact | TDF Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-254 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.03208 | 119.3706 | System Intact | TDF Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-254 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.03208 | 119.3706 | System Intact | TDF Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T1 | GEN-2024-255 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.031854 | 103.3038 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-255 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | A | 1187 | 0.041988 | 103.8656 | System Intact | TDF Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-255 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.054077 | 106.1409 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-255 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.053419 | 107.841 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-255 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.053419 | 109.5335 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-255 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.053419 | 109.534 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-255 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.053419 | 112.0538 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-255 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.068359 | 114.5102 | System Intact | TDF Impact | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-255 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.062929 | 114.6214 | System Intact | TDF Impact | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-255 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.053419 | 116.5975 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-255 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.035412 | 119.3706 | System Intact | TDF Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-255 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.035412 | 119.3706 | System Intact | TDF Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-255 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.035412 | 119.3706 | System Intact | TDF Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-255 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.031938 | 119.5141 | System Intact | TDF Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-255 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.031938 | 119.5141 | System Intact | TDF Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-255 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.031938 | 119.5141 | System Intact | TDF Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-258 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | B | 756 | 0.053896 | 101.463 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild line 541200 PHILL 7 345 541201 SIBLEY 7 345 1
Thermal | 00NR | 1 | 29WP | T1 | GEN-2024-258 | FROM->TO | 532937 NEOSHO 5 161 764310 G20-079-TAP 161 1 | B | 533 | 0.039852 | 101.6771 | P23:345:AECI:7BLACKBERRY:653::: | TDF Impact | Rebuild line 532937 NEOSHO 5 161 764310 G20-079-TAP 161 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-258 | FROM->TO | 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | B | 956 | 0.46631 | 101.9427 | P23:345:AECI:7BLACKBERRY:6_2::: | TDF Impact | Rebuild line 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-258 | FROM->TO | 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | B | 956 | 0.46631 | 101.9438 | P23:345:AECI:7BLACKBERRY:6_3::: | TDF Impact | Rebuild line 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-258 | FROM->TO | 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | B | 956 | 0.46655 | 103.0407 | Single 300739 7BLACKBERRY 345 785580 G24-287-TAP 345 1 | TDF Impact | Rebuild line 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-258 | FROM->TO | 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | B | 956 | 0.46729 | 103.5013 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | TDF Impact | Rebuild line 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-258 | FROM->TO | 532793 NEOSHO 7 345 3WXFMR 536:N345 TX-2 161 2 | B | 550 | 0.030731 | 103.5308 | Single 533021 NEOSHO4 138 533023 N34534 138 1 | TDF Impact | Add 3-winding transformer 532793 NEOSHO 7 345 532825 N345 2 1 13 532939 N345 4 5 161 M2
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-258 | FROM->TO | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.16311 | 104.394 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-258 | FROM->TO | 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | B | 956 | 0.46826 | 105.9563 | P23:345:AECI:7BLACKBERRY:6_2::: | TDF Impact | Rebuild line 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-258 | FROM->TO | 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | B | 956 | 0.46826 | 105.9589 | P23:345:AECI:7BLACKBERRY:6_3::: | TDF Impact | Rebuild line 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-258 | FROM->TO | 532793 NEOSHO 7 345 3WXFMR 536:N345 TX-2 161 2 | B | 550 | 0.030696 | 111.3295 | Single 533021 NEOSHO4 138 533023 N34534 138 1 | TDF Impact | Add 3-winding transformer 532793 NEOSHO 7 345 532825 N345 2 1 13 532939 N345 4 5 161 M2
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-258 | FROM->TO | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.14906 | 111.8275 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-258 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | B | 756 | 0.054964 | 117.5821 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild line 541200 PHILL 7 345 541201 SIBLEY 7 345 1
Thermal | 03ALL | 1 | 29WP | T1 | GEN-2024-259 | FROM->TO | 547467 ORO110 5 161 547494 OAK432 5 161 1 | B | 335 | 0.20173 | 100.5104 | Single 547485 CAR3955 161 547491 PUR4215 161 1 | TDF Impact | Rebuild line 547467 ORO110 5 161 547494 OAK432 5 161 1
Thermal | 03ALL | 1 | 29WP | T1 | GEN-2024-259 | FROM->TO | 547467 ORO110 5 161 547494 OAK432 5 161 1 | B | 335 | 0.20173 | 101.6854 | Single 547476 ASB3495 161 547491 PUR4215 161 1 | TDF Impact | Rebuild line 547467 ORO110 5 161 547494 OAK432 5 161 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-259 | FROM->TO | 505488 CARTHAG5 161 3WXFMR 537:CRG X2 161 1 | B | 84 | 0.046957 | 101.7304 | Single 505490 CARTHG2 69 505488 CARTHAG5 161 505487 'CRG X1 1 ' 13 1 | TDF Impact | Carthage_Add_transformer_fixed.idv :
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-259 | FROM->TO | 547477 CJ 366 5 161 547490 FIR417 5 161 1 | B | 290 | 0.61775 | 102.0779 | Single 505488 CARTHAG5 161 547485 CAR3955 161 1 | TDF Impact | Rebuild line 547477 CJ 366 5 161 547490 FIR417 5 161 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-259 | FROM->TO | 505492 SPRGFLD5 161 549970 CLAY 5 161 1 | B | 223 | 0.030153 | 102.2021 | P12:345:AECI:HUBEN:MORGAN_345:1:: | TDF Impact | Rebuild line 505492 SPRGFLD5 161 549970 CLAY 5 161 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-259 | FROM->TO | 505488 CARTHAG5 161 3WXFMR 300:CRG X1 161 1 | B | 84 | 0.047277 | 102.3328 | Single 505490 CARTHG2 69 505488 CARTHAG5 161 505489 'CRG X2 1 ' 13 1 | TDF Impact | Carthage_Add_transformer_fixed.idv :
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-259 | FROM->TO | 547476 ASB349 5 161 547491 PUR421 5 161 1 | B | 290 | 0.56525 | 102.4213 | Single 547467 ORO1105 161 547490 FIR4175 161 1 | TDF Impact | Rebuild line 547476 ASB349 5 161 547491 PUR421 5 161 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-259 | FROM->TO | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.071752 | 104.394 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-259 | FROM->TO | 547477 CJ 366 5 161 547490 FIR417 5 161 1 | B | 290 | 0.61775 | 105.6274 | Single 547485 CAR3955 161 547491 PUR4215 161 1 | TDF Impact | Rebuild line 547477 CJ 366 5 161 547490 FIR417 5 161 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-259 | FROM->TO | 547476 ASB349 5 161 547477 CJ 366 5 161 1 | B | 290 | 0.61775 | 106.0936 | Single 505488 CARTHAG5 161 547485 CAR3955 161 1 | TDF Impact | Rebuild line 547476 ASB349 5 161 547477 CJ 366 5 161 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-259 | FROM->TO | 547476 ASB349 5 161 547491 PUR421 5 161 1 | B | 290 | 0.56525 | 106.3247 | Single 547477 CJ3665 161 547490 FIR4175 161 1 | TDF Impact | Rebuild line 547476 ASB349 5 161 547491 PUR421 5 161 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-259 | FROM->TO | 547477 CJ 366 5 161 547490 FIR417 5 161 1 | B | 290 | 0.61775 | 107.2979 | Single 547476 ASB3495 161 547491 PUR4215 161 1 | TDF Impact | Rebuild line 547477 CJ 366 5 161 547490 FIR417 5 161 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-259 | FROM->TO | 547476 ASB349 5 161 547491 PUR421 5 161 1 | B | 290 | 0.55875 | 107.5272 | Single 547467 ORO1105 161 547490 FIR4175 161 1 | TDF Impact | Rebuild line 547476 ASB349 5 161 547491 PUR421 5 161 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-259 | FROM->TO | 547477 CJ 366 5 161 547490 FIR417 5 161 1 | B | 290 | 0.61185 | 107.916 | Single 505488 CARTHAG5 161 547485 CAR3955 161 1 | TDF Impact | Rebuild line 547477 CJ 366 5 161 547490 FIR417 5 161 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-259 | FROM->TO | 505488 CARTHAG5 161 3WXFMR 537:CRG X2 161 1 | B | 84 | 0.04632 | 108.0024 | Single 505490 CARTHG2 69 505488 CARTHAG5 161 505487 'CRG X1 1 ' 13 1 | TDF Impact | Carthage_Add_transformer_fixed.idv :
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-259 | FROM->TO | 505488 CARTHAG5 161 3WXFMR 300:CRG X1 161 1 | B | 84 | 0.046635 | 108.6433 | Single 505490 CARTHG2 69 505488 CARTHAG5 161 505489 'CRG X2 1 ' 13 1 | TDF Impact | Carthage_Add_transformer_fixed.idv :
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-259 | FROM->TO | 547476 ASB349 5 161 547491 PUR421 5 161 1 | B | 290 | 0.56525 | 108.9532 | Single 547476 ASB3495 161 547477 CJ3665 161 1 | TDF Impact | Rebuild line 547476 ASB349 5 161 547491 PUR421 5 161 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-259 | FROM->TO | 547476 ASB349 5 161 547477 CJ 366 5 161 1 | B | 290 | 0.61775 | 109.6462 | Single 547485 CAR3955 161 547491 PUR4215 161 1 | TDF Impact | Rebuild line 547476 ASB349 5 161 547477 CJ 366 5 161 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-259 | FROM->TO | 547476 ASB349 5 161 547477 CJ 366 5 161 1 | B | 290 | 0.61775 | 111.3193 | Single 547476 ASB3495 161 547491 PUR4215 161 1 | TDF Impact | Rebuild line 547476 ASB349 5 161 547477 CJ 366 5 161 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-259 | FROM->TO | 547476 ASB349 5 161 547491 PUR421 5 161 1 | B | 290 | 0.55875 | 111.3423 | Single 547477 CJ3665 161 547490 FIR4175 161 1 | TDF Impact | Rebuild line 547476 ASB349 5 161 547491 PUR421 5 161 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-259 | FROM->TO | 547477 CJ 366 5 161 547490 FIR417 5 161 1 | B | 290 | 0.61185 | 111.3879 | Single 547485 CAR3955 161 547491 PUR4215 161 1 | TDF Impact | Rebuild line 547477 CJ 366 5 161 547490 FIR417 5 161 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-259 | FROM->TO | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.071524 | 111.8275 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-259 | FROM->TO | 547476 ASB349 5 161 547477 CJ 366 5 161 1 | B | 290 | 0.61185 | 111.8627 | Single 505488 CARTHAG5 161 547485 CAR3955 161 1 | TDF Impact | Rebuild line 547476 ASB349 5 161 547477 CJ 366 5 161 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-259 | FROM->TO | 547477 CJ 366 5 161 547490 FIR417 5 161 1 | B | 335 | 0.61764 | 112.3667 | Single 505488 CARTHAG5 161 547485 CAR3955 161 1 | TDF Impact | Rebuild line 547477 CJ 366 5 161 547490 FIR417 5 161 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-259 | FROM->TO | 547477 CJ 366 5 161 547490 FIR417 5 161 1 | B | 290 | 0.61185 | 113.0237 | Single 547476 ASB3495 161 547491 PUR4215 161 1 | TDF Impact | Rebuild line 547477 CJ 366 5 161 547490 FIR417 5 161 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-259 | FROM->TO | 547476 ASB349 5 161 547491 PUR421 5 161 1 | B | 290 | 0.55875 | 113.9097 | Single 547476 ASB3495 161 547477 CJ3665 161 1 | TDF Impact | Rebuild line 547476 ASB349 5 161 547491 PUR421 5 161 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-259 | FROM->TO | 547476 ASB349 5 161 547477 CJ 366 5 161 1 | B | 290 | 0.61185 | 115.3377 | Single 547485 CAR3955 161 547491 PUR4215 161 1 | TDF Impact | Rebuild line 547476 ASB349 5 161 547477 CJ 366 5 161 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-259 | FROM->TO | 547477 CJ 366 5 161 547490 FIR417 5 161 1 | B | 335 | 0.61764 | 115.5462 | Single 547485 CAR3955 161 547491 PUR4215 161 1 | TDF Impact | Rebuild line 547477 CJ 366 5 161 547490 FIR417 5 161 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-259 | FROM->TO | 547476 ASB349 5 161 547491 PUR421 5 161 1 | B | 322 | 0.56534 | 115.6824 | Single 547467 ORO1105 161 547490 FIR4175 161 1 | TDF Impact | Rebuild line 547476 ASB349 5 161 547491 PUR421 5 161 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-259 | FROM->TO | 547476 ASB349 5 161 547477 CJ 366 5 161 1 | B | 290 | 0.61185 | 116.976 | Single 547476 ASB3495 161 547491 PUR4215 161 1 | TDF Impact | Rebuild line 547476 ASB349 5 161 547477 CJ 366 5 161 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-259 | FROM->TO | 547477 CJ 366 5 161 547490 FIR417 5 161 1 | B | 335 | 0.61764 | 117.0461 | Single 547476 ASB3495 161 547491 PUR4215 161 1 | TDF Impact | Rebuild line 547477 CJ 366 5 161 547490 FIR417 5 161 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-259 | FROM->TO | 547476 ASB349 5 161 547491 PUR421 5 161 1 | B | 322 | 0.56534 | 119.3328 | Single 547477 CJ3665 161 547490 FIR4175 161 1 | TDF Impact | Rebuild line 547476 ASB349 5 161 547491 PUR421 5 161 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-259 | FROM->TO | 547476 ASB349 5 161 547477 CJ 366 5 161 1 | B | 322 | 0.61764 | 120.6626 | Single 505488 CARTHAG5 161 547485 CAR3955 161 1 | TDF Impact | Rebuild line 547476 ASB349 5 161 547477 CJ 366 5 161 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-259 | FROM->TO | 547476 ASB349 5 161 547491 PUR421 5 161 1 | B | 322 | 0.56534 | 121.7911 | Single 547476 ASB3495 161 547477 CJ3665 161 1 | TDF Impact | Rebuild line 547476 ASB349 5 161 547491 PUR421 5 161 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-259 | FROM->TO | 547476 ASB349 5 161 547477 CJ 366 5 161 1 | B | 322 | 0.61764 | 123.9749 | Single 547485 CAR3955 161 547491 PUR4215 161 1 | TDF Impact | Rebuild line 547476 ASB349 5 161 547477 CJ 366 5 161 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-259 | FROM->TO | 547476 ASB349 5 161 547477 CJ 366 5 161 1 | B | 322 | 0.61764 | 125.5385 | Single 547476 ASB3495 161 547491 PUR4215 161 1 | TDF Impact | Rebuild line 547476 ASB349 5 161 547477 CJ 366 5 161 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-260 | FROM->TO | 541253 ST JOE 5 161 541394 AVENUECTY 5 161 1 | A | 161 | 0.05106 | 100.5556 | System Intact | TDF Impact | Rebuild line 541253 ST JOE 5 161 541394 AVENUECTY 5 161 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-260 | FROM->TO | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.060519 | 104.394 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-260 | FROM->TO | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.06942 | 111.8275 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-261 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.071579 | 100.0488 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-261 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.06252 | 100.533 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-261 | FROM->TO | 528333 LE-WEST_SUB3 115 528334 LE-NRTH_INT3 115 1 | B | 199.39 | 0.99794 | 102.4732 | Single 527891 HOBBS_INT3 115 784800 G24-261-TAP 115 1 | TDF Impact | Rebuild line 528333 LE-WEST_SUB3 115 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-261 | FROM->TO | 528333 LE-WEST_SUB3 115 528334 LE-NRTH_INT3 115 1 | B | 199.39 | 0.99783 | 102.7319 | Single 527891 HOBBS_INT3 115 784800 G24-261-TAP 115 1 | TDF Impact | Rebuild line 528333 LE-WEST_SUB3 115 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-261 | FROM->TO | 528333 LE-WEST_SUB3 115 528334 LE-NRTH_INT3 115 1 | B | 199.39 | 0.9977 | 103.3987 | Single 527891 HOBBS_INT3 115 784800 G24-261-TAP 115 1 | TDF Impact | Rebuild line 528333 LE-WEST_SUB3 115 528334 LE-NRTH_INT3 115 1
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-261 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.075251 | 103.9266 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-261 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.074703 | 104.7552 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-261 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.074703 | 104.888 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-261 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.078317 | 107.2243 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-261 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063415 | 107.2793 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-261 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063415 | 107.2794 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-261 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.078317 | 107.2951 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-261 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063415 | 107.3093 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-261 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063415 | 107.7557 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-261 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063415 | 108.2747 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-261 | FROM->TO | 523961 POTTER_CO 7 345 3WXFMR 526:WAUK 90343-A 230 1 | B | 559 | 0.10911 | 108.8994 | P42:345:SPS:HITCHLAND-1R15:::EHV: | Cumulative Impact | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-261 | FROM->TO | 523961 POTTER_CO 7 345 3WXFMR 526:WAUK 90343-A 230 1 | B | 559 | 0.10911 | 108.9122 | Single 523097 HITCHLAND7 345 523961 POTTER_CO7 345 1 | Cumulative Impact | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-261 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063415 | 111.3621 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-261 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.072667 | 115.0541 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-261 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.075808 | 118.9427 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-261 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.075808 | 119.313 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-265 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.071535 | 100.0488 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-265 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.062518 | 100.533 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-265 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.075186 | 103.9266 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-265 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.074664 | 104.7552 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-265 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.074664 | 104.888 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-265 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.078256 | 107.2243 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-265 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063416 | 107.2793 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-265 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063416 | 107.2794 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-265 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.078256 | 107.2951 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-265 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063416 | 107.3093 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-265 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063416 | 107.7557 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-265 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063416 | 108.2747 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-265 | FROM->TO | 523961 POTTER_CO 7 345 3WXFMR 526:WAUK 90343-A 230 1 | B | 559 | 0.10698 | 108.8994 | P42:345:SPS:HITCHLAND-1R15:::EHV: | Cumulative Impact | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-265 | FROM->TO | 523961 POTTER_CO 7 345 3WXFMR 526:WAUK 90343-A 230 1 | B | 559 | 0.10698 | 108.9122 | Single 523097 HITCHLAND7 345 523961 POTTER_CO7 345 1 | Cumulative Impact | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-265 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063416 | 111.3621 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-265 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.072627 | 115.0541 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-265 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.075771 | 118.9427 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-265 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.075771 | 119.313 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 04ALL | 1 | 26SP | T1 | GEN-2024-268 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.042166 | 103.0993 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T1 | GEN-2024-268 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.044147 | 103.3038 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-268 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | A | 1187 | 0.077086 | 103.8656 | System Intact | TDF Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-268 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.085573 | 104.9177 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-268 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.082325 | 106.1409 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-268 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.08397 | 106.3238 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-268 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.077531 | 106.5158 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-268 | FROM->TO | 515302 FTSMITH7 345 3WXFMR 524:524:FTSMITH1 500 1 | B | 693 | 0.14687 | 107.4747 | P12:161:EES:FTSMTHW5%:FTSMITH7%:FTSMTH511:HV: | Cumulative Impact | Add 3-winding transformer 515302 FTSMITH7 345 515305 FTSMITH8 500 515726 FTSMTH11 13 M2
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-268 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.081668 | 107.841 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-268 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.077531 | 108.059 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-268 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.081668 | 109.5335 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-268 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.081668 | 109.534 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-268 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.081668 | 112.0538 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-268 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.081668 | 116.5975 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-268 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.059166 | 119.3706 | System Intact | TDF Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-268 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.059166 | 119.3706 | System Intact | TDF Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-268 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.059166 | 119.3706 | System Intact | TDF Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-268 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.057764 | 119.5141 | System Intact | TDF Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-268 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.057764 | 119.5141 | System Intact | TDF Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-268 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.057764 | 119.5141 | System Intact | TDF Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-268 | FROM->TO | 515302 FTSMITH7 345 3WXFMR 524:524:FTSMITH5 345 5 | B | 493 | 0.11309 | 126.769 | P12:345:EES:FTSMITH7%:FTSMITH8%:FTSMTH111:EHV: | Cumulative Impact | Add 3-winding transformer 515301 FTSMTHW5 161 515302 FTSMITH7 345 515728 FTSMTH51 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-268 | FROM->TO | 516092 OKTAHA 5 161 3WXFMR OKTAHA 5 69 7 | B | 112 | 0.053035 | 128.9125 | P22:345:EES:MUSKOGE7!:::EHV: | TDF Impact | Rebuild 3-winding transformer 516092 OKTAHA 5 161 516093 OKTAHA 2 69 516095 OKTAHA71 13 7
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-268 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.059823 | 136.5828 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-268 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.059823 | 136.5828 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-268 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.059823 | 136.5828 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-268 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.06238 | 136.8919 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-268 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.06238 | 136.8919 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-268 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.06238 | 136.8919 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-268 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.063869 | 136.9237 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-268 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.063869 | 136.9237 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-268 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.063869 | 136.9237 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-268 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.058239 | 139.3736 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-268 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.058239 | 139.3736 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-268 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.058239 | 139.3736 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-268 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.06416 | 140.3415 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-268 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.06416 | 140.3415 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-268 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.06416 | 140.3415 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-268 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.06215 | 140.6152 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-268 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.06215 | 140.6152 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-268 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.06215 | 140.6152 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-268 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.068374 | 141.6076 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-268 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.068374 | 141.6076 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-268 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.068374 | 141.6076 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-268 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.065754 | 142.5086 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-268 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.065754 | 142.5086 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-268 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.065754 | 142.5086 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-268 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.063627 | 142.6431 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-268 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.063627 | 142.6431 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-268 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.063627 | 142.6431 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-268 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.06675 | 142.7223 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-268 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.06675 | 142.7223 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-268 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.06675 | 142.7223 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-268 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.061561 | 143.2233 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-268 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.061561 | 143.2233 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-268 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.061561 | 143.2233 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-268 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.064246 | 143.8401 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-268 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.064246 | 143.8401 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-268 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.064246 | 143.8401 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-268 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.063627 | 145.1309 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-268 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.063627 | 145.1309 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-268 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.063627 | 145.1309 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-268 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.063627 | 145.1356 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-268 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.063627 | 145.1356 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-268 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.063627 | 145.1356 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-268 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.061561 | 145.7578 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-268 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.061561 | 145.7578 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-268 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.061561 | 145.7578 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-268 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.061561 | 145.7646 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-268 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.061561 | 145.7646 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-268 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.061561 | 145.7646 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-268 | FROM->TO | 516092 OKTAHA 5 161 3WXFMR OKTAHA 5 69 7 | B | 112 | 0.052675 | 147.7196 | P22:345:EES:MUSKOGE7!:::EHV: | TDF Impact | Rebuild 3-winding transformer 516092 OKTAHA 5 161 516093 OKTAHA 2 69 516095 OKTAHA71 13 7
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-268 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.063627 | 148.805 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-268 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.063627 | 148.805 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-268 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.063627 | 148.805 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-268 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.061561 | 149.8057 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-268 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.061561 | 149.8057 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-268 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.061561 | 149.8057 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-268 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.063627 | 155.6146 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-268 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.063627 | 155.6146 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-268 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.063627 | 155.6146 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-268 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.061561 | 157.3662 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-268 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.061561 | 157.3662 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-268 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.061561 | 157.3662 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-268 | FROM->TO | 516092 OKTAHA 5 161 3WXFMR OKTAHA 5 69 7 | B | 112 | 0.053712 | 165.8816 | P22:345:EES:MUSKOGE7!:::EHV: | TDF Impact | Rebuild 3-winding transformer 516092 OKTAHA 5 161 516093 OKTAHA 2 69 516095 OKTAHA71 13 7
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-276 | FROM->TO | 532857 TECHILL6 230 3WXFMR 536:TECHILL TX-3 115 1 | B | 308 | 0.37394 | 100.5744 | Single 533151 AUBURN3 115 533194 SHERWOD3 115 1 | TDF Impact | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-276 | FROM->TO | 532857 TECHILL6 230 3WXFMR 536:TECHILL TX-3 115 1 | B | 308 | 0.38342 | 100.9894 | Single 532853 LAWHILL6 230 533250 LWRNCHL3 115 532882 'LAWHILL1 ' 14 1 | TDF Impact | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-276 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | B | 756 | 0.056853 | 101.463 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild line 541200 PHILL 7 345 541201 SIBLEY 7 345 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-276 | FROM->TO | 532857 TECHILL6 230 3WXFMR 536:TECHILL TX-3 115 1 | B | 308 | 0.40613 | 101.8154 | P23:345:KCPL-WERE:241WGARDNER-R12-13:::EHV: | TDF Impact | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-276 | FROM->TO | 532857 TECHILL6 230 3WXFMR 536:TECHILL TX-3 115 1 | B | 308 | 0.40636 | 102.0848 | P12:345:WERE:SWIS-WGAR-345:::EHV: | TDF Impact | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-276 | FROM->TO | 532857 TECHILL6 230 3WXFMR 536:TECHILL TX-3 115 1 | B | 308 | 0.38024 | 103.3692 | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-276 | FROM->TO | 532857 TECHILL6 230 3WXFMR 536:TECHILL TX-3 115 1 | B | 308 | 0.3936 | 104.0586 | P12:230:WERE:LAWH-SWIS-230:HV: | TDF Impact | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-276 | FROM->TO | 532857 TECHILL6 230 3WXFMR 536:TECHILL TX-3 115 1 | A | 280 | 0.38057 | 104.1336 | System Intact | TDF Impact | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-276 | FROM->TO | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.073711 | 104.394 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-276 | FROM->TO | 532857 TECHILL6 230 3WXFMR 536:TECHILL TX-3 115 1 | B | 308 | 0.37824 | 104.549 | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-276 | FROM->TO | 532857 TECHILL6 230 3WXFMR 536:TECHILL TX-3 115 1 | B | 308 | 0.35723 | 105.4253 | Single 532765 HOYT7 345 533163 HOYT3 115 532804 'HOYT 1 ' 14 1 | TDF Impact | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-276 | FROM->TO | 532857 TECHILL6 230 3WXFMR 536:TECHILL TX-3 115 1 | B | 308 | 0.37815 | 106.4727 | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-276 | FROM->TO | 532857 TECHILL6 230 3WXFMR 536:TECHILL TX-3 115 1 | B | 308 | 0.40654 | 108.1006 | P23:345:KCPL-WERE:241WGARDNER-R12-13:::EHV: | TDF Impact | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-276 | FROM->TO | 532857 TECHILL6 230 3WXFMR 536:TECHILL TX-3 115 1 | B | 308 | 0.40677 | 108.3536 | P12:345:WERE:SWIS-WGAR-345:::EHV: | TDF Impact | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-276 | FROM->TO | 532857 TECHILL6 230 3WXFMR 536:TECHILL TX-3 115 1 | B | 308 | 0.36951 | 111.133 | Single 532851 AUBURN6 230 533151 AUBURN3 115 532880 'AUBURN 1 ' 14 1 | TDF Impact | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-276 | FROM->TO | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.080915 | 111.8275 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-276 | FROM->TO | 532857 TECHILL6 230 3WXFMR 536:TECHILL TX-3 115 1 | B | 308 | 0.37866 | 112.2643 | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-276 | FROM->TO | 532857 TECHILL6 230 3WXFMR 536:TECHILL TX-3 115 1 | B | 308 | 0.35756 | 112.6424 | Single 532765 HOYT7 345 533163 HOYT3 115 532804 'HOYT 1 ' 14 1 | TDF Impact | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-276 | FROM->TO | 532857 TECHILL6 230 3WXFMR 536:TECHILL TX-3 115 1 | B | 308 | 0.37857 | 114.3033 | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-276 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | B | 756 | 0.057243 | 117.5821 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild line 541200 PHILL 7 345 541201 SIBLEY 7 345 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-276 | FROM->TO | 532857 TECHILL6 230 3WXFMR 536:TECHILL TX-3 115 1 | B | 308 | 0.36987 | 119.1646 | Single 532851 AUBURN6 230 533151 AUBURN3 115 532880 'AUBURN 1 ' 14 1 | TDF Impact | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-277 | FROM->TO | 532857 TECHILL6 230 3WXFMR 536:TECHILL TX-3 115 1 | B | 308 | 0.37394 | 100.5744 | Single 533151 AUBURN3 115 533194 SHERWOD3 115 1 | TDF Impact | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-277 | FROM->TO | 532857 TECHILL6 230 3WXFMR 536:TECHILL TX-3 115 1 | B | 308 | 0.38342 | 100.9894 | Single 532853 LAWHILL6 230 533250 LWRNCHL3 115 532882 'LAWHILL1 ' 14 1 | TDF Impact | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-277 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | B | 756 | 0.056853 | 101.463 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild line 541200 PHILL 7 345 541201 SIBLEY 7 345 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-277 | FROM->TO | 532857 TECHILL6 230 3WXFMR 536:TECHILL TX-3 115 1 | B | 308 | 0.40613 | 101.8154 | P23:345:KCPL-WERE:241WGARDNER-R12-13:::EHV: | TDF Impact | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-277 | FROM->TO | 532857 TECHILL6 230 3WXFMR 536:TECHILL TX-3 115 1 | B | 308 | 0.40636 | 102.0848 | P12:345:WERE:SWIS-WGAR-345:::EHV: | TDF Impact | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-277 | FROM->TO | 532857 TECHILL6 230 3WXFMR 536:TECHILL TX-3 115 1 | B | 308 | 0.38024 | 103.3692 | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-277 | FROM->TO | 532857 TECHILL6 230 3WXFMR 536:TECHILL TX-3 115 1 | B | 308 | 0.3936 | 104.0586 | P12:230:WERE:LAWH-SWIS-230:HV: | TDF Impact | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-277 | FROM->TO | 532857 TECHILL6 230 3WXFMR 536:TECHILL TX-3 115 1 | A | 280 | 0.38057 | 104.1336 | System Intact | TDF Impact | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-277 | FROM->TO | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.073711 | 104.394 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-277 | FROM->TO | 532857 TECHILL6 230 3WXFMR 536:TECHILL TX-3 115 1 | B | 308 | 0.37824 | 104.549 | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-277 | FROM->TO | 532857 TECHILL6 230 3WXFMR 536:TECHILL TX-3 115 1 | B | 308 | 0.35723 | 105.4253 | Single 532765 HOYT7 345 533163 HOYT3 115 532804 'HOYT 1 ' 14 1 | TDF Impact | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-277 | FROM->TO | 532857 TECHILL6 230 3WXFMR 536:TECHILL TX-3 115 1 | B | 308 | 0.37815 | 106.4727 | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-277 | FROM->TO | 532857 TECHILL6 230 3WXFMR 536:TECHILL TX-3 115 1 | B | 308 | 0.40654 | 108.1006 | P23:345:KCPL-WERE:241WGARDNER-R12-13:::EHV: | TDF Impact | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-277 | FROM->TO | 532857 TECHILL6 230 3WXFMR 536:TECHILL TX-3 115 1 | B | 308 | 0.40677 | 108.3536 | P12:345:WERE:SWIS-WGAR-345:::EHV: | TDF Impact | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-277 | FROM->TO | 532857 TECHILL6 230 3WXFMR 536:TECHILL TX-3 115 1 | B | 308 | 0.36951 | 111.133 | Single 532851 AUBURN6 230 533151 AUBURN3 115 532880 'AUBURN 1 ' 14 1 | TDF Impact | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-277 | FROM->TO | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.080915 | 111.8275 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-277 | FROM->TO | 532857 TECHILL6 230 3WXFMR 536:TECHILL TX-3 115 1 | B | 308 | 0.37866 | 112.2643 | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-277 | FROM->TO | 532857 TECHILL6 230 3WXFMR 536:TECHILL TX-3 115 1 | B | 308 | 0.35756 | 112.6424 | Single 532765 HOYT7 345 533163 HOYT3 115 532804 'HOYT 1 ' 14 1 | TDF Impact | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-277 | FROM->TO | 532857 TECHILL6 230 3WXFMR 536:TECHILL TX-3 115 1 | B | 308 | 0.37857 | 114.3033 | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-277 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | B | 756 | 0.057243 | 117.5821 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild line 541200 PHILL 7 345 541201 SIBLEY 7 345 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-277 | FROM->TO | 532857 TECHILL6 230 3WXFMR 536:TECHILL TX-3 115 1 | B | 308 | 0.36987 | 119.1646 | Single 532851 AUBURN6 230 533151 AUBURN3 115 532880 'AUBURN 1 ' 14 1 | TDF Impact | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-280 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.071916 | 100.0488 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-280 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.062525 | 100.533 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-280 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.075765 | 103.9266 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-280 | FROM->TO | 527020 SIDEWINDER 7 345 527896 HOBBS_INT 7 345 1 | B | 797 | 0.45927 | 104.3766 | Single 528027 RDRUNNER7 345 528604 ANDREWS6 345 1 | TDF Impact | 22.DIS2001_ERIS_G00_Line_Uprate_Hobbs_to_Sidewinder_345kV_Line.idv : DISIS-2020-001 Upgrade
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-280 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.075004 | 104.7552 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-280 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.075004 | 104.888 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-280 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.078793 | 107.2243 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-280 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063383 | 107.2793 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-280 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063383 | 107.2794 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-280 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.078793 | 107.2951 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-280 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063383 | 107.3093 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-280 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063383 | 107.7557 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-280 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063383 | 108.2747 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-280 | FROM->TO | 523961 POTTER_CO 7 345 3WXFMR 526:WAUK 90343-A 230 1 | B | 559 | 0.12625 | 108.8994 | P42:345:SPS:HITCHLAND-1R15:::EHV: | Cumulative Impact | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-280 | FROM->TO | 523961 POTTER_CO 7 345 3WXFMR 526:WAUK 90343-A 230 1 | B | 559 | 0.12625 | 108.9122 | Single 523097 HITCHLAND7 345 523961 POTTER_CO7 345 1 | Cumulative Impact | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-280 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063383 | 111.3621 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-280 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.072931 | 115.0541 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-280 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.076038 | 118.9427 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-280 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.076038 | 119.313 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-281 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.071795 | 100.0488 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-281 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.062481 | 100.533 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T1 | GEN-2024-281 | FROM->TO | 528547 S_JAL 3 115 528561 DOLLARHIDE 3 115 1 | B | 117 | 0.35529 | 100.6934 | Single 528526 TEAGUE3 115 785400 G24-281-TAP 115 1 | TDF Impact | Rebuild line 528547 S_JAL 3 115 528561 DOLLARHIDE 3 115 1
Thermal | 05ALL | 1 | 26SP | T1 | GEN-2024-281 | FROM->TO | 528547 S_JAL 3 115 528561 DOLLARHIDE 3 115 1 | B | 106 | 0.3431 | 102.8747 | Single 528540 WHITTEN3 115 528547 S_JAL3 115 1 | TDF Impact | Rebuild line 528547 S_JAL 3 115 528561 DOLLARHIDE 3 115 1
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-281 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.075621 | 103.9266 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T1 | GEN-2024-281 | FROM->TO | 528547 S_JAL 3 115 528561 DOLLARHIDE 3 115 1 | B | 117 | 0.15078 | 104.3377 | P12:115:SPS:W81.1.CUSMTN.PONDEROSA:::HV: | Cumulative Impact | Rebuild line 528547 S_JAL 3 115 528561 DOLLARHIDE 3 115 1
Thermal | 05ALL | 1 | 29WP | T1 | GEN-2024-281 | FROM->TO | 528547 S_JAL 3 115 528561 DOLLARHIDE 3 115 1 | B | 117 | 0.15078 | 104.3377 | Single 528239 CUSTERMTN3 115 528240 PONDEROSA3 115 1 | Cumulative Impact | Rebuild line 528547 S_JAL 3 115 528561 DOLLARHIDE 3 115 1
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-281 | FROM->TO | 527020 SIDEWINDER 7 345 527896 HOBBS_INT 7 345 1 | B | 797 | 0.19835 | 104.3766 | Single 528027 RDRUNNER7 345 528604 ANDREWS6 345 1 | Cumulative Impact | 22.DIS2001_ERIS_G00_Line_Uprate_Hobbs_to_Sidewinder_345kV_Line.idv : DISIS-2020-001 Upgrade
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-281 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.074889 | 104.7552 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-281 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.074889 | 104.888 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T1 | GEN-2024-281 | FROM->TO | 528547 S_JAL 3 115 528561 DOLLARHIDE 3 115 1 | B | 117 | 0.27081 | 106.022 | Single 528239 CUSTERMTN3 115 528540 WHITTEN3 115 1 | TDF Impact | Rebuild line 528547 S_JAL 3 115 528561 DOLLARHIDE 3 115 1
Thermal | 05ALL | 1 | 29WP | T1 | GEN-2024-281 | FROM->TO | 528547 S_JAL 3 115 528561 DOLLARHIDE 3 115 1 | B | 117 | 0.27081 | 106.022 | P12:115:SPS:W96.1.CUSMTN.WHITT:::HV: | TDF Impact | Rebuild line 528547 S_JAL 3 115 528561 DOLLARHIDE 3 115 1
Thermal | 05ALL | 1 | 26SP | T1 | GEN-2024-281 | FROM->TO | 528547 S_JAL 3 115 528561 DOLLARHIDE 3 115 1 | B | 106 | 0.37615 | 106.096 | Single 528526 TEAGUE3 115 528596 CARDINAL3 115 1 | TDF Impact | Rebuild line 528547 S_JAL 3 115 528561 DOLLARHIDE 3 115 1
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-281 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.078655 | 107.2243 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-281 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063343 | 107.2793 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-281 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063343 | 107.2794 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-281 | FROM->TO | 528526 TEAGUE 3 115 528596 CARDINAL 3 115 1 | B | 175 | 0.76089 | 107.2879 | P12:115:SPS:W96.1.CUSMTN.WHITT:::HV: | TDF Impact | Multi - Battle Axe - Wolfcamp Tap 115 kV DblCkt_Battle Axe - Ponderosa - Dollarhide 115 kV New Line.idv : PID : 900119, NTC, 2025 ITP, ISD: 6/1/2029
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-281 | FROM->TO | 528526 TEAGUE 3 115 528596 CARDINAL 3 115 1 | B | 175 | 0.76089 | 107.2879 | Single 528239 CUSTERMTN3 115 528540 WHITTEN3 115 1 | TDF Impact | Multi - Battle Axe - Wolfcamp Tap 115 kV DblCkt_Battle Axe - Ponderosa - Dollarhide 115 kV New Line.idv : PID : 900119, NTC, 2025 ITP, ISD: 6/1/2029
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-281 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.078655 | 107.2951 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-281 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063343 | 107.3093 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-281 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063343 | 107.7557 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-281 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063343 | 108.2747 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T1 | GEN-2024-281 | FROM->TO | 528547 S_JAL 3 115 528561 DOLLARHIDE 3 115 1 | B | 106 | 0.37615 | 108.5231 | Single 528526 TEAGUE3 115 785400 G24-281-TAP 115 1 | TDF Impact | Rebuild line 528547 S_JAL 3 115 528561 DOLLARHIDE 3 115 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-281 | FROM->TO | 528526 TEAGUE 3 115 528596 CARDINAL 3 115 1 | B | 175 | 0.76596 | 108.6317 | Single 528239 CUSTERMTN3 115 528540 WHITTEN3 115 1 | TDF Impact | Multi - Battle Axe - Wolfcamp Tap 115 kV DblCkt_Battle Axe - Ponderosa - Dollarhide 115 kV New Line.idv : PID : 900119, NTC, 2025 ITP, ISD: 6/1/2029
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-281 | FROM->TO | 528526 TEAGUE 3 115 528596 CARDINAL 3 115 1 | B | 175 | 0.76596 | 108.6317 | P12:115:SPS:W96.1.CUSMTN.WHITT:::HV: | TDF Impact | Multi - Battle Axe - Wolfcamp Tap 115 kV DblCkt_Battle Axe - Ponderosa - Dollarhide 115 kV New Line.idv : PID : 900119, NTC, 2025 ITP, ISD: 6/1/2029
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-281 | FROM->TO | 523961 POTTER_CO 7 345 3WXFMR 526:WAUK 90343-A 230 1 | B | 559 | 0.12526 | 108.8994 | P42:345:SPS:HITCHLAND-1R15:::EHV: | Cumulative Impact | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-281 | FROM->TO | 523961 POTTER_CO 7 345 3WXFMR 526:WAUK 90343-A 230 1 | B | 559 | 0.12526 | 108.9122 | Single 523097 HITCHLAND7 345 523961 POTTER_CO7 345 1 | Cumulative Impact | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028
Thermal | 05ALL | 1 | 29WP | T1 | GEN-2024-281 | FROM->TO | 528547 S_JAL 3 115 528561 DOLLARHIDE 3 115 1 | B | 117 | 0.34733 | 109.4992 | Single 528540 WHITTEN3 115 528547 S_JAL3 115 1 | TDF Impact | Rebuild line 528547 S_JAL 3 115 528561 DOLLARHIDE 3 115 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-281 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063343 | 111.3621 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T1 | GEN-2024-281 | FROM->TO | 528547 S_JAL 3 115 528561 DOLLARHIDE 3 115 1 | B | 106 | 0.35517 | 113.6348 | Single 528526 TEAGUE3 115 528596 CARDINAL3 115 1 | TDF Impact | Rebuild line 528547 S_JAL 3 115 528561 DOLLARHIDE 3 115 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-281 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.072838 | 115.0541 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T1 | GEN-2024-281 | FROM->TO | 528547 S_JAL 3 115 528561 DOLLARHIDE 3 115 1 | B | 106 | 0.35517 | 115.5818 | Single 528526 TEAGUE3 115 785400 G24-281-TAP 115 1 | TDF Impact | Rebuild line 528547 S_JAL 3 115 528561 DOLLARHIDE 3 115 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-281 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.075949 | 118.9427 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-281 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.075949 | 119.313 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T1 | GEN-2024-281 | FROM->TO | 528526 TEAGUE 3 115 528596 CARDINAL 3 115 1 | B | 194 | 1 | 122.347 | Single 528547 S_JAL3 115 785400 G24-281-TAP 115 1 | TDF Impact | Rebuild line 528526 TEAGUE 3 115 528596 CARDINAL 3 115 1
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-281 | FROM->TO | 528526 TEAGUE 3 115 528596 CARDINAL 3 115 1 | B | 194 | 1 | 122.4773 | Single 528547 S_JAL3 115 785400 G24-281-TAP 115 1 | TDF Impact | Multi - Battle Axe - Wolfcamp Tap 115 kV DblCkt_Battle Axe - Ponderosa - Dollarhide 115 kV New Line.idv : PID : 900119, NTC, 2025 ITP, ISD: 6/1/2029
Thermal | 05ALL | 1 | 29SP | T1 | GEN-2024-281 | FROM->TO | 528547 S_JAL 3 115 528561 DOLLARHIDE 3 115 1 | B | 106 | 0.3476 | 123.1033 | Single 528540 WHITTEN3 115 528547 S_JAL3 115 1 | TDF Impact | Rebuild line 528547 S_JAL 3 115 528561 DOLLARHIDE 3 115 1
Thermal | 05ALL | 1 | 29SP | T1 | GEN-2024-281 | FROM->TO | 528547 S_JAL 3 115 528561 DOLLARHIDE 3 115 1 | B | 106 | 0.27091 | 123.623 | Single 528239 CUSTERMTN3 115 528540 WHITTEN3 115 1 | TDF Impact | Rebuild line 528547 S_JAL 3 115 528561 DOLLARHIDE 3 115 1
Thermal | 05ALL | 1 | 29SP | T1 | GEN-2024-281 | FROM->TO | 528547 S_JAL 3 115 528561 DOLLARHIDE 3 115 1 | B | 106 | 0.27091 | 123.623 | P12:115:SPS:W96.1.CUSMTN.WHITT:::HV: | TDF Impact | Rebuild line 528547 S_JAL 3 115 528561 DOLLARHIDE 3 115 1
Thermal | 05ALL | 1 | 29SP | T1 | GEN-2024-281 | FROM->TO | 528547 S_JAL 3 115 528561 DOLLARHIDE 3 115 1 | B | 106 | 0.15043 | 123.9245 | P12:115:SPS:W81.1.CUSMTN.PONDEROSA:::HV: | Cumulative Impact | Rebuild line 528547 S_JAL 3 115 528561 DOLLARHIDE 3 115 1
Thermal | 05ALL | 1 | 29SP | T1 | GEN-2024-281 | FROM->TO | 528547 S_JAL 3 115 528561 DOLLARHIDE 3 115 1 | B | 106 | 0.15043 | 123.9245 | Single 528239 CUSTERMTN3 115 528240 PONDEROSA3 115 1 | Cumulative Impact | Rebuild line 528547 S_JAL 3 115 528561 DOLLARHIDE 3 115 1
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-281 | FROM->TO | 528526 TEAGUE 3 115 528596 CARDINAL 3 115 1 | B | 194 | 0.99937 | 124.999 | Single 528540 WHITTEN3 115 528547 S_JAL3 115 1 | TDF Impact | Multi - Battle Axe - Wolfcamp Tap 115 kV DblCkt_Battle Axe - Ponderosa - Dollarhide 115 kV New Line.idv : PID : 900119, NTC, 2025 ITP, ISD: 6/1/2029
Thermal | 05ALL | 1 | 29SP | T1 | GEN-2024-281 | FROM->TO | 528526 TEAGUE 3 115 528596 CARDINAL 3 115 1 | B | 175 | 1 | 135.7216 | Single 528547 S_JAL3 115 785400 G24-281-TAP 115 1 | TDF Impact | Rebuild line 528526 TEAGUE 3 115 528596 CARDINAL 3 115 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-281 | FROM->TO | 528526 TEAGUE 3 115 528596 CARDINAL 3 115 1 | B | 175 | 1 | 135.7454 | Single 528547 S_JAL3 115 785400 G24-281-TAP 115 1 | TDF Impact | Multi - Battle Axe - Wolfcamp Tap 115 kV DblCkt_Battle Axe - Ponderosa - Dollarhide 115 kV New Line.idv : PID : 900119, NTC, 2025 ITP, ISD: 6/1/2029
Thermal | 05ALL | 1 | 26SP | T1 | GEN-2024-281 | FROM->TO | 528526 TEAGUE 3 115 528596 CARDINAL 3 115 1 | B | 175 | 1 | 136.0524 | Single 528547 S_JAL3 115 785400 G24-281-TAP 115 1 | TDF Impact | Rebuild line 528526 TEAGUE 3 115 528596 CARDINAL 3 115 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-281 | FROM->TO | 528526 TEAGUE 3 115 528596 CARDINAL 3 115 1 | B | 175 | 1 | 136.1207 | Single 528547 S_JAL3 115 785400 G24-281-TAP 115 1 | TDF Impact | Multi - Battle Axe - Wolfcamp Tap 115 kV DblCkt_Battle Axe - Ponderosa - Dollarhide 115 kV New Line.idv : PID : 900119, NTC, 2025 ITP, ISD: 6/1/2029
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-281 | FROM->TO | 528526 TEAGUE 3 115 528596 CARDINAL 3 115 1 | B | 175 | 0.9994 | 138.2602 | Single 528540 WHITTEN3 115 528547 S_JAL3 115 1 | TDF Impact | Multi - Battle Axe - Wolfcamp Tap 115 kV DblCkt_Battle Axe - Ponderosa - Dollarhide 115 kV New Line.idv : PID : 900119, NTC, 2025 ITP, ISD: 6/1/2029
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-281 | FROM->TO | 528526 TEAGUE 3 115 528596 CARDINAL 3 115 1 | B | 175 | 0.99933 | 138.672 | Single 528540 WHITTEN3 115 528547 S_JAL3 115 1 | TDF Impact | Multi - Battle Axe - Wolfcamp Tap 115 kV DblCkt_Battle Axe - Ponderosa - Dollarhide 115 kV New Line.idv : PID : 900119, NTC, 2025 ITP, ISD: 6/1/2029
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-286 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.059852 | 103.8575 | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-286 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.061554 | 104.6172 | P23:345:AEPW:PITTSBURG CB 3433A NBTB:::: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-286 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.059566 | 105.6255 | Single 510907 PITTSB-7 345 787110 G24-338-TAP 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-286 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.064493 | 110.0508 | P22:345:EES:MUSKOGE7!:::EHV: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-286 | FROM->TO | 515308 3RDST 5 161 515356 JSTREET5 161 1 | B | 223 | 0.057316 | 110.2081 | Single 515231 KEEFTON7 345 780360 G24-113-TAP 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-286 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.061279 | 110.6242 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-286 | FROM->TO | 505552 GORE 5 161 505558 MUSKTAP5 161 1 | B | 201 | 0.10949 | 111.1438 | P22:345:EES:MUSKOGE7!:::EHV: | Cumulative Impact | Rebuild line 505552 GORE 5 161 505558 MUSKTAP5 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-286 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.0606 | 111.1525 | Single 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-286 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.059566 | 111.5464 | Single 514809 JOHNCO7 345 787110 G24-338-TAP 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-286 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.059566 | 111.595 | P42:345:OKGE:SB_JOCO7311:::EHV: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-286 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.0606 | 111.7065 | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-286 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.061675 | 115.5426 | Single 514809 JOHNCO7 345 787110 G24-338-TAP 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-286 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.061675 | 115.6069 | P42:345:OKGE:SB_JOCO7311:::EHV: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-286 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.070892 | 117.3852 | P22:345:EES:MUSKOGE7!:::EHV: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-286 | FROM->TO | 505522 VAN BUR5 161 505524 LIBERTY5 161 1 | B | 222 | 0.0868 | 117.409 | P22:345:EES:MUSKOGE7!:::EHV: | Cumulative Impact | Rebuild line 505522 VAN BUR5 161 505524 LIBERTY5 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-286 | FROM->TO | 505552 GORE 5 161 505558 MUSKTAP5 161 1 | B | 201 | 0.11181 | 117.908 | P22:345:EES:MUSKOGE7!:::EHV: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-287 | FROM->TO | 532793 NEOSHO 7 345 3WXFMR 536:N345 TX-2 161 2 | B | 550 | 0.036056 | 101.4582 | Single 533021 NEOSHO4 138 533023 N34534 138 1 | TDF Impact | Add 3-winding transformer 532793 NEOSHO 7 345 532825 N345 2 1 13 532939 N345 4 5 161 M2
Thermal | 00NR | 1 | 29WP | T1 | GEN-2024-287 | FROM->TO | 532937 NEOSHO 5 161 764310 G20-079-TAP 161 1 | B | 533 | 0.051543 | 101.6771 | P23:345:AECI:7BLACKBERRY:653::: | TDF Impact | Rebuild line 532937 NEOSHO 5 161 764310 G20-079-TAP 161 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-287 | FROM->TO | 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | B | 956 | 0.46631 | 101.9427 | P23:345:AECI:7BLACKBERRY:6_2::: | TDF Impact | Rebuild line 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-287 | FROM->TO | 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | B | 956 | 0.46631 | 101.9438 | P23:345:AECI:7BLACKBERRY:6_3::: | TDF Impact | Rebuild line 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-287 | FROM->TO | 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | B | 956 | 0.46655 | 103.0407 | Single 300739 7BLACKBERRY 345 785580 G24-287-TAP 345 1 | TDF Impact | Rebuild line 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-287 | FROM->TO | 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | B | 956 | 0.46729 | 103.5013 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | TDF Impact | Rebuild line 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-287 | FROM->TO | 532793 NEOSHO 7 345 3WXFMR 536:N345 TX-2 161 2 | B | 550 | 0.040304 | 103.5308 | Single 533021 NEOSHO4 138 533023 N34534 138 1 | TDF Impact | Add 3-winding transformer 532793 NEOSHO 7 345 532825 N345 2 1 13 532939 N345 4 5 161 M2
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-287 | FROM->TO | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.20108 | 104.394 | P23:345:AECI:7BLACKBERRY:653::: | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-287 | FROM->TO | 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | B | 956 | 0.46826 | 105.9563 | P23:345:AECI:7BLACKBERRY:6_2::: | TDF Impact | Rebuild line 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-287 | FROM->TO | 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1 | B | 956 | 0.46826 | 105.9589 | P23:345:AECI:7BLACKBERRY:6_3::: | TDF Impact | Rebuild line 532797 WOLFCRK7 345 766141 G21-096-TAP 345 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-287 | FROM->TO | 532793 NEOSHO 7 345 3WXFMR 536:N345 TX-2 161 2 | B | 550 | 0.040376 | 111.3295 | Single 533021 NEOSHO4 138 533023 N34534 138 1 | TDF Impact | Add 3-winding transformer 532793 NEOSHO 7 345 532825 N345 2 1 13 532939 N345 4 5 161 M2
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-287 | FROM->TO | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.17841 | 111.8275 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-293 | FROM->TO | 515302 FTSMITH7 345 3WXFMR 524:524:FTSMITH5 345 5 | B | 493 | 0.060592 | 104.5961 | P42:500:OKGE:SB_FTTH8585:::EHV: | Cumulative Impact | Add 3-winding transformer 515301 FTSMTHW5 161 515302 FTSMITH7 345 515728 FTSMTH51 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-293 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.057504 | 104.6172 | P23:345:AEPW:PITTSBURG CB 3433A NBTB:::: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-293 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.055516 | 105.6255 | Single 510907 PITTSB-7 345 787110 G24-338-TAP 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-293 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.05287 | 110.6242 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-293 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.052191 | 111.1525 | Single 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-293 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.055516 | 111.5464 | Single 514809 JOHNCO7 345 787110 G24-338-TAP 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-293 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.055516 | 111.595 | P42:345:OKGE:SB_JOCO7311:::EHV: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-293 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.052191 | 111.7065 | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-293 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.058794 | 115.5426 | Single 514809 JOHNCO7 345 787110 G24-338-TAP 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-293 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.058794 | 115.6069 | P42:345:OKGE:SB_JOCO7311:::EHV: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 04ALL | 1 | 26SP | T1 | GEN-2024-294 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.036255 | 103.0993 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T1 | GEN-2024-294 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.038696 | 103.3038 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-294 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | A | 1187 | 0.081003 | 103.8656 | System Intact | TDF Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-294 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.10887 | 104.9177 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-294 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.085857 | 106.1409 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-294 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.10659 | 106.3238 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-294 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.17148 | 106.5158 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-294 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.0852 | 107.841 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-294 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.17148 | 108.059 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-294 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.0852 | 109.5335 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-294 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.0852 | 109.534 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-294 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.0852 | 112.0538 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-294 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.0852 | 116.5975 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-294 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.060017 | 119.3706 | System Intact | TDF Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-294 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.060017 | 119.3706 | System Intact | TDF Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-294 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.060017 | 119.3706 | System Intact | TDF Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-294 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.057339 | 119.5141 | System Intact | TDF Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-294 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.057339 | 119.5141 | System Intact | TDF Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-294 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.057339 | 119.5141 | System Intact | TDF Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-294 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.12687 | 136.5828 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-294 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.12687 | 136.5828 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-294 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.12687 | 136.5828 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-294 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.063036 | 136.8919 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-294 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.063036 | 136.8919 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-294 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.063036 | 136.8919 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-294 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.066222 | 136.9237 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-294 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.066222 | 136.9237 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-294 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.066222 | 136.9237 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-294 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.12747 | 139.3736 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-294 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.12747 | 139.3736 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-294 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.12747 | 139.3736 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-294 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.064895 | 140.3415 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-294 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.064895 | 140.3415 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-294 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.064895 | 140.3415 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-294 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.061493 | 140.6152 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-294 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.061493 | 140.6152 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-294 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.061493 | 140.6152 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-294 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.089493 | 141.6076 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-294 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.089493 | 141.6076 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-294 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.089493 | 141.6076 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-294 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.085694 | 142.5086 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-294 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.085694 | 142.5086 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-294 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.085694 | 142.5086 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-294 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.064362 | 142.6431 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-294 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.064362 | 142.6431 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-294 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.064362 | 142.6431 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-294 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.086305 | 142.7223 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-294 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.086305 | 142.7223 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-294 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.086305 | 142.7223 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-294 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.060904 | 143.2233 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-294 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.060904 | 143.2233 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-294 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.060904 | 143.2233 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-294 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.082631 | 143.8401 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-294 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.082631 | 143.8401 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-294 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.082631 | 143.8401 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-294 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.064362 | 145.1309 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-294 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.064362 | 145.1309 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-294 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.064362 | 145.1309 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-294 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.064362 | 145.1356 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-294 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.064362 | 145.1356 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-294 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.064362 | 145.1356 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-294 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.060904 | 145.7578 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-294 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.060904 | 145.7578 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-294 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.060904 | 145.7578 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-294 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.060904 | 145.7646 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-294 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.060904 | 145.7646 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-294 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.060904 | 145.7646 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-294 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.064362 | 148.805 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-294 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.064362 | 148.805 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-294 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.064362 | 148.805 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-294 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.060904 | 149.8057 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-294 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.060904 | 149.8057 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-294 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.060904 | 149.8057 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-294 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.064362 | 155.6146 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-294 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.064362 | 155.6146 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-294 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.064362 | 155.6146 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-294 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.060904 | 157.3662 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-294 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.060904 | 157.3662 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-294 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.060904 | 157.3662 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-295 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.071428 | 100.0488 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-295 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.062206 | 100.533 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-295 | FROM->TO | 523959 POTTER_CO 6 230 524010 ROLLHILLS 6 230 1 | B | 548 | 0.05006 | 103.4659 | MULTIGEN523979 | Cumulative Impact | Rebuild line 523959 POTTER_CO 6 230 524010 ROLLHILLS 6 230 1
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-295 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.075201 | 103.9266 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-295 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.074517 | 104.7552 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-295 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.074517 | 104.888 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-295 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.078232 | 107.2243 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-295 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063068 | 107.2793 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-295 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063068 | 107.2794 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-295 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.078232 | 107.2951 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-295 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063068 | 107.3093 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-295 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063068 | 107.7557 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-295 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063068 | 108.2747 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-295 | FROM->TO | 523961 POTTER_CO 7 345 3WXFMR 526:WAUK 90343-A 230 1 | B | 559 | 0.1342 | 108.8994 | P42:345:SPS:HITCHLAND-1R15:::EHV: | Cumulative Impact | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-295 | FROM->TO | 523961 POTTER_CO 7 345 3WXFMR 526:WAUK 90343-A 230 1 | B | 559 | 0.1342 | 108.9122 | Single 523097 HITCHLAND7 345 523961 POTTER_CO7 345 1 | Cumulative Impact | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-295 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063068 | 111.3621 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-295 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.072475 | 115.0541 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-295 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.075582 | 118.9427 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-295 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.075582 | 119.313 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 04ALL | 1 | 26SP | T1 | GEN-2024-296 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.035606 | 103.0993 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T1 | GEN-2024-296 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.038054 | 103.3038 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-296 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | A | 1187 | 0.062853 | 103.8656 | System Intact | TDF Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-296 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.069779 | 104.9177 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-296 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.068612 | 106.1409 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-296 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.068535 | 106.3238 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-296 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.064137 | 106.5158 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-296 | FROM->TO | 515302 FTSMITH7 345 3WXFMR 524:524:FTSMITH1 500 1 | B | 693 | 0.080261 | 107.4747 | P12:161:EES:FTSMTHW5%:FTSMITH7%:FTSMTH511:HV: | Cumulative Impact | Add 3-winding transformer 515302 FTSMITH7 345 515305 FTSMITH8 500 515726 FTSMTH11 13 M2
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-296 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.067954 | 107.841 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-296 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.064137 | 108.059 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-296 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.067954 | 109.5335 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-296 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.067954 | 109.534 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-296 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.067954 | 112.0538 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-296 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.034766 | 114.5102 | System Intact | TDF Impact | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-296 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.067954 | 116.5975 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-296 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.049365 | 119.3706 | System Intact | TDF Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-296 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.049365 | 119.3706 | System Intact | TDF Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-296 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.049365 | 119.3706 | System Intact | TDF Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-296 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.047193 | 119.5141 | System Intact | TDF Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-296 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.047193 | 119.5141 | System Intact | TDF Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-296 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.047193 | 119.5141 | System Intact | TDF Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-296 | FROM->TO | 515302 FTSMITH7 345 3WXFMR 524:524:FTSMITH5 345 5 | B | 493 | 0.061469 | 126.769 | P12:345:EES:FTSMITH7%:FTSMITH8%:FTSMTH111:EHV: | Cumulative Impact | Add 3-winding transformer 515301 FTSMTHW5 161 515302 FTSMITH7 345 515728 FTSMTH51 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-296 | FROM->TO | 516092 OKTAHA 5 161 3WXFMR OKTAHA 5 69 7 | B | 112 | 0.038637 | 128.9125 | P22:345:EES:MUSKOGE7!:::EHV: | TDF Impact | Rebuild 3-winding transformer 516092 OKTAHA 5 161 516093 OKTAHA 2 69 516095 OKTAHA71 13 7
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-296 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.050633 | 136.5828 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-296 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.050633 | 136.5828 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-296 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.050633 | 136.5828 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-296 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051096 | 136.8919 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-296 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051096 | 136.8919 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-296 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051096 | 136.8919 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-296 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.053429 | 136.9237 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-296 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.053429 | 136.9237 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-296 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.053429 | 136.9237 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-296 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.05466 | 140.3415 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-296 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.05466 | 140.3415 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-296 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.05466 | 140.3415 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-296 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051817 | 140.6152 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-296 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051817 | 140.6152 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-296 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051817 | 140.6152 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-296 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.056914 | 141.6076 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-296 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.056914 | 141.6076 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-296 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.056914 | 141.6076 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-296 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.054917 | 142.5086 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-296 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.054917 | 142.5086 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-296 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.054917 | 142.5086 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-296 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.054127 | 142.6431 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-296 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.054127 | 142.6431 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-296 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.054127 | 142.6431 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-296 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.054395 | 142.7223 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-296 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.054395 | 142.7223 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-296 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.054395 | 142.7223 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-296 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051228 | 143.2233 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-296 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051228 | 143.2233 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-296 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051228 | 143.2233 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-296 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.052519 | 143.8401 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-296 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.052519 | 143.8401 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-296 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.052519 | 143.8401 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-296 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.054127 | 145.1309 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-296 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.054127 | 145.1309 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-296 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.054127 | 145.1309 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-296 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.054127 | 145.1356 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-296 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.054127 | 145.1356 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-296 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.054127 | 145.1356 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-296 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051228 | 145.7578 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-296 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051228 | 145.7578 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-296 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051228 | 145.7578 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-296 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051228 | 145.7646 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-296 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051228 | 145.7646 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-296 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051228 | 145.7646 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-296 | FROM->TO | 516092 OKTAHA 5 161 3WXFMR OKTAHA 5 69 7 | B | 112 | 0.038657 | 147.7196 | P22:345:EES:MUSKOGE7!:::EHV: | TDF Impact | Rebuild 3-winding transformer 516092 OKTAHA 5 161 516093 OKTAHA 2 69 516095 OKTAHA71 13 7
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-296 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.054127 | 148.805 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-296 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.054127 | 148.805 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-296 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.054127 | 148.805 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-296 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051228 | 149.8057 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-296 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051228 | 149.8057 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-296 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051228 | 149.8057 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-296 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.054127 | 155.6146 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-296 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.054127 | 155.6146 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-296 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.054127 | 155.6146 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-296 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051228 | 157.3662 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-296 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051228 | 157.3662 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-296 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051228 | 157.3662 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-296 | FROM->TO | 516092 OKTAHA 5 161 3WXFMR OKTAHA 5 69 7 | B | 112 | 0.039303 | 165.8816 | P22:345:EES:MUSKOGE7!:::EHV: | TDF Impact | Rebuild 3-winding transformer 516092 OKTAHA 5 161 516093 OKTAHA 2 69 516095 OKTAHA71 13 7
Thermal | 04ALL | 1 | 26SP | T1 | GEN-2024-297 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.035606 | 103.0993 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T1 | GEN-2024-297 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.038054 | 103.3038 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-297 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | A | 1187 | 0.062853 | 103.8656 | System Intact | TDF Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-297 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.069779 | 104.9177 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-297 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.068612 | 106.1409 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-297 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.068535 | 106.3238 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-297 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.064137 | 106.5158 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-297 | FROM->TO | 515302 FTSMITH7 345 3WXFMR 524:524:FTSMITH1 500 1 | B | 693 | 0.080261 | 107.4747 | P12:161:EES:FTSMTHW5%:FTSMITH7%:FTSMTH511:HV: | Cumulative Impact | Add 3-winding transformer 515302 FTSMITH7 345 515305 FTSMITH8 500 515726 FTSMTH11 13 M2
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-297 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.067954 | 107.841 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-297 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.064137 | 108.059 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-297 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.067954 | 109.5335 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-297 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.067954 | 109.534 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-297 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.067954 | 112.0538 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-297 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.034766 | 114.5102 | System Intact | TDF Impact | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-297 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.067954 | 116.5975 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-297 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.049365 | 119.3706 | System Intact | TDF Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-297 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.049365 | 119.3706 | System Intact | TDF Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-297 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.049365 | 119.3706 | System Intact | TDF Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-297 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.047193 | 119.5141 | System Intact | TDF Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-297 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.047193 | 119.5141 | System Intact | TDF Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-297 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.047193 | 119.5141 | System Intact | TDF Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-297 | FROM->TO | 515302 FTSMITH7 345 3WXFMR 524:524:FTSMITH5 345 5 | B | 493 | 0.061469 | 126.769 | P12:345:EES:FTSMITH7%:FTSMITH8%:FTSMTH111:EHV: | Cumulative Impact | Add 3-winding transformer 515301 FTSMTHW5 161 515302 FTSMITH7 345 515728 FTSMTH51 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-297 | FROM->TO | 516092 OKTAHA 5 161 3WXFMR OKTAHA 5 69 7 | B | 112 | 0.038637 | 128.9125 | P22:345:EES:MUSKOGE7!:::EHV: | TDF Impact | Rebuild 3-winding transformer 516092 OKTAHA 5 161 516093 OKTAHA 2 69 516095 OKTAHA71 13 7
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-297 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.050633 | 136.5828 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-297 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.050633 | 136.5828 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-297 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.050633 | 136.5828 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-297 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051096 | 136.8919 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-297 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051096 | 136.8919 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-297 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051096 | 136.8919 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-297 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.053429 | 136.9237 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-297 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.053429 | 136.9237 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-297 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.053429 | 136.9237 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-297 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.05466 | 140.3415 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-297 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.05466 | 140.3415 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-297 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.05466 | 140.3415 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-297 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051817 | 140.6152 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-297 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051817 | 140.6152 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-297 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051817 | 140.6152 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-297 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.056914 | 141.6076 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-297 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.056914 | 141.6076 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-297 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.056914 | 141.6076 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-297 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.054917 | 142.5086 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-297 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.054917 | 142.5086 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-297 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.054917 | 142.5086 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-297 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.054127 | 142.6431 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-297 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.054127 | 142.6431 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-297 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.054127 | 142.6431 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-297 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.054395 | 142.7223 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-297 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.054395 | 142.7223 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-297 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.054395 | 142.7223 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-297 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051228 | 143.2233 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-297 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051228 | 143.2233 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-297 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051228 | 143.2233 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-297 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.052519 | 143.8401 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-297 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.052519 | 143.8401 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-297 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.052519 | 143.8401 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-297 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.054127 | 145.1309 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-297 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.054127 | 145.1309 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-297 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.054127 | 145.1309 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-297 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.054127 | 145.1356 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-297 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.054127 | 145.1356 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-297 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.054127 | 145.1356 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-297 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051228 | 145.7578 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-297 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051228 | 145.7578 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-297 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051228 | 145.7578 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-297 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051228 | 145.7646 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-297 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051228 | 145.7646 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-297 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051228 | 145.7646 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-297 | FROM->TO | 516092 OKTAHA 5 161 3WXFMR OKTAHA 5 69 7 | B | 112 | 0.038657 | 147.7196 | P22:345:EES:MUSKOGE7!:::EHV: | TDF Impact | Rebuild 3-winding transformer 516092 OKTAHA 5 161 516093 OKTAHA 2 69 516095 OKTAHA71 13 7
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-297 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.054127 | 148.805 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-297 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.054127 | 148.805 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-297 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.054127 | 148.805 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-297 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051228 | 149.8057 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-297 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051228 | 149.8057 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-297 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051228 | 149.8057 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-297 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.054127 | 155.6146 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-297 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.054127 | 155.6146 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-297 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.054127 | 155.6146 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-297 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051228 | 157.3662 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-297 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051228 | 157.3662 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-297 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051228 | 157.3662 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-297 | FROM->TO | 516092 OKTAHA 5 161 3WXFMR OKTAHA 5 69 7 | B | 112 | 0.039303 | 165.8816 | P22:345:EES:MUSKOGE7!:::EHV: | TDF Impact | Rebuild 3-winding transformer 516092 OKTAHA 5 161 516093 OKTAHA 2 69 516095 OKTAHA71 13 7
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-299 | FROM->TO | 515308 3RDST 5 161 515356 JSTREET5 161 1 | B | 223 | 0.060181 | 101.2281 | P22:345:EES:MUSKOGE7!:::EHV: | Cumulative Impact | Rebuild line 515308 3RDST 5 161 515356 JSTREET5 161 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-299 | FROM->TO | 515306 ARKOMA 5 161 515308 3RDST 5 161 1 | B | 335 | 0.12508 | 102.7878 | Single 515231 KEEFTON7 345 780360 G24-113-TAP 345 1 | Cumulative Impact | Rebuild line 515306 ARKOMA 5 161 515308 3RDST 5 161 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-299 | FROM->TO | 515301 FTSMTHW5 161 515306 ARKOMA 5 161 1 | B | 359 | 0.12508 | 103.2993 | Single 515231 KEEFTON7 345 780360 G24-113-TAP 345 1 | Cumulative Impact | Rebuild line 515301 FTSMTHW5 161 515306 ARKOMA 5 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-299 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.060454 | 103.8575 | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-299 | FROM->TO | 515302 FTSMITH7 345 3WXFMR 524:524:FTSMITH5 345 5 | B | 493 | 0.25769 | 104.5961 | P42:500:OKGE:SB_FTTH8585:::EHV: | TDF Impact | Add 3-winding transformer 515301 FTSMTHW5 161 515302 FTSMITH7 345 515728 FTSMTH51 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-299 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.065072 | 104.6172 | P23:345:AEPW:PITTSBURG CB 3433A NBTB:::: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-299 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.063084 | 105.6255 | Single 510907 PITTSB-7 345 787110 G24-338-TAP 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-299 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.084061 | 110.0508 | P22:345:EES:MUSKOGE7!:::EHV: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-299 | FROM->TO | 515308 3RDST 5 161 515356 JSTREET5 161 1 | B | 223 | 0.10437 | 110.2081 | Single 515231 KEEFTON7 345 780360 G24-113-TAP 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-299 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.062324 | 110.6242 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-299 | FROM->TO | 505552 GORE 5 161 505558 MUSKTAP5 161 1 | B | 201 | 0.062357 | 111.1438 | P22:345:EES:MUSKOGE7!:::EHV: | Cumulative Impact | Rebuild line 505552 GORE 5 161 505558 MUSKTAP5 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-299 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.061645 | 111.1525 | Single 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-299 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.063084 | 111.5464 | Single 514809 JOHNCO7 345 787110 G24-338-TAP 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-299 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.063084 | 111.595 | P42:345:OKGE:SB_JOCO7311:::EHV: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-299 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.061645 | 111.7065 | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-299 | FROM->TO | 515301 FTSMTHW5 161 515306 ARKOMA 5 161 1 | B | 359 | 0.1277 | 113.1202 | Single 515231 KEEFTON7 345 780360 G24-113-TAP 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-299 | FROM->TO | 515306 ARKOMA 5 161 515308 3RDST 5 161 1 | B | 335 | 0.1277 | 113.225 | Single 515231 KEEFTON7 345 780360 G24-113-TAP 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-299 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.065036 | 115.5426 | Single 514809 JOHNCO7 345 787110 G24-338-TAP 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-299 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.065036 | 115.6069 | P42:345:OKGE:SB_JOCO7311:::EHV: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-299 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.087791 | 117.3852 | P22:345:EES:MUSKOGE7!:::EHV: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-299 | FROM->TO | 505522 VAN BUR5 161 505524 LIBERTY5 161 1 | B | 222 | 0.069571 | 117.409 | P22:345:EES:MUSKOGE7!:::EHV: | Cumulative Impact | Rebuild line 505522 VAN BUR5 161 505524 LIBERTY5 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-299 | FROM->TO | 505552 GORE 5 161 505558 MUSKTAP5 161 1 | B | 201 | 0.06136 | 117.908 | P22:345:EES:MUSKOGE7!:::EHV: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-303 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.073927 | 100.0488 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-303 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063268 | 100.533 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-303 | FROM->TO | 523959 POTTER_CO 6 230 524010 ROLLHILLS 6 230 1 | B | 548 | 0.058886 | 103.4659 | MULTIGEN523979 | Cumulative Impact | Rebuild line 523959 POTTER_CO 6 230 524010 ROLLHILLS 6 230 1
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-303 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.078438 | 103.9266 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-303 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.076912 | 104.7552 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-303 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.076912 | 104.888 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-303 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.081361 | 107.2243 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-303 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.064084 | 107.2793 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-303 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.064084 | 107.2794 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-303 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.081361 | 107.2951 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-303 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.064084 | 107.3093 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-303 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.064084 | 107.7557 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-303 | FROM->TO | 531512 HARBNGR7 345 3WXFMR 534:HARBGR345 345 1 | B | 385 | 0.050041 | 107.8261 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Add 3-winding transformer 531510 HARBNGR3 115 531511 HARBNGR-1 13 531512 HARBNGR7 345 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-303 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.064084 | 108.2747 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-303 | FROM->TO | 523961 POTTER_CO 7 345 3WXFMR 526:WAUK 90343-A 230 1 | B | 559 | 0.15263 | 108.8994 | P42:345:SPS:HITCHLAND-1R15:::EHV: | Cumulative Impact | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-303 | FROM->TO | 523961 POTTER_CO 7 345 3WXFMR 526:WAUK 90343-A 230 1 | B | 559 | 0.15263 | 108.9122 | Single 523097 HITCHLAND7 345 523961 POTTER_CO7 345 1 | Cumulative Impact | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-303 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.064084 | 111.3621 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-303 | FROM->TO | 523959 POTTER_CO 6 230 524010 ROLLHILLS 6 230 1 | B | 548 | 0.053245 | 114.0984 | MULTIGEN523978 | Cumulative Impact | Rebuild line 523959 POTTER_CO 6 230 524010 ROLLHILLS 6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-303 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.074928 | 115.0541 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-303 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.07793 | 118.9427 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-303 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.07793 | 119.313 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-304 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.073927 | 100.0488 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-304 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063268 | 100.533 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-304 | FROM->TO | 523959 POTTER_CO 6 230 524010 ROLLHILLS 6 230 1 | B | 548 | 0.058886 | 103.4659 | MULTIGEN523979 | Cumulative Impact | Rebuild line 523959 POTTER_CO 6 230 524010 ROLLHILLS 6 230 1
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-304 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.078438 | 103.9266 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-304 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.076912 | 104.7552 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-304 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.076912 | 104.888 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-304 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.081361 | 107.2243 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-304 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.064084 | 107.2793 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-304 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.064084 | 107.2794 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-304 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.081361 | 107.2951 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-304 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.064084 | 107.3093 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-304 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.064084 | 107.7557 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-304 | FROM->TO | 531512 HARBNGR7 345 3WXFMR 534:HARBGR345 345 1 | B | 385 | 0.050041 | 107.8261 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Add 3-winding transformer 531510 HARBNGR3 115 531511 HARBNGR-1 13 531512 HARBNGR7 345 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-304 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.064084 | 108.2747 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-304 | FROM->TO | 523961 POTTER_CO 7 345 3WXFMR 526:WAUK 90343-A 230 1 | B | 559 | 0.15263 | 108.8994 | P42:345:SPS:HITCHLAND-1R15:::EHV: | Cumulative Impact | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-304 | FROM->TO | 523961 POTTER_CO 7 345 3WXFMR 526:WAUK 90343-A 230 1 | B | 559 | 0.15263 | 108.9122 | Single 523097 HITCHLAND7 345 523961 POTTER_CO7 345 1 | Cumulative Impact | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-304 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.064084 | 111.3621 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-304 | FROM->TO | 523959 POTTER_CO 6 230 524010 ROLLHILLS 6 230 1 | B | 548 | 0.053245 | 114.0984 | MULTIGEN523978 | Cumulative Impact | Rebuild line 523959 POTTER_CO 6 230 524010 ROLLHILLS 6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-304 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.074928 | 115.0541 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-304 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.07793 | 118.9427 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-304 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.07793 | 119.313 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-310 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.072522 | 100.0488 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-310 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.062842 | 100.533 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-310 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.076461 | 103.9266 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-310 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.07559 | 104.7552 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-310 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.07559 | 104.888 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-310 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.079469 | 107.2243 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-310 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063728 | 107.2793 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-310 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063728 | 107.2794 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-310 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.079469 | 107.2951 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-310 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063728 | 107.3093 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-310 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063728 | 107.7557 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-310 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063728 | 108.2747 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-310 | FROM->TO | 523961 POTTER_CO 7 345 3WXFMR 526:WAUK 90343-A 230 1 | B | 559 | 0.10959 | 108.8994 | P42:345:SPS:HITCHLAND-1R15:::EHV: | Cumulative Impact | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-310 | FROM->TO | 523961 POTTER_CO 7 345 3WXFMR 526:WAUK 90343-A 230 1 | B | 559 | 0.10959 | 108.9122 | Single 523097 HITCHLAND7 345 523961 POTTER_CO7 345 1 | Cumulative Impact | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-310 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063728 | 111.3621 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-310 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.073588 | 115.0541 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-310 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.076673 | 118.9427 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-310 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.076673 | 119.313 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-311 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.072522 | 100.0488 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-311 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.062842 | 100.533 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-311 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.076461 | 103.9266 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-311 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.07559 | 104.7552 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-311 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.07559 | 104.888 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-311 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.079469 | 107.2243 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-311 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063728 | 107.2793 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-311 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063728 | 107.2794 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-311 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.079469 | 107.2951 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-311 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063728 | 107.3093 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-311 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063728 | 107.7557 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-311 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063728 | 108.2747 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-311 | FROM->TO | 523961 POTTER_CO 7 345 3WXFMR 526:WAUK 90343-A 230 1 | B | 559 | 0.10959 | 108.8994 | P42:345:SPS:HITCHLAND-1R15:::EHV: | Cumulative Impact | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-311 | FROM->TO | 523961 POTTER_CO 7 345 3WXFMR 526:WAUK 90343-A 230 1 | B | 559 | 0.10959 | 108.9122 | Single 523097 HITCHLAND7 345 523961 POTTER_CO7 345 1 | Cumulative Impact | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-311 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063728 | 111.3621 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-311 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.073588 | 115.0541 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-311 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.076673 | 118.9427 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-311 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.076673 | 119.313 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-317 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | B | 234 | 0.03308 | 100.0952 | P45:345:OKGE:SB_MICO_NOBF:::EHV: | TDF Impact | Rebuild line 515802 GRACMNT4 138 520814 ANADARK4 138 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-317 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.059965 | 100.533 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-317 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | B | 173 | 0.04048 | 101.8021 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Rebuild line 511467 L.E.S.-4 138 511494 COMMTAP4 138 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-317 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | B | 173 | 0.041044 | 102.1634 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | TDF Impact | Rebuild line 511467 L.E.S.-4 138 511494 COMMTAP4 138 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-317 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | B | 234 | 0.03308 | 102.6013 | P23:345:OKGE:IF_MICO7302:::EHV: | TDF Impact | Rebuild line 515802 GRACMNT4 138 520814 ANADARK4 138 1
Thermal | 00NR | 1 | 29SP | T1 | GEN-2024-317 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | B | 211 | 0.037743 | 104.2208 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Rebuild line 511494 COMMTAP4 138 529304 OMDUNCN4 138 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-317 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | B | 173 | 0.041136 | 104.3322 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Rebuild line 511467 L.E.S.-4 138 511494 COMMTAP4 138 1
Thermal | 00NR | 1 | 29SP | T1 | GEN-2024-317 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | B | 211 | 0.038202 | 104.4644 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | TDF Impact | Rebuild line 511494 COMMTAP4 138 529304 OMDUNCN4 138 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-317 | FROM->TO | 511467 L.E.S.-4 138 511494 COMMTAP4 138 1 | B | 173 | 0.041701 | 104.979 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | TDF Impact | Rebuild line 511467 L.E.S.-4 138 511494 COMMTAP4 138 1
Thermal | 00NR | 1 | 26SP | T1 | GEN-2024-317 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | B | 211 | 0.037854 | 105.818 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Rebuild line 511494 COMMTAP4 138 529304 OMDUNCN4 138 1
Thermal | 00NR | 1 | 26SP | T1 | GEN-2024-317 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | B | 211 | 0.038315 | 106.2948 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | TDF Impact | Rebuild line 511494 COMMTAP4 138 529304 OMDUNCN4 138 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-317 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.060959 | 107.2793 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-317 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.060959 | 107.2794 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-317 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.060959 | 107.3093 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-317 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.060959 | 107.7557 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-317 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.060959 | 108.2747 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-317 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | B | 234 | 0.039296 | 110.8778 | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | Rebuild line 515802 GRACMNT4 138 520814 ANADARK4 138 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-317 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.060959 | 111.3621 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-317 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | B | 171 | 0.033408 | 111.9556 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Rebuild line 511494 COMMTAP4 138 529304 OMDUNCN4 138 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-317 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | B | 171 | 0.033736 | 112.1038 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | TDF Impact | Rebuild line 511494 COMMTAP4 138 529304 OMDUNCN4 138 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-317 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | B | 171 | 0.033502 | 113.7961 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Rebuild line 511494 COMMTAP4 138 529304 OMDUNCN4 138 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-317 | FROM->TO | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | B | 171 | 0.033828 | 114.1433 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | TDF Impact | Rebuild line 511494 COMMTAP4 138 529304 OMDUNCN4 138 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-317 | FROM->TO | 511468 L.E.S.-7 345 3WXFMR 520:LES 5 345 2 | B | 515 | 0.10855 | 114.3077 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-317 | FROM->TO | 511468 L.E.S.-7 345 3WXFMR 520:LES 5 345 2 | B | 515 | 0.10966 | 114.3448 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-317 | FROM->TO | 511468 L.E.S.-7 345 3WXFMR 520:LES 5 345 2 | B | 515 | 0.11496 | 115.3782 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | TDF Impact | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-317 | FROM->TO | 511468 L.E.S.-7 345 3WXFMR 520:LES 5 345 2 | B | 515 | 0.11615 | 116.8526 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | TDF Impact | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2
Thermal | 04ALL | 1 | 29SP | T1 | GEN-2024-318 | FROM->TO | 509790 CATOOSA4 138 512636 CATSAGR4 138 Z1 | B | 272 | 0.10233 | 100.1562 | Single 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | Cumulative Impact | Rebuild line 509790 CATOOSA4 138 512636 CATSAGR4 138 Z1
Thermal | 04ALL | 1 | 26SP | T1 | GEN-2024-318 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.05991 | 103.0993 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T1 | GEN-2024-318 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.067087 | 103.3038 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-318 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | A | 1187 | 0.11582 | 103.8656 | System Intact | TDF Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-318 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.12952 | 104.9177 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-318 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.12311 | 106.1409 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-318 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.12757 | 106.3238 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-318 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.12747 | 106.5158 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-318 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.12245 | 107.841 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-318 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.12747 | 108.059 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-318 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.12245 | 109.5335 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-318 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.12245 | 109.534 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | FROM->TO | 509790 CATOOSA4 138 512636 CATSAGR4 138 Z1 | B | 218 | 0.088363 | 110.4083 | Single 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | Cumulative Impact | Rebuild line 509790 CATOOSA4 138 512636 CATSAGR4 138 Z1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-318 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.12245 | 112.0538 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T1 | GEN-2024-318 | FROM->TO | 509790 CATOOSA4 138 512636 CATSAGR4 138 Z1 | B | 272 | 0.10119 | 112.6598 | Single 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | Cumulative Impact | Rebuild line 509790 CATOOSA4 138 512636 CATSAGR4 138 Z1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-318 | FROM->TO | 509817 T.NO.--4 138 509900 46ST-TP-4 138 1 | B | 151 | 0.084943 | 113.7874 | Single 509784 A.A.---4 138 786510 G24-318-TAP 138 1 | TDF Impact | 520_T.NO.4-46ST-TP-PPTAP_rebuild.idv : 2023 ITP, PID: 93019, NTC, ISD: 1/21/2027
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | FROM->TO | 512623 CATSAGD4 138 3WXFMR 523:CATAUTO1 138 1 | B | 188 | 0.10148 | 114.3439 | P13:138-161:GRDA:CATAUTO2:::HV: | Cumulative Impact | Add 3-winding transformer 512623 CATSAGD4 138 512638 CATSAGR5 161 512833 CATTER1 1 13 M2
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | FROM->TO | 512623 CATSAGD4 138 3WXFMR 523:CATAUTO1 138 1 | B | 188 | 0.10148 | 114.3439 | Single 509790 CATOOSA4 138 512636 CATSAGR4 138 Z1 | Cumulative Impact | Add 3-winding transformer 512623 CATSAGD4 138 512638 CATSAGR5 161 512833 CATTER1 1 13 M2
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | FROM->TO | 512636 CATSAGR4 138 3WXFMR 523:CATAUTO2 138 2 | B | 188 | 0.10178 | 114.6833 | P13:138-161:GRDA:CATAUTO1:::HV: | Cumulative Impact | Add 3-winding transformer 512636 CATSAGR4 138 512638 CATSAGR5 161 512834 CATTER2 1 13 M2
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | FROM->TO | 512636 CATSAGR4 138 3WXFMR 523:CATAUTO2 138 2 | B | 188 | 0.10178 | 114.6833 | Single 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | Cumulative Impact | Add 3-winding transformer 512636 CATSAGR4 138 512638 CATSAGR5 161 512834 CATTER2 1 13 M2
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | FROM->TO | 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | B | 188 | 0.10148 | 115.0684 | P13:138-161:GRDA:CATAUTO2:::HV: | Cumulative Impact | Rebuild line 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | FROM->TO | 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | B | 188 | 0.10148 | 115.0684 | Single 509790 CATOOSA4 138 512636 CATSAGR4 138 Z1 | Cumulative Impact | Rebuild line 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-318 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.12245 | 116.5975 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.090293 | 119.3706 | System Intact | TDF Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.090293 | 119.3706 | System Intact | TDF Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.090293 | 119.3706 | System Intact | TDF Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.082972 | 119.5141 | System Intact | TDF Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.082972 | 119.5141 | System Intact | TDF Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.082972 | 119.5141 | System Intact | TDF Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-318 | FROM->TO | 509790 CATOOSA4 138 512636 CATSAGR4 138 Z1 | B | 218 | 0.086732 | 124.6315 | Single 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | Cumulative Impact | Rebuild line 509790 CATOOSA4 138 512636 CATSAGR4 138 Z1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | FROM->TO | 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | B | 188 | 0.079363 | 126.4273 | Single 300795 4OOLOGAHKAMO 138 513124 OOLOGAH4 138 Z1 | Cumulative Impact | Rebuild line 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | FROM->TO | 512636 CATSAGR4 138 3WXFMR 523:CATAUTO2 138 2 | B | 188 | 0.088363 | 127.8636 | Single 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | Cumulative Impact | Add 3-winding transformer 512636 CATSAGR4 138 512638 CATSAGR5 161 512834 CATTER2 1 13 M2
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | FROM->TO | 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | A | 150 | 0.073334 | 132.7121 | System Intact | TDF Impact | Rebuild line 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.099529 | 136.5828 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.099529 | 136.5828 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.099529 | 136.5828 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.096213 | 136.8919 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.096213 | 136.8919 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.096213 | 136.8919 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.10262 | 136.9237 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.10262 | 136.9237 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.10262 | 136.9237 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.090148 | 139.3736 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.090148 | 139.3736 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.090148 | 139.3736 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | FROM->TO | 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | B | 188 | 0.077098 | 139.5037 | P22:345:EES:CLARKSV7!:::EHV: | Cumulative Impact | Rebuild line 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.097183 | 140.3415 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.097183 | 140.3415 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.097183 | 140.3415 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.08885 | 140.6152 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.08885 | 140.6152 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.08885 | 140.6152 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.10489 | 141.6076 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.10489 | 141.6076 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.10489 | 141.6076 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.10163 | 142.5086 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.10163 | 142.5086 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.10163 | 142.5086 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.09665 | 142.6431 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.09665 | 142.6431 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.09665 | 142.6431 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.097144 | 142.7223 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.097144 | 142.7223 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.097144 | 142.7223 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-318 | FROM->TO | 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | B | 188 | 0.077739 | 143.0169 | Single 300795 4OOLOGAHKAMO 138 513124 OOLOGAH4 138 Z1 | Cumulative Impact | Rebuild line 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.088261 | 143.2233 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.088261 | 143.2233 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.088261 | 143.2233 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-318 | FROM->TO | 512636 CATSAGR4 138 3WXFMR 523:CATAUTO2 138 2 | B | 188 | 0.086732 | 143.4156 | Single 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | Cumulative Impact | Add 3-winding transformer 512636 CATSAGR4 138 512638 CATSAGR5 161 512834 CATTER2 1 13 M2
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.093985 | 143.8401 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.093985 | 143.8401 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.093985 | 143.8401 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.09665 | 145.1309 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.09665 | 145.1309 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.09665 | 145.1309 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.09665 | 145.1356 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.09665 | 145.1356 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.09665 | 145.1356 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.088261 | 145.7578 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.088261 | 145.7578 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.088261 | 145.7578 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.088261 | 145.7646 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.088261 | 145.7646 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.088261 | 145.7646 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.09665 | 148.805 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.09665 | 148.805 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.09665 | 148.805 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | FROM->TO | 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | B | 188 | 0.10355 | 149.5687 | Single 509790 CATOOSA4 138 512636 CATSAGR4 138 Z1 | Cumulative Impact | Rebuild line 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | FROM->TO | 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | B | 188 | 0.10355 | 149.5687 | P13:138-161:GRDA:CATAUTO2:::HV: | Cumulative Impact | Rebuild line 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.088261 | 149.8057 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.088261 | 149.8057 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.088261 | 149.8057 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-318 | FROM->TO | 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | A | 150 | 0.072008 | 149.9079 | System Intact | TDF Impact | Rebuild line 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | FROM->TO | 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | B | 188 | 0.082831 | 150.3111 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | Cumulative Impact | Rebuild line 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | FROM->TO | 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | B | 188 | 0.07332 | 152.0562 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB:::: | Cumulative Impact | Rebuild line 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | FROM->TO | 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | B | 188 | 0.073324 | 152.2091 | P12:345:EES:CHAMSPR7!:CLARKSV7!:1:EHV: | Cumulative Impact | Rebuild line 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.09665 | 155.6146 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.09665 | 155.6146 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.09665 | 155.6146 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-318 | FROM->TO | 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | B | 188 | 0.075168 | 155.7771 | P22:345:EES:CLARKSV7!:::EHV: | Cumulative Impact | Rebuild line 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.088261 | 157.3662 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.088261 | 157.3662 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.088261 | 157.3662 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | FROM->TO | 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | B | 188 | 0.082831 | 160.386 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Cumulative Impact | Rebuild line 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-318 | FROM->TO | 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | B | 188 | 0.071734 | 161.2104 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB:::: | Cumulative Impact | Rebuild line 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-318 | FROM->TO | 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | B | 188 | 0.071738 | 161.3969 | P12:345:EES:CHAMSPR7!:CLARKSV7!:1:EHV: | Cumulative Impact | Rebuild line 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-318 | FROM->TO | 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | B | 188 | 0.080534 | 165.4608 | P12:345:GRDA:GREC TAP7-IGLOOV 7:::EHV: | Cumulative Impact | Rebuild line 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-318 | FROM->TO | 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | B | 188 | 0.10167 | 168.9167 | Single 509790 CATOOSA4 138 512636 CATSAGR4 138 Z1 | Cumulative Impact | Rebuild line 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-318 | FROM->TO | 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | B | 188 | 0.10167 | 168.9167 | P13:138-161:GRDA:CATAUTO2:::HV: | Cumulative Impact | Rebuild line 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-318 | FROM->TO | 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | B | 188 | 0.080534 | 175.1417 | Single 765721 G21-047-TAP 345 785790 G24-294-TAP 345 1 | Cumulative Impact | Rebuild line 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | FROM->TO | 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | B | 188 | 0.082831 | 180.2339 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | Cumulative Impact | Rebuild line 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | FROM->TO | 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | B | 188 | 0.082831 | 190.5992 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Rebuild line 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-318 | FROM->TO | 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | B | 188 | 0.080534 | 194.2647 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | Cumulative Impact | Rebuild line 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-318 | FROM->TO | 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | B | 188 | 0.080534 | 203.1414 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Rebuild line 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-319 | FROM->TO | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.07478 | 104.394 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-319 | FROM->TO | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.080962 | 111.8275 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-320 | FROM->TO | 533243 JAGGARD3 115 533261 PENTAGN3 115 1 | B | 201 | 0.58103 | 100.9823 | Single 532772 STRANGR7 345 784560 G24-253-TAP 345 1 | TDF Impact | Rebuild line 533243 JAGGARD3 115 533261 PENTAGN3 115 1
Thermal | 03ALL | 1 | 29WP | T1 | GEN-2024-320 | FROM->TO | 533243 JAGGARD3 115 533261 PENTAGN3 115 1 | B | 260 | 0.59117 | 104.2675 | Single 532772 STRANGR7 345 784560 G24-253-TAP 345 1 | TDF Impact | Rebuild line 533243 JAGGARD3 115 533261 PENTAGN3 115 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-320 | FROM->TO | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.074636 | 104.394 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-320 | FROM->TO | 533243 JAGGARD3 115 533261 PENTAGN3 115 1 | B | 201 | 0.58386 | 106.1269 | P23:345:WERE:STRA-345-643:::EHV: | TDF Impact | Rebuild line 533243 JAGGARD3 115 533261 PENTAGN3 115 1
Thermal | 03ALL | 1 | 29WP | T1 | GEN-2024-320 | FROM->TO | 533243 JAGGARD3 115 533261 PENTAGN3 115 1 | B | 260 | 0.60767 | 106.7178 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | Rebuild line 533243 JAGGARD3 115 533261 PENTAGN3 115 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-320 | FROM->TO | 533243 JAGGARD3 115 533261 PENTAGN3 115 1 | B | 201 | 0.58103 | 107.2439 | Single 532775 87TH7 345 784560 G24-253-TAP 345 1 | TDF Impact | Rebuild line 533243 JAGGARD3 115 533261 PENTAGN3 115 1
Thermal | 03ALL | 1 | 29WP | T1 | GEN-2024-320 | FROM->TO | 533243 JAGGARD3 115 533261 PENTAGN3 115 1 | B | 260 | 0.59117 | 108.9944 | Single 532775 87TH7 345 784560 G24-253-TAP 345 1 | TDF Impact | Rebuild line 533243 JAGGARD3 115 533261 PENTAGN3 115 1
Thermal | 03ALL | 1 | 29WP | T1 | GEN-2024-320 | FROM->TO | 533243 JAGGARD3 115 533261 PENTAGN3 115 1 | B | 260 | 0.59394 | 109.1652 | P23:345:WERE:STRA-345-643:::EHV: | TDF Impact | Rebuild line 533243 JAGGARD3 115 533261 PENTAGN3 115 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-320 | FROM->TO | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.081121 | 111.8275 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-320 | FROM->TO | 533243 JAGGARD3 115 533261 PENTAGN3 115 1 | B | 201 | 0.59743 | 112.035 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | Rebuild line 533243 JAGGARD3 115 533261 PENTAGN3 115 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-323 | FROM->TO | 514809 JOHNCO 7 345 3WXFMR 524:524:JOHNCOT3 345 3 | B | 478 | 0.079452 | 100.3203 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-323 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.26635 | 100.5325 | Single 510907 PITTSB-7 345 515422 C-RIVER7 345 1 | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-323 | FROM->TO | 337909 8ANO% 500 515305 FTSMITH8 500 1 | B | 1299 | 0.092125 | 102.9598 | P52:345:AEPW:NR4PITTSB-7:::: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-323 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.23836 | 103.8575 | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-323 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.18688 | 104.6172 | P23:345:AEPW:PITTSBURG CB 3433A NBTB:::: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-323 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.18489 | 105.6255 | Single 510907 PITTSB-7 345 787110 G24-338-TAP 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-323 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.25517 | 107.6782 | 272864 | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-323 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.25596 | 108.0084 | Single 515422 C-RIVER7 345 785850 G24-296-TAP 345 1 | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-323 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.2076 | 110.0508 | P22:345:EES:MUSKOGE7!:::EHV: | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-323 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.23963 | 110.6242 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-323 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.23895 | 111.1525 | Single 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-323 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.18489 | 111.5464 | Single 514809 JOHNCO7 345 787110 G24-338-TAP 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-323 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.18489 | 111.595 | P42:345:OKGE:SB_JOCO7311:::EHV: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-323 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.23895 | 111.7065 | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-323 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.25422 | 113.8068 | 272864 | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-323 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.25493 | 114.1963 | Single 515422 C-RIVER7 345 785850 G24-296-TAP 345 1 | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-323 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.25596 | 114.4578 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-323 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.18621 | 115.5426 | Single 514809 JOHNCO7 345 787110 G24-338-TAP 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-323 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.18621 | 115.6069 | P42:345:OKGE:SB_JOCO7311:::EHV: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-323 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.20921 | 117.3852 | P22:345:EES:MUSKOGE7!:::EHV: | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-323 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.25493 | 120.547 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-323 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.26457 | 121.1336 | Single 510907 PITTSB-7 345 515422 C-RIVER7 345 1 | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-323 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.26364 | 126.6467 | Single 510907 PITTSB-7 345 515422 C-RIVER7 345 1 | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-323 | FROM->TO | 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 | B | 222 | 0.060025 | 126.6708 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-323 | FROM->TO | 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 | B | 222 | 0.061086 | 130.823 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-330 | FROM->TO | 532995 OTTRCRK4 138 533001 ALTOONA4 138 1 | B | 98 | 0.11425 | 101.1469 | Single 767240 G22-013-TAP 345 779250 G24-076-TAP 345 1 | Cumulative Impact | Rebuild line 532995 OTTRCRK4 138 533001 ALTOONA4 138 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-330 | FROM->TO | 532995 OTTRCRK4 138 533001 ALTOONA4 138 1 | B | 111 | 0.11599 | 102.5368 | P42:345:OKGE:SB_SOER7383:::EHV: | Cumulative Impact | Rebuild line 532995 OTTRCRK4 138 533001 ALTOONA4 138 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-330 | FROM->TO | 532995 OTTRCRK4 138 533001 ALTOONA4 138 1 | B | 111 | 0.1166 | 102.5825 | Single 780720 G24-125-TAP 345 780840 G24-129-TAP 345 1 | Cumulative Impact | Rebuild line 532995 OTTRCRK4 138 533001 ALTOONA4 138 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-330 | FROM->TO | 532995 OTTRCRK4 138 533001 ALTOONA4 138 1 | B | 111 | 0.1166 | 102.652 | Single 532777 NRSS7 345 780840 G24-129-TAP 345 1 | Cumulative Impact | Rebuild line 532995 OTTRCRK4 138 533001 ALTOONA4 138 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-330 | FROM->TO | 532995 OTTRCRK4 138 533001 ALTOONA4 138 1 | B | 98 | 0.11892 | 102.8917 | P42:345:OKGE:SB_SOER7383:::EHV: | Cumulative Impact | Rebuild line 532995 OTTRCRK4 138 533001 ALTOONA4 138 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-330 | FROM->TO | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.056208 | 104.394 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-330 | FROM->TO | 532995 OTTRCRK4 138 533001 ALTOONA4 138 1 | B | 111 | 0.1118 | 104.6404 | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | Cumulative Impact | Rebuild line 532995 OTTRCRK4 138 533001 ALTOONA4 138 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-330 | FROM->TO | 532995 OTTRCRK4 138 533001 ALTOONA4 138 1 | B | 98 | 0.11425 | 105.9967 | Single 532793 NEOSHO7 345 779250 G24-076-TAP 345 1 | Cumulative Impact | Rebuild line 532995 OTTRCRK4 138 533001 ALTOONA4 138 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-330 | FROM->TO | 532995 OTTRCRK4 138 533001 ALTOONA4 138 1 | B | 111 | 0.11553 | 107.4514 | P23:345:WERE:N345-345-20:EHV: | Cumulative Impact | Rebuild line 532995 OTTRCRK4 138 533001 ALTOONA4 138 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-330 | FROM->TO | 532995 OTTRCRK4 138 533001 ALTOONA4 138 1 | B | 98 | 0.11841 | 107.7742 | P23:345:WERE:N345-345-20:EHV: | Cumulative Impact | Rebuild line 532995 OTTRCRK4 138 533001 ALTOONA4 138 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-330 | FROM->TO | 532995 OTTRCRK4 138 533001 ALTOONA4 138 1 | B | 98 | 0.1193 | 108.0307 | P52:345:WERE:NRSS7:EHV: | Cumulative Impact | Rebuild line 532995 OTTRCRK4 138 533001 ALTOONA4 138 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-330 | FROM->TO | 532995 OTTRCRK4 138 533001 ALTOONA4 138 1 | B | 111 | 0.11356 | 109.0745 | Single 765200 G20-090-TAP 345 785580 G24-287-TAP 345 1 | Cumulative Impact | Rebuild line 532995 OTTRCRK4 138 533001 ALTOONA4 138 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-330 | FROM->TO | 532995 OTTRCRK4 138 533001 ALTOONA4 138 1 | B | 98 | 0.11617 | 109.2071 | Single 765200 G20-090-TAP 345 785580 G24-287-TAP 345 1 | Cumulative Impact | Rebuild line 532995 OTTRCRK4 138 533001 ALTOONA4 138 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-330 | FROM->TO | 532995 OTTRCRK4 138 533001 ALTOONA4 138 1 | B | 111 | 0.11628 | 110.0013 | P52:345:WERE:NRSS7:EHV: | Cumulative Impact | Rebuild line 532995 OTTRCRK4 138 533001 ALTOONA4 138 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-330 | FROM->TO | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.063595 | 111.8275 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-330 | FROM->TO | 532995 OTTRCRK4 138 533001 ALTOONA4 138 1 | B | 111 | 0.11336 | 113.0914 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Rebuild line 532995 OTTRCRK4 138 533001 ALTOONA4 138 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-330 | FROM->TO | 532995 OTTRCRK4 138 533001 ALTOONA4 138 1 | B | 98 | 0.11596 | 113.6003 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Rebuild line 532995 OTTRCRK4 138 533001 ALTOONA4 138 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-330 | FROM->TO | 532995 OTTRCRK4 138 533001 ALTOONA4 138 1 | B | 111 | 0.11356 | 114.2451 | Single 300739 7BLACKBERRY 345 785580 G24-287-TAP 345 1 | Cumulative Impact | Rebuild line 532995 OTTRCRK4 138 533001 ALTOONA4 138 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-330 | FROM->TO | 532995 OTTRCRK4 138 533001 ALTOONA4 138 1 | B | 98 | 0.11617 | 115.3566 | Single 300739 7BLACKBERRY 345 785580 G24-287-TAP 345 1 | Cumulative Impact | Rebuild line 532995 OTTRCRK4 138 533001 ALTOONA4 138 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-330 | FROM->TO | 532995 OTTRCRK4 138 533001 ALTOONA4 138 1 | B | 98 | 0.11896 | 116.1863 | P12:345:WERE:NRSS-N345-345:EHV: | Cumulative Impact | Rebuild line 532995 OTTRCRK4 138 533001 ALTOONA4 138 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-330 | FROM->TO | 532995 OTTRCRK4 138 533001 ALTOONA4 138 1 | B | 98 | 0.092742 | 116.2498 | Single 533005 NEPARSN4 138 533022 NEOSHON4 138 1 | Cumulative Impact | Rebuild line 532995 OTTRCRK4 138 533001 ALTOONA4 138 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-330 | FROM->TO | 532995 OTTRCRK4 138 533001 ALTOONA4 138 1 | B | 111 | 0.11601 | 116.6599 | P12:345:WERE:NRSS-N345-345:EHV: | Cumulative Impact | Rebuild line 532995 OTTRCRK4 138 533001 ALTOONA4 138 1
Thermal | 04ALL | 1 | 29SP | T1 | GEN-2024-333 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.032199 | 103.3038 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-333 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | A | 1187 | 0.043478 | 103.8656 | System Intact | TDF Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-333 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.05256 | 106.1409 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-333 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.051902 | 107.841 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-333 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.051902 | 109.5335 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-333 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.051902 | 109.534 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-333 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.051902 | 112.0538 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-333 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.063841 | 114.5102 | System Intact | TDF Impact | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-333 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.057874 | 114.6214 | System Intact | TDF Impact | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-333 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.051902 | 116.5975 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-333 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.036696 | 119.3706 | System Intact | TDF Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-333 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.036696 | 119.3706 | System Intact | TDF Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-333 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.036696 | 119.3706 | System Intact | TDF Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-333 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.033791 | 119.5141 | System Intact | TDF Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-333 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.033791 | 119.5141 | System Intact | TDF Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-333 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.033791 | 119.5141 | System Intact | TDF Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-336 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.0713 | 100.0488 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-336 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.062504 | 100.533 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-336 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.074829 | 103.9266 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-336 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.074453 | 104.7552 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-336 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.074453 | 104.888 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-336 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.077923 | 107.2243 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-336 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063414 | 107.2793 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-336 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063414 | 107.2794 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-336 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.077923 | 107.2951 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-336 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063414 | 107.3093 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-336 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063414 | 107.7557 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-336 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063414 | 108.2747 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-336 | FROM->TO | 523961 POTTER_CO 7 345 3WXFMR 526:WAUK 90343-A 230 1 | B | 559 | 0.096423 | 108.8994 | P42:345:SPS:HITCHLAND-1R15:::EHV: | Cumulative Impact | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-336 | FROM->TO | 523961 POTTER_CO 7 345 3WXFMR 526:WAUK 90343-A 230 1 | B | 559 | 0.096423 | 108.9122 | Single 523097 HITCHLAND7 345 523961 POTTER_CO7 345 1 | Cumulative Impact | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-336 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063414 | 111.3621 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-336 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.072395 | 115.0541 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-336 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.075565 | 118.9427 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-336 | FROM->TO | 511490 ELKCITY6 230 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.075565 | 119.313 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 04ALL | 1 | 29SP | T1 | GEN-2024-338 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.030106 | 103.3038 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-338 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | A | 1187 | 0.043288 | 103.8656 | System Intact | TDF Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-338 | FROM->TO | 511468 L.E.S.-7 345 3WXFMR 520:LES 5 345 2 | B | 515 | 0.055836 | 114.3077 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-338 | FROM->TO | 511468 L.E.S.-7 345 3WXFMR 520:LES 5 345 2 | B | 515 | 0.056415 | 114.3448 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-338 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.040998 | 114.5102 | System Intact | TDF Impact | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-338 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.034968 | 114.6214 | System Intact | TDF Impact | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-338 | FROM->TO | 511468 L.E.S.-7 345 3WXFMR 520:LES 5 345 2 | B | 515 | 0.05404 | 115.3782 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | TDF Impact | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-338 | FROM->TO | 511468 L.E.S.-7 345 3WXFMR 520:LES 5 345 2 | B | 515 | 0.05474 | 116.8526 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | TDF Impact | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-338 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | B | 1000 | 0.079305 | 116.8554 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | Cumulative Impact | Rebuild line 508359 WELSH 7 345 508841 WILKES 7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-338 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.035908 | 119.3706 | System Intact | TDF Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-338 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.035908 | 119.3706 | System Intact | TDF Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-338 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.035908 | 119.3706 | System Intact | TDF Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-338 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.032549 | 119.5141 | System Intact | TDF Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-338 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.032549 | 119.5141 | System Intact | TDF Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-338 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.032549 | 119.5141 | System Intact | TDF Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-339 | FROM->TO | 533243 JAGGARD3 115 533261 PENTAGN3 115 1 | B | 201 | 0.11408 | 100.9823 | Single 532772 STRANGR7 345 784560 G24-253-TAP 345 1 | Cumulative Impact | Rebuild line 533243 JAGGARD3 115 533261 PENTAGN3 115 1
Thermal | 03ALL | 1 | 29WP | T1 | GEN-2024-339 | FROM->TO | 533243 JAGGARD3 115 533261 PENTAGN3 115 1 | B | 260 | 0.115 | 104.2675 | Single 532772 STRANGR7 345 784560 G24-253-TAP 345 1 | Cumulative Impact | Rebuild line 533243 JAGGARD3 115 533261 PENTAGN3 115 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-339 | FROM->TO | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.070512 | 104.394 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-339 | FROM->TO | 533243 JAGGARD3 115 533261 PENTAGN3 115 1 | B | 201 | 0.12093 | 106.1269 | P23:345:WERE:STRA-345-643:::EHV: | Cumulative Impact | Rebuild line 533243 JAGGARD3 115 533261 PENTAGN3 115 1
Thermal | 03ALL | 1 | 29WP | T1 | GEN-2024-339 | FROM->TO | 533243 JAGGARD3 115 533261 PENTAGN3 115 1 | B | 260 | 0.10721 | 106.7178 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild line 533243 JAGGARD3 115 533261 PENTAGN3 115 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-339 | FROM->TO | 533243 JAGGARD3 115 533261 PENTAGN3 115 1 | B | 201 | 0.11408 | 107.2439 | Single 532775 87TH7 345 784560 G24-253-TAP 345 1 | Cumulative Impact | Rebuild line 533243 JAGGARD3 115 533261 PENTAGN3 115 1
Thermal | 03ALL | 1 | 29WP | T1 | GEN-2024-339 | FROM->TO | 533243 JAGGARD3 115 533261 PENTAGN3 115 1 | B | 260 | 0.115 | 108.9944 | Single 532775 87TH7 345 784560 G24-253-TAP 345 1 | Cumulative Impact | Rebuild line 533243 JAGGARD3 115 533261 PENTAGN3 115 1
Thermal | 03ALL | 1 | 29WP | T1 | GEN-2024-339 | FROM->TO | 533243 JAGGARD3 115 533261 PENTAGN3 115 1 | B | 260 | 0.12213 | 109.1652 | P23:345:WERE:STRA-345-643:::EHV: | Cumulative Impact | Rebuild line 533243 JAGGARD3 115 533261 PENTAGN3 115 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-339 | FROM->TO | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.077813 | 111.8275 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-339 | FROM->TO | 533243 JAGGARD3 115 533261 PENTAGN3 115 1 | B | 201 | 0.10436 | 112.035 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild line 533243 JAGGARD3 115 533261 PENTAGN3 115 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-340 | FROM->TO | 514908 ARCADIA7 345 3WXFMR 524:524:ARCADIA4 345 4 | B | 448 | 0.077444 | 103.8945 | P13:138:OKGE:BKRBKR_3W024:::HV: | Cumulative Impact | Add 3-winding transformer 514907 ARCADIA4 138 514908 ARCADIA7 345 515700 ARCADI41 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-340 | FROM->TO | 787170 G24-340-TAP 345 787290 G24-344-TAP 345 1 | B | 1143 | 1 | 119.5799 | P23:345:AEPW:RIVERSIDE CB 3405A NBTB:::: | TDF Impact | Rebuild line 787170 G24-340-TAP 345 787290 G24-344-TAP 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-340 | FROM->TO | 787170 G24-340-TAP 345 787290 G24-344-TAP 345 1 | B | 1143 | 1 | 119.5812 | Single 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1 | TDF Impact | Rebuild line 787170 G24-340-TAP 345 787290 G24-344-TAP 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-340 | FROM->TO | 787170 G24-340-TAP 345 787290 G24-344-TAP 345 1 | B | 1055 | 1 | 129.5721 | P23:345:AEPW:RIVERSIDE CB 3405A NBTB:::: | TDF Impact | Rebuild line 787170 G24-340-TAP 345 787290 G24-344-TAP 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-340 | FROM->TO | 787170 G24-340-TAP 345 787290 G24-344-TAP 345 1 | B | 1055 | 1 | 129.5722 | Single 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1 | TDF Impact | Rebuild line 787170 G24-340-TAP 345 787290 G24-344-TAP 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-340 | FROM->TO | 787170 G24-340-TAP 345 787290 G24-344-TAP 345 1 | B | 1055 | 1 | 129.6353 | P23:345:AEPW:RIVERSIDE CB 3405A NBTB:::: | TDF Impact | Rebuild line 787170 G24-340-TAP 345 787290 G24-344-TAP 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-340 | FROM->TO | 787170 G24-340-TAP 345 787290 G24-344-TAP 345 1 | B | 1055 | 1 | 129.6354 | Single 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1 | TDF Impact | Rebuild line 787170 G24-340-TAP 345 787290 G24-344-TAP 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-341 | FROM->TO | 514809 JOHNCO 7 345 3WXFMR 524:524:JOHNCOT3 345 3 | B | 478 | 0.16504 | 100.3203 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-341 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.5095 | 100.5325 | Single 510907 PITTSB-7 345 515422 C-RIVER7 345 1 | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-341 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.38953 | 103.8575 | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-341 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.43148 | 104.6172 | P23:345:AEPW:PITTSBURG CB 3433A NBTB:::: | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-341 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.42949 | 105.6255 | Single 510907 PITTSB-7 345 787110 G24-338-TAP 345 1 | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-341 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.46688 | 107.6782 | 272864 | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-341 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.46852 | 108.0084 | Single 515422 C-RIVER7 345 785850 G24-296-TAP 345 1 | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-341 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.37838 | 110.0508 | P22:345:EES:MUSKOGE7!:::EHV: | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-341 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.39265 | 110.6242 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-341 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.39197 | 111.1525 | Single 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-341 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.42949 | 111.5464 | Single 514809 JOHNCO7 345 787110 G24-338-TAP 345 1 | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-341 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.42949 | 111.595 | P42:345:OKGE:SB_JOCO7311:::EHV: | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-341 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.39197 | 111.7065 | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-341 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.46837 | 113.8068 | 272864 | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-341 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.46989 | 114.1963 | Single 515422 C-RIVER7 345 785850 G24-296-TAP 345 1 | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-341 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.46852 | 114.4578 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-341 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.43266 | 115.5426 | Single 514809 JOHNCO7 345 787110 G24-338-TAP 345 1 | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-341 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.43266 | 115.6069 | P42:345:OKGE:SB_JOCO7311:::EHV: | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-341 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.38109 | 117.3852 | P22:345:EES:MUSKOGE7!:::EHV: | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-341 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.46989 | 120.547 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-341 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.50534 | 121.1336 | Single 510907 PITTSB-7 345 515422 C-RIVER7 345 1 | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-341 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.50669 | 126.6467 | Single 510907 PITTSB-7 345 515422 C-RIVER7 345 1 | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-341 | FROM->TO | 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 | B | 222 | 0.090288 | 126.6708 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-341 | FROM->TO | 514808 JOHNCO 4 138 515122 SXMLCKT4 138 1 | B | 222 | 0.09149 | 130.823 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | FROM->TO | 508548 KNOXLEE4 138 509059 CHEROKE4 138 1 | B | 350 | 0.076057 | 100.1039 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 508548 KNOXLEE4 138 509059 CHEROKE4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | FROM->TO | 508596 BRANDYBR4 138 509092 EASTON 4 138 1 | B | 575 | 0.099664 | 100.139 | Single 508595 HALLSVLS4 138 775840 G23-193-TAP 138 1 | Cumulative Impact | Rebuild line 508596 BRANDYBR4 138 509092 EASTON 4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | FROM->TO | 508562 PIRKEY 4 138 508596 BRANDYBR4 138 1 | B | 575 | 0.099664 | 100.2299 | Single 508595 HALLSVLS4 138 775840 G23-193-TAP 138 1 | Cumulative Impact | Rebuild line 508562 PIRKEY 4 138 508596 BRANDYBR4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | FROM->TO | 509083 ROKHILL4 138 509102 NEWPROS4 138 1 | B | 289 | 0.054102 | 100.3166 | Single 334197 7ROCKYCRK% 345 783930 G24-232-TAP 345 1 | Cumulative Impact | Rebuild line 509083 ROKHILL4 138 509102 NEWPROS4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | FROM->TO | 514809 JOHNCO 7 345 3WXFMR 524:524:JOHNCOT3 345 3 | B | 478 | 0.053518 | 100.3203 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | FROM->TO | 509083 ROKHILL4 138 509102 NEWPROS4 138 1 | B | 289 | 0.054102 | 100.4359 | P23:345:EES::7ROCKYCRK%:1:EHV: | Cumulative Impact | Rebuild line 509083 ROKHILL4 138 509102 NEWPROS4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | FROM->TO | 508563 PIRKEY 7 345 508832 DIANA 7 345 1 | B | 1306 | 0.64541 | 100.4992 | P23:345:AEPW:TENASKA CB 12840 NBTB:::: | TDF Impact | Rebuild line 508563 PIRKEY 7 345 508832 DIANA 7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | FROM->TO | 508563 PIRKEY 7 345 508832 DIANA 7 345 1 | B | 1306 | 0.64541 | 100.4992 | P22:345:EES:TENRUSK7!:::EHV: | TDF Impact | Rebuild line 508563 PIRKEY 7 345 508832 DIANA 7 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-343 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.17697 | 100.5325 | Single 510907 PITTSB-7 345 515422 C-RIVER7 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | FROM->TO | 508563 PIRKEY 7 345 508832 DIANA 7 345 1 | B | 1306 | 0.64541 | 100.6276 | P23:345:AEPW:TENASKA CB 12860 NBTB:::: | TDF Impact | Rebuild line 508563 PIRKEY 7 345 508832 DIANA 7 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-343 | FROM->TO | 508566 SABMINT4 138 508569 SEMRSHL4 138 1 | B | 333 | 0.16698 | 100.7592 | P12:345:AEPW:PIRKEY7:DIANA7::: | Cumulative Impact | Rebuild line 508566 SABMINT4 138 508569 SEMRSHL4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | FROM->TO | 508563 PIRKEY 7 345 508832 DIANA 7 345 1 | B | 1306 | 0.64453 | 100.8185 | P12:345:EES:LEBROCK7!:TENRUSK7!:1:EHV: | TDF Impact | Rebuild line 508563 PIRKEY 7 345 508832 DIANA 7 345 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-343 | FROM->TO | 508808 LONGWD 4 138 508816 OAKPH 4 138 1 | B | 395 | 0.054061 | 100.8572 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 508808 LONGWD 4 138 508816 OAKPH 4 138 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-343 | FROM->TO | 508566 SABMINT4 138 508569 SEMRSHL4 138 1 | B | 333 | 0.16607 | 100.8957 | P23:345:AEPW:PIRKEY CB 13430 NBTB:::: | Cumulative Impact | Rebuild line 508566 SABMINT4 138 508569 SEMRSHL4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | FROM->TO | 508562 PIRKEY 4 138 508566 SABMINT4 138 1 | B | 340 | 0.16602 | 101.0119 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | Cumulative Impact | Rebuild line 508562 PIRKEY 4 138 508566 SABMINT4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | FROM->TO | 508298 LYDIA 7 345 510911 VALIANT7 345 1 | B | 1176 | 0.33496 | 101.2347 | P23:345:AEPW:VALLIANT CB 3413A NBTB:::: | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | FROM->TO | 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.31375 | 101.4921 | Single 337376 7SAREPTA% 345 788340 G24-379-TAP 345 1 | TDF Impact | Rebuild line 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-343 | FROM->TO | 508562 PIRKEY 4 138 508566 SABMINT4 138 1 | B | 395 | 0.1814 | 101.7389 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | Cumulative Impact | Rebuild line 508562 PIRKEY 4 138 508566 SABMINT4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | FROM->TO | 508298 LYDIA 7 345 510911 VALIANT7 345 1 | B | 1176 | 0.36976 | 102.11 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB:::: | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-343 | FROM->TO | 508808 LONGWD 4 138 508816 OAKPH 4 138 1 | B | 395 | 0.054462 | 102.188 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 508808 LONGWD 4 138 508816 OAKPH 4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | FROM->TO | 508563 PIRKEY 7 345 508832 DIANA 7 345 1 | B | 1306 | 0.64541 | 102.3045 | P23:345:AEPW:TENASKA CB 12850 NBTB:::: | TDF Impact | Rebuild line 508563 PIRKEY 7 345 508832 DIANA 7 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | FROM->TO | 508298 LYDIA 7 345 510911 VALIANT7 345 1 | B | 1176 | 0.36533 | 102.3256 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB:::: | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-343 | FROM->TO | 508548 KNOXLEE4 138 509059 CHEROKE4 138 1 | B | 395 | 0.10683 | 102.6963 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 508548 KNOXLEE4 138 509059 CHEROKE4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | FROM->TO | 508298 LYDIA 7 345 510911 VALIANT7 345 1 | B | 1176 | 0.36733 | 102.7311 | Single 508072 NWTXARK7 345 764520 G20-020-TAP 345 1 | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-343 | FROM->TO | 508566 SABMINT4 138 508569 SEMRSHL4 138 1 | B | 333 | 0.1659 | 102.9158 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | Cumulative Impact | Rebuild line 508566 SABMINT4 138 508569 SEMRSHL4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | FROM->TO | 337909 8ANO% 500 515305 FTSMITH8 500 1 | B | 1299 | 0.17284 | 102.9598 | P52:345:AEPW:NR4PITTSB-7:::: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | FROM->TO | 508298 LYDIA 7 345 510911 VALIANT7 345 1 | B | 1176 | 0.36733 | 103.2181 | Single 510911 VALIANT7 345 764520 G20-020-TAP 345 1 | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | FROM->TO | 508562 PIRKEY 4 138 508566 SABMINT4 138 1 | B | 340 | 0.16629 | 103.3905 | P12:345:AEPW:PIRKEY7:DIANA7::: | Cumulative Impact | Rebuild line 508562 PIRKEY 4 138 508566 SABMINT4 138 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-343 | FROM->TO | 509059 CHEROKE4 138 509087 TATUM 4 138 1 | B | 350 | 0.090802 | 103.4947 | Single 334197 7ROCKYCRK% 345 783930 G24-232-TAP 345 1 | Cumulative Impact | Rebuild line 509059 CHEROKE4 138 509087 TATUM 4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | FROM->TO | 508562 PIRKEY 4 138 508566 SABMINT4 138 1 | B | 340 | 0.16538 | 103.5186 | P23:345:AEPW:PIRKEY CB 13430 NBTB:::: | Cumulative Impact | Rebuild line 508562 PIRKEY 4 138 508566 SABMINT4 138 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-343 | FROM->TO | 509059 CHEROKE4 138 509087 TATUM 4 138 1 | B | 350 | 0.090802 | 103.5551 | P23:345:EES::7ROCKYCRK%:1:EHV: | Cumulative Impact | Rebuild line 509059 CHEROKE4 138 509087 TATUM 4 138 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-343 | FROM->TO | 509059 CHEROKE4 138 509087 TATUM 4 138 1 | A | 241 | 0.07447 | 103.7761 | System Intact | TDF Impact | Rebuild line 509059 CHEROKE4 138 509087 TATUM 4 138 1
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-343 | FROM->TO | 509059 CHEROKE4 138 509087 TATUM 4 138 1 | B | 379 | 0.10683 | 103.8167 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 509059 CHEROKE4 138 509087 TATUM 4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | FROM->TO | 508563 PIRKEY 7 345 508832 DIANA 7 345 1 | B | 1306 | 0.63815 | 103.8202 | P12:345:EES:TENRUSK7!:CROCKET7%:1:EHV: | TDF Impact | Rebuild line 508563 PIRKEY 7 345 508832 DIANA 7 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.1691 | 103.8575 | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-343 | FROM->TO | 508548 KNOXLEE4 138 509059 CHEROKE4 138 1 | B | 395 | 0.10676 | 103.881 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 508548 KNOXLEE4 138 509059 CHEROKE4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | FROM->TO | 508563 PIRKEY 7 345 508832 DIANA 7 345 1 | B | 1306 | 0.64467 | 104.1826 | P23:345:EES::7ROCKYCRK%:1:EHV: | TDF Impact | Rebuild line 508563 PIRKEY 7 345 508832 DIANA 7 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | FROM->TO | 508563 PIRKEY 7 345 508832 DIANA 7 345 1 | B | 1306 | 0.64467 | 104.1965 | Single 334197 7ROCKYCRK% 345 783930 G24-232-TAP 345 1 | TDF Impact | Rebuild line 508563 PIRKEY 7 345 508832 DIANA 7 345 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-343 | FROM->TO | 509059 CHEROKE4 138 509087 TATUM 4 138 1 | B | 350 | 0.13348 | 104.4359 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | Cumulative Impact | Rebuild line 509059 CHEROKE4 138 509087 TATUM 4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.14916 | 104.6172 | P23:345:AEPW:PITTSBURG CB 3433A NBTB:::: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | FROM->TO | 508563 PIRKEY 7 345 508832 DIANA 7 345 1 | B | 1306 | 0.64158 | 104.8435 | Single 509241 CROCKET7 345 783930 G24-232-TAP 345 1 | TDF Impact | Rebuild line 508563 PIRKEY 7 345 508832 DIANA 7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | FROM->TO | 508298 LYDIA 7 345 510911 VALIANT7 345 1 | B | 1176 | 0.36681 | 104.9032 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB:::: | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | FROM->TO | 508298 LYDIA 7 345 510911 VALIANT7 345 1 | B | 1176 | 0.36221 | 105.0459 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB:::: | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | FROM->TO | 508562 PIRKEY 4 138 508566 SABMINT4 138 1 | B | 340 | 0.16525 | 105.1363 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | Cumulative Impact | Rebuild line 508562 PIRKEY 4 138 508566 SABMINT4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | FROM->TO | 337904 5RUSSELVL.S 161 505508 DARDANE5 161 1 | B | 396 | 0.05054 | 105.2411 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | FROM->TO | 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.36898 | 105.3575 | Single 508072 NWTXARK7 345 508359 WELSH7 345 1 | TDF Impact | Rebuild line 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | FROM->TO | 508563 PIRKEY 7 345 3WXFMR 520:PIRKEY 1 345 1 | B | 600 | 0.35968 | 105.446 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | TDF Impact | Add 3-winding transformer 508562 PIRKEY 4 138 508563 PIRKEY 7 345 508587 PIRKY1-1 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | FROM->TO | 508298 LYDIA 7 345 510911 VALIANT7 345 1 | B | 1176 | 0.3643 | 105.4715 | Single 508072 NWTXARK7 345 764520 G20-020-TAP 345 1 | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | FROM->TO | 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.36945 | 105.5739 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB:::: | TDF Impact | Rebuild line 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | FROM->TO | 508563 PIRKEY 7 345 3WXFMR 520:PIRKEY 1 345 1 | B | 600 | 0.35951 | 105.587 | P12:345:AEPW:PIRKEY7:DIANA7::: | TDF Impact | Add 3-winding transformer 508562 PIRKEY 4 138 508563 PIRKEY 7 345 508587 PIRKY1-1 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.14717 | 105.6255 | Single 510907 PITTSB-7 345 787110 G24-338-TAP 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | FROM->TO | 508563 PIRKEY 7 345 3WXFMR 520:PIRKEY 1 345 1 | B | 600 | 0.35729 | 105.7524 | P23:345:AEPW:PIRKEY CB 13430 NBTB:::: | TDF Impact | Add 3-winding transformer 508562 PIRKEY 4 138 508563 PIRKEY 7 345 508587 PIRKY1-1 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-343 | FROM->TO | 508563 PIRKEY 7 345 3WXFMR 520:PIRKEY 1 345 1 | B | 600 | 0.36108 | 107.221 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | TDF Impact | Add 3-winding transformer 508562 PIRKEY 4 138 508563 PIRKEY 7 345 508587 PIRKY1-1 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-343 | FROM->TO | 508563 PIRKEY 7 345 3WXFMR 520:PIRKEY 1 345 1 | B | 600 | 0.3609 | 107.3935 | P12:345:AEPW:PIRKEY7:DIANA7::: | TDF Impact | Add 3-winding transformer 508562 PIRKEY 4 138 508563 PIRKEY 7 345 508587 PIRKY1-1 13 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-343 | FROM->TO | 509059 CHEROKE4 138 509087 TATUM 4 138 1 | A | 241 | 0.074465 | 107.463 | System Intact | TDF Impact | Rebuild line 509059 CHEROKE4 138 509087 TATUM 4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | FROM->TO | 508298 LYDIA 7 345 510911 VALIANT7 345 1 | B | 1176 | 0.3643 | 107.4903 | Single 510911 VALIANT7 345 764520 G20-020-TAP 345 1 | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-343 | FROM->TO | 508563 PIRKEY 7 345 3WXFMR 520:PIRKEY 1 345 1 | B | 600 | 0.35868 | 107.566 | P23:345:AEPW:PIRKEY CB 13430 NBTB:::: | TDF Impact | Add 3-winding transformer 508562 PIRKEY 4 138 508563 PIRKEY 7 345 508587 PIRKY1-1 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.17388 | 107.6782 | 272864 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.1736 | 108.0084 | Single 515422 C-RIVER7 345 785850 G24-296-TAP 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | FROM->TO | 508563 PIRKEY 7 345 3WXFMR 520:PIRKEY 1 345 1 | B | 600 | 0.3616 | 108.1269 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | TDF Impact | Add 3-winding transformer 508562 PIRKEY 4 138 508563 PIRKEY 7 345 508587 PIRKY1-1 13 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-343 | FROM->TO | 508548 KNOXLEE4 138 509059 CHEROKE4 138 1 | B | 395 | 0.10681 | 108.1364 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 508548 KNOXLEE4 138 509059 CHEROKE4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | FROM->TO | 508563 PIRKEY 7 345 3WXFMR 520:PIRKEY 1 345 1 | B | 600 | 0.36141 | 108.244 | P12:345:AEPW:PIRKEY7:DIANA7::: | TDF Impact | Add 3-winding transformer 508562 PIRKEY 4 138 508563 PIRKEY 7 345 508587 PIRKY1-1 13 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-343 | FROM->TO | 509059 CHEROKE4 138 509087 TATUM 4 138 1 | B | 350 | 0.13326 | 108.3478 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | Cumulative Impact | Rebuild line 509059 CHEROKE4 138 509087 TATUM 4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | FROM->TO | 508563 PIRKEY 7 345 3WXFMR 520:PIRKEY 1 345 1 | B | 600 | 0.35918 | 108.3741 | P23:345:AEPW:PIRKEY CB 13430 NBTB:::: | TDF Impact | Add 3-winding transformer 508562 PIRKEY 4 138 508563 PIRKEY 7 345 508587 PIRKY1-1 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | FROM->TO | 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.3669 | 108.4857 | Single 508072 NWTXARK7 345 508359 WELSH7 345 1 | TDF Impact | Rebuild line 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | FROM->TO | 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.36715 | 108.6558 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB:::: | TDF Impact | Rebuild line 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | FROM->TO | 337904 5RUSSELVL.S 161 505508 DARDANE5 161 1 | B | 396 | 0.050336 | 108.6948 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | FROM->TO | 337904 5RUSSELVL.S 161 505508 DARDANE5 161 1 | B | 396 | 0.050285 | 108.894 | P42:500:OKGE:SB_FTTH8585:::EHV: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | FROM->TO | 508563 PIRKEY 7 345 508832 DIANA 7 345 1 | B | 1306 | 0.64158 | 109.3114 | P23:345:EES::7ROCKYCRK%:1:EHV: | TDF Impact | Rebuild line 508563 PIRKEY 7 345 508832 DIANA 7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | FROM->TO | 508563 PIRKEY 7 345 508832 DIANA 7 345 1 | B | 1306 | 0.64158 | 109.3236 | Single 334197 7ROCKYCRK% 345 783930 G24-232-TAP 345 1 | TDF Impact | Rebuild line 508563 PIRKEY 7 345 508832 DIANA 7 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.15379 | 110.0508 | P22:345:EES:MUSKOGE7!:::EHV: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.17009 | 110.6242 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.16942 | 111.1525 | Single 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | FROM->TO | 508596 BRANDYBR4 138 509092 EASTON 4 138 1 | B | 575 | 0.2059 | 111.2382 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | TDF Impact | Rebuild line 508596 BRANDYBR4 138 509092 EASTON 4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | FROM->TO | 508562 PIRKEY 4 138 508596 BRANDYBR4 138 1 | B | 575 | 0.2059 | 111.3326 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | TDF Impact | Rebuild line 508562 PIRKEY 4 138 508596 BRANDYBR4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | FROM->TO | 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.37991 | 111.4242 | P23:345:AEPW:WELSH CB 10610 NBTB:::: | TDF Impact | Rebuild line 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.14717 | 111.5464 | Single 514809 JOHNCO7 345 787110 G24-338-TAP 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | FROM->TO | 508596 BRANDYBR4 138 509092 EASTON 4 138 1 | B | 575 | 0.20552 | 111.5836 | P12:345:AEPW:PIRKEY7:DIANA7::: | TDF Impact | Rebuild line 508596 BRANDYBR4 138 509092 EASTON 4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.14717 | 111.595 | P42:345:OKGE:SB_JOCO7311:::EHV: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | FROM->TO | 508562 PIRKEY 4 138 508596 BRANDYBR4 138 1 | B | 575 | 0.20552 | 111.678 | P12:345:AEPW:PIRKEY7:DIANA7::: | TDF Impact | Rebuild line 508562 PIRKEY 4 138 508596 BRANDYBR4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.16942 | 111.7065 | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | FROM->TO | 508596 BRANDYBR4 138 509092 EASTON 4 138 1 | B | 575 | 0.20398 | 111.7191 | P23:345:AEPW:PIRKEY CB 13430 NBTB:::: | TDF Impact | Rebuild line 508596 BRANDYBR4 138 509092 EASTON 4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | FROM->TO | 508562 PIRKEY 4 138 508596 BRANDYBR4 138 1 | B | 575 | 0.20398 | 111.8135 | P23:345:AEPW:PIRKEY CB 13430 NBTB:::: | TDF Impact | Rebuild line 508562 PIRKEY 4 138 508596 BRANDYBR4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.1715 | 113.8068 | 272864 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.17117 | 114.1963 | Single 515422 C-RIVER7 345 785850 G24-296-TAP 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | FROM->TO | 508596 BRANDYBR4 138 509092 EASTON 4 138 1 | B | 575 | 0.20709 | 114.411 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | TDF Impact | Rebuild line 508596 BRANDYBR4 138 509092 EASTON 4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.1736 | 114.4578 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | FROM->TO | 508562 PIRKEY 4 138 508596 BRANDYBR4 138 1 | B | 575 | 0.20709 | 114.5042 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | TDF Impact | Rebuild line 508562 PIRKEY 4 138 508596 BRANDYBR4 138 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-343 | FROM->TO | 509059 CHEROKE4 138 509087 TATUM 4 138 1 | B | 350 | 0.10676 | 114.6003 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 509059 CHEROKE4 138 509087 TATUM 4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | FROM->TO | 508596 BRANDYBR4 138 509092 EASTON 4 138 1 | B | 575 | 0.20667 | 114.6867 | P12:345:AEPW:PIRKEY7:DIANA7::: | TDF Impact | Rebuild line 508596 BRANDYBR4 138 509092 EASTON 4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | FROM->TO | 508562 PIRKEY 4 138 508596 BRANDYBR4 138 1 | B | 575 | 0.20667 | 114.7799 | P12:345:AEPW:PIRKEY7:DIANA7::: | TDF Impact | Rebuild line 508562 PIRKEY 4 138 508596 BRANDYBR4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | FROM->TO | 508596 BRANDYBR4 138 509092 EASTON 4 138 1 | B | 575 | 0.20512 | 114.8054 | P23:345:AEPW:PIRKEY CB 13430 NBTB:::: | TDF Impact | Rebuild line 508596 BRANDYBR4 138 509092 EASTON 4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | FROM->TO | 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.37797 | 114.8273 | P23:345:AEPW:WELSH CB 10610 NBTB:::: | TDF Impact | Rebuild line 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | FROM->TO | 508562 PIRKEY 4 138 508596 BRANDYBR4 138 1 | B | 575 | 0.20512 | 114.8987 | P23:345:AEPW:PIRKEY CB 13430 NBTB:::: | TDF Impact | Rebuild line 508562 PIRKEY 4 138 508596 BRANDYBR4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.14843 | 115.5426 | Single 514809 JOHNCO7 345 787110 G24-338-TAP 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.14843 | 115.6069 | P42:345:OKGE:SB_JOCO7311:::EHV: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.15615 | 117.3852 | P22:345:EES:MUSKOGE7!:::EHV: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-343 | FROM->TO | 509059 CHEROKE4 138 509087 TATUM 4 138 1 | B | 350 | 0.10681 | 119.3858 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 509059 CHEROKE4 138 509087 TATUM 4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.17117 | 120.547 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | FROM->TO | 508566 SABMINT4 138 508569 SEMRSHL4 138 1 | B | 272 | 0.16715 | 120.6323 | P12:345:AEPW:PIRKEY7:DIANA7::: | Cumulative Impact | Rebuild line 508566 SABMINT4 138 508569 SEMRSHL4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | FROM->TO | 508566 SABMINT4 138 508569 SEMRSHL4 138 1 | B | 272 | 0.16624 | 120.7719 | P23:345:AEPW:PIRKEY CB 13430 NBTB:::: | Cumulative Impact | Rebuild line 508566 SABMINT4 138 508569 SEMRSHL4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.17696 | 121.1336 | Single 510907 PITTSB-7 345 515422 C-RIVER7 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | FROM->TO | 508566 SABMINT4 138 508569 SEMRSHL4 138 1 | B | 272 | 0.16602 | 122.2855 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | Cumulative Impact | Rebuild line 508566 SABMINT4 138 508569 SEMRSHL4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | FROM->TO | 508566 SABMINT4 138 508569 SEMRSHL4 138 1 | B | 272 | 0.16629 | 125.2491 | P12:345:AEPW:PIRKEY7:DIANA7::: | Cumulative Impact | Rebuild line 508566 SABMINT4 138 508569 SEMRSHL4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | FROM->TO | 508566 SABMINT4 138 508569 SEMRSHL4 138 1 | B | 272 | 0.16538 | 125.4088 | P23:345:AEPW:PIRKEY CB 13430 NBTB:::: | Cumulative Impact | Rebuild line 508566 SABMINT4 138 508569 SEMRSHL4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.1746 | 126.6467 | Single 510907 PITTSB-7 345 515422 C-RIVER7 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | FROM->TO | 508566 SABMINT4 138 508569 SEMRSHL4 138 1 | B | 272 | 0.16525 | 127.4298 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | Cumulative Impact | Rebuild line 508566 SABMINT4 138 508569 SEMRSHL4 138 1
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-343 | FROM->TO | 507732 GENMOTR4 138 507759 SW SHV 4 138 1 | B | 234 | 0.059731 | 130.7071 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 507732 GENMOTR4 138 507759 SW SHV 4 138 1
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-343 | FROM->TO | 507727 FLOURNY4 138 507732 GENMOTR4 138 1 | B | 234 | 0.059731 | 131.1509 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 507727 FLOURNY4 138 507732 GENMOTR4 138 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-343 | FROM->TO | 507732 GENMOTR4 138 507759 SW SHV 4 138 1 | B | 188 | 0.059572 | 177.8938 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 507732 GENMOTR4 138 507759 SW SHV 4 138 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-343 | FROM->TO | 507727 FLOURNY4 138 507732 GENMOTR4 138 1 | B | 188 | 0.059572 | 178.6318 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 507727 FLOURNY4 138 507732 GENMOTR4 138 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-343 | FROM->TO | 507732 GENMOTR4 138 507759 SW SHV 4 138 1 | B | 188 | 0.059932 | 185.2751 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 507732 GENMOTR4 138 507759 SW SHV 4 138 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-343 | FROM->TO | 507727 FLOURNY4 138 507732 GENMOTR4 138 1 | B | 188 | 0.059932 | 185.8438 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 507727 FLOURNY4 138 507732 GENMOTR4 138 1
Thermal | 04ALL | 1 | 26SP | T1 | GEN-2024-344 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.043208 | 103.0993 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T1 | GEN-2024-344 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.044849 | 103.3038 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-344 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | A | 1187 | 0.070083 | 103.8656 | System Intact | TDF Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-344 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.076508 | 104.9177 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-344 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.078681 | 106.1409 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-344 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.07567 | 106.3238 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-344 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.075281 | 106.5158 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-344 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.078023 | 107.841 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-344 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.075281 | 108.059 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-344 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.078023 | 109.5335 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-344 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.078023 | 109.534 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-344 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.078023 | 112.0538 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-344 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.053252 | 114.5102 | System Intact | TDF Impact | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-344 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.045122 | 114.6214 | System Intact | TDF Impact | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-344 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.078023 | 116.5975 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-344 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.054918 | 119.3706 | System Intact | TDF Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-344 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.054918 | 119.3706 | System Intact | TDF Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-344 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.054918 | 119.3706 | System Intact | TDF Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-344 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.054314 | 119.5141 | System Intact | TDF Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-344 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.054314 | 119.5141 | System Intact | TDF Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-344 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.054314 | 119.5141 | System Intact | TDF Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-344 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.059221 | 136.5828 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-344 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.059221 | 136.5828 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-344 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.059221 | 136.5828 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-344 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.058869 | 136.8919 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-344 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.058869 | 136.8919 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-344 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.058869 | 136.8919 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-344 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.059552 | 136.9237 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-344 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.059552 | 136.9237 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-344 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.059552 | 136.9237 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-344 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.058699 | 139.3736 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-344 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.058699 | 139.3736 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-344 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.058699 | 139.3736 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-344 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.062452 | 140.3415 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-344 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.062452 | 140.3415 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-344 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.062452 | 140.3415 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-344 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.061203 | 140.6152 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-344 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.061203 | 140.6152 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-344 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.061203 | 140.6152 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-344 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.061874 | 141.6076 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-344 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.061874 | 141.6076 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-344 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.061874 | 141.6076 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-344 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.060556 | 142.5086 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-344 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.060556 | 142.5086 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-344 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.060556 | 142.5086 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-344 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.061919 | 142.6431 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-344 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.061919 | 142.6431 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-344 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.061919 | 142.6431 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-344 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.061043 | 142.7223 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-344 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.061043 | 142.7223 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-344 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.061043 | 142.7223 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-344 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.060614 | 143.2233 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-344 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.060614 | 143.2233 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-344 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.060614 | 143.2233 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-344 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.059745 | 143.8401 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-344 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.059745 | 143.8401 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-344 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.059745 | 143.8401 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-344 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.061919 | 145.1309 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-344 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.061919 | 145.1309 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-344 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.061919 | 145.1309 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-344 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.061919 | 145.1356 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-344 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.061919 | 145.1356 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-344 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.061919 | 145.1356 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-344 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.060614 | 145.7578 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-344 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.060614 | 145.7578 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-344 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.060614 | 145.7578 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-344 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.060614 | 145.7646 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-344 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.060614 | 145.7646 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-344 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.060614 | 145.7646 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-344 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.061919 | 148.805 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-344 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.061919 | 148.805 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-344 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.061919 | 148.805 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-344 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.060614 | 149.8057 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-344 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.060614 | 149.8057 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-344 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.060614 | 149.8057 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-344 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.061919 | 155.6146 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-344 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.061919 | 155.6146 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-344 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.061919 | 155.6146 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-344 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.060614 | 157.3662 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-344 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.060614 | 157.3662 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-344 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.060614 | 157.3662 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-352 | FROM->TO | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.065665 | 104.394 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-352 | FROM->TO | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.073357 | 111.8275 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T1 | GEN-2024-360 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.032074 | 103.3038 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-360 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | A | 1187 | 0.048731 | 103.8656 | System Intact | TDF Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-360 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.053959 | 104.9177 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-360 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.05626 | 106.1409 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-360 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.053287 | 106.3238 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-360 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.051964 | 106.5158 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-360 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.055602 | 107.841 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-360 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.051964 | 108.059 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-360 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.055602 | 109.5335 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-360 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.055602 | 109.534 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-360 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.055602 | 112.0538 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-360 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.051239 | 114.5102 | System Intact | TDF Impact | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-360 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.044936 | 114.6214 | System Intact | TDF Impact | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-360 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.055602 | 116.5975 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-360 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.040063 | 119.3706 | System Intact | TDF Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-360 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.040063 | 119.3706 | System Intact | TDF Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-360 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.040063 | 119.3706 | System Intact | TDF Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-360 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.037146 | 119.5141 | System Intact | TDF Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-360 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.037146 | 119.5141 | System Intact | TDF Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-360 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.037146 | 119.5141 | System Intact | TDF Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T1 | GEN-2024-361 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.039261 | 103.0993 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T1 | GEN-2024-361 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.042101 | 103.3038 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-361 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | A | 1187 | 0.064716 | 103.8656 | System Intact | TDF Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-361 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.071255 | 104.9177 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-361 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.074833 | 106.1409 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-361 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.070467 | 106.3238 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-361 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.070322 | 106.5158 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-361 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.074175 | 107.841 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-361 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.070322 | 108.059 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-361 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.074175 | 109.5335 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-361 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.074175 | 109.534 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-361 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.074175 | 112.0538 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-361 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.055684 | 114.5102 | System Intact | TDF Impact | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-361 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.049707 | 114.6214 | System Intact | TDF Impact | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-361 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.074175 | 116.5975 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-361 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.051669 | 119.3706 | System Intact | TDF Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-361 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.051669 | 119.3706 | System Intact | TDF Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-361 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.051669 | 119.3706 | System Intact | TDF Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-361 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.048912 | 119.5141 | System Intact | TDF Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-361 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.048912 | 119.5141 | System Intact | TDF Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-361 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.048912 | 119.5141 | System Intact | TDF Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-361 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.056265 | 136.5828 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-361 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.056265 | 136.5828 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-361 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.056265 | 136.5828 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-361 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.053978 | 136.8919 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-361 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.053978 | 136.8919 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-361 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.053978 | 136.8919 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-361 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.05693 | 136.9237 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-361 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.05693 | 136.9237 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-361 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.05693 | 136.9237 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-361 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.053508 | 139.3736 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-361 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.053508 | 139.3736 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-361 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.053508 | 139.3736 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-361 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.060429 | 140.3415 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-361 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.060429 | 140.3415 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-361 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.060429 | 140.3415 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-361 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.056977 | 140.6152 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-361 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.056977 | 140.6152 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-361 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.056977 | 140.6152 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-361 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.058741 | 141.6076 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-361 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.058741 | 141.6076 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-361 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.058741 | 141.6076 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-361 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.057503 | 142.5086 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-361 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.057503 | 142.5086 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-361 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.057503 | 142.5086 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-361 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.059896 | 142.6431 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-361 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.059896 | 142.6431 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-361 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.059896 | 142.6431 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-361 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.055485 | 142.7223 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-361 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.055485 | 142.7223 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-361 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.055485 | 142.7223 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-361 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.056388 | 143.2233 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-361 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.056388 | 143.2233 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-361 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.056388 | 143.2233 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-361 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.054377 | 143.8401 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-361 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.054377 | 143.8401 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-361 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.054377 | 143.8401 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-361 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.059896 | 145.1309 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-361 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.059896 | 145.1309 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-361 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.059896 | 145.1309 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-361 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.059896 | 145.1356 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-361 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.059896 | 145.1356 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-361 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.059896 | 145.1356 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-361 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.056388 | 145.7578 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-361 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.056388 | 145.7578 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-361 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.056388 | 145.7578 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-361 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.056388 | 145.7646 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-361 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.056388 | 145.7646 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-361 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.056388 | 145.7646 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-361 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.059896 | 148.805 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-361 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.059896 | 148.805 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-361 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.059896 | 148.805 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-361 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.056388 | 149.8057 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-361 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.056388 | 149.8057 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-361 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.056388 | 149.8057 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-361 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.059896 | 155.6146 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-361 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.059896 | 155.6146 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-361 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.059896 | 155.6146 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-361 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.056388 | 157.3662 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-361 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.056388 | 157.3662 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-361 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.056388 | 157.3662 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-362 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | A | 1187 | 0.037951 | 103.8656 | System Intact | TDF Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-362 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.057995 | 114.5102 | System Intact | TDF Impact | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-362 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.05271 | 114.6214 | System Intact | TDF Impact | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-362 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.032941 | 119.3706 | System Intact | TDF Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-362 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.032941 | 119.3706 | System Intact | TDF Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-362 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.032941 | 119.3706 | System Intact | TDF Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-370 | FROM->TO | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.067484 | 104.394 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-370 | FROM->TO | 541204 SMTHVL 5 161 541221 PLTCTY 5 161 1 | B | 297 | 1 | 109.8349 | Single 541203 NASHUA5 161 541204 SMTHVL5 161 1 | TDF Impact | Rebuild line 541204 SMTHVL 5 161 541221 PLTCTY 5 161 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-370 | FROM->TO | 541214 TWA 5 161 541318 NCONGRS5 161 1 | B | 193 | 0.50058 | 109.9324 | Single 541203 NASHUA5 161 541204 SMTHVL5 161 1 | TDF Impact | Rebuild line 541214 TWA 5 161 541318 NCONGRS5 161 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-370 | FROM->TO | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.075433 | 111.8275 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-370 | FROM->TO | 541204 SMTHVL 5 161 541221 PLTCTY 5 161 1 | B | 261 | 1 | 123.916 | Single 541203 NASHUA5 161 541204 SMTHVL5 161 1 | TDF Impact | Rebuild line 541204 SMTHVL 5 161 541221 PLTCTY 5 161 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-370 | FROM->TO | 541204 SMTHVL 5 161 541221 PLTCTY 5 161 1 | B | 261 | 1 | 124.0382 | Single 541203 NASHUA5 161 541204 SMTHVL5 161 1 | TDF Impact | Rebuild line 541204 SMTHVL 5 161 541221 PLTCTY 5 161 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-372 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.079313 | 100.5915 | P23:345:MEC:HIGHLAND:903::EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-372 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.079313 | 100.6154 | P23:345:MEC:HIGHLAND:902::EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-372 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.067479 | 100.6843 | P12:230.0:UMZ:# N-1 #:: LINE TWIN CH4-SIOUXCY4-1 :HV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-372 | FROM->TO | 652564 SIOUXCY3 345 3WXFMR 652:652: SC2 KU1B 230 1 | B | 750 | 0.052001 | 100.7724 | P23:345:XEL:396 BKR SPK:::EHV: | TDF Impact | Add 3-winding transformer 652305 SIOUXC29 13 652552 SIOUXCY2 230 652564 SIOUXCY3 345 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-372 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.079313 | 101.5782 | Single 635368 OBRIEN3 345 635400 HIGHLAND3 345 1 | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-372 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.079313 | 101.5782 | P12:345:MEC:OBRIEN:HIGHLAND:1REACTOR:EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-372 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.080161 | 103.0767 | P23:345:MEC:OBRIEN:903::EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-372 | FROM->TO | 635200 RAUN 3 345 652564 SIOUXCY3 345 1 | B | 981 | 0.080326 | 104.0624 | P23:345:MEC:OBRIEN:906::EHV: | TDF Impact | Rebuild line 635200 RAUN 3 345 652564 SIOUXCY3 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-373 | FROM->TO | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | A | 1187 | 0.037721 | 103.8656 | System Intact | TDF Impact | Rebuild line 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-373 | FROM->TO | 511468 L.E.S.-7 345 3WXFMR 520:LES 5 345 2 | B | 515 | 0.035707 | 114.3077 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-373 | FROM->TO | 511468 L.E.S.-7 345 3WXFMR 520:LES 5 345 2 | B | 515 | 0.036292 | 114.3448 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-373 | FROM->TO | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.034779 | 114.5102 | System Intact | TDF Impact | Rebuild line 515543 RENFROW7 345 763421 G18-128-TAP 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-373 | FROM->TO | 511468 L.E.S.-7 345 3WXFMR 520:LES 5 345 2 | B | 515 | 0.033171 | 115.3782 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | TDF Impact | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-373 | FROM->TO | 511468 L.E.S.-7 345 3WXFMR 520:LES 5 345 2 | B | 515 | 0.033889 | 116.8526 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | TDF Impact | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-373 | FROM->TO | 508359 WELSH 7 345 508841 WILKES 7 345 1 | B | 1000 | 0.12764 | 116.8554 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | Cumulative Impact | Rebuild line 508359 WELSH 7 345 508841 WILKES 7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-373 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.031488 | 119.3706 | System Intact | TDF Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-373 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.031488 | 119.3706 | System Intact | TDF Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-373 | FROM->TO | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.031488 | 119.3706 | System Intact | TDF Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 00NR | 1 | 29WP | T1 | GEN-2024-374 | FROM->TO | 652497 MAURINE4 230 659351 BISON___-GE4 230 1 | B | 398 | 0.099352 | 100.8995 | Single 652424 BELFELD3 345 800121 MAURINE2 345 1 | TDF Impact | Rebuild line 652497 MAURINE4 230 659351 BISON___-GE4 230 1
Thermal | 00NR | 1 | 29WP | T1 | GEN-2024-374 | FROM->TO | 652573 STEGALL 4 230 652873 STEGALL-LNX3 230 Z | B | 349 | 0.15179 | 101.6614 | Single 659131 LARAMIE_-MB3 345 800120 UNDERWOOD2 345 1 | TDF Impact | Rebuild line 652573 STEGALL 4 230 652873 STEGALL-LNX3 230 Z
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-374 | FROM->TO | 640404 WAYSIDE 4 230 652484 NUNDRWD4 230 1 | B | 352 | 0.20091 | 102.1541 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | TDF Impact | Rebuild line 640404 WAYSIDE 4 230 652484 NUNDRWD4 230 1
Thermal | 00NR | 1 | 29SP | T1 | GEN-2024-374 | FROM->TO | 653570 ALIANCE 7 115 659815 BOXBUTE-TS7 115 1 | B | 91 | 0.045206 | 105.5047 | P12:230.0:UMZ:# N-1 #:: LINE WAYSIDE 4-STEGALL-LNX3-1 :HV: | TDF Impact | Rebuild line 653570 ALIANCE 7 115 659815 BOXBUTE-TS7 115 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-374 | FROM->TO | 653312 MORRILL 7 115 659814 SNAKECK-TS7 115 1 | B | 109 | 0.069673 | 105.5966 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR_:HV: | TDF Impact | 640_NPPD_Rebuild_Morill_Gering_115.idv : 2024 ITP, PID: TBD, ISD: Unknown
Thermal | 00NR | 1 | 29SP | T1 | GEN-2024-374 | FROM->TO | 653570 ALIANCE 7 115 659815 BOXBUTE-TS7 115 1 | B | 91 | 0.045206 | 105.6007 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR_:HV: | TDF Impact | Rebuild line 653570 ALIANCE 7 115 659815 BOXBUTE-TS7 115 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-374 | FROM->TO | 653312 MORRILL 7 115 659814 SNAKECK-TS7 115 1 | B | 109 | 0.069673 | 105.6073 | P12:230.0:UMZ:# N-1 #:: LINE STEGALL 4-STEGALL-LNX3-Z :HV: | TDF Impact | 640_NPPD_Rebuild_Morill_Gering_115.idv : 2024 ITP, PID: TBD, ISD: Unknown
Thermal | 00NR | 1 | 29SP | T1 | GEN-2024-374 | FROM->TO | 653570 ALIANCE 7 115 659815 BOXBUTE-TS7 115 1 | B | 91 | 0.045206 | 105.6156 | P12:230.0:UMZ:# N-1 #:: LINE STEGALL 4-STEGALL-LNX3-Z :HV: | TDF Impact | Rebuild line 653570 ALIANCE 7 115 659815 BOXBUTE-TS7 115 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-374 | FROM->TO | 653312 MORRILL 7 115 659814 SNAKECK-TS7 115 1 | B | 109 | 0.069673 | 105.6302 | P12:230.0:UMZ:# N-1 #:: LINE WAYSIDE 4-STEGALL-LNX3-1 :HV: | TDF Impact | 640_NPPD_Rebuild_Morill_Gering_115.idv : 2024 ITP, PID: TBD, ISD: Unknown
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-374 | FROM->TO | 652573 STEGALL 4 230 652873 STEGALL-LNX3 230 Z | B | 320 | 0.14972 | 108.7838 | Single 659131 LARAMIE_-MB3 345 800120 UNDERWOOD2 345 1 | TDF Impact | Rebuild line 652573 STEGALL 4 230 652873 STEGALL-LNX3 230 Z
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-374 | FROM->TO | 640404 WAYSIDE 4 230 652484 NUNDRWD4 230 1 | B | 352 | 0.17033 | 111.9467 | Single 659131 LARAMIE_-MB3 345 800120 UNDERWOOD2 345 1 | TDF Impact | Rebuild line 640404 WAYSIDE 4 230 652484 NUNDRWD4 230 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-374 | FROM->TO | 640338 SCOTBLF 7 115 653313 GERING TAP 115 1 | B | 109 | 0.069673 | 113.0132 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR_:HV: | TDF Impact | 640_NPPD_Rebuild_Scotsbluff_Gering_115.idv : 2024 ITP, PID: 94819, NTC, ISD: Unknown
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-374 | FROM->TO | 640338 SCOTBLF 7 115 653313 GERING TAP 115 1 | B | 109 | 0.069673 | 113.0223 | P12:230.0:UMZ:# N-1 #:: LINE STEGALL 4-STEGALL-LNX3-Z :HV: | TDF Impact | 640_NPPD_Rebuild_Scotsbluff_Gering_115.idv : 2024 ITP, PID: 94819, NTC, ISD: Unknown
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-374 | FROM->TO | 640338 SCOTBLF 7 115 653313 GERING TAP 115 1 | B | 109 | 0.069673 | 113.076 | P12:230.0:UMZ:# N-1 #:: LINE WAYSIDE 4-STEGALL-LNX3-1 :HV: | TDF Impact | 640_NPPD_Rebuild_Scotsbluff_Gering_115.idv : 2024 ITP, PID: 94819, NTC, ISD: Unknown
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-374 | FROM->TO | 652484 NUNDRWD4 230 652884 NUNDRWD-LNX3 230 Z | B | 398 | 0.11683 | 115.6175 | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 | TDF Impact | Rebuild line 652484 NUNDRWD4 230 652884 NUNDRWD-LNX3 230 Z
Thermal | 00NR | 1 | 26SP | T1 | GEN-2024-374 | FROM->TO | 653312 MORRILL 7 115 659814 SNAKECK-TS7 115 1 | B | 109 | 0.077263 | 118.1191 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR_:HV: | TDF Impact | Rebuild line 653312 MORRILL 7 115 659814 SNAKECK-TS7 115 1
Thermal | 00NR | 1 | 26SP | T1 | GEN-2024-374 | FROM->TO | 653312 MORRILL 7 115 659814 SNAKECK-TS7 115 1 | B | 109 | 0.077263 | 118.1328 | P12:230.0:UMZ:# N-1 #:: LINE STEGALL 4-STEGALL-LNX3-Z :HV: | TDF Impact | Rebuild line 653312 MORRILL 7 115 659814 SNAKECK-TS7 115 1
Thermal | 00NR | 1 | 26SP | T1 | GEN-2024-374 | FROM->TO | 653312 MORRILL 7 115 659814 SNAKECK-TS7 115 1 | B | 109 | 0.077263 | 118.1767 | P12:230.0:UMZ:# N-1 #:: LINE WAYSIDE 4-STEGALL-LNX3-1 :HV: | TDF Impact | Rebuild line 653312 MORRILL 7 115 659814 SNAKECK-TS7 115 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | FROM->TO | 508548 KNOXLEE4 138 509059 CHEROKE4 138 1 | B | 350 | 0.077151 | 100.1039 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 508548 KNOXLEE4 138 509059 CHEROKE4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | FROM->TO | 508596 BRANDYBR4 138 509092 EASTON 4 138 1 | B | 575 | 0.1018 | 100.139 | Single 508595 HALLSVLS4 138 775840 G23-193-TAP 138 1 | Cumulative Impact | Rebuild line 508596 BRANDYBR4 138 509092 EASTON 4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | FROM->TO | 508562 PIRKEY 4 138 508596 BRANDYBR4 138 1 | B | 575 | 0.1018 | 100.2299 | Single 508595 HALLSVLS4 138 775840 G23-193-TAP 138 1 | Cumulative Impact | Rebuild line 508562 PIRKEY 4 138 508596 BRANDYBR4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | FROM->TO | 509083 ROKHILL4 138 509102 NEWPROS4 138 1 | B | 289 | 0.053925 | 100.3166 | Single 334197 7ROCKYCRK% 345 783930 G24-232-TAP 345 1 | Cumulative Impact | Rebuild line 509083 ROKHILL4 138 509102 NEWPROS4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | FROM->TO | 514809 JOHNCO 7 345 3WXFMR 524:524:JOHNCOT3 345 3 | B | 478 | 0.05376 | 100.3203 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | FROM->TO | 509083 ROKHILL4 138 509102 NEWPROS4 138 1 | B | 289 | 0.053925 | 100.4359 | P23:345:EES::7ROCKYCRK%:1:EHV: | Cumulative Impact | Rebuild line 509083 ROKHILL4 138 509102 NEWPROS4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | FROM->TO | 508563 PIRKEY 7 345 508832 DIANA 7 345 1 | B | 1306 | 0.64541 | 100.4992 | P23:345:AEPW:TENASKA CB 12840 NBTB:::: | TDF Impact | Rebuild line 508563 PIRKEY 7 345 508832 DIANA 7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | FROM->TO | 508563 PIRKEY 7 345 508832 DIANA 7 345 1 | B | 1306 | 0.64541 | 100.4992 | P22:345:EES:TENRUSK7!:::EHV: | TDF Impact | Rebuild line 508563 PIRKEY 7 345 508832 DIANA 7 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-377 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.17782 | 100.5325 | Single 510907 PITTSB-7 345 515422 C-RIVER7 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | FROM->TO | 508563 PIRKEY 7 345 508832 DIANA 7 345 1 | B | 1306 | 0.64541 | 100.6276 | P23:345:AEPW:TENASKA CB 12860 NBTB:::: | TDF Impact | Rebuild line 508563 PIRKEY 7 345 508832 DIANA 7 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-377 | FROM->TO | 508566 SABMINT4 138 508569 SEMRSHL4 138 1 | B | 333 | 0.16881 | 100.7592 | P12:345:AEPW:PIRKEY7:DIANA7::: | Cumulative Impact | Rebuild line 508566 SABMINT4 138 508569 SEMRSHL4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | FROM->TO | 508563 PIRKEY 7 345 508832 DIANA 7 345 1 | B | 1306 | 0.64453 | 100.8185 | P12:345:EES:LEBROCK7!:TENRUSK7!:1:EHV: | TDF Impact | Rebuild line 508563 PIRKEY 7 345 508832 DIANA 7 345 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-377 | FROM->TO | 508808 LONGWD 4 138 508816 OAKPH 4 138 1 | B | 395 | 0.054599 | 100.8572 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 508808 LONGWD 4 138 508816 OAKPH 4 138 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-377 | FROM->TO | 508566 SABMINT4 138 508569 SEMRSHL4 138 1 | B | 333 | 0.16909 | 100.8957 | P23:345:AEPW:PIRKEY CB 13430 NBTB:::: | Cumulative Impact | Rebuild line 508566 SABMINT4 138 508569 SEMRSHL4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | FROM->TO | 508562 PIRKEY 4 138 508566 SABMINT4 138 1 | B | 340 | 0.16789 | 101.0119 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | Cumulative Impact | Rebuild line 508562 PIRKEY 4 138 508566 SABMINT4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | FROM->TO | 508298 LYDIA 7 345 510911 VALIANT7 345 1 | B | 1176 | 0.33652 | 101.2347 | P23:345:AEPW:VALLIANT CB 3413A NBTB:::: | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | FROM->TO | 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.31567 | 101.4921 | Single 337376 7SAREPTA% 345 788340 G24-379-TAP 345 1 | TDF Impact | Rebuild line 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-377 | FROM->TO | 508562 PIRKEY 4 138 508566 SABMINT4 138 1 | B | 395 | 0.18333 | 101.7389 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | Cumulative Impact | Rebuild line 508562 PIRKEY 4 138 508566 SABMINT4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | FROM->TO | 508298 LYDIA 7 345 510911 VALIANT7 345 1 | B | 1176 | 0.37145 | 102.11 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB:::: | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-377 | FROM->TO | 508808 LONGWD 4 138 508816 OAKPH 4 138 1 | B | 395 | 0.055003 | 102.188 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 508808 LONGWD 4 138 508816 OAKPH 4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | FROM->TO | 508563 PIRKEY 7 345 508832 DIANA 7 345 1 | B | 1306 | 0.64541 | 102.3045 | P23:345:AEPW:TENASKA CB 12850 NBTB:::: | TDF Impact | Rebuild line 508563 PIRKEY 7 345 508832 DIANA 7 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | FROM->TO | 508298 LYDIA 7 345 510911 VALIANT7 345 1 | B | 1176 | 0.36697 | 102.3256 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB:::: | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-377 | FROM->TO | 508548 KNOXLEE4 138 509059 CHEROKE4 138 1 | B | 395 | 0.10795 | 102.6963 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 508548 KNOXLEE4 138 509059 CHEROKE4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | FROM->TO | 508298 LYDIA 7 345 510911 VALIANT7 345 1 | B | 1176 | 0.36898 | 102.7311 | Single 508072 NWTXARK7 345 764520 G20-020-TAP 345 1 | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-377 | FROM->TO | 508566 SABMINT4 138 508569 SEMRSHL4 138 1 | B | 333 | 0.16776 | 102.9158 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | Cumulative Impact | Rebuild line 508566 SABMINT4 138 508569 SEMRSHL4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | FROM->TO | 337909 8ANO% 500 515305 FTSMITH8 500 1 | B | 1299 | 0.17236 | 102.9598 | P52:345:AEPW:NR4PITTSB-7:::: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | FROM->TO | 508298 LYDIA 7 345 510911 VALIANT7 345 1 | B | 1176 | 0.36898 | 103.2181 | Single 510911 VALIANT7 345 764520 G20-020-TAP 345 1 | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | FROM->TO | 508562 PIRKEY 4 138 508566 SABMINT4 138 1 | B | 340 | 0.16812 | 103.3905 | P12:345:AEPW:PIRKEY7:DIANA7::: | Cumulative Impact | Rebuild line 508562 PIRKEY 4 138 508566 SABMINT4 138 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-377 | FROM->TO | 509059 CHEROKE4 138 509087 TATUM 4 138 1 | B | 350 | 0.090489 | 103.4947 | Single 334197 7ROCKYCRK% 345 783930 G24-232-TAP 345 1 | Cumulative Impact | Rebuild line 509059 CHEROKE4 138 509087 TATUM 4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | FROM->TO | 508562 PIRKEY 4 138 508566 SABMINT4 138 1 | B | 340 | 0.1684 | 103.5186 | P23:345:AEPW:PIRKEY CB 13430 NBTB:::: | Cumulative Impact | Rebuild line 508562 PIRKEY 4 138 508566 SABMINT4 138 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-377 | FROM->TO | 509059 CHEROKE4 138 509087 TATUM 4 138 1 | B | 350 | 0.090489 | 103.5551 | P23:345:EES::7ROCKYCRK%:1:EHV: | Cumulative Impact | Rebuild line 509059 CHEROKE4 138 509087 TATUM 4 138 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-377 | FROM->TO | 509059 CHEROKE4 138 509087 TATUM 4 138 1 | A | 241 | 0.075261 | 103.7761 | System Intact | TDF Impact | Rebuild line 509059 CHEROKE4 138 509087 TATUM 4 138 1
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-377 | FROM->TO | 509059 CHEROKE4 138 509087 TATUM 4 138 1 | B | 379 | 0.10795 | 103.8167 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 509059 CHEROKE4 138 509087 TATUM 4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | FROM->TO | 508563 PIRKEY 7 345 508832 DIANA 7 345 1 | B | 1306 | 0.63815 | 103.8202 | P12:345:EES:TENRUSK7!:CROCKET7%:1:EHV: | TDF Impact | Rebuild line 508563 PIRKEY 7 345 508832 DIANA 7 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.16973 | 103.8575 | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-377 | FROM->TO | 508548 KNOXLEE4 138 509059 CHEROKE4 138 1 | B | 395 | 0.10789 | 103.881 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 508548 KNOXLEE4 138 509059 CHEROKE4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | FROM->TO | 508563 PIRKEY 7 345 508832 DIANA 7 345 1 | B | 1306 | 0.64566 | 104.1826 | P23:345:EES::7ROCKYCRK%:1:EHV: | TDF Impact | Rebuild line 508563 PIRKEY 7 345 508832 DIANA 7 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | FROM->TO | 508563 PIRKEY 7 345 508832 DIANA 7 345 1 | B | 1306 | 0.64566 | 104.1965 | Single 334197 7ROCKYCRK% 345 783930 G24-232-TAP 345 1 | TDF Impact | Rebuild line 508563 PIRKEY 7 345 508832 DIANA 7 345 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-377 | FROM->TO | 509059 CHEROKE4 138 509087 TATUM 4 138 1 | B | 350 | 0.1349 | 104.4359 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | Cumulative Impact | Rebuild line 509059 CHEROKE4 138 509087 TATUM 4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.14968 | 104.6172 | P23:345:AEPW:PITTSBURG CB 3433A NBTB:::: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | FROM->TO | 508563 PIRKEY 7 345 508832 DIANA 7 345 1 | B | 1306 | 0.64257 | 104.8435 | Single 509241 CROCKET7 345 783930 G24-232-TAP 345 1 | TDF Impact | Rebuild line 508563 PIRKEY 7 345 508832 DIANA 7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | FROM->TO | 508298 LYDIA 7 345 510911 VALIANT7 345 1 | B | 1176 | 0.36852 | 104.9032 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB:::: | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | FROM->TO | 508298 LYDIA 7 345 510911 VALIANT7 345 1 | B | 1176 | 0.36388 | 105.0459 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB:::: | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | FROM->TO | 508562 PIRKEY 4 138 508566 SABMINT4 138 1 | B | 340 | 0.16711 | 105.1363 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | Cumulative Impact | Rebuild line 508562 PIRKEY 4 138 508566 SABMINT4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | FROM->TO | 337904 5RUSSELVL.S 161 505508 DARDANE5 161 1 | B | 396 | 0.050294 | 105.2411 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | FROM->TO | 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.37095 | 105.3575 | Single 508072 NWTXARK7 345 508359 WELSH7 345 1 | TDF Impact | Rebuild line 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | FROM->TO | 508563 PIRKEY 7 345 3WXFMR 520:PIRKEY 1 345 1 | B | 600 | 0.36411 | 105.446 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | TDF Impact | Add 3-winding transformer 508562 PIRKEY 4 138 508563 PIRKEY 7 345 508587 PIRKY1-1 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | FROM->TO | 508298 LYDIA 7 345 510911 VALIANT7 345 1 | B | 1176 | 0.36598 | 105.4715 | Single 508072 NWTXARK7 345 764520 G20-020-TAP 345 1 | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | FROM->TO | 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.37142 | 105.5739 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB:::: | TDF Impact | Rebuild line 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | FROM->TO | 508563 PIRKEY 7 345 3WXFMR 520:PIRKEY 1 345 1 | B | 600 | 0.36394 | 105.587 | P12:345:AEPW:PIRKEY7:DIANA7::: | TDF Impact | Add 3-winding transformer 508562 PIRKEY 4 138 508563 PIRKEY 7 345 508587 PIRKY1-1 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.14769 | 105.6255 | Single 510907 PITTSB-7 345 787110 G24-338-TAP 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | FROM->TO | 508563 PIRKEY 7 345 3WXFMR 520:PIRKEY 1 345 1 | B | 600 | 0.36464 | 105.7524 | P23:345:AEPW:PIRKEY CB 13430 NBTB:::: | TDF Impact | Add 3-winding transformer 508562 PIRKEY 4 138 508563 PIRKEY 7 345 508587 PIRKY1-1 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-377 | FROM->TO | 508563 PIRKEY 7 345 3WXFMR 520:PIRKEY 1 345 1 | B | 600 | 0.36551 | 107.221 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | TDF Impact | Add 3-winding transformer 508562 PIRKEY 4 138 508563 PIRKEY 7 345 508587 PIRKY1-1 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-377 | FROM->TO | 508563 PIRKEY 7 345 3WXFMR 520:PIRKEY 1 345 1 | B | 600 | 0.36534 | 107.3935 | P12:345:AEPW:PIRKEY7:DIANA7::: | TDF Impact | Add 3-winding transformer 508562 PIRKEY 4 138 508563 PIRKEY 7 345 508587 PIRKY1-1 13 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-377 | FROM->TO | 509059 CHEROKE4 138 509087 TATUM 4 138 1 | A | 241 | 0.075257 | 107.463 | System Intact | TDF Impact | Rebuild line 509059 CHEROKE4 138 509087 TATUM 4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | FROM->TO | 508298 LYDIA 7 345 510911 VALIANT7 345 1 | B | 1176 | 0.36598 | 107.4903 | Single 510911 VALIANT7 345 764520 G20-020-TAP 345 1 | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-377 | FROM->TO | 508563 PIRKEY 7 345 3WXFMR 520:PIRKEY 1 345 1 | B | 600 | 0.36603 | 107.566 | P23:345:AEPW:PIRKEY CB 13430 NBTB:::: | TDF Impact | Add 3-winding transformer 508562 PIRKEY 4 138 508563 PIRKEY 7 345 508587 PIRKY1-1 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.17467 | 107.6782 | 272864 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.17439 | 108.0084 | Single 515422 C-RIVER7 345 785850 G24-296-TAP 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | FROM->TO | 508563 PIRKEY 7 345 3WXFMR 520:PIRKEY 1 345 1 | B | 600 | 0.36603 | 108.1269 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | TDF Impact | Add 3-winding transformer 508562 PIRKEY 4 138 508563 PIRKEY 7 345 508587 PIRKY1-1 13 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-377 | FROM->TO | 508548 KNOXLEE4 138 509059 CHEROKE4 138 1 | B | 395 | 0.10794 | 108.1364 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 508548 KNOXLEE4 138 509059 CHEROKE4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | FROM->TO | 508563 PIRKEY 7 345 3WXFMR 520:PIRKEY 1 345 1 | B | 600 | 0.36584 | 108.244 | P12:345:AEPW:PIRKEY7:DIANA7::: | TDF Impact | Add 3-winding transformer 508562 PIRKEY 4 138 508563 PIRKEY 7 345 508587 PIRKY1-1 13 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-377 | FROM->TO | 509059 CHEROKE4 138 509087 TATUM 4 138 1 | B | 350 | 0.13468 | 108.3478 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | Cumulative Impact | Rebuild line 509059 CHEROKE4 138 509087 TATUM 4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | FROM->TO | 508563 PIRKEY 7 345 3WXFMR 520:PIRKEY 1 345 1 | B | 600 | 0.36653 | 108.3741 | P23:345:AEPW:PIRKEY CB 13430 NBTB:::: | TDF Impact | Add 3-winding transformer 508562 PIRKEY 4 138 508563 PIRKEY 7 345 508587 PIRKY1-1 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | FROM->TO | 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.36889 | 108.4857 | Single 508072 NWTXARK7 345 508359 WELSH7 345 1 | TDF Impact | Rebuild line 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | FROM->TO | 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.36915 | 108.6558 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB:::: | TDF Impact | Rebuild line 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | FROM->TO | 337904 5RUSSELVL.S 161 505508 DARDANE5 161 1 | B | 396 | 0.050088 | 108.6948 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | FROM->TO | 337904 5RUSSELVL.S 161 505508 DARDANE5 161 1 | B | 396 | 0.050038 | 108.894 | P42:500:OKGE:SB_FTTH8585:::EHV: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | FROM->TO | 508563 PIRKEY 7 345 508832 DIANA 7 345 1 | B | 1306 | 0.64257 | 109.3114 | P23:345:EES::7ROCKYCRK%:1:EHV: | TDF Impact | Rebuild line 508563 PIRKEY 7 345 508832 DIANA 7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | FROM->TO | 508563 PIRKEY 7 345 508832 DIANA 7 345 1 | B | 1306 | 0.64257 | 109.3236 | Single 334197 7ROCKYCRK% 345 783930 G24-232-TAP 345 1 | TDF Impact | Rebuild line 508563 PIRKEY 7 345 508832 DIANA 7 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.15435 | 110.0508 | P22:345:EES:MUSKOGE7!:::EHV: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.17073 | 110.6242 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.17005 | 111.1525 | Single 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | FROM->TO | 508596 BRANDYBR4 138 509092 EASTON 4 138 1 | B | 575 | 0.20896 | 111.2382 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | TDF Impact | Rebuild line 508596 BRANDYBR4 138 509092 EASTON 4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | FROM->TO | 508562 PIRKEY 4 138 508596 BRANDYBR4 138 1 | B | 575 | 0.20896 | 111.3326 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | TDF Impact | Rebuild line 508562 PIRKEY 4 138 508596 BRANDYBR4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | FROM->TO | 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.38218 | 111.4242 | P23:345:AEPW:WELSH CB 10610 NBTB:::: | TDF Impact | Rebuild line 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.14769 | 111.5464 | Single 514809 JOHNCO7 345 787110 G24-338-TAP 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | FROM->TO | 508596 BRANDYBR4 138 509092 EASTON 4 138 1 | B | 575 | 0.2086 | 111.5836 | P12:345:AEPW:PIRKEY7:DIANA7::: | TDF Impact | Rebuild line 508596 BRANDYBR4 138 509092 EASTON 4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.14769 | 111.595 | P42:345:OKGE:SB_JOCO7311:::EHV: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | FROM->TO | 508562 PIRKEY 4 138 508596 BRANDYBR4 138 1 | B | 575 | 0.2086 | 111.678 | P12:345:AEPW:PIRKEY7:DIANA7::: | TDF Impact | Rebuild line 508562 PIRKEY 4 138 508596 BRANDYBR4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.17005 | 111.7065 | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | FROM->TO | 508596 BRANDYBR4 138 509092 EASTON 4 138 1 | B | 575 | 0.20908 | 111.7191 | P23:345:AEPW:PIRKEY CB 13430 NBTB:::: | TDF Impact | Rebuild line 508596 BRANDYBR4 138 509092 EASTON 4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | FROM->TO | 508562 PIRKEY 4 138 508596 BRANDYBR4 138 1 | B | 575 | 0.20908 | 111.8135 | P23:345:AEPW:PIRKEY CB 13430 NBTB:::: | TDF Impact | Rebuild line 508562 PIRKEY 4 138 508596 BRANDYBR4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.1723 | 113.8068 | 272864 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.17197 | 114.1963 | Single 515422 C-RIVER7 345 785850 G24-296-TAP 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | FROM->TO | 508596 BRANDYBR4 138 509092 EASTON 4 138 1 | B | 575 | 0.21015 | 114.411 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | TDF Impact | Rebuild line 508596 BRANDYBR4 138 509092 EASTON 4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.17439 | 114.4578 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | FROM->TO | 508562 PIRKEY 4 138 508596 BRANDYBR4 138 1 | B | 575 | 0.21015 | 114.5042 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | TDF Impact | Rebuild line 508562 PIRKEY 4 138 508596 BRANDYBR4 138 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-377 | FROM->TO | 509059 CHEROKE4 138 509087 TATUM 4 138 1 | B | 350 | 0.10789 | 114.6003 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 509059 CHEROKE4 138 509087 TATUM 4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | FROM->TO | 508596 BRANDYBR4 138 509092 EASTON 4 138 1 | B | 575 | 0.20975 | 114.6867 | P12:345:AEPW:PIRKEY7:DIANA7::: | TDF Impact | Rebuild line 508596 BRANDYBR4 138 509092 EASTON 4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | FROM->TO | 508562 PIRKEY 4 138 508596 BRANDYBR4 138 1 | B | 575 | 0.20975 | 114.7799 | P12:345:AEPW:PIRKEY7:DIANA7::: | TDF Impact | Rebuild line 508562 PIRKEY 4 138 508596 BRANDYBR4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | FROM->TO | 508596 BRANDYBR4 138 509092 EASTON 4 138 1 | B | 575 | 0.21022 | 114.8054 | P23:345:AEPW:PIRKEY CB 13430 NBTB:::: | TDF Impact | Rebuild line 508596 BRANDYBR4 138 509092 EASTON 4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | FROM->TO | 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.38027 | 114.8273 | P23:345:AEPW:WELSH CB 10610 NBTB:::: | TDF Impact | Rebuild line 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | FROM->TO | 508562 PIRKEY 4 138 508596 BRANDYBR4 138 1 | B | 575 | 0.21022 | 114.8987 | P23:345:AEPW:PIRKEY CB 13430 NBTB:::: | TDF Impact | Rebuild line 508562 PIRKEY 4 138 508596 BRANDYBR4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.14895 | 115.5426 | Single 514809 JOHNCO7 345 787110 G24-338-TAP 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.14895 | 115.6069 | P42:345:OKGE:SB_JOCO7311:::EHV: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.15671 | 117.3852 | P22:345:EES:MUSKOGE7!:::EHV: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-377 | FROM->TO | 509059 CHEROKE4 138 509087 TATUM 4 138 1 | B | 350 | 0.10794 | 119.3858 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 509059 CHEROKE4 138 509087 TATUM 4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.17197 | 120.547 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | FROM->TO | 508566 SABMINT4 138 508569 SEMRSHL4 138 1 | B | 272 | 0.16898 | 120.6323 | P12:345:AEPW:PIRKEY7:DIANA7::: | Cumulative Impact | Rebuild line 508566 SABMINT4 138 508569 SEMRSHL4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | FROM->TO | 508566 SABMINT4 138 508569 SEMRSHL4 138 1 | B | 272 | 0.16926 | 120.7719 | P23:345:AEPW:PIRKEY CB 13430 NBTB:::: | Cumulative Impact | Rebuild line 508566 SABMINT4 138 508569 SEMRSHL4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.17779 | 121.1336 | Single 510907 PITTSB-7 345 515422 C-RIVER7 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | FROM->TO | 508566 SABMINT4 138 508569 SEMRSHL4 138 1 | B | 272 | 0.16789 | 122.2855 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | Cumulative Impact | Rebuild line 508566 SABMINT4 138 508569 SEMRSHL4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | FROM->TO | 508566 SABMINT4 138 508569 SEMRSHL4 138 1 | B | 272 | 0.16812 | 125.2491 | P12:345:AEPW:PIRKEY7:DIANA7::: | Cumulative Impact | Rebuild line 508566 SABMINT4 138 508569 SEMRSHL4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | FROM->TO | 508566 SABMINT4 138 508569 SEMRSHL4 138 1 | B | 272 | 0.1684 | 125.4088 | P23:345:AEPW:PIRKEY CB 13430 NBTB:::: | Cumulative Impact | Rebuild line 508566 SABMINT4 138 508569 SEMRSHL4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.17544 | 126.6467 | Single 510907 PITTSB-7 345 515422 C-RIVER7 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | FROM->TO | 508566 SABMINT4 138 508569 SEMRSHL4 138 1 | B | 272 | 0.16711 | 127.4298 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | Cumulative Impact | Rebuild line 508566 SABMINT4 138 508569 SEMRSHL4 138 1
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-377 | FROM->TO | 507732 GENMOTR4 138 507759 SW SHV 4 138 1 | B | 234 | 0.060318 | 130.7071 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 507732 GENMOTR4 138 507759 SW SHV 4 138 1
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-377 | FROM->TO | 507727 FLOURNY4 138 507732 GENMOTR4 138 1 | B | 234 | 0.060318 | 131.1509 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 507727 FLOURNY4 138 507732 GENMOTR4 138 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-377 | FROM->TO | 507732 GENMOTR4 138 507759 SW SHV 4 138 1 | B | 188 | 0.060156 | 177.8938 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 507732 GENMOTR4 138 507759 SW SHV 4 138 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-377 | FROM->TO | 507727 FLOURNY4 138 507732 GENMOTR4 138 1 | B | 188 | 0.060156 | 178.6318 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 507727 FLOURNY4 138 507732 GENMOTR4 138 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-377 | FROM->TO | 507732 GENMOTR4 138 507759 SW SHV 4 138 1 | B | 188 | 0.060519 | 185.2751 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 507732 GENMOTR4 138 507759 SW SHV 4 138 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-377 | FROM->TO | 507727 FLOURNY4 138 507732 GENMOTR4 138 1 | B | 188 | 0.060519 | 185.8438 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 507727 FLOURNY4 138 507732 GENMOTR4 138 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-379 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.14413 | 100.5325 | Single 510907 PITTSB-7 345 515422 C-RIVER7 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-379 | FROM->TO | 508808 LONGWD 4 138 508816 OAKPH 4 138 1 | B | 395 | 0.095384 | 100.8572 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 508808 LONGWD 4 138 508816 OAKPH 4 138 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-379 | FROM->TO | 508809 LONGWD 7 345 3WXFMR 520:LONGWOOD 345 1 | B | 580 | 0.45335 | 100.9587 | P23:345:AEPW:LONGWOOD CB 1N60 NBTB:::: | TDF Impact | Add 3-winding transformer 508808 LONGWD 4 138 508809 LONGWD 7 345 508819 LONGW1-1 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-379 | FROM->TO | 508298 LYDIA 7 345 510911 VALIANT7 345 1 | B | 1176 | 0.27355 | 101.2347 | P23:345:AEPW:VALLIANT CB 3413A NBTB:::: | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-379 | FROM->TO | 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.29858 | 101.4921 | Single 337376 7SAREPTA% 345 788340 G24-379-TAP 345 1 | TDF Impact | Rebuild line 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-379 | FROM->TO | 508298 LYDIA 7 345 510911 VALIANT7 345 1 | B | 1176 | 0.30266 | 102.11 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB:::: | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-379 | FROM->TO | 508808 LONGWD 4 138 508816 OAKPH 4 138 1 | B | 395 | 0.095591 | 102.188 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 508808 LONGWD 4 138 508816 OAKPH 4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-379 | FROM->TO | 508298 LYDIA 7 345 510911 VALIANT7 345 1 | B | 1176 | 0.30065 | 102.3256 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB:::: | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-379 | FROM->TO | 508298 LYDIA 7 345 510911 VALIANT7 345 1 | B | 1176 | 0.30203 | 102.7311 | Single 508072 NWTXARK7 345 764520 G20-020-TAP 345 1 | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-379 | FROM->TO | 337909 8ANO% 500 515305 FTSMITH8 500 1 | B | 1299 | 0.1989 | 102.9598 | P52:345:AEPW:NR4PITTSB-7:::: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-379 | FROM->TO | 508298 LYDIA 7 345 510911 VALIANT7 345 1 | B | 1176 | 0.30203 | 103.2181 | Single 510911 VALIANT7 345 764520 G20-020-TAP 345 1 | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-379 | FROM->TO | 507711 ARSHILL4 138 507742 MCWILLI4 138 1 | B | 308 | 0.064976 | 103.6738 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 507711 ARSHILL4 138 507742 MCWILLI4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-379 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.14515 | 103.8575 | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-379 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.12946 | 104.6172 | P23:345:AEPW:PITTSBURG CB 3433A NBTB:::: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-379 | FROM->TO | 508298 LYDIA 7 345 510911 VALIANT7 345 1 | B | 1176 | 0.29864 | 104.9032 | P23:345:AEPW:NW TEXARKANA CB 15440 NBTB:::: | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-379 | FROM->TO | 508298 LYDIA 7 345 510911 VALIANT7 345 1 | B | 1176 | 0.29654 | 105.0459 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB:::: | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-379 | FROM->TO | 337904 5RUSSELVL.S 161 505508 DARDANE5 161 1 | B | 396 | 0.062955 | 105.2411 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-379 | FROM->TO | 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.27977 | 105.3575 | Single 508072 NWTXARK7 345 508359 WELSH7 345 1 | TDF Impact | Rebuild line 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-379 | FROM->TO | 508298 LYDIA 7 345 510911 VALIANT7 345 1 | B | 1176 | 0.29796 | 105.4715 | Single 508072 NWTXARK7 345 764520 G20-020-TAP 345 1 | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-379 | FROM->TO | 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.28018 | 105.5739 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB:::: | TDF Impact | Rebuild line 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-379 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.12748 | 105.6255 | Single 510907 PITTSB-7 345 787110 G24-338-TAP 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-379 | FROM->TO | 508298 LYDIA 7 345 510911 VALIANT7 345 1 | B | 1176 | 0.29796 | 107.4903 | Single 510911 VALIANT7 345 764520 G20-020-TAP 345 1 | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-379 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.1435 | 107.6782 | 272864 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-379 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.14287 | 108.0084 | Single 515422 C-RIVER7 345 785850 G24-296-TAP 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-379 | FROM->TO | 508808 LONGWD 4 138 508816 OAKPH 4 138 1 | B | 188 | 0.056818 | 108.4656 | P12:345:AEPW:SWSHV7:LONGWD7::: | Cumulative Impact | Rebuild line 508808 LONGWD 4 138 508816 OAKPH 4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-379 | FROM->TO | 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.2767 | 108.4857 | Single 508072 NWTXARK7 345 508359 WELSH7 345 1 | TDF Impact | Rebuild line 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-379 | FROM->TO | 507711 ARSHILL4 138 507742 MCWILLI4 138 1 | B | 308 | 0.065528 | 108.5009 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 507711 ARSHILL4 138 507742 MCWILLI4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-379 | FROM->TO | 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.27693 | 108.6558 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB:::: | TDF Impact | Rebuild line 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-379 | FROM->TO | 337904 5RUSSELVL.S 161 505508 DARDANE5 161 1 | B | 396 | 0.062821 | 108.6948 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-379 | FROM->TO | 337904 5RUSSELVL.S 161 505508 DARDANE5 161 1 | B | 396 | 0.062755 | 108.894 | P42:500:OKGE:SB_FTTH8585:::EHV: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-379 | FROM->TO | 337904 5RUSSELVL.S 161 505508 DARDANE5 161 1 | B | 396 | 0.062053 | 109.6472 | P42:500:OKGE:SB_FTTH8585:::EHV: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-379 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.1331 | 110.0508 | P22:345:EES:MUSKOGE7!:::EHV: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-379 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.14605 | 110.6242 | P23:345:AEPW:TERRYRD_CB_3405A_NBTB:::: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-379 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.14537 | 111.1525 | Single 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-379 | FROM->TO | 337904 5RUSSELVL.S 161 505508 DARDANE5 161 1 | B | 396 | 0.061164 | 111.3177 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-379 | FROM->TO | 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.23811 | 111.4242 | P23:345:AEPW:WELSH CB 10610 NBTB:::: | TDF Impact | Rebuild line 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-379 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.12748 | 111.5464 | Single 514809 JOHNCO7 345 787110 G24-338-TAP 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-379 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.12748 | 111.595 | P42:345:OKGE:SB_JOCO7311:::EHV: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-379 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.14537 | 111.7065 | Single 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-379 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.14064 | 113.8068 | 272864 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-379 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.13998 | 114.1963 | Single 515422 C-RIVER7 345 785850 G24-296-TAP 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-379 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.14287 | 114.4578 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-379 | FROM->TO | 337904 5RUSSELVL.S 161 505508 DARDANE5 161 1 | B | 396 | 0.061021 | 114.7438 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-379 | FROM->TO | 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.23506 | 114.8273 | P23:345:AEPW:WELSH CB 10610 NBTB:::: | TDF Impact | Rebuild line 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-379 | FROM->TO | 508809 LONGWD 7 345 3WXFMR 520:LONGWOOD 345 1 | B | 580 | 0.26982 | 115.4467 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | TDF Impact | Add 3-winding transformer 508808 LONGWD 4 138 508809 LONGWD 7 345 508819 LONGW1-1 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-379 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.1287 | 115.5426 | Single 514809 JOHNCO7 345 787110 G24-338-TAP 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-379 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.1287 | 115.6069 | P42:345:OKGE:SB_JOCO7311:::EHV: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-379 | FROM->TO | 508809 LONGWD 7 345 3WXFMR 520:LONGWOOD 345 1 | B | 580 | 0.269 | 116.5224 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | TDF Impact | Add 3-winding transformer 508808 LONGWD 4 138 508809 LONGWD 7 345 508819 LONGW1-1 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-379 | FROM->TO | 508808 LONGWD 4 138 508816 OAKPH 4 138 1 | B | 188 | 0.10377 | 116.7759 | P23:345:AEPW:LONGWOOD CB 1N60 NBTB:::: | Cumulative Impact | Rebuild line 508808 LONGWD 4 138 508816 OAKPH 4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-379 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.13572 | 117.3852 | P22:345:EES:MUSKOGE7!:::EHV: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-379 | FROM->TO | 507732 GENMOTR4 138 507759 SW SHV 4 138 1 | B | 188 | 0.082518 | 117.8377 | P12:345:AEPW:SWSHV7:LONGWD7::: | Cumulative Impact | Rebuild line 507732 GENMOTR4 138 507759 SW SHV 4 138 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-379 | FROM->TO | 507727 FLOURNY4 138 507732 GENMOTR4 138 1 | B | 188 | 0.082518 | 118.5971 | P12:345:AEPW:SWSHV7:LONGWD7::: | Cumulative Impact | Rebuild line 507727 FLOURNY4 138 507732 GENMOTR4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-379 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.13998 | 120.547 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-379 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.14482 | 121.1336 | Single 510907 PITTSB-7 345 515422 C-RIVER7 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-379 | FROM->TO | 507732 GENMOTR4 138 507759 SW SHV 4 138 1 | B | 188 | 0.082738 | 121.8939 | P12:345:AEPW:SWSHV7:LONGWD7::: | Cumulative Impact | Rebuild line 507732 GENMOTR4 138 507759 SW SHV 4 138 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-379 | FROM->TO | 507727 FLOURNY4 138 507732 GENMOTR4 138 1 | B | 188 | 0.082738 | 122.4956 | P12:345:AEPW:SWSHV7:LONGWD7::: | Cumulative Impact | Rebuild line 507727 FLOURNY4 138 507732 GENMOTR4 138 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-379 | FROM->TO | 507732 GENMOTR4 138 507759 SW SHV 4 138 1 | B | 188 | 0.12486 | 124.0032 | P23:345:AEPW:LONGWOOD CB 1N60 NBTB:::: | Cumulative Impact | Rebuild line 507732 GENMOTR4 138 507759 SW SHV 4 138 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-379 | FROM->TO | 507727 FLOURNY4 138 507732 GENMOTR4 138 1 | B | 188 | 0.12486 | 124.76 | P23:345:AEPW:LONGWOOD CB 1N60 NBTB:::: | Cumulative Impact | Rebuild line 507727 FLOURNY4 138 507732 GENMOTR4 138 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-379 | FROM->TO | 507732 GENMOTR4 138 507759 SW SHV 4 138 1 | B | 188 | 0.12483 | 125.9124 | P23:345:AEPW:LONGWOOD CB 1N60 NBTB:::: | Cumulative Impact | Rebuild line 507732 GENMOTR4 138 507759 SW SHV 4 138 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-379 | FROM->TO | 507727 FLOURNY4 138 507732 GENMOTR4 138 1 | B | 188 | 0.12483 | 126.5061 | P23:345:AEPW:LONGWOOD CB 1N60 NBTB:::: | Cumulative Impact | Rebuild line 507727 FLOURNY4 138 507732 GENMOTR4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-379 | FROM->TO | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | B | 956 | 0.142 | 126.6467 | Single 510907 PITTSB-7 345 515422 C-RIVER7 345 1 | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-379 | FROM->TO | 507732 GENMOTR4 138 507759 SW SHV 4 138 1 | B | 234 | 0.092201 | 130.7071 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 507732 GENMOTR4 138 507759 SW SHV 4 138 1
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-379 | FROM->TO | 507727 FLOURNY4 138 507732 GENMOTR4 138 1 | B | 234 | 0.092201 | 131.1509 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 507727 FLOURNY4 138 507732 GENMOTR4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-379 | FROM->TO | 508808 LONGWD 4 138 508816 OAKPH 4 138 1 | B | 188 | 0.050505 | 156.8154 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 508808 LONGWD 4 138 508816 OAKPH 4 138 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-379 | FROM->TO | 507732 GENMOTR4 138 507759 SW SHV 4 138 1 | B | 188 | 0.092194 | 177.8938 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 507732 GENMOTR4 138 507759 SW SHV 4 138 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-379 | FROM->TO | 507727 FLOURNY4 138 507732 GENMOTR4 138 1 | B | 188 | 0.092194 | 178.6318 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 507727 FLOURNY4 138 507732 GENMOTR4 138 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-379 | FROM->TO | 507732 GENMOTR4 138 507759 SW SHV 4 138 1 | B | 188 | 0.09243 | 185.2751 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 507732 GENMOTR4 138 507759 SW SHV 4 138 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-379 | FROM->TO | 507727 FLOURNY4 138 507732 GENMOTR4 138 1 | B | 188 | 0.09243 | 185.8438 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 507727 FLOURNY4 138 507732 GENMOTR4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | ASGI-2024-001 | TO->FROM | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | B | 956 | 0.05207 | 100.2221 | P42:345:NPPD:BKR-TOB-3304:::: | Cumulative Impact | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | ASGI-2024-001 | TO->FROM | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | B | 956 | 0.053576 | 102.2146 | P42:345:NPPD:BKR-MOR-3312:::: | Cumulative Impact | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
Thermal | 05ALL | 1 | 29SP | T0 | ASGI-2024-002 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.057894 | 100.0488 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | ASGI-2024-002 | TO->FROM | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | B | 997 | 0.099874 | 100.166 | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | Cumulative Impact | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | T0 | ASGI-2024-002 | TO->FROM | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | B | 997 | 0.10506 | 100.7286 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | T0 | ASGI-2024-002 | TO->FROM | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | B | 997 | 0.10506 | 101.1047 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 29WP | T0 | ASGI-2024-002 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.059621 | 103.9266 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | ASGI-2024-002 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.059404 | 104.7552 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | ASGI-2024-002 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.059404 | 104.888 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | ASGI-2024-002 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.061086 | 107.2243 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | ASGI-2024-002 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.061086 | 107.2951 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | ASGI-2024-002 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.059256 | 107.5866 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | ASGI-2024-002 | TO->FROM | 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | B | 997 | 0.08174 | 109.7018 | Single 525832 TUCO_INT7 345 526000 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1
Thermal | 05ALL | 1 | 29SP | T0 | ASGI-2024-002 | TO->FROM | 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | B | 997 | 0.078365 | 111.09 | Single 525832 TUCO_INT7 345 526000 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1
Thermal | 05ALL | 1 | 26SP | T0 | ASGI-2024-002 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.060772 | 111.723 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | ASGI-2024-002 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.060772 | 111.8755 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | ASGI-2024-002 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.059256 | 115.0541 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | ASGI-2024-002 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.060772 | 118.9427 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | ASGI-2024-002 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.060772 | 119.313 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 03ALL | 1 | 26SP | T0 | ASGI-2024-003 | TO->FROM | 640277 MOORE 3 345 640525 TOBIAS 3 345 1 | B | 956 | 0.056034 | 100.5946 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640525 TOBIAS 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | ASGI-2024-007 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.039553 | 242.4879 | System Intact | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | ASGI-2024-008 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.039553 | 242.4879 | System Intact | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | ASGI-2024-020 | TO->FROM | 533417 EMCPHER3 115 533426 MANVILE3 115 1 | B | 128 | 1 | 106.5478 | Single 533426 MANVILE3 115 533437 MOHAWK3 115 1 | TDF Impact | Rebuild line 533417 EMCPHER3 115 533426 MANVILE3 115 1
Thermal | 00ALL | 1 | 26SP | T0 | ASGI-2024-020 | TO->FROM | 533417 EMCPHER3 115 533426 MANVILE3 115 1 | B | 128 | 1 | 107.8314 | Single 533426 MANVILE3 115 533437 MOHAWK3 115 1 | TDF Impact | Rebuild line 533417 EMCPHER3 115 533426 MANVILE3 115 1
Thermal | 00ALL | 1 | 29WP | T0 | ASGI-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.071323 | 217.9772 | P42:345:NPPD:BKR-TOB-3304:::: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | ASGI-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.070561 | 230.5239 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | ASGI-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.075593 | 236.1008 | P42:345:NPPD:BKR-TOB-3304:::: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | ASGI-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.075043 | 248.1828 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 04ALL | 1 | 29WP | T1 | ASGI-2024-023 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | B | 297 | 0.23564 | 100.8571 | Single 337376 7SAREPTA% 345 788340 G24-379-TAP 345 1 | TDF Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 04ALL | 1 | 29WP | T1 | ASGI-2024-023 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | B | 297 | 0.23564 | 100.9094 | Single 508809 LONGWD7 345 788340 G24-379-TAP 345 1 | TDF Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 04ALL | 1 | 29WP | T1 | ASGI-2024-023 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | B | 297 | 0.23748 | 102.9874 | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | TDF Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 04ALL | 1 | 26SP | T0 | ASGI-2024-023 | TO->FROM | 507454 TURK 4 138 3WXFMR 520:TURK 2 138 1 | B | 177 | 0.99985 | 103.2017 | Single 338874 3LEWISVILLE# 115 338875 3PATMOS.W# 115 1 | TDF Impact | 2023ITP PORTFOLIO - REPLACE TURK 138_115 KV CKT 1 XFMR.idv : 2023 ITP upgrade, PID : 92976, NTC, ISD : 4/25/2027
Thermal | 04ALL | 1 | 26SP | T0 | ASGI-2024-023 | TO->FROM | 507454 TURK 4 138 3WXFMR 520:TURK 2 138 1 | B | 177 | 0.99985 | 105.218 | P12:115:EES-EAI-AEPW:3COUCH:FULTON3::: | TDF Impact | 2023ITP PORTFOLIO - REPLACE TURK 138_115 KV CKT 1 XFMR.idv : 2023 ITP upgrade, PID : 92976, NTC, ISD : 4/25/2027
Thermal | 04ALL | 1 | 26SP | T0 | ASGI-2024-023 | TO->FROM | 507454 TURK 4 138 3WXFMR 520:TURK 2 138 1 | B | 177 | 0.99985 | 105.218 | P12:115:EES-EAI:COUCH:LEWISV:1 | TDF Impact | 2023ITP PORTFOLIO - REPLACE TURK 138_115 KV CKT 1 XFMR.idv : 2023 ITP upgrade, PID : 92976, NTC, ISD : 4/25/2027
Thermal | 04ALL | 1 | 26SP | T0 | ASGI-2024-023 | TO->FROM | 507454 TURK 4 138 3WXFMR 520:TURK 2 138 1 | B | 177 | 0.99985 | 105.218 | P12:115:EES:3COUCH%:FULTON 3:1:HV: | TDF Impact | 2023ITP PORTFOLIO - REPLACE TURK 138_115 KV CKT 1 XFMR.idv : 2023 ITP upgrade, PID : 92976, NTC, ISD : 4/25/2027
Thermal | 04ALL | 1 | 26SP | T0 | ASGI-2024-023 | TO->FROM | 507454 TURK 4 138 3WXFMR 520:TURK 2 138 1 | B | 177 | 0.99985 | 105.2371 | Single 338875 3PATMOS.W# 115 503912 FULTON3 115 1 | TDF Impact | 2023ITP PORTFOLIO - REPLACE TURK 138_115 KV CKT 1 XFMR.idv : 2023 ITP upgrade, PID : 92976, NTC, ISD : 4/25/2027
Thermal | 04ALL | 1 | 26SP | T0 | ASGI-2024-023 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | A | 157 | 0.24464 | 148.4151 | System Intact | TDF Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 04ALL | 1 | 29SP | T0 | ASGI-2024-023 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | A | 157 | 0.23102 | 150.7438 | System Intact | TDF Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 04ALL | 1 | 29WP | T0 | ASGI-2024-023 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | A | 159 | 0.23108 | 153.3873 | System Intact | TDF Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 04ALL | 1 | 26SP | T0 | ASGI-2024-023 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | B | 157 | 0.2472 | 163.8943 | P42:345:AEPW:WILKES CB 1W10 NBTB+FAULT:::: | TDF Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 04ALL | 1 | 26SP | T0 | ASGI-2024-023 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | B | 157 | 0.24788 | 164.1389 | P23:345:AEPW:LONGWOOD CB 1N60 NBTB:::: | TDF Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 04ALL | 1 | 26SP | T0 | ASGI-2024-023 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | B | 157 | 0.2988 | 165.0676 | P12:138:EES:TURK 4%:TURK 7:TURK 11:HV: | TDF Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 04ALL | 1 | 26SP | T0 | ASGI-2024-023 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | B | 157 | 0.2988 | 165.1328 | P12:345:AEPW:TURK7:NWTXARK7::: | TDF Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 04ALL | 1 | 29SP | T0 | ASGI-2024-023 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | B | 157 | 0.23448 | 166.8647 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 04ALL | 1 | 29SP | T0 | ASGI-2024-023 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | B | 157 | 0.23376 | 167.3028 | P12:345:AEPW:LONGWD7:WILKES7::: | TDF Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 04ALL | 1 | 29SP | T0 | ASGI-2024-023 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | B | 157 | 0.23773 | 167.7909 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | TDF Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 04ALL | 1 | 29SP | T0 | ASGI-2024-023 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | B | 157 | 0.23451 | 168.3565 | P23:345:AEPW:LONGWOOD CB 1N60 NBTB:::: | TDF Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 04ALL | 1 | 29SP | T0 | ASGI-2024-023 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | B | 157 | 0.23249 | 168.3752 | Single 509241 CROCKET7 345 783930 G24-232-TAP 345 1 | TDF Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 04ALL | 1 | 26SP | T0 | ASGI-2024-023 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | B | 157 | 0.24617 | 168.4565 | P23:345:EES::7ROCKYCRK%:1:EHV: | TDF Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 04ALL | 1 | 26SP | T0 | ASGI-2024-023 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | B | 157 | 0.24617 | 168.4618 | Single 334197 7ROCKYCRK% 345 783930 G24-232-TAP 345 1 | TDF Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 04ALL | 1 | 26SP | T0 | ASGI-2024-023 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | B | 157 | 0.24758 | 169.3329 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 04ALL | 1 | 29WP | T0 | ASGI-2024-023 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | B | 159 | 0.2338 | 170.4506 | 267135_a | TDF Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 04ALL | 1 | 29WP | T0 | ASGI-2024-023 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | B | 159 | 0.2338 | 170.8665 | P12:345:AEPW:LONGWD7:WILKES7::: | TDF Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 04ALL | 1 | 29WP | T0 | ASGI-2024-023 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | B | 159 | 0.23381 | 170.9002 | P42:345:AEPW:WILKES CB 1W10 NBTB+FAULT:::: | TDF Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 04ALL | 1 | 26SP | T0 | ASGI-2024-023 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | B | 157 | 0.25058 | 172.2965 | Single 508809 LONGWD7 345 788340 G24-379-TAP 345 1 | TDF Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 04ALL | 1 | 26SP | T0 | ASGI-2024-023 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | B | 157 | 0.25058 | 172.3873 | Single 337376 7SAREPTA% 345 788340 G24-379-TAP 345 1 | TDF Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 04ALL | 1 | 29WP | T0 | ASGI-2024-023 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | B | 159 | 0.23456 | 172.5507 | P23:345:AEPW:LONGWOOD CB 1N60 NBTB:::: | TDF Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 04ALL | 1 | 29WP | T0 | ASGI-2024-023 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | B | 159 | 0.23268 | 174.1213 | P23:345:EES::7ROCKYCRK%:1:EHV: | TDF Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 04ALL | 1 | 29WP | T0 | ASGI-2024-023 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | B | 159 | 0.23268 | 174.1237 | Single 334197 7ROCKYCRK% 345 783930 G24-232-TAP 345 1 | TDF Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 04ALL | 1 | 29SP | T0 | ASGI-2024-023 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | B | 157 | 0.23249 | 175.1779 | Single 334197 7ROCKYCRK% 345 783930 G24-232-TAP 345 1 | TDF Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 04ALL | 1 | 29SP | T0 | ASGI-2024-023 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | B | 157 | 0.23249 | 175.1865 | P23:345:EES::7ROCKYCRK%:1:EHV: | TDF Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 04ALL | 1 | 29WP | T0 | ASGI-2024-023 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | B | 159 | 0.23438 | 176.4098 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 04ALL | 1 | 26SP | T0 | ASGI-2024-023 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | B | 157 | 0.25119 | 177.0636 | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | TDF Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 04ALL | 1 | 29WP | T0 | ASGI-2024-023 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | B | 159 | 0.23758 | 179.8598 | Single 337376 7SAREPTA% 345 788340 G24-379-TAP 345 1 | TDF Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 04ALL | 1 | 29WP | T0 | ASGI-2024-023 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | B | 159 | 0.23758 | 179.951 | Single 508809 LONGWD7 345 788340 G24-379-TAP 345 1 | TDF Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 04ALL | 1 | 29SP | T0 | ASGI-2024-023 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | B | 157 | 0.2374 | 180.7536 | Single 337376 7SAREPTA% 345 788340 G24-379-TAP 345 1 | TDF Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 04ALL | 1 | 29SP | T0 | ASGI-2024-023 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | B | 157 | 0.2374 | 180.8803 | Single 508809 LONGWD7 345 788340 G24-379-TAP 345 1 | TDF Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 04ALL | 1 | 29WP | T0 | ASGI-2024-023 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | B | 159 | 0.23822 | 184.4152 | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | TDF Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 04ALL | 1 | 29SP | T0 | ASGI-2024-023 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | B | 157 | 0.23806 | 185.7511 | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | TDF Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 03ALL | 1 | 29SP | T0 | ASGI-2024-024 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.067311 | 101.6955 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 03ALL | 1 | 29SP | T0 | ASGI-2024-024 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.067311 | 101.6955 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29SP | T0 | ASGI-2024-024 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.067311 | 101.6955 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 26SP | T1 | ASGI-2024-024 | TO->FROM | 541369 MIDWAY_5 161 541394 AVENUECTY 5 161 1 | A | 161 | 0.07657 | 104.1401 | System Intact | TDF Impact | Rebuild line 541369 MIDWAY_5 161 541394 AVENUECTY 5 161 1
Thermal | 03ALL | 1 | 26SP | T1 | ASGI-2024-024 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.063321 | 105.0133 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 29WP | T1 | ASGI-2024-024 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.059098 | 106.2154 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 29WP | T0 | ASGI-2024-024 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.060149 | 106.5956 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 03ALL | 1 | 29WP | T0 | ASGI-2024-024 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.060149 | 106.5956 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29WP | T0 | ASGI-2024-024 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.060149 | 106.5956 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29SP | T0 | ASGI-2024-024 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.062656 | 106.8199 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 03ALL | 1 | 29SP | T0 | ASGI-2024-024 | TO->FROM | 541254 EAST 5 161 541401 EASTOWN5 161 1 | B | 334 | 0.094484 | 108.1532 | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT_1 | Cumulative Impact | Rebuild line 541254 EAST 5 161 541401 EASTOWN5 161 1
Thermal | 03ALL | 1 | 29SP | T0 | ASGI-2024-024 | TO->FROM | 541254 EAST 5 161 541401 EASTOWN5 161 1 | B | 334 | 0.094484 | 108.1532 | P23:345:GMO-AECI:STJOE-R3-14:::EHV: | Cumulative Impact | Rebuild line 541254 EAST 5 161 541401 EASTOWN5 161 1
Thermal | 03ALL | 1 | 29SP | T0 | ASGI-2024-024 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.052676 | 108.3331 | P42:345:NPPD:BKR-TOB-3304:::: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 03ALL | 1 | 26SP | T0 | ASGI-2024-024 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.069113 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 03ALL | 1 | 26SP | T0 | ASGI-2024-024 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.069113 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 26SP | T0 | ASGI-2024-024 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.069113 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29SP | T0 | ASGI-2024-024 | TO->FROM | 541254 EAST 5 161 541401 EASTOWN5 161 1 | B | 334 | 0.10358 | 117.1628 | Single 541199 STJOE7 345 541400 EASTOWN7 345 1 | Cumulative Impact | Rebuild line 541254 EAST 5 161 541401 EASTOWN5 161 1
Thermal | 03ALL | 1 | 29SP | T0 | ASGI-2024-024 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.11564 | 117.7598 | P55:345:OPPD:S3458 3::FN13:EHV: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 03ALL | 1 | 29SP | T1 | ASGI-2024-024 | TO->FROM | 541251 MARYVLE5 161 541369 MIDWAY_5 161 1 | A | 161 | 0.076884 | 118.7915 | System Intact | TDF Impact | Rebuild line 541251 MARYVLE5 161 541369 MIDWAY_5 161 1
Thermal | 03ALL | 1 | 29SP | T1 | ASGI-2024-024 | TO->FROM | 541369 MIDWAY_5 161 541394 AVENUECTY 5 161 1 | A | 161 | 0.076884 | 127.6857 | System Intact | TDF Impact | Rebuild line 541369 MIDWAY_5 161 541394 AVENUECTY 5 161 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-003 | TO->FROM | 514934 DRAPER 7 345 515045 SEMINOL7 345 2 | B | 717 | 0.063566 | 104.675 | P42:345:OKGE:SB_SEOL7385:::EHV: | Cumulative Impact | Rebuild line 514934 DRAPER 7 345 515045 SEMINOL7 345 2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-003 | TO->FROM | 515336 VBI 2 69 3WXFMR 524:524:VBI2 161 2 | A | 76 | 0.032857 | 108.2991 | System Intact | TDF Impact | Rebuild 3-winding transformer 515336 VBI 2 69 515339 VBI 5 161 515769 VBI 1 13 2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-003 | TO->FROM | 514934 DRAPER 7 345 515045 SEMINOL7 345 2 | B | 717 | 0.06744 | 109.0105 | P42:345:OKGE:SB_SEOL7385:::EHV: | Cumulative Impact | Rebuild line 514934 DRAPER 7 345 515045 SEMINOL7 345 2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-003 | TO->FROM | 515336 VBI 2 69 3WXFMR 524:524:VBI2 161 2 | A | 76 | 0.034842 | 117.4893 | System Intact | TDF Impact | Rebuild 3-winding transformer 515336 VBI 2 69 515339 VBI 5 161 515769 VBI 1 13 2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-015 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.07111 | 100.0488 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-015 | TO->FROM | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | B | 997 | 0.18224 | 100.166 | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | Cumulative Impact | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-015 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.062562 | 100.533 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-015 | TO->FROM | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | B | 997 | 0.1861 | 100.7286 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-015 | TO->FROM | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | B | 997 | 0.1861 | 101.1047 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-015 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063503 | 102.9616 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-015 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063503 | 102.9634 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-015 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063503 | 103.0288 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-015 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063503 | 103.4739 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-015 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.074481 | 103.9266 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-015 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063503 | 104.1493 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-015 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.074292 | 104.7552 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-015 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.074292 | 104.888 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-015 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.077605 | 107.2243 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-015 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063503 | 107.2793 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-015 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063503 | 107.2794 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-015 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.077605 | 107.2951 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-015 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063503 | 107.3093 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-015 | TO->FROM | 523959 POTTER_CO 6 230 3WXFMR 526:WAUK 90343-A 230 1 | B | 559 | 0.074012 | 107.3794 | P42:345:SPS:HITCHLAND-1R15:::EHV: | Cumulative Impact | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-015 | TO->FROM | 523959 POTTER_CO 6 230 3WXFMR 526:WAUK 90343-A 230 1 | B | 559 | 0.074012 | 107.3953 | Single 523097 HITCHLAND7 345 523961 POTTER_CO7 345 1 | Cumulative Impact | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-015 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.072215 | 107.5866 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-015 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063503 | 107.7557 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-015 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063503 | 108.1822 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-015 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063503 | 108.2747 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-015 | TO->FROM | 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | B | 997 | 0.33316 | 109.7018 | Single 525832 TUCO_INT7 345 526000 CRAWFISH_DR 345 2 | TDF Impact | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-015 | TO->FROM | 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | B | 997 | 0.3331 | 111.09 | Single 525832 TUCO_INT7 345 526000 CRAWFISH_DR 345 2 | TDF Impact | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-015 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063503 | 111.3621 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-015 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.075415 | 111.723 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-015 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.075415 | 111.8755 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-015 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.072215 | 115.0541 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-015 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.075415 | 118.9427 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-015 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.075415 | 119.313 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.39999 | 100.1843 | P42:345:NPPD:BKR-CPR-3310:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-017 | TO->FROM | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | B | 956 | 0.18564 | 100.2221 | P42:345:NPPD:BKR-TOB-3304:::: | Cumulative Impact | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.32694 | 100.3683 | System Intact | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-017 | TO->FROM | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | B | 956 | 0.15066 | 100.3823 | P42:345:NPPD:BKR-TOB-3304:::: | Cumulative Impact | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.3291 | 100.5881 | P55:345:MEC:NORTHBORO | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.3291 | 100.6014 | P23:345:MEC:NORTHBORO:901::EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.33548 | 101.1272 | P42:345:NPPD:BKR-CPR-3304:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-017 | TO->FROM | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | B | 956 | 0.14667 | 101.3156 | Single 640312 PAULINE3 345 640525 TOBIAS3 345 1 | Cumulative Impact | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.32581 | 101.865 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.32908 | 101.8856 | P23:345:MEC:ORIENT:902::EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.3291 | 101.919 | P12:345:MEC:ORIENT:NORTHBORO:1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.32877 | 102.124 | P55:345:MEC:ORIENT | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-017 | TO->FROM | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | B | 956 | 0.21394 | 102.2146 | P42:345:NPPD:BKR-MOR-3312:::: | TDF Impact | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-017 | TO->FROM | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | B | 956 | 0.15375 | 102.6296 | P42:345:NPPD:BKR-TOB-3304:::: | Cumulative Impact | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-017 | TO->FROM | 640278 SHELDON7 115 640591 OLIVECREEK 7 115 1 | B | 400 | 0.14967 | 103.3162 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Rebuild line 640278 SHELDON7 115 640591 OLIVECREEK 7 115 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-017 | TO->FROM | 640278 SHELDON7 115 640591 OLIVECREEK 7 115 2 | B | 400 | 0.14967 | 103.3162 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Rebuild line 640278 SHELDON7 115 640591 OLIVECREEK 7 115 2
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.28814 | 103.5564 | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-017 | TO->FROM | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | B | 956 | 0.14975 | 104.1025 | Single 640312 PAULINE3 345 640525 TOBIAS3 345 1 | Cumulative Impact | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.32548 | 104.5429 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-017 | TO->FROM | 645454 S3454 3 345 650185 WAGENER 3 345 1 | B | 982 | 0.16662 | 104.6262 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Rebuild line 645454 S3454 3 345 650185 WAGENER 3 345 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.32991 | 105.6094 | P55:345:MEC:NORTHBORO | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.32991 | 105.6094 | P23:345:MEC:NORTHBORO:901::EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.33626 | 105.894 | P42:345:NPPD:BKR-CPR-3304:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-017 | TO->FROM | 650185 WAGENER 3 345 650189 103&ROKEBY3 345 1 | B | 1158 | 0.23794 | 105.9892 | P42:345:NPPD:BKR-MOR-3310:::: | TDF Impact | Rebuild line 650185 WAGENER 3 345 650189 103&ROKEBY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-017 | TO->FROM | 650185 WAGENER 3 345 650189 103&ROKEBY3 345 1 | B | 1158 | 0.23794 | 105.9892 | P42:345:NPPD:L3502A.MOORE.MCCOOL.CB3310:::: | TDF Impact | Rebuild line 650185 WAGENER 3 345 650189 103&ROKEBY3 345 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.32988 | 106.0256 | P23:345:MEC:ORIENT:902::EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.32964 | 106.0311 | P55:345:MEC:ORIENT | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.32991 | 106.0554 | P12:345:MEC:ORIENT:NORTHBORO:1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-017 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.036935 | 106.6762 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.28817 | 106.9411 | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-017 | TO->FROM | 640278 SHELDON7 115 640591 OLIVECREEK 7 115 1 | B | 400 | 0.14939 | 107.3677 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Rebuild line 640278 SHELDON7 115 640591 OLIVECREEK 7 115 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-017 | TO->FROM | 640278 SHELDON7 115 640591 OLIVECREEK 7 115 2 | B | 400 | 0.14939 | 107.3677 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Rebuild line 640278 SHELDON7 115 640591 OLIVECREEK 7 115 2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-017 | TO->FROM | 640127 COLMB.E7 115 3WXFMR 640:COL.EAST T4 345 1 | B | 336 | 0.055374 | 108.1031 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | TDF Impact | Add 3-winding transformer 640125 COLMB.E3 345 640127 COLMB.E7 115 640129 COLMB.T9 13 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.32656 | 108.859 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-017 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.037085 | 108.9935 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-017 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.037085 | 109.0153 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-017 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.036941 | 109.4444 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-017 | TO->FROM | 640139 COOPER 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.46393 | 109.7418 | P42:345:NPPD:BKR-MOR-3308:::: | TDF Impact | Rebuild line 640139 COOPER 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-017 | TO->FROM | 645456 S3456 3 345 645458 S3458 3 345 1 | B | 982 | 0.040305 | 109.8564 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Rebuild line 645456 S3456 3 345 645458 S3458 3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-017 | TO->FROM | 640127 COLMB.E7 115 3WXFMR 640:COL.EAST T4 345 1 | B | 336 | 0.053886 | 111.4413 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | TDF Impact | Add 3-winding transformer 640125 COLMB.E3 345 640127 COLMB.E7 115 640129 COLMB.T9 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-017 | TO->FROM | 640139 COOPER 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.46353 | 111.8885 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | TDF Impact | Rebuild line 640139 COOPER 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.30176 | 113.2096 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.28946 | 115.9916 | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-017 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.037506 | 118.0094 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-017 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.036511 | 119.5678 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.36742 | 120.1399 | Single 640600 DAYKIN3 345 771999 G23-222-POI 345 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.36618 | 120.7011 | Single 640600 DAYKIN3 345 771999 G23-222-POI 345 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-017 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.036511 | 120.8848 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-017 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.03666 | 121.2729 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-017 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.03666 | 121.3014 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-017 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.14359 | 121.3265 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-017 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.14359 | 121.3266 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-017 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.036496 | 121.5027 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-017 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.14254 | 121.5754 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-017 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.14254 | 121.5756 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.30326 | 121.9917 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-017 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.03666 | 122.5957 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-017 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.03666 | 122.6148 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-017 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.036496 | 122.8495 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-017 | TO->FROM | 645454 S3454 3 345 650185 WAGENER 3 345 1 | B | 982 | 0.23703 | 124.4523 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | Rebuild line 645454 S3454 3 345 650185 WAGENER 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-017 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.14397 | 125.6647 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-017 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.14397 | 125.6649 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-017 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.14292 | 125.7875 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-017 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.14292 | 125.7878 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-017 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.037142 | 130.4818 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-017 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.037142 | 132.0705 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-017 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.036362 | 146.377 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-017 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.036527 | 148.5944 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-017 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.036527 | 148.6147 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-017 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.036368 | 148.9728 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-017 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.036362 | 149.1688 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-017 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.036527 | 151.4021 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-017 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.036527 | 151.42 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-017 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.036368 | 151.7992 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-017 | TO->FROM | 640088 BPS SUB7 115 3WXFMR 640:BPS_345_115 T1 345 1 | B | 417 | 0.11523 | 159.9374 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-017 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.037063 | 159.9633 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-017 | TO->FROM | 640088 BPS SUB7 115 3WXFMR 640:BPS_345_115 T1 345 1 | B | 417 | 0.11516 | 161.1357 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-017 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.037063 | 163.2816 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-017 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.21062 | 171.4724 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | TDF Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-017 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.21062 | 171.4729 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | TDF Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-017 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.21045 | 173.7124 | P42:345:NPPD:BKR-MOR-3308:::: | TDF Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-017 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.21045 | 173.713 | P42:345:NPPD:BKR-MOR-3308:::: | TDF Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 3WXFMR 640:MOORE T1 345 1 | B | 400 | 0.22823 | 185.3265 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | TDF Impact | Add 3-winding transformer 640277 MOORE 3 345 640278 SHELDON7 115 640280 MOORE 9 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.64894 | 194.842 | System Intact | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 3WXFMR 640:MOORE T1 345 1 | B | 400 | 0.22746 | 195.4671 | P42:345:NPPD:BKR-MOR-3308:::: | TDF Impact | Add 3-winding transformer 640277 MOORE 3 345 640278 SHELDON7 115 640280 MOORE 9 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.65092 | 202.7501 | System Intact | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.66267 | 203.5263 | P13:115-345:NPPD:T590::MONOLITH.CKT2:: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.66267 | 203.5263 | P13:115-345:NPPD:T590::MONOLITH.CKT1:: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.66794 | 203.9708 | P42:345:NPPD:BKR-CPR-3304:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.65522 | 205.4343 | P23:345:MEC:ORIENT:902::EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.65527 | 205.5053 | P12:345:MEC:ORIENT:NORTHBORO:1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.65461 | 205.9776 | P55:345:MEC:ORIENT | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.64809 | 211.0729 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.65682 | 212.8881 | P55:345:MEC:NORTHBORO | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.65682 | 212.8881 | P23:345:MEC:NORTHBORO:901::EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.66944 | 213.5137 | P42:345:NPPD:BKR-CPR-3304:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.65676 | 213.736 | P23:345:MEC:ORIENT:902::EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.65628 | 213.7657 | P55:345:MEC:ORIENT | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.65682 | 213.7914 | P12:345:MEC:ORIENT:NORTHBORO:1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.57418 | 217.9772 | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.65017 | 219.8543 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.60102 | 230.5239 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.57684 | 236.1008 | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.7362 | 242.4879 | System Intact | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.73582 | 247.7008 | Single 640600 DAYKIN3 345 771999 G23-222-POI 345 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.60407 | 248.1828 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.7336 | 248.2416 | Single 640600 DAYKIN3 345 771999 G23-222-POI 345 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.74226 | 250.2801 | P55:345:MEC:NORTHBORO | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.74226 | 250.2801 | P23:345:MEC:NORTHBORO:901::EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.74695 | 250.332 | Single 640076 BEATRCE7 115 640208 HARBINE7 115 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.74226 | 251.4352 | P12:345:MEC:ORIENT:NORTHBORO:1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.74228 | 251.4821 | P23:345:MEC:ORIENT:902::EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.74237 | 251.8126 | P55:345:MEC:ORIENT | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.76123 | 255.4845 | P42:345:NPPD:BKR-CPR-3304:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.90152 | 257.5476 | P42:345:NPPD:BKR-CPR-3310:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.90152 | 257.5667 | Single 640139 COOPER3 345 640590 OLIVECREEK3 345 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-017 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.75004 | 260.7181 | Single 640088 BPSSUB7 115 771999 G23-222-POI 345 771998 'NEW_TER_BPS ' 13 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.23741 | 100.1843 | P42:345:NPPD:BKR-CPR-3310:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | TO->FROM | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | B | 956 | 0.17558 | 100.2221 | P42:345:NPPD:BKR-TOB-3304:::: | Cumulative Impact | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.17231 | 100.3683 | System Intact | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-018 | TO->FROM | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | B | 956 | 0.12761 | 100.3823 | P42:345:NPPD:BKR-TOB-3304:::: | Cumulative Impact | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | TO->FROM | 640088 BPS SUB7 115 3WXFMR 640:BPS_345_115 T1 345 1 | B | 417 | 0.16295 | 100.483 | P42:345:NPPD:L3502A.MOORE.MCCOOL.CB3310:::: | Cumulative Impact | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | TO->FROM | 640088 BPS SUB7 115 3WXFMR 640:BPS_345_115 T1 345 1 | B | 417 | 0.16295 | 100.483 | P42:345:NPPD:BKR-MOR-3310:::: | Cumulative Impact | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.17439 | 100.5881 | P55:345:MEC:NORTHBORO | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.17439 | 100.6014 | P23:345:MEC:NORTHBORO:901::EHV: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.1802 | 101.1272 | P42:345:NPPD:BKR-CPR-3304:::: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-018 | TO->FROM | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | B | 956 | 0.13318 | 101.3156 | Single 640312 PAULINE3 345 640525 TOBIAS3 345 1 | Cumulative Impact | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.17141 | 101.865 | P55:345:OPPD:S3740 3::FN13:EHV: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.17436 | 101.8856 | P23:345:MEC:ORIENT:902::EHV: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.17439 | 101.919 | P12:345:MEC:ORIENT:NORTHBORO:1 | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.17408 | 102.124 | P55:345:MEC:ORIENT | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | TO->FROM | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | B | 956 | 0.20256 | 102.2146 | P42:345:NPPD:BKR-MOR-3312:::: | TDF Impact | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-018 | TO->FROM | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | B | 956 | 0.13058 | 102.6296 | P42:345:NPPD:BKR-TOB-3304:::: | Cumulative Impact | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | TO->FROM | 640278 SHELDON7 115 640591 OLIVECREEK 7 115 1 | B | 400 | 0.10726 | 103.3162 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Rebuild line 640278 SHELDON7 115 640591 OLIVECREEK 7 115 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | TO->FROM | 640278 SHELDON7 115 640591 OLIVECREEK 7 115 2 | B | 400 | 0.10726 | 103.3162 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Rebuild line 640278 SHELDON7 115 640591 OLIVECREEK 7 115 2
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.22488 | 103.5564 | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-018 | TO->FROM | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | B | 956 | 0.1362 | 104.1025 | Single 640312 PAULINE3 345 640525 TOBIAS3 345 1 | Cumulative Impact | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.17093 | 104.5429 | P55:345:OPPD:S3740 3::FN13:EHV: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-018 | TO->FROM | 645454 S3454 3 345 650185 WAGENER 3 345 1 | B | 982 | 0.15425 | 104.6262 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Rebuild line 645454 S3454 3 345 650185 WAGENER 3 345 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.17515 | 105.6094 | P55:345:MEC:NORTHBORO | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.17515 | 105.6094 | P23:345:MEC:NORTHBORO:901::EHV: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-018 | TO->FROM | 640088 BPS SUB7 115 3WXFMR 640:BPS_345_115 T1 345 1 | B | 417 | 0.22042 | 105.8248 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | TDF Impact | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.18093 | 105.894 | P42:345:NPPD:BKR-CPR-3304:::: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-018 | TO->FROM | 650185 WAGENER 3 345 650189 103&ROKEBY3 345 1 | B | 1158 | 0.21116 | 105.9892 | P42:345:NPPD:BKR-MOR-3310:::: | TDF Impact | Rebuild line 650185 WAGENER 3 345 650189 103&ROKEBY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-018 | TO->FROM | 650185 WAGENER 3 345 650189 103&ROKEBY3 345 1 | B | 1158 | 0.21116 | 105.9892 | P42:345:NPPD:L3502A.MOORE.MCCOOL.CB3310:::: | TDF Impact | Rebuild line 650185 WAGENER 3 345 650189 103&ROKEBY3 345 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.17512 | 106.0256 | P23:345:MEC:ORIENT:902::EHV: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.1749 | 106.0311 | P55:345:MEC:ORIENT | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.17515 | 106.0554 | P12:345:MEC:ORIENT:NORTHBORO:1 | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-018 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.034913 | 106.6762 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.22461 | 106.9411 | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | TO->FROM | 640278 SHELDON7 115 640591 OLIVECREEK 7 115 1 | B | 400 | 0.10664 | 107.3677 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Rebuild line 640278 SHELDON7 115 640591 OLIVECREEK 7 115 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | TO->FROM | 640278 SHELDON7 115 640591 OLIVECREEK 7 115 2 | B | 400 | 0.10664 | 107.3677 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Rebuild line 640278 SHELDON7 115 640591 OLIVECREEK 7 115 2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-018 | TO->FROM | 640127 COLMB.E7 115 3WXFMR 640:COL.EAST T4 345 1 | B | 336 | 0.050004 | 108.1031 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | TDF Impact | Add 3-winding transformer 640125 COLMB.E3 345 640127 COLMB.E7 115 640129 COLMB.T9 13 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.17195 | 108.859 | P55:345:OPPD:S3740 3::FN13:EHV: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-018 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.03505 | 108.9935 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-018 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.03505 | 109.0153 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-018 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.034923 | 109.4444 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | TO->FROM | 640139 COOPER 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.43259 | 109.7418 | P42:345:NPPD:BKR-MOR-3308:::: | TDF Impact | Rebuild line 640139 COOPER 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-018 | TO->FROM | 645456 S3456 3 345 645458 S3458 3 345 1 | B | 982 | 0.03953 | 109.8564 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Rebuild line 645456 S3456 3 345 645458 S3458 3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-018 | TO->FROM | 640127 COLMB.E7 115 3WXFMR 640:COL.EAST T4 345 1 | B | 336 | 0.048521 | 111.4413 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | TDF Impact | Add 3-winding transformer 640125 COLMB.E3 345 640127 COLMB.E7 115 640129 COLMB.T9 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | TO->FROM | 640139 COOPER 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.43171 | 111.8885 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | TDF Impact | Rebuild line 640139 COOPER 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.2362 | 113.2096 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.22587 | 115.9916 | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | TO->FROM | 640076 BEATRCE7 115 640088 BPS SUB7 115 1 | B | 193 | 0.062317 | 116.5529 | Single 640076 BEATRCE7 115 640088 BPSSUB7 115 2 | Cumulative Impact | DIS2301_P2_G00_ERIS_2_640_NPPD_TO_1000_DAYKIN_345KV_SUB.idv : DISIS_2023 Identified Upgrade
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | TO->FROM | 640076 BEATRCE7 115 640088 BPS SUB7 115 1 | B | 193 | 0.062317 | 116.5529 | Single 640076 BEATRCE7 115 640088 BPSSUB7 115 2 | Cumulative Impact | DIS2301_P2_G00_ERIS_3_640_NPPD_TO_2000_add_BPS_345_Lines_Rev34.idv : DISIS_2023 Identified Upgrade
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-018 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.035431 | 118.0094 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-018 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.034552 | 119.5678 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.32424 | 120.1399 | Single 640600 DAYKIN3 345 771999 G23-222-POI 345 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.32311 | 120.7011 | Single 640600 DAYKIN3 345 771999 G23-222-POI 345 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-018 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.034552 | 120.8848 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-018 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.034689 | 121.2729 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-018 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.034689 | 121.3014 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-018 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.066519 | 121.3265 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-018 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.066519 | 121.3266 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-018 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.034542 | 121.5027 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-018 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.064932 | 121.5754 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-018 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.064932 | 121.5756 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.23767 | 121.9917 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-018 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.034689 | 122.5957 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-018 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.034689 | 122.6148 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-018 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.034542 | 122.8495 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-018 | TO->FROM | 645454 S3454 3 345 650185 WAGENER 3 345 1 | B | 982 | 0.22122 | 124.4523 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | Rebuild line 645454 S3454 3 345 650185 WAGENER 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-018 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.066824 | 125.6647 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-018 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.066823 | 125.6649 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-018 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.065232 | 125.7875 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-018 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.065231 | 125.7878 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-018 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.035134 | 130.4818 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-018 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.035134 | 132.0705 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-018 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.034372 | 146.377 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-018 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.034525 | 148.5944 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-018 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.034525 | 148.6147 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-018 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.034382 | 148.9728 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-018 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.034372 | 149.1688 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | TO->FROM | 640234 HUMBOLT5 161 3WXFMR 640:HUMBOLDT T2 161 1 | B | 126 | 0.11827 | 149.6902 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | Cumulative Impact | Add 3-winding transformer 640234 HUMBOLT5 161 640235 HUMBOLT7 115 643087 HUMBOLDT T29 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-018 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.034525 | 151.4021 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-018 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.034525 | 151.42 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-018 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.034382 | 151.7992 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | TO->FROM | 640076 BEATRCE7 115 640088 BPS SUB7 115 1 | B | 193 | 0.13921 | 152.117 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | Cumulative Impact | DIS2301_P2_G00_ERIS_2_640_NPPD_TO_1000_DAYKIN_345KV_SUB.idv : DISIS_2023 Identified Upgrade
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | TO->FROM | 640076 BEATRCE7 115 640088 BPS SUB7 115 1 | B | 193 | 0.13921 | 152.117 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | Cumulative Impact | DIS2301_P2_G00_ERIS_3_640_NPPD_TO_2000_add_BPS_345_Lines_Rev34.idv : DISIS_2023 Identified Upgrade
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | TO->FROM | 640235 HUMBOLT7 115 640361 STEINER7 115 1 | B | 121 | 0.11827 | 152.1307 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | Cumulative Impact | Rebuild line 640235 HUMBOLT7 115 640361 STEINER7 115 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | TO->FROM | 640088 BPS SUB7 115 3WXFMR 640:BPS_345_115 T1 345 1 | B | 417 | 0.23297 | 159.9374 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | TDF Impact | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-018 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.035021 | 159.9633 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | TO->FROM | 640088 BPS SUB7 115 3WXFMR 640:BPS_345_115 T1 345 1 | B | 417 | 0.23284 | 161.1357 | P42:345:NPPD:BKR-MOR-3308:::: | TDF Impact | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-018 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.035021 | 163.2816 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.16766 | 171.4724 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.16766 | 171.4729 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.16729 | 173.7124 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.16729 | 173.713 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | TO->FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 | B | 99 | 0.087347 | 179.5021 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | Cumulative Impact | Rebuild line 640169 FAIRBRY7 115 640208 HARBINE7 115 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 3WXFMR 640:MOORE T1 345 1 | B | 400 | 0.23142 | 185.3265 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | TDF Impact | Add 3-winding transformer 640277 MOORE 3 345 640278 SHELDON7 115 640280 MOORE 9 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.34608 | 194.842 | System Intact | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 3WXFMR 640:MOORE T1 345 1 | B | 400 | 0.22973 | 195.4671 | P42:345:NPPD:BKR-MOR-3308:::: | TDF Impact | Add 3-winding transformer 640277 MOORE 3 345 640278 SHELDON7 115 640280 MOORE 9 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.348 | 202.7501 | System Intact | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.34833 | 203.5263 | P13:115-345:NPPD:T590::MONOLITH.CKT2:: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.34833 | 203.5263 | P13:115-345:NPPD:T590::MONOLITH.CKT1:: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.36356 | 203.9708 | P42:345:NPPD:BKR-CPR-3304:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.35202 | 205.4343 | P23:345:MEC:ORIENT:902::EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.35207 | 205.5053 | P12:345:MEC:ORIENT:NORTHBORO:1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.35145 | 205.9776 | P55:345:MEC:ORIENT | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.34526 | 211.0729 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.35361 | 212.8881 | P55:345:MEC:NORTHBORO | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.35361 | 212.8881 | P23:345:MEC:NORTHBORO:901::EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.36505 | 213.5137 | P42:345:NPPD:BKR-CPR-3304:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.35355 | 213.736 | P23:345:MEC:ORIENT:902::EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.3531 | 213.7657 | P55:345:MEC:ORIENT | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.35361 | 213.7914 | P12:345:MEC:ORIENT:NORTHBORO:1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.46477 | 217.9772 | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.34728 | 219.8543 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.48757 | 230.5239 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.46752 | 236.1008 | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.67359 | 242.4879 | System Intact | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.67304 | 247.7008 | Single 640600 DAYKIN3 345 771999 G23-222-POI 345 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.4907 | 248.1828 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.67092 | 248.2416 | Single 640600 DAYKIN3 345 771999 G23-222-POI 345 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.67965 | 250.2801 | P55:345:MEC:NORTHBORO | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.67965 | 250.2801 | P23:345:MEC:NORTHBORO:901::EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.69504 | 250.332 | Single 640076 BEATRCE7 115 640208 HARBINE7 115 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.67965 | 251.4352 | P12:345:MEC:ORIENT:NORTHBORO:1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.67968 | 251.4821 | P23:345:MEC:ORIENT:902::EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.67976 | 251.8126 | P55:345:MEC:ORIENT | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.69841 | 255.4845 | P42:345:NPPD:BKR-CPR-3304:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.83163 | 257.5476 | P42:345:NPPD:BKR-CPR-3310:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.83163 | 257.5667 | Single 640139 COOPER3 345 640590 OLIVECREEK3 345 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.75004 | 260.7181 | Single 640088 BPSSUB7 115 771999 G23-222-POI 345 771998 'NEW_TER_BPS ' 13 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-018 | TO->FROM | 640088 BPS SUB7 115 3WXFMR 640:BPS_345_115 T1 345 1 | B | 417 | 1 | 354.6039 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | TDF Impact | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.23741 | 100.1843 | P42:345:NPPD:BKR-CPR-3310:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | TO->FROM | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | B | 956 | 0.17558 | 100.2221 | P42:345:NPPD:BKR-TOB-3304:::: | Cumulative Impact | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.17231 | 100.3683 | System Intact | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-019 | TO->FROM | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | B | 956 | 0.12761 | 100.3823 | P42:345:NPPD:BKR-TOB-3304:::: | Cumulative Impact | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | TO->FROM | 640088 BPS SUB7 115 3WXFMR 640:BPS_345_115 T1 345 1 | B | 417 | 0.16295 | 100.483 | P42:345:NPPD:L3502A.MOORE.MCCOOL.CB3310:::: | Cumulative Impact | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | TO->FROM | 640088 BPS SUB7 115 3WXFMR 640:BPS_345_115 T1 345 1 | B | 417 | 0.16295 | 100.483 | P42:345:NPPD:BKR-MOR-3310:::: | Cumulative Impact | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.17439 | 100.5881 | P55:345:MEC:NORTHBORO | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.17439 | 100.6014 | P23:345:MEC:NORTHBORO:901::EHV: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.1802 | 101.1272 | P42:345:NPPD:BKR-CPR-3304:::: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-019 | TO->FROM | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | B | 956 | 0.13318 | 101.3156 | Single 640312 PAULINE3 345 640525 TOBIAS3 345 1 | Cumulative Impact | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.17141 | 101.865 | P55:345:OPPD:S3740 3::FN13:EHV: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.17436 | 101.8856 | P23:345:MEC:ORIENT:902::EHV: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.17439 | 101.919 | P12:345:MEC:ORIENT:NORTHBORO:1 | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.17408 | 102.124 | P55:345:MEC:ORIENT | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | TO->FROM | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | B | 956 | 0.20256 | 102.2146 | P42:345:NPPD:BKR-MOR-3312:::: | TDF Impact | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-019 | TO->FROM | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | B | 956 | 0.13058 | 102.6296 | P42:345:NPPD:BKR-TOB-3304:::: | Cumulative Impact | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | TO->FROM | 640278 SHELDON7 115 640591 OLIVECREEK 7 115 1 | B | 400 | 0.10726 | 103.3162 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Rebuild line 640278 SHELDON7 115 640591 OLIVECREEK 7 115 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | TO->FROM | 640278 SHELDON7 115 640591 OLIVECREEK 7 115 2 | B | 400 | 0.10726 | 103.3162 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Rebuild line 640278 SHELDON7 115 640591 OLIVECREEK 7 115 2
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.22488 | 103.5564 | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-019 | TO->FROM | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | B | 956 | 0.1362 | 104.1025 | Single 640312 PAULINE3 345 640525 TOBIAS3 345 1 | Cumulative Impact | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.17093 | 104.5429 | P55:345:OPPD:S3740 3::FN13:EHV: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-019 | TO->FROM | 645454 S3454 3 345 650185 WAGENER 3 345 1 | B | 982 | 0.15425 | 104.6262 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Rebuild line 645454 S3454 3 345 650185 WAGENER 3 345 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.17515 | 105.6094 | P55:345:MEC:NORTHBORO | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.17515 | 105.6094 | P23:345:MEC:NORTHBORO:901::EHV: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-019 | TO->FROM | 640088 BPS SUB7 115 3WXFMR 640:BPS_345_115 T1 345 1 | B | 417 | 0.22042 | 105.8248 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | TDF Impact | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.18093 | 105.894 | P42:345:NPPD:BKR-CPR-3304:::: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-019 | TO->FROM | 650185 WAGENER 3 345 650189 103&ROKEBY3 345 1 | B | 1158 | 0.21116 | 105.9892 | P42:345:NPPD:BKR-MOR-3310:::: | TDF Impact | Rebuild line 650185 WAGENER 3 345 650189 103&ROKEBY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-019 | TO->FROM | 650185 WAGENER 3 345 650189 103&ROKEBY3 345 1 | B | 1158 | 0.21116 | 105.9892 | P42:345:NPPD:L3502A.MOORE.MCCOOL.CB3310:::: | TDF Impact | Rebuild line 650185 WAGENER 3 345 650189 103&ROKEBY3 345 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.17512 | 106.0256 | P23:345:MEC:ORIENT:902::EHV: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.1749 | 106.0311 | P55:345:MEC:ORIENT | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.17515 | 106.0554 | P12:345:MEC:ORIENT:NORTHBORO:1 | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-019 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.034913 | 106.6762 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.22461 | 106.9411 | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | TO->FROM | 640278 SHELDON7 115 640591 OLIVECREEK 7 115 1 | B | 400 | 0.10664 | 107.3677 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Rebuild line 640278 SHELDON7 115 640591 OLIVECREEK 7 115 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | TO->FROM | 640278 SHELDON7 115 640591 OLIVECREEK 7 115 2 | B | 400 | 0.10664 | 107.3677 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Rebuild line 640278 SHELDON7 115 640591 OLIVECREEK 7 115 2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-019 | TO->FROM | 640127 COLMB.E7 115 3WXFMR 640:COL.EAST T4 345 1 | B | 336 | 0.050004 | 108.1031 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | TDF Impact | Add 3-winding transformer 640125 COLMB.E3 345 640127 COLMB.E7 115 640129 COLMB.T9 13 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.17195 | 108.859 | P55:345:OPPD:S3740 3::FN13:EHV: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-019 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.03505 | 108.9935 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-019 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.03505 | 109.0153 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-019 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.034923 | 109.4444 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | TO->FROM | 640139 COOPER 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.43259 | 109.7418 | P42:345:NPPD:BKR-MOR-3308:::: | TDF Impact | Rebuild line 640139 COOPER 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-019 | TO->FROM | 645456 S3456 3 345 645458 S3458 3 345 1 | B | 982 | 0.03953 | 109.8564 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Rebuild line 645456 S3456 3 345 645458 S3458 3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-019 | TO->FROM | 640127 COLMB.E7 115 3WXFMR 640:COL.EAST T4 345 1 | B | 336 | 0.048521 | 111.4413 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | TDF Impact | Add 3-winding transformer 640125 COLMB.E3 345 640127 COLMB.E7 115 640129 COLMB.T9 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | TO->FROM | 640139 COOPER 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.43171 | 111.8885 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | TDF Impact | Rebuild line 640139 COOPER 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.2362 | 113.2096 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.22587 | 115.9916 | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | TO->FROM | 640076 BEATRCE7 115 640088 BPS SUB7 115 1 | B | 193 | 0.062317 | 116.5529 | Single 640076 BEATRCE7 115 640088 BPSSUB7 115 2 | Cumulative Impact | DIS2301_P2_G00_ERIS_2_640_NPPD_TO_1000_DAYKIN_345KV_SUB.idv : DISIS_2023 Identified Upgrade
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | TO->FROM | 640076 BEATRCE7 115 640088 BPS SUB7 115 1 | B | 193 | 0.062317 | 116.5529 | Single 640076 BEATRCE7 115 640088 BPSSUB7 115 2 | Cumulative Impact | DIS2301_P2_G00_ERIS_3_640_NPPD_TO_2000_add_BPS_345_Lines_Rev34.idv : DISIS_2023 Identified Upgrade
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-019 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.035431 | 118.0094 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-019 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.034552 | 119.5678 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.32424 | 120.1399 | Single 640600 DAYKIN3 345 771999 G23-222-POI 345 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.32311 | 120.7011 | Single 640600 DAYKIN3 345 771999 G23-222-POI 345 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-019 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.034552 | 120.8848 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-019 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.034689 | 121.2729 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-019 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.034689 | 121.3014 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-019 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.066519 | 121.3265 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-019 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.066519 | 121.3266 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-019 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.034542 | 121.5027 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-019 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.064932 | 121.5754 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-019 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.064932 | 121.5756 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.23767 | 121.9917 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-019 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.034689 | 122.5957 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-019 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.034689 | 122.6148 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-019 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.034542 | 122.8495 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-019 | TO->FROM | 645454 S3454 3 345 650185 WAGENER 3 345 1 | B | 982 | 0.22122 | 124.4523 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | Rebuild line 645454 S3454 3 345 650185 WAGENER 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-019 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.066824 | 125.6647 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-019 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.066823 | 125.6649 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-019 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.065232 | 125.7875 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-019 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.065231 | 125.7878 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-019 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.035134 | 130.4818 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-019 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.035134 | 132.0705 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-019 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.034372 | 146.377 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-019 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.034525 | 148.5944 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-019 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.034525 | 148.6147 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-019 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.034382 | 148.9728 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-019 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.034372 | 149.1688 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | TO->FROM | 640234 HUMBOLT5 161 3WXFMR 640:HUMBOLDT T2 161 1 | B | 126 | 0.11827 | 149.6902 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | Cumulative Impact | Add 3-winding transformer 640234 HUMBOLT5 161 640235 HUMBOLT7 115 643087 HUMBOLDT T29 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-019 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.034525 | 151.4021 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-019 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.034525 | 151.42 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-019 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.034382 | 151.7992 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | TO->FROM | 640076 BEATRCE7 115 640088 BPS SUB7 115 1 | B | 193 | 0.13921 | 152.117 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | Cumulative Impact | DIS2301_P2_G00_ERIS_2_640_NPPD_TO_1000_DAYKIN_345KV_SUB.idv : DISIS_2023 Identified Upgrade
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | TO->FROM | 640076 BEATRCE7 115 640088 BPS SUB7 115 1 | B | 193 | 0.13921 | 152.117 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | Cumulative Impact | DIS2301_P2_G00_ERIS_3_640_NPPD_TO_2000_add_BPS_345_Lines_Rev34.idv : DISIS_2023 Identified Upgrade
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | TO->FROM | 640235 HUMBOLT7 115 640361 STEINER7 115 1 | B | 121 | 0.11827 | 152.1307 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | Cumulative Impact | Rebuild line 640235 HUMBOLT7 115 640361 STEINER7 115 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | TO->FROM | 640088 BPS SUB7 115 3WXFMR 640:BPS_345_115 T1 345 1 | B | 417 | 0.23297 | 159.9374 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | TDF Impact | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-019 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.035021 | 159.9633 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | TO->FROM | 640088 BPS SUB7 115 3WXFMR 640:BPS_345_115 T1 345 1 | B | 417 | 0.23284 | 161.1357 | P42:345:NPPD:BKR-MOR-3308:::: | TDF Impact | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-019 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.035021 | 163.2816 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.16766 | 171.4724 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.16766 | 171.4729 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.16729 | 173.7124 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.16729 | 173.713 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | TO->FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 | B | 99 | 0.087347 | 179.5021 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | Cumulative Impact | Rebuild line 640169 FAIRBRY7 115 640208 HARBINE7 115 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 3WXFMR 640:MOORE T1 345 1 | B | 400 | 0.23142 | 185.3265 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | TDF Impact | Add 3-winding transformer 640277 MOORE 3 345 640278 SHELDON7 115 640280 MOORE 9 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.34608 | 194.842 | System Intact | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 3WXFMR 640:MOORE T1 345 1 | B | 400 | 0.22973 | 195.4671 | P42:345:NPPD:BKR-MOR-3308:::: | TDF Impact | Add 3-winding transformer 640277 MOORE 3 345 640278 SHELDON7 115 640280 MOORE 9 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.348 | 202.7501 | System Intact | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.34833 | 203.5263 | P13:115-345:NPPD:T590::MONOLITH.CKT2:: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.34833 | 203.5263 | P13:115-345:NPPD:T590::MONOLITH.CKT1:: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.36356 | 203.9708 | P42:345:NPPD:BKR-CPR-3304:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.35202 | 205.4343 | P23:345:MEC:ORIENT:902::EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.35207 | 205.5053 | P12:345:MEC:ORIENT:NORTHBORO:1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.35145 | 205.9776 | P55:345:MEC:ORIENT | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.34526 | 211.0729 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.35361 | 212.8881 | P55:345:MEC:NORTHBORO | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.35361 | 212.8881 | P23:345:MEC:NORTHBORO:901::EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.36505 | 213.5137 | P42:345:NPPD:BKR-CPR-3304:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.35355 | 213.736 | P23:345:MEC:ORIENT:902::EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.3531 | 213.7657 | P55:345:MEC:ORIENT | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.35361 | 213.7914 | P12:345:MEC:ORIENT:NORTHBORO:1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.46477 | 217.9772 | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.34728 | 219.8543 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.48757 | 230.5239 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.46752 | 236.1008 | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.67359 | 242.4879 | System Intact | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.67304 | 247.7008 | Single 640600 DAYKIN3 345 771999 G23-222-POI 345 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.4907 | 248.1828 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.67092 | 248.2416 | Single 640600 DAYKIN3 345 771999 G23-222-POI 345 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.67965 | 250.2801 | P55:345:MEC:NORTHBORO | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.67965 | 250.2801 | P23:345:MEC:NORTHBORO:901::EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.69504 | 250.332 | Single 640076 BEATRCE7 115 640208 HARBINE7 115 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.67965 | 251.4352 | P12:345:MEC:ORIENT:NORTHBORO:1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.67968 | 251.4821 | P23:345:MEC:ORIENT:902::EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.67976 | 251.8126 | P55:345:MEC:ORIENT | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.69841 | 255.4845 | P42:345:NPPD:BKR-CPR-3304:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.83163 | 257.5476 | P42:345:NPPD:BKR-CPR-3310:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.83163 | 257.5667 | Single 640139 COOPER3 345 640590 OLIVECREEK3 345 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.75004 | 260.7181 | Single 640088 BPSSUB7 115 771999 G23-222-POI 345 771998 'NEW_TER_BPS ' 13 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-019 | TO->FROM | 640088 BPS SUB7 115 3WXFMR 640:BPS_345_115 T1 345 1 | B | 417 | 1 | 354.6039 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | TDF Impact | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.39999 | 100.1843 | P42:345:NPPD:BKR-CPR-3310:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-020 | TO->FROM | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | B | 956 | 0.18564 | 100.2221 | P42:345:NPPD:BKR-TOB-3304:::: | Cumulative Impact | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.32694 | 100.3683 | System Intact | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-020 | TO->FROM | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | B | 956 | 0.15066 | 100.3823 | P42:345:NPPD:BKR-TOB-3304:::: | Cumulative Impact | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.3291 | 100.5881 | P55:345:MEC:NORTHBORO | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.3291 | 100.6014 | P23:345:MEC:NORTHBORO:901::EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.33548 | 101.1272 | P42:345:NPPD:BKR-CPR-3304:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-020 | TO->FROM | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | B | 956 | 0.14667 | 101.3156 | Single 640312 PAULINE3 345 640525 TOBIAS3 345 1 | Cumulative Impact | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.32581 | 101.865 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.32908 | 101.8856 | P23:345:MEC:ORIENT:902::EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.3291 | 101.919 | P12:345:MEC:ORIENT:NORTHBORO:1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.32877 | 102.124 | P55:345:MEC:ORIENT | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-020 | TO->FROM | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | B | 956 | 0.21394 | 102.2146 | P42:345:NPPD:BKR-MOR-3312:::: | TDF Impact | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-020 | TO->FROM | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | B | 956 | 0.15375 | 102.6296 | P42:345:NPPD:BKR-TOB-3304:::: | Cumulative Impact | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-020 | TO->FROM | 640278 SHELDON7 115 640591 OLIVECREEK 7 115 1 | B | 400 | 0.14967 | 103.3162 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Rebuild line 640278 SHELDON7 115 640591 OLIVECREEK 7 115 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-020 | TO->FROM | 640278 SHELDON7 115 640591 OLIVECREEK 7 115 2 | B | 400 | 0.14967 | 103.3162 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Rebuild line 640278 SHELDON7 115 640591 OLIVECREEK 7 115 2
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.28814 | 103.5564 | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-020 | TO->FROM | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | B | 956 | 0.14975 | 104.1025 | Single 640312 PAULINE3 345 640525 TOBIAS3 345 1 | Cumulative Impact | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.32548 | 104.5429 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-020 | TO->FROM | 645454 S3454 3 345 650185 WAGENER 3 345 1 | B | 982 | 0.16662 | 104.6262 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Rebuild line 645454 S3454 3 345 650185 WAGENER 3 345 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.32991 | 105.6094 | P55:345:MEC:NORTHBORO | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.32991 | 105.6094 | P23:345:MEC:NORTHBORO:901::EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.33626 | 105.894 | P42:345:NPPD:BKR-CPR-3304:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-020 | TO->FROM | 650185 WAGENER 3 345 650189 103&ROKEBY3 345 1 | B | 1158 | 0.23794 | 105.9892 | P42:345:NPPD:BKR-MOR-3310:::: | TDF Impact | Rebuild line 650185 WAGENER 3 345 650189 103&ROKEBY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-020 | TO->FROM | 650185 WAGENER 3 345 650189 103&ROKEBY3 345 1 | B | 1158 | 0.23794 | 105.9892 | P42:345:NPPD:L3502A.MOORE.MCCOOL.CB3310:::: | TDF Impact | Rebuild line 650185 WAGENER 3 345 650189 103&ROKEBY3 345 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.32988 | 106.0256 | P23:345:MEC:ORIENT:902::EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.32964 | 106.0311 | P55:345:MEC:ORIENT | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.32991 | 106.0554 | P12:345:MEC:ORIENT:NORTHBORO:1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-020 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.036935 | 106.6762 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.28817 | 106.9411 | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-020 | TO->FROM | 640278 SHELDON7 115 640591 OLIVECREEK 7 115 1 | B | 400 | 0.14939 | 107.3677 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Rebuild line 640278 SHELDON7 115 640591 OLIVECREEK 7 115 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-020 | TO->FROM | 640278 SHELDON7 115 640591 OLIVECREEK 7 115 2 | B | 400 | 0.14939 | 107.3677 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Rebuild line 640278 SHELDON7 115 640591 OLIVECREEK 7 115 2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-020 | TO->FROM | 640127 COLMB.E7 115 3WXFMR 640:COL.EAST T4 345 1 | B | 336 | 0.055374 | 108.1031 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | TDF Impact | Add 3-winding transformer 640125 COLMB.E3 345 640127 COLMB.E7 115 640129 COLMB.T9 13 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.32656 | 108.859 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-020 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.037085 | 108.9935 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-020 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.037085 | 109.0153 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-020 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.036941 | 109.4444 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-020 | TO->FROM | 640139 COOPER 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.46393 | 109.7418 | P42:345:NPPD:BKR-MOR-3308:::: | TDF Impact | Rebuild line 640139 COOPER 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-020 | TO->FROM | 645456 S3456 3 345 645458 S3458 3 345 1 | B | 982 | 0.040305 | 109.8564 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Rebuild line 645456 S3456 3 345 645458 S3458 3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-020 | TO->FROM | 640127 COLMB.E7 115 3WXFMR 640:COL.EAST T4 345 1 | B | 336 | 0.053886 | 111.4413 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | TDF Impact | Add 3-winding transformer 640125 COLMB.E3 345 640127 COLMB.E7 115 640129 COLMB.T9 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-020 | TO->FROM | 640139 COOPER 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.46353 | 111.8885 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | TDF Impact | Rebuild line 640139 COOPER 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.30176 | 113.2096 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.28946 | 115.9916 | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-020 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.037506 | 118.0094 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-020 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.036511 | 119.5678 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.36742 | 120.1399 | Single 640600 DAYKIN3 345 771999 G23-222-POI 345 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.36618 | 120.7011 | Single 640600 DAYKIN3 345 771999 G23-222-POI 345 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-020 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.036511 | 120.8848 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-020 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.03666 | 121.2729 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-020 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.03666 | 121.3014 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-020 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.14359 | 121.3265 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-020 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.14359 | 121.3266 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-020 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.036496 | 121.5027 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-020 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.14254 | 121.5754 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-020 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.14254 | 121.5756 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.30326 | 121.9917 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-020 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.03666 | 122.5957 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-020 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.03666 | 122.6148 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-020 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.036496 | 122.8495 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-020 | TO->FROM | 645454 S3454 3 345 650185 WAGENER 3 345 1 | B | 982 | 0.23703 | 124.4523 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | Rebuild line 645454 S3454 3 345 650185 WAGENER 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-020 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.14397 | 125.6647 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-020 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.14397 | 125.6649 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-020 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.14292 | 125.7875 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-020 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.14292 | 125.7878 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-020 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.037142 | 130.4818 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-020 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.037142 | 132.0705 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-020 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.036362 | 146.377 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-020 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.036527 | 148.5944 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-020 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.036527 | 148.6147 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-020 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.036368 | 148.9728 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-020 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.036362 | 149.1688 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-020 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.036527 | 151.4021 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-020 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.036527 | 151.42 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-020 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.036368 | 151.7992 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-020 | TO->FROM | 640088 BPS SUB7 115 3WXFMR 640:BPS_345_115 T1 345 1 | B | 417 | 0.11523 | 159.9374 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-020 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.037063 | 159.9633 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-020 | TO->FROM | 640088 BPS SUB7 115 3WXFMR 640:BPS_345_115 T1 345 1 | B | 417 | 0.11516 | 161.1357 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-020 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.037063 | 163.2816 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-020 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.21062 | 171.4724 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | TDF Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-020 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.21062 | 171.4729 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | TDF Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-020 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.21045 | 173.7124 | P42:345:NPPD:BKR-MOR-3308:::: | TDF Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-020 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.21045 | 173.713 | P42:345:NPPD:BKR-MOR-3308:::: | TDF Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 3WXFMR 640:MOORE T1 345 1 | B | 400 | 0.22823 | 185.3265 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | TDF Impact | Add 3-winding transformer 640277 MOORE 3 345 640278 SHELDON7 115 640280 MOORE 9 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.64894 | 194.842 | System Intact | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 3WXFMR 640:MOORE T1 345 1 | B | 400 | 0.22746 | 195.4671 | P42:345:NPPD:BKR-MOR-3308:::: | TDF Impact | Add 3-winding transformer 640277 MOORE 3 345 640278 SHELDON7 115 640280 MOORE 9 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.65092 | 202.7501 | System Intact | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.66267 | 203.5263 | P13:115-345:NPPD:T590::MONOLITH.CKT2:: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.66267 | 203.5263 | P13:115-345:NPPD:T590::MONOLITH.CKT1:: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.66794 | 203.9708 | P42:345:NPPD:BKR-CPR-3304:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.65522 | 205.4343 | P23:345:MEC:ORIENT:902::EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.65527 | 205.5053 | P12:345:MEC:ORIENT:NORTHBORO:1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.65461 | 205.9776 | P55:345:MEC:ORIENT | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.64809 | 211.0729 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.65682 | 212.8881 | P55:345:MEC:NORTHBORO | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.65682 | 212.8881 | P23:345:MEC:NORTHBORO:901::EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.66944 | 213.5137 | P42:345:NPPD:BKR-CPR-3304:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.65676 | 213.736 | P23:345:MEC:ORIENT:902::EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.65628 | 213.7657 | P55:345:MEC:ORIENT | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.65682 | 213.7914 | P12:345:MEC:ORIENT:NORTHBORO:1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.57418 | 217.9772 | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.65017 | 219.8543 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.60102 | 230.5239 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.57684 | 236.1008 | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.7362 | 242.4879 | System Intact | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.73582 | 247.7008 | Single 640600 DAYKIN3 345 771999 G23-222-POI 345 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.60407 | 248.1828 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.7336 | 248.2416 | Single 640600 DAYKIN3 345 771999 G23-222-POI 345 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.74226 | 250.2801 | P55:345:MEC:NORTHBORO | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.74226 | 250.2801 | P23:345:MEC:NORTHBORO:901::EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.74695 | 250.332 | Single 640076 BEATRCE7 115 640208 HARBINE7 115 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.74226 | 251.4352 | P12:345:MEC:ORIENT:NORTHBORO:1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.74228 | 251.4821 | P23:345:MEC:ORIENT:902::EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.74237 | 251.8126 | P55:345:MEC:ORIENT | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.76123 | 255.4845 | P42:345:NPPD:BKR-CPR-3304:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.90152 | 257.5476 | P42:345:NPPD:BKR-CPR-3310:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.90152 | 257.5667 | Single 640139 COOPER3 345 640590 OLIVECREEK3 345 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-020 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.75004 | 260.7181 | Single 640088 BPSSUB7 115 771999 G23-222-POI 345 771998 'NEW_TER_BPS ' 13 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.39999 | 100.1843 | P42:345:NPPD:BKR-CPR-3310:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-021 | TO->FROM | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | B | 956 | 0.18564 | 100.2221 | P42:345:NPPD:BKR-TOB-3304:::: | Cumulative Impact | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.32694 | 100.3683 | System Intact | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-021 | TO->FROM | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | B | 956 | 0.15066 | 100.3823 | P42:345:NPPD:BKR-TOB-3304:::: | Cumulative Impact | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.3291 | 100.5881 | P55:345:MEC:NORTHBORO | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.3291 | 100.6014 | P23:345:MEC:NORTHBORO:901::EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.33548 | 101.1272 | P42:345:NPPD:BKR-CPR-3304:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-021 | TO->FROM | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | B | 956 | 0.14667 | 101.3156 | Single 640312 PAULINE3 345 640525 TOBIAS3 345 1 | Cumulative Impact | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.32581 | 101.865 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.32908 | 101.8856 | P23:345:MEC:ORIENT:902::EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.3291 | 101.919 | P12:345:MEC:ORIENT:NORTHBORO:1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.32877 | 102.124 | P55:345:MEC:ORIENT | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-021 | TO->FROM | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | B | 956 | 0.21394 | 102.2146 | P42:345:NPPD:BKR-MOR-3312:::: | TDF Impact | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-021 | TO->FROM | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | B | 956 | 0.15375 | 102.6296 | P42:345:NPPD:BKR-TOB-3304:::: | Cumulative Impact | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-021 | TO->FROM | 640278 SHELDON7 115 640591 OLIVECREEK 7 115 1 | B | 400 | 0.14967 | 103.3162 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Rebuild line 640278 SHELDON7 115 640591 OLIVECREEK 7 115 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-021 | TO->FROM | 640278 SHELDON7 115 640591 OLIVECREEK 7 115 2 | B | 400 | 0.14967 | 103.3162 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Rebuild line 640278 SHELDON7 115 640591 OLIVECREEK 7 115 2
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.28814 | 103.5564 | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-021 | TO->FROM | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | B | 956 | 0.14975 | 104.1025 | Single 640312 PAULINE3 345 640525 TOBIAS3 345 1 | Cumulative Impact | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.32548 | 104.5429 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-021 | TO->FROM | 645454 S3454 3 345 650185 WAGENER 3 345 1 | B | 982 | 0.16662 | 104.6262 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Rebuild line 645454 S3454 3 345 650185 WAGENER 3 345 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.32991 | 105.6094 | P55:345:MEC:NORTHBORO | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.32991 | 105.6094 | P23:345:MEC:NORTHBORO:901::EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.33626 | 105.894 | P42:345:NPPD:BKR-CPR-3304:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-021 | TO->FROM | 650185 WAGENER 3 345 650189 103&ROKEBY3 345 1 | B | 1158 | 0.23794 | 105.9892 | P42:345:NPPD:BKR-MOR-3310:::: | TDF Impact | Rebuild line 650185 WAGENER 3 345 650189 103&ROKEBY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-021 | TO->FROM | 650185 WAGENER 3 345 650189 103&ROKEBY3 345 1 | B | 1158 | 0.23794 | 105.9892 | P42:345:NPPD:L3502A.MOORE.MCCOOL.CB3310:::: | TDF Impact | Rebuild line 650185 WAGENER 3 345 650189 103&ROKEBY3 345 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.32988 | 106.0256 | P23:345:MEC:ORIENT:902::EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.32964 | 106.0311 | P55:345:MEC:ORIENT | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.32991 | 106.0554 | P12:345:MEC:ORIENT:NORTHBORO:1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-021 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.036935 | 106.6762 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.28817 | 106.9411 | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-021 | TO->FROM | 640278 SHELDON7 115 640591 OLIVECREEK 7 115 1 | B | 400 | 0.14939 | 107.3677 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Rebuild line 640278 SHELDON7 115 640591 OLIVECREEK 7 115 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-021 | TO->FROM | 640278 SHELDON7 115 640591 OLIVECREEK 7 115 2 | B | 400 | 0.14939 | 107.3677 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Rebuild line 640278 SHELDON7 115 640591 OLIVECREEK 7 115 2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-021 | TO->FROM | 640127 COLMB.E7 115 3WXFMR 640:COL.EAST T4 345 1 | B | 336 | 0.055374 | 108.1031 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | TDF Impact | Add 3-winding transformer 640125 COLMB.E3 345 640127 COLMB.E7 115 640129 COLMB.T9 13 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.32656 | 108.859 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-021 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.037085 | 108.9935 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-021 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.037085 | 109.0153 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-021 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.036941 | 109.4444 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-021 | TO->FROM | 640139 COOPER 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.46393 | 109.7418 | P42:345:NPPD:BKR-MOR-3308:::: | TDF Impact | Rebuild line 640139 COOPER 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-021 | TO->FROM | 645456 S3456 3 345 645458 S3458 3 345 1 | B | 982 | 0.040305 | 109.8564 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Rebuild line 645456 S3456 3 345 645458 S3458 3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-021 | TO->FROM | 640127 COLMB.E7 115 3WXFMR 640:COL.EAST T4 345 1 | B | 336 | 0.053886 | 111.4413 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | TDF Impact | Add 3-winding transformer 640125 COLMB.E3 345 640127 COLMB.E7 115 640129 COLMB.T9 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-021 | TO->FROM | 640139 COOPER 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.46353 | 111.8885 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | TDF Impact | Rebuild line 640139 COOPER 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.30176 | 113.2096 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.28946 | 115.9916 | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-021 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.037506 | 118.0094 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-021 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.036511 | 119.5678 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.36742 | 120.1399 | Single 640600 DAYKIN3 345 771999 G23-222-POI 345 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.36618 | 120.7011 | Single 640600 DAYKIN3 345 771999 G23-222-POI 345 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-021 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.036511 | 120.8848 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-021 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.03666 | 121.2729 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-021 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.03666 | 121.3014 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-021 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.14359 | 121.3265 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-021 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.14359 | 121.3266 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-021 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.036496 | 121.5027 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-021 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.14254 | 121.5754 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-021 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.14254 | 121.5756 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.30326 | 121.9917 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-021 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.03666 | 122.5957 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-021 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.03666 | 122.6148 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-021 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.036496 | 122.8495 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-021 | TO->FROM | 645454 S3454 3 345 650185 WAGENER 3 345 1 | B | 982 | 0.23703 | 124.4523 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | Rebuild line 645454 S3454 3 345 650185 WAGENER 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-021 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.14397 | 125.6647 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-021 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.14397 | 125.6649 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-021 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.14292 | 125.7875 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-021 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.14292 | 125.7878 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-021 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.037142 | 130.4818 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-021 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.037142 | 132.0705 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-021 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.036362 | 146.377 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-021 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.036527 | 148.5944 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-021 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.036527 | 148.6147 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-021 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.036368 | 148.9728 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-021 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.036362 | 149.1688 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-021 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.036527 | 151.4021 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-021 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.036527 | 151.42 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-021 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.036368 | 151.7992 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-021 | TO->FROM | 640088 BPS SUB7 115 3WXFMR 640:BPS_345_115 T1 345 1 | B | 417 | 0.11523 | 159.9374 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-021 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.037063 | 159.9633 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-021 | TO->FROM | 640088 BPS SUB7 115 3WXFMR 640:BPS_345_115 T1 345 1 | B | 417 | 0.11516 | 161.1357 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-021 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.037063 | 163.2816 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-021 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.21062 | 171.4724 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | TDF Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-021 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.21062 | 171.4729 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | TDF Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-021 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.21045 | 173.7124 | P42:345:NPPD:BKR-MOR-3308:::: | TDF Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-021 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.21045 | 173.713 | P42:345:NPPD:BKR-MOR-3308:::: | TDF Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 3WXFMR 640:MOORE T1 345 1 | B | 400 | 0.22823 | 185.3265 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | TDF Impact | Add 3-winding transformer 640277 MOORE 3 345 640278 SHELDON7 115 640280 MOORE 9 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.64894 | 194.842 | System Intact | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 3WXFMR 640:MOORE T1 345 1 | B | 400 | 0.22746 | 195.4671 | P42:345:NPPD:BKR-MOR-3308:::: | TDF Impact | Add 3-winding transformer 640277 MOORE 3 345 640278 SHELDON7 115 640280 MOORE 9 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.65092 | 202.7501 | System Intact | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.66267 | 203.5263 | P13:115-345:NPPD:T590::MONOLITH.CKT2:: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.66267 | 203.5263 | P13:115-345:NPPD:T590::MONOLITH.CKT1:: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.66794 | 203.9708 | P42:345:NPPD:BKR-CPR-3304:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.65522 | 205.4343 | P23:345:MEC:ORIENT:902::EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.65527 | 205.5053 | P12:345:MEC:ORIENT:NORTHBORO:1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.65461 | 205.9776 | P55:345:MEC:ORIENT | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.64809 | 211.0729 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.65682 | 212.8881 | P55:345:MEC:NORTHBORO | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.65682 | 212.8881 | P23:345:MEC:NORTHBORO:901::EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.66944 | 213.5137 | P42:345:NPPD:BKR-CPR-3304:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.65676 | 213.736 | P23:345:MEC:ORIENT:902::EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.65628 | 213.7657 | P55:345:MEC:ORIENT | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.65682 | 213.7914 | P12:345:MEC:ORIENT:NORTHBORO:1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.57418 | 217.9772 | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.65017 | 219.8543 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.60102 | 230.5239 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.57684 | 236.1008 | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.7362 | 242.4879 | System Intact | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.73582 | 247.7008 | Single 640600 DAYKIN3 345 771999 G23-222-POI 345 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.60407 | 248.1828 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.7336 | 248.2416 | Single 640600 DAYKIN3 345 771999 G23-222-POI 345 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.74226 | 250.2801 | P55:345:MEC:NORTHBORO | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.74226 | 250.2801 | P23:345:MEC:NORTHBORO:901::EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.74695 | 250.332 | Single 640076 BEATRCE7 115 640208 HARBINE7 115 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.74226 | 251.4352 | P12:345:MEC:ORIENT:NORTHBORO:1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.74228 | 251.4821 | P23:345:MEC:ORIENT:902::EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.74237 | 251.8126 | P55:345:MEC:ORIENT | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.76123 | 255.4845 | P42:345:NPPD:BKR-CPR-3304:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.90152 | 257.5476 | P42:345:NPPD:BKR-CPR-3310:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.90152 | 257.5667 | Single 640139 COOPER3 345 640590 OLIVECREEK3 345 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-021 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.75004 | 260.7181 | Single 640088 BPSSUB7 115 771999 G23-222-POI 345 771998 'NEW_TER_BPS ' 13 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.23741 | 100.1843 | P42:345:NPPD:BKR-CPR-3310:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | TO->FROM | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | B | 956 | 0.17558 | 100.2221 | P42:345:NPPD:BKR-TOB-3304:::: | Cumulative Impact | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.17231 | 100.3683 | System Intact | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-022 | TO->FROM | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | B | 956 | 0.12761 | 100.3823 | P42:345:NPPD:BKR-TOB-3304:::: | Cumulative Impact | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | TO->FROM | 640088 BPS SUB7 115 3WXFMR 640:BPS_345_115 T1 345 1 | B | 417 | 0.16295 | 100.483 | P42:345:NPPD:L3502A.MOORE.MCCOOL.CB3310:::: | Cumulative Impact | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | TO->FROM | 640088 BPS SUB7 115 3WXFMR 640:BPS_345_115 T1 345 1 | B | 417 | 0.16295 | 100.483 | P42:345:NPPD:BKR-MOR-3310:::: | Cumulative Impact | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.17439 | 100.5881 | P55:345:MEC:NORTHBORO | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.17439 | 100.6014 | P23:345:MEC:NORTHBORO:901::EHV: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.1802 | 101.1272 | P42:345:NPPD:BKR-CPR-3304:::: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-022 | TO->FROM | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | B | 956 | 0.13318 | 101.3156 | Single 640312 PAULINE3 345 640525 TOBIAS3 345 1 | Cumulative Impact | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.17141 | 101.865 | P55:345:OPPD:S3740 3::FN13:EHV: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.17436 | 101.8856 | P23:345:MEC:ORIENT:902::EHV: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.17439 | 101.919 | P12:345:MEC:ORIENT:NORTHBORO:1 | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.17408 | 102.124 | P55:345:MEC:ORIENT | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | TO->FROM | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | B | 956 | 0.20256 | 102.2146 | P42:345:NPPD:BKR-MOR-3312:::: | TDF Impact | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-022 | TO->FROM | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | B | 956 | 0.13058 | 102.6296 | P42:345:NPPD:BKR-TOB-3304:::: | Cumulative Impact | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | TO->FROM | 640278 SHELDON7 115 640591 OLIVECREEK 7 115 1 | B | 400 | 0.10726 | 103.3162 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Rebuild line 640278 SHELDON7 115 640591 OLIVECREEK 7 115 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | TO->FROM | 640278 SHELDON7 115 640591 OLIVECREEK 7 115 2 | B | 400 | 0.10726 | 103.3162 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Rebuild line 640278 SHELDON7 115 640591 OLIVECREEK 7 115 2
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.22488 | 103.5564 | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-022 | TO->FROM | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | B | 956 | 0.1362 | 104.1025 | Single 640312 PAULINE3 345 640525 TOBIAS3 345 1 | Cumulative Impact | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.17093 | 104.5429 | P55:345:OPPD:S3740 3::FN13:EHV: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-022 | TO->FROM | 645454 S3454 3 345 650185 WAGENER 3 345 1 | B | 982 | 0.15425 | 104.6262 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Rebuild line 645454 S3454 3 345 650185 WAGENER 3 345 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.17515 | 105.6094 | P55:345:MEC:NORTHBORO | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.17515 | 105.6094 | P23:345:MEC:NORTHBORO:901::EHV: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-022 | TO->FROM | 640088 BPS SUB7 115 3WXFMR 640:BPS_345_115 T1 345 1 | B | 417 | 0.22042 | 105.8248 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | TDF Impact | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.18093 | 105.894 | P42:345:NPPD:BKR-CPR-3304:::: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-022 | TO->FROM | 650185 WAGENER 3 345 650189 103&ROKEBY3 345 1 | B | 1158 | 0.21116 | 105.9892 | P42:345:NPPD:BKR-MOR-3310:::: | TDF Impact | Rebuild line 650185 WAGENER 3 345 650189 103&ROKEBY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-022 | TO->FROM | 650185 WAGENER 3 345 650189 103&ROKEBY3 345 1 | B | 1158 | 0.21116 | 105.9892 | P42:345:NPPD:L3502A.MOORE.MCCOOL.CB3310:::: | TDF Impact | Rebuild line 650185 WAGENER 3 345 650189 103&ROKEBY3 345 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.17512 | 106.0256 | P23:345:MEC:ORIENT:902::EHV: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.1749 | 106.0311 | P55:345:MEC:ORIENT | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.17515 | 106.0554 | P12:345:MEC:ORIENT:NORTHBORO:1 | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-022 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.034913 | 106.6762 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.22461 | 106.9411 | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | TO->FROM | 640278 SHELDON7 115 640591 OLIVECREEK 7 115 1 | B | 400 | 0.10664 | 107.3677 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Rebuild line 640278 SHELDON7 115 640591 OLIVECREEK 7 115 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | TO->FROM | 640278 SHELDON7 115 640591 OLIVECREEK 7 115 2 | B | 400 | 0.10664 | 107.3677 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Rebuild line 640278 SHELDON7 115 640591 OLIVECREEK 7 115 2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-022 | TO->FROM | 640127 COLMB.E7 115 3WXFMR 640:COL.EAST T4 345 1 | B | 336 | 0.050004 | 108.1031 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | TDF Impact | Add 3-winding transformer 640125 COLMB.E3 345 640127 COLMB.E7 115 640129 COLMB.T9 13 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.17195 | 108.859 | P55:345:OPPD:S3740 3::FN13:EHV: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-022 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.03505 | 108.9935 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-022 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.03505 | 109.0153 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-022 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.034923 | 109.4444 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | TO->FROM | 640139 COOPER 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.43259 | 109.7418 | P42:345:NPPD:BKR-MOR-3308:::: | TDF Impact | Rebuild line 640139 COOPER 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-022 | TO->FROM | 645456 S3456 3 345 645458 S3458 3 345 1 | B | 982 | 0.03953 | 109.8564 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Rebuild line 645456 S3456 3 345 645458 S3458 3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-022 | TO->FROM | 640127 COLMB.E7 115 3WXFMR 640:COL.EAST T4 345 1 | B | 336 | 0.048521 | 111.4413 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | TDF Impact | Add 3-winding transformer 640125 COLMB.E3 345 640127 COLMB.E7 115 640129 COLMB.T9 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | TO->FROM | 640139 COOPER 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.43171 | 111.8885 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | TDF Impact | Rebuild line 640139 COOPER 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.2362 | 113.2096 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.22587 | 115.9916 | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | TO->FROM | 640076 BEATRCE7 115 640088 BPS SUB7 115 1 | B | 193 | 0.062317 | 116.5529 | Single 640076 BEATRCE7 115 640088 BPSSUB7 115 2 | Cumulative Impact | DIS2301_P2_G00_ERIS_2_640_NPPD_TO_1000_DAYKIN_345KV_SUB.idv : DISIS_2023 Identified Upgrade
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | TO->FROM | 640076 BEATRCE7 115 640088 BPS SUB7 115 1 | B | 193 | 0.062317 | 116.5529 | Single 640076 BEATRCE7 115 640088 BPSSUB7 115 2 | Cumulative Impact | DIS2301_P2_G00_ERIS_3_640_NPPD_TO_2000_add_BPS_345_Lines_Rev34.idv : DISIS_2023 Identified Upgrade
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-022 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.035431 | 118.0094 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-022 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.034552 | 119.5678 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.32424 | 120.1399 | Single 640600 DAYKIN3 345 771999 G23-222-POI 345 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.32311 | 120.7011 | Single 640600 DAYKIN3 345 771999 G23-222-POI 345 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-022 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.034552 | 120.8848 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-022 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.034689 | 121.2729 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-022 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.034689 | 121.3014 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-022 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.066519 | 121.3265 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-022 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.066519 | 121.3266 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-022 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.034542 | 121.5027 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-022 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.064932 | 121.5754 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-022 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.064932 | 121.5756 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.23767 | 121.9917 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-022 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.034689 | 122.5957 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-022 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.034689 | 122.6148 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-022 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.034542 | 122.8495 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-022 | TO->FROM | 645454 S3454 3 345 650185 WAGENER 3 345 1 | B | 982 | 0.22122 | 124.4523 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | Rebuild line 645454 S3454 3 345 650185 WAGENER 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-022 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.066824 | 125.6647 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-022 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.066823 | 125.6649 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-022 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.065232 | 125.7875 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-022 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.065231 | 125.7878 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-022 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.035134 | 130.4818 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-022 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.035134 | 132.0705 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-022 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.034372 | 146.377 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-022 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.034525 | 148.5944 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-022 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.034525 | 148.6147 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-022 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.034382 | 148.9728 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-022 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.034372 | 149.1688 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | TO->FROM | 640234 HUMBOLT5 161 3WXFMR 640:HUMBOLDT T2 161 1 | B | 126 | 0.11827 | 149.6902 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | Cumulative Impact | Add 3-winding transformer 640234 HUMBOLT5 161 640235 HUMBOLT7 115 643087 HUMBOLDT T29 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-022 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.034525 | 151.4021 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-022 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.034525 | 151.42 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-022 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.034382 | 151.7992 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | TO->FROM | 640076 BEATRCE7 115 640088 BPS SUB7 115 1 | B | 193 | 0.13921 | 152.117 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | Cumulative Impact | DIS2301_P2_G00_ERIS_2_640_NPPD_TO_1000_DAYKIN_345KV_SUB.idv : DISIS_2023 Identified Upgrade
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | TO->FROM | 640076 BEATRCE7 115 640088 BPS SUB7 115 1 | B | 193 | 0.13921 | 152.117 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | Cumulative Impact | DIS2301_P2_G00_ERIS_3_640_NPPD_TO_2000_add_BPS_345_Lines_Rev34.idv : DISIS_2023 Identified Upgrade
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | TO->FROM | 640235 HUMBOLT7 115 640361 STEINER7 115 1 | B | 121 | 0.11827 | 152.1307 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | Cumulative Impact | Rebuild line 640235 HUMBOLT7 115 640361 STEINER7 115 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | TO->FROM | 640088 BPS SUB7 115 3WXFMR 640:BPS_345_115 T1 345 1 | B | 417 | 0.23297 | 159.9374 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | TDF Impact | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-022 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.035021 | 159.9633 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | TO->FROM | 640088 BPS SUB7 115 3WXFMR 640:BPS_345_115 T1 345 1 | B | 417 | 0.23284 | 161.1357 | P42:345:NPPD:BKR-MOR-3308:::: | TDF Impact | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-022 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.035021 | 163.2816 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.16766 | 171.4724 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.16766 | 171.4729 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.16729 | 173.7124 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.16729 | 173.713 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | TO->FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 | B | 99 | 0.087347 | 179.5021 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | Cumulative Impact | Rebuild line 640169 FAIRBRY7 115 640208 HARBINE7 115 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 3WXFMR 640:MOORE T1 345 1 | B | 400 | 0.23142 | 185.3265 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | TDF Impact | Add 3-winding transformer 640277 MOORE 3 345 640278 SHELDON7 115 640280 MOORE 9 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.34608 | 194.842 | System Intact | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 3WXFMR 640:MOORE T1 345 1 | B | 400 | 0.22973 | 195.4671 | P42:345:NPPD:BKR-MOR-3308:::: | TDF Impact | Add 3-winding transformer 640277 MOORE 3 345 640278 SHELDON7 115 640280 MOORE 9 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.348 | 202.7501 | System Intact | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.34833 | 203.5263 | P13:115-345:NPPD:T590::MONOLITH.CKT2:: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.34833 | 203.5263 | P13:115-345:NPPD:T590::MONOLITH.CKT1:: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.36356 | 203.9708 | P42:345:NPPD:BKR-CPR-3304:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.35202 | 205.4343 | P23:345:MEC:ORIENT:902::EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.35207 | 205.5053 | P12:345:MEC:ORIENT:NORTHBORO:1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.35145 | 205.9776 | P55:345:MEC:ORIENT | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.34526 | 211.0729 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.35361 | 212.8881 | P55:345:MEC:NORTHBORO | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.35361 | 212.8881 | P23:345:MEC:NORTHBORO:901::EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.36505 | 213.5137 | P42:345:NPPD:BKR-CPR-3304:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.35355 | 213.736 | P23:345:MEC:ORIENT:902::EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.3531 | 213.7657 | P55:345:MEC:ORIENT | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.35361 | 213.7914 | P12:345:MEC:ORIENT:NORTHBORO:1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.46477 | 217.9772 | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.34728 | 219.8543 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.48757 | 230.5239 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.46752 | 236.1008 | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.67359 | 242.4879 | System Intact | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.67304 | 247.7008 | Single 640600 DAYKIN3 345 771999 G23-222-POI 345 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.4907 | 248.1828 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.67092 | 248.2416 | Single 640600 DAYKIN3 345 771999 G23-222-POI 345 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.67965 | 250.2801 | P55:345:MEC:NORTHBORO | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.67965 | 250.2801 | P23:345:MEC:NORTHBORO:901::EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.69504 | 250.332 | Single 640076 BEATRCE7 115 640208 HARBINE7 115 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.67965 | 251.4352 | P12:345:MEC:ORIENT:NORTHBORO:1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.67968 | 251.4821 | P23:345:MEC:ORIENT:902::EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.67976 | 251.8126 | P55:345:MEC:ORIENT | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.69841 | 255.4845 | P42:345:NPPD:BKR-CPR-3304:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.83163 | 257.5476 | P42:345:NPPD:BKR-CPR-3310:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.83163 | 257.5667 | Single 640139 COOPER3 345 640590 OLIVECREEK3 345 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.75004 | 260.7181 | Single 640088 BPSSUB7 115 771999 G23-222-POI 345 771998 'NEW_TER_BPS ' 13 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-022 | TO->FROM | 640088 BPS SUB7 115 3WXFMR 640:BPS_345_115 T1 345 1 | B | 417 | 1 | 354.6039 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | TDF Impact | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.23741 | 100.1843 | P42:345:NPPD:BKR-CPR-3310:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | TO->FROM | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | B | 956 | 0.17558 | 100.2221 | P42:345:NPPD:BKR-TOB-3304:::: | Cumulative Impact | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.17231 | 100.3683 | System Intact | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-023 | TO->FROM | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | B | 956 | 0.12761 | 100.3823 | P42:345:NPPD:BKR-TOB-3304:::: | Cumulative Impact | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | TO->FROM | 640088 BPS SUB7 115 3WXFMR 640:BPS_345_115 T1 345 1 | B | 417 | 0.16295 | 100.483 | P42:345:NPPD:L3502A.MOORE.MCCOOL.CB3310:::: | Cumulative Impact | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | TO->FROM | 640088 BPS SUB7 115 3WXFMR 640:BPS_345_115 T1 345 1 | B | 417 | 0.16295 | 100.483 | P42:345:NPPD:BKR-MOR-3310:::: | Cumulative Impact | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.17439 | 100.5881 | P55:345:MEC:NORTHBORO | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.17439 | 100.6014 | P23:345:MEC:NORTHBORO:901::EHV: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.1802 | 101.1272 | P42:345:NPPD:BKR-CPR-3304:::: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-023 | TO->FROM | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | B | 956 | 0.13318 | 101.3156 | Single 640312 PAULINE3 345 640525 TOBIAS3 345 1 | Cumulative Impact | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.17141 | 101.865 | P55:345:OPPD:S3740 3::FN13:EHV: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.17436 | 101.8856 | P23:345:MEC:ORIENT:902::EHV: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.17439 | 101.919 | P12:345:MEC:ORIENT:NORTHBORO:1 | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.17408 | 102.124 | P55:345:MEC:ORIENT | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | TO->FROM | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | B | 956 | 0.20256 | 102.2146 | P42:345:NPPD:BKR-MOR-3312:::: | TDF Impact | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-023 | TO->FROM | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | B | 956 | 0.13058 | 102.6296 | P42:345:NPPD:BKR-TOB-3304:::: | Cumulative Impact | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | TO->FROM | 640278 SHELDON7 115 640591 OLIVECREEK 7 115 1 | B | 400 | 0.10726 | 103.3162 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Rebuild line 640278 SHELDON7 115 640591 OLIVECREEK 7 115 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | TO->FROM | 640278 SHELDON7 115 640591 OLIVECREEK 7 115 2 | B | 400 | 0.10726 | 103.3162 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Rebuild line 640278 SHELDON7 115 640591 OLIVECREEK 7 115 2
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.22488 | 103.5564 | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-023 | TO->FROM | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | B | 956 | 0.1362 | 104.1025 | Single 640312 PAULINE3 345 640525 TOBIAS3 345 1 | Cumulative Impact | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.17093 | 104.5429 | P55:345:OPPD:S3740 3::FN13:EHV: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-023 | TO->FROM | 645454 S3454 3 345 650185 WAGENER 3 345 1 | B | 982 | 0.15425 | 104.6262 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Rebuild line 645454 S3454 3 345 650185 WAGENER 3 345 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.17515 | 105.6094 | P55:345:MEC:NORTHBORO | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.17515 | 105.6094 | P23:345:MEC:NORTHBORO:901::EHV: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-023 | TO->FROM | 640088 BPS SUB7 115 3WXFMR 640:BPS_345_115 T1 345 1 | B | 417 | 0.22042 | 105.8248 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | TDF Impact | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.18093 | 105.894 | P42:345:NPPD:BKR-CPR-3304:::: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-023 | TO->FROM | 650185 WAGENER 3 345 650189 103&ROKEBY3 345 1 | B | 1158 | 0.21116 | 105.9892 | P42:345:NPPD:BKR-MOR-3310:::: | TDF Impact | Rebuild line 650185 WAGENER 3 345 650189 103&ROKEBY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-023 | TO->FROM | 650185 WAGENER 3 345 650189 103&ROKEBY3 345 1 | B | 1158 | 0.21116 | 105.9892 | P42:345:NPPD:L3502A.MOORE.MCCOOL.CB3310:::: | TDF Impact | Rebuild line 650185 WAGENER 3 345 650189 103&ROKEBY3 345 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.17512 | 106.0256 | P23:345:MEC:ORIENT:902::EHV: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.1749 | 106.0311 | P55:345:MEC:ORIENT | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.17515 | 106.0554 | P12:345:MEC:ORIENT:NORTHBORO:1 | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-023 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.034913 | 106.6762 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.22461 | 106.9411 | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | TO->FROM | 640278 SHELDON7 115 640591 OLIVECREEK 7 115 1 | B | 400 | 0.10664 | 107.3677 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Rebuild line 640278 SHELDON7 115 640591 OLIVECREEK 7 115 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | TO->FROM | 640278 SHELDON7 115 640591 OLIVECREEK 7 115 2 | B | 400 | 0.10664 | 107.3677 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Rebuild line 640278 SHELDON7 115 640591 OLIVECREEK 7 115 2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-023 | TO->FROM | 640127 COLMB.E7 115 3WXFMR 640:COL.EAST T4 345 1 | B | 336 | 0.050004 | 108.1031 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | TDF Impact | Add 3-winding transformer 640125 COLMB.E3 345 640127 COLMB.E7 115 640129 COLMB.T9 13 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.17195 | 108.859 | P55:345:OPPD:S3740 3::FN13:EHV: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-023 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.03505 | 108.9935 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-023 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.03505 | 109.0153 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-023 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.034923 | 109.4444 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | TO->FROM | 640139 COOPER 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.43259 | 109.7418 | P42:345:NPPD:BKR-MOR-3308:::: | TDF Impact | Rebuild line 640139 COOPER 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-023 | TO->FROM | 645456 S3456 3 345 645458 S3458 3 345 1 | B | 982 | 0.03953 | 109.8564 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Rebuild line 645456 S3456 3 345 645458 S3458 3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-023 | TO->FROM | 640127 COLMB.E7 115 3WXFMR 640:COL.EAST T4 345 1 | B | 336 | 0.048521 | 111.4413 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | TDF Impact | Add 3-winding transformer 640125 COLMB.E3 345 640127 COLMB.E7 115 640129 COLMB.T9 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | TO->FROM | 640139 COOPER 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.43171 | 111.8885 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | TDF Impact | Rebuild line 640139 COOPER 3 345 640590 OLIVECREEK 3 345 1
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.2362 | 113.2096 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.22587 | 115.9916 | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | TO->FROM | 640076 BEATRCE7 115 640088 BPS SUB7 115 1 | B | 193 | 0.062317 | 116.5529 | Single 640076 BEATRCE7 115 640088 BPSSUB7 115 2 | Cumulative Impact | DIS2301_P2_G00_ERIS_2_640_NPPD_TO_1000_DAYKIN_345KV_SUB.idv : DISIS_2023 Identified Upgrade
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | TO->FROM | 640076 BEATRCE7 115 640088 BPS SUB7 115 1 | B | 193 | 0.062317 | 116.5529 | Single 640076 BEATRCE7 115 640088 BPSSUB7 115 2 | Cumulative Impact | DIS2301_P2_G00_ERIS_3_640_NPPD_TO_2000_add_BPS_345_Lines_Rev34.idv : DISIS_2023 Identified Upgrade
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-023 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.035431 | 118.0094 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-023 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.034552 | 119.5678 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.32424 | 120.1399 | Single 640600 DAYKIN3 345 771999 G23-222-POI 345 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.32311 | 120.7011 | Single 640600 DAYKIN3 345 771999 G23-222-POI 345 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-023 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.034552 | 120.8848 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-023 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.034689 | 121.2729 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-023 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.034689 | 121.3014 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-023 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.066519 | 121.3265 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-023 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.066519 | 121.3266 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-023 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.034542 | 121.5027 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-023 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.064932 | 121.5754 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-023 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.064932 | 121.5756 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.23767 | 121.9917 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-023 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.034689 | 122.5957 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-023 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.034689 | 122.6148 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-023 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.034542 | 122.8495 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-023 | TO->FROM | 645454 S3454 3 345 650185 WAGENER 3 345 1 | B | 982 | 0.22122 | 124.4523 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | Rebuild line 645454 S3454 3 345 650185 WAGENER 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-023 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.066824 | 125.6647 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-023 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.066823 | 125.6649 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-023 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.065232 | 125.7875 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-023 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.065231 | 125.7878 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-023 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.035134 | 130.4818 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-023 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.035134 | 132.0705 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-023 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.034372 | 146.377 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-023 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.034525 | 148.5944 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-023 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.034525 | 148.6147 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-023 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.034382 | 148.9728 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-023 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.034372 | 149.1688 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | TO->FROM | 640234 HUMBOLT5 161 3WXFMR 640:HUMBOLDT T2 161 1 | B | 126 | 0.11827 | 149.6902 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | Cumulative Impact | Add 3-winding transformer 640234 HUMBOLT5 161 640235 HUMBOLT7 115 643087 HUMBOLDT T29 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-023 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.034525 | 151.4021 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-023 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.034525 | 151.42 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-023 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.034382 | 151.7992 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | TO->FROM | 640076 BEATRCE7 115 640088 BPS SUB7 115 1 | B | 193 | 0.13921 | 152.117 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | Cumulative Impact | DIS2301_P2_G00_ERIS_2_640_NPPD_TO_1000_DAYKIN_345KV_SUB.idv : DISIS_2023 Identified Upgrade
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | TO->FROM | 640076 BEATRCE7 115 640088 BPS SUB7 115 1 | B | 193 | 0.13921 | 152.117 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | Cumulative Impact | DIS2301_P2_G00_ERIS_3_640_NPPD_TO_2000_add_BPS_345_Lines_Rev34.idv : DISIS_2023 Identified Upgrade
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | TO->FROM | 640235 HUMBOLT7 115 640361 STEINER7 115 1 | B | 121 | 0.11827 | 152.1307 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | Cumulative Impact | Rebuild line 640235 HUMBOLT7 115 640361 STEINER7 115 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | TO->FROM | 640088 BPS SUB7 115 3WXFMR 640:BPS_345_115 T1 345 1 | B | 417 | 0.23297 | 159.9374 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | TDF Impact | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-023 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.035021 | 159.9633 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | TO->FROM | 640088 BPS SUB7 115 3WXFMR 640:BPS_345_115 T1 345 1 | B | 417 | 0.23284 | 161.1357 | P42:345:NPPD:BKR-MOR-3308:::: | TDF Impact | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-023 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.035021 | 163.2816 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.16766 | 171.4724 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.16766 | 171.4729 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T1 345 1 | B | 417 | 0.16729 | 173.7124 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640596 OLIVECRK.T19 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | TO->FROM | 640591 OLIVECREEK 7 115 3WXFMR 640:MONOLITH T2 345 1 | B | 417 | 0.16729 | 173.713 | P42:345:NPPD:BKR-MOR-3308:::: | Cumulative Impact | Add 3-winding transformer 640590 OLIVECREEK 3 345 640591 OLIVECREEK 7 115 640597 OLIVECRK.T29 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | TO->FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 | B | 99 | 0.087347 | 179.5021 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | Cumulative Impact | Rebuild line 640169 FAIRBRY7 115 640208 HARBINE7 115 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 3WXFMR 640:MOORE T1 345 1 | B | 400 | 0.23142 | 185.3265 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1:: | TDF Impact | Add 3-winding transformer 640277 MOORE 3 345 640278 SHELDON7 115 640280 MOORE 9 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.34608 | 194.842 | System Intact | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 3WXFMR 640:MOORE T1 345 1 | B | 400 | 0.22973 | 195.4671 | P42:345:NPPD:BKR-MOR-3308:::: | TDF Impact | Add 3-winding transformer 640277 MOORE 3 345 640278 SHELDON7 115 640280 MOORE 9 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.348 | 202.7501 | System Intact | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.34833 | 203.5263 | P13:115-345:NPPD:T590::MONOLITH.CKT2:: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.34833 | 203.5263 | P13:115-345:NPPD:T590::MONOLITH.CKT1:: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.36356 | 203.9708 | P42:345:NPPD:BKR-CPR-3304:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.35202 | 205.4343 | P23:345:MEC:ORIENT:902::EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.35207 | 205.5053 | P12:345:MEC:ORIENT:NORTHBORO:1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.35145 | 205.9776 | P55:345:MEC:ORIENT | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.34526 | 211.0729 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.35361 | 212.8881 | P55:345:MEC:NORTHBORO | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.35361 | 212.8881 | P23:345:MEC:NORTHBORO:901::EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.36505 | 213.5137 | P42:345:NPPD:BKR-CPR-3304:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.35355 | 213.736 | P23:345:MEC:ORIENT:902::EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.3531 | 213.7657 | P55:345:MEC:ORIENT | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.35361 | 213.7914 | P12:345:MEC:ORIENT:NORTHBORO:1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.46477 | 217.9772 | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.34728 | 219.8543 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.48757 | 230.5239 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.46752 | 236.1008 | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.67359 | 242.4879 | System Intact | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.67304 | 247.7008 | Single 640600 DAYKIN3 345 771999 G23-222-POI 345 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.4907 | 248.1828 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.67092 | 248.2416 | Single 640600 DAYKIN3 345 771999 G23-222-POI 345 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.67965 | 250.2801 | P55:345:MEC:NORTHBORO | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.67965 | 250.2801 | P23:345:MEC:NORTHBORO:901::EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.69504 | 250.332 | Single 640076 BEATRCE7 115 640208 HARBINE7 115 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.67965 | 251.4352 | P12:345:MEC:ORIENT:NORTHBORO:1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.67968 | 251.4821 | P23:345:MEC:ORIENT:902::EHV: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.67976 | 251.8126 | P55:345:MEC:ORIENT | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.69841 | 255.4845 | P42:345:NPPD:BKR-CPR-3304:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.83163 | 257.5476 | P42:345:NPPD:BKR-CPR-3310:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.83163 | 257.5667 | Single 640139 COOPER3 345 640590 OLIVECREEK3 345 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.75004 | 260.7181 | Single 640088 BPSSUB7 115 771999 G23-222-POI 345 771998 'NEW_TER_BPS ' 13 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-023 | TO->FROM | 640088 BPS SUB7 115 3WXFMR 640:BPS_345_115 T1 345 1 | B | 417 | 1 | 354.6039 | Single 640590 OLIVECREEK3 345 771999 G23-222-POI 345 1 | TDF Impact | Add 3-winding transformer 640088 BPS SUB7 115 771998 NEW_TER_BPS 13 771999 G23-222-POI 345 M2
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-025 | TO->FROM | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | B | 1059 | 0.052602 | 100.2166 | P12:345:AEPW:R.S.S.-7:ONETA--7::: | Cumulative Impact | Rebuild line 509745 CLARKSV7 345 515224 MUSKOGE7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-025 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | A | 157 | 0.035966 | 148.4151 | System Intact | TDF Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-025 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | A | 157 | 0.037145 | 150.7438 | System Intact | TDF Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-025 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | A | 159 | 0.037221 | 153.3873 | System Intact | TDF Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-025 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | B | 159 | 0.050823 | 184.4152 | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | Cumulative Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-025 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | B | 157 | 0.050683 | 185.7511 | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | Cumulative Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 01ALL | 1 | 26SP | T0 | GEN-2024-035 | TO->FROM | 652522 SUMMIT-7 115 655457 BRISTOL-ER7 115 1 | B | 119 | 0.13093 | 102.2469 | P12:345.0:UMZ:# N-1 #:: LINE GROTON__-BE3-CROCKER_-BE3-1 :EHV: | Cumulative Impact | Rebuild line 652522 SUMMIT-7 115 655457 BRISTOL-ER7 115 1
Thermal | 01ALL | 1 | 26SP | T0 | GEN-2024-035 | TO->FROM | 652522 SUMMIT-7 115 655457 BRISTOL-ER7 115 1 | B | 119 | 0.13093 | 103.7992 | P23:345:UMZB:# 7110 #:: CKE IN SD. CKE BREAKER FAULT (192):EHV: | Cumulative Impact | Rebuild line 652522 SUMMIT-7 115 655457 BRISTOL-ER7 115 1
Thermal | 01ALL | 1 | 29SP | T0 | GEN-2024-035 | TO->FROM | 652522 SUMMIT-7 115 655457 BRISTOL-ER7 115 1 | B | 119 | 0.13097 | 104.9568 | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-CROCKER_-BE3-1 :EHV: | Cumulative Impact | Rebuild line 652522 SUMMIT-7 115 655457 BRISTOL-ER7 115 1
Thermal | 01ALL | 1 | 26SP | T0 | GEN-2024-035 | TO->FROM | 652522 SUMMIT-7 115 655457 BRISTOL-ER7 115 1 | B | 119 | 0.13093 | 116.9606 | P12:345.0:UMZ:# N-1 #:: LINE WATERTN3-CROCKER_-BE3-1 :EHV: | Cumulative Impact | Rebuild line 652522 SUMMIT-7 115 655457 BRISTOL-ER7 115 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-041 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063539 | 100.0488 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-041 | TO->FROM | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | B | 997 | 0.21512 | 100.166 | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-041 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.06007 | 100.533 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-041 | TO->FROM | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | B | 997 | 0.21637 | 100.7286 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-041 | TO->FROM | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | B | 997 | 0.21637 | 101.1047 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-041 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.061064 | 102.9616 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-041 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.061064 | 102.9634 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-041 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.061064 | 103.0288 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-041 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.061064 | 103.4739 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-041 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.06472 | 103.9266 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-041 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.061064 | 104.1493 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-041 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.06719 | 104.7552 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-041 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.06719 | 104.888 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-041 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.068321 | 107.2243 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-041 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.061064 | 107.2793 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-041 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.061064 | 107.2794 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-041 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.068321 | 107.2951 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-041 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.061064 | 107.3093 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-041 | TO->FROM | 523959 POTTER_CO 6 230 3WXFMR 526:WAUK 90343-A 230 1 | B | 559 | 0.058962 | 107.3794 | P42:345:SPS:HITCHLAND-1R15:::EHV: | Cumulative Impact | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-041 | TO->FROM | 523959 POTTER_CO 6 230 3WXFMR 526:WAUK 90343-A 230 1 | B | 559 | 0.058962 | 107.3953 | Single 523097 HITCHLAND7 345 523961 POTTER_CO7 345 1 | Cumulative Impact | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-041 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.064672 | 107.5866 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-041 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.061064 | 107.7557 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-041 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.061064 | 108.1822 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-041 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.061064 | 108.2747 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-041 | TO->FROM | 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | B | 997 | 0.8268 | 109.7018 | Single 525832 TUCO_INT7 345 526000 CRAWFISH_DR 345 2 | TDF Impact | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-041 | TO->FROM | 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | B | 997 | 0.82672 | 111.09 | Single 525832 TUCO_INT7 345 526000 CRAWFISH_DR 345 2 | TDF Impact | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-041 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.061064 | 111.3621 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-041 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.068348 | 111.723 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-041 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.068348 | 111.8755 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-041 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.064672 | 115.0541 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-041 | TO->FROM | 511467 L.E.S.-4 138 3WXFMR 520:LES 5 345 2 | B | 515 | 0.030947 | 115.4941 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | TDF Impact | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2
Thermal | 05ALL | 1 | 29L | T0 | GEN-2024-041 | TO->FROM | 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | B | 997 | 0.79034 | 116.6859 | Single 525832 TUCO_INT7 345 526000 CRAWFISH_DR 345 2 | TDF Impact | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-041 | TO->FROM | 511467 L.E.S.-4 138 3WXFMR 520:LES 5 345 2 | B | 515 | 0.03192 | 117.1585 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | TDF Impact | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-041 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.068348 | 118.9427 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-041 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.068348 | 119.313 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-042 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063539 | 100.0488 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-042 | TO->FROM | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | B | 997 | 0.21512 | 100.166 | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-042 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.06007 | 100.533 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-042 | TO->FROM | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | B | 997 | 0.21637 | 100.7286 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-042 | TO->FROM | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | B | 997 | 0.21637 | 101.1047 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-042 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.061064 | 102.9616 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-042 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.061064 | 102.9634 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-042 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.061064 | 103.0288 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-042 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.061064 | 103.4739 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-042 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.06472 | 103.9266 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-042 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.061064 | 104.1493 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-042 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.06719 | 104.7552 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-042 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.06719 | 104.888 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-042 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.068321 | 107.2243 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-042 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.061064 | 107.2793 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-042 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.061064 | 107.2794 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-042 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.068321 | 107.2951 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-042 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.061064 | 107.3093 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-042 | TO->FROM | 523959 POTTER_CO 6 230 3WXFMR 526:WAUK 90343-A 230 1 | B | 559 | 0.058962 | 107.3794 | P42:345:SPS:HITCHLAND-1R15:::EHV: | Cumulative Impact | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-042 | TO->FROM | 523959 POTTER_CO 6 230 3WXFMR 526:WAUK 90343-A 230 1 | B | 559 | 0.058962 | 107.3953 | Single 523097 HITCHLAND7 345 523961 POTTER_CO7 345 1 | Cumulative Impact | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-042 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.064672 | 107.5866 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-042 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.061064 | 107.7557 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-042 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.061064 | 108.1822 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-042 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.061064 | 108.2747 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-042 | TO->FROM | 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | B | 997 | 0.8268 | 109.7018 | Single 525832 TUCO_INT7 345 526000 CRAWFISH_DR 345 2 | TDF Impact | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-042 | TO->FROM | 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | B | 997 | 0.82672 | 111.09 | Single 525832 TUCO_INT7 345 526000 CRAWFISH_DR 345 2 | TDF Impact | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-042 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.061064 | 111.3621 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-042 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.068348 | 111.723 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-042 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.068348 | 111.8755 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-042 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.064672 | 115.0541 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-042 | TO->FROM | 511467 L.E.S.-4 138 3WXFMR 520:LES 5 345 2 | B | 515 | 0.030947 | 115.4941 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | TDF Impact | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2
Thermal | 05ALL | 1 | 29L | T0 | GEN-2024-042 | TO->FROM | 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | B | 997 | 0.79034 | 116.6859 | Single 525832 TUCO_INT7 345 526000 CRAWFISH_DR 345 2 | TDF Impact | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-042 | TO->FROM | 511467 L.E.S.-4 138 3WXFMR 520:LES 5 345 2 | B | 515 | 0.03192 | 117.1585 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | TDF Impact | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-042 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.068348 | 118.9427 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-042 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.068348 | 119.313 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-043 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.073998 | 100.0488 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-043 | TO->FROM | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | B | 997 | 0.17018 | 100.166 | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | Cumulative Impact | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-043 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063318 | 100.533 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-043 | TO->FROM | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | B | 997 | 0.17421 | 100.7286 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-043 | TO->FROM | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | B | 997 | 0.17421 | 101.1047 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-043 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.06414 | 102.9616 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-043 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.06414 | 102.9634 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-043 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.06414 | 103.0288 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-043 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.06414 | 103.4739 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-043 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.078508 | 103.9266 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-043 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.06414 | 104.1493 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-043 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.076983 | 104.7552 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-043 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.076983 | 104.888 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-043 | TO->FROM | 531510 HARBNGR3 115 3WXFMR 534:HARBGR345 345 1 | B | 385 | 0.050062 | 105.7318 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Add 3-winding transformer 531510 HARBNGR3 115 531511 HARBNGR-1 13 531512 HARBNGR7 345 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-043 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.081431 | 107.2243 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-043 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.06414 | 107.2793 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-043 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.06414 | 107.2794 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-043 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.081431 | 107.2951 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-043 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.06414 | 107.3093 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-043 | TO->FROM | 523959 POTTER_CO 6 230 3WXFMR 526:WAUK 90343-A 230 1 | B | 559 | 0.14831 | 107.3794 | P42:345:SPS:HITCHLAND-1R15:::EHV: | Cumulative Impact | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-043 | TO->FROM | 523959 POTTER_CO 6 230 3WXFMR 526:WAUK 90343-A 230 1 | B | 559 | 0.14831 | 107.3953 | Single 523097 HITCHLAND7 345 523961 POTTER_CO7 345 1 | Cumulative Impact | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-043 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.075003 | 107.5866 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-043 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.06414 | 107.7557 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-043 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.06414 | 108.1822 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-043 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.06414 | 108.2747 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-043 | TO->FROM | 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | B | 997 | 0.17684 | 109.7018 | Single 525832 TUCO_INT7 345 526000 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-043 | TO->FROM | 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | B | 997 | 0.1776 | 111.09 | Single 525832 TUCO_INT7 345 526000 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-043 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.06414 | 111.3621 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-043 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.078004 | 111.723 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-043 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.078004 | 111.8755 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-043 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.075003 | 115.0541 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29L | T0 | GEN-2024-043 | TO->FROM | 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | B | 997 | 0.14122 | 116.6859 | Single 525832 TUCO_INT7 345 526000 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-043 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.078004 | 118.9427 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-043 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.078004 | 119.313 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-043 | TO->FROM | 531405 WALKMYR3 115 531510 HARBNGR3 115 1 | B | 331.39 | 0.050062 | 122.4803 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild line 531405 WALKMYR3 115 531510 HARBNGR3 115 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-051 | TO->FROM | 652552 SIOUXCY2 230 3WXFMR 652:652: SC2 KU1B 230 1 | B | 750 | 0.033131 | 100.7724 | P23:345:XEL:396 BKR SPK:::EHV: | TDF Impact | Add 3-winding transformer 652305 SIOUXC29 13 652552 SIOUXCY2 230 652564 SIOUXCY3 345 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-051 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.10434 | 101.6704 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-051 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.10434 | 103.1149 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-051 | TO->FROM | 645454 S3454 3 345 650185 WAGENER 3 345 1 | B | 982 | 0.19287 | 104.6262 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Rebuild line 645454 S3454 3 345 650185 WAGENER 3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-051 | TO->FROM | 646221 S1221 5 161 646255 S1255 5 161 1 | B | 352 | 0.032672 | 105.1616 | P23:345:OPPD:FUTURE 56-55&56-58:::EHV: | TDF Impact | Rebuild line 646221 S1221 5 161 646255 S1255 5 161 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-051 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | A | 110 | 0.10605 | 105.8619 | System Intact | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-051 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.11043 | 106.3207 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-051 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.12476 | 106.6762 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-051 | TO->FROM | 640127 COLMB.E7 115 3WXFMR 640:COL.EAST T4 345 1 | B | 336 | 0.044935 | 108.1031 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | TDF Impact | Add 3-winding transformer 640125 COLMB.E3 345 640127 COLMB.E7 115 640129 COLMB.T9 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-051 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.12495 | 108.9935 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-051 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.12495 | 109.0153 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-051 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.12585 | 109.4444 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-051 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.10747 | 110.3426 | P42:345:LES:L1485::NW68&HOLDREGE.WAGENER.CB3006:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-051 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.1063 | 111.0459 | P13:161-345:OPPD:TX01::S3454.CKT1:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-051 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.1063 | 111.0459 | P13:161-345:OPPD:S1254 T1:::HV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-051 | TO->FROM | 640127 COLMB.E7 115 3WXFMR 640:COL.EAST T4 345 1 | B | 336 | 0.043428 | 111.4413 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | TDF Impact | Add 3-winding transformer 640125 COLMB.E3 345 640127 COLMB.E7 115 640129 COLMB.T9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-051 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.10747 | 112.4118 | P42:345:LES:L1485::NW68&HOLDREGE.WAGENER.CB3006:: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-051 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.1063 | 112.9897 | P13:161-345:OPPD:TX01::S3454.CKT1:: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-051 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.1063 | 112.9897 | P13:161-345:OPPD:S1254 T1:::HV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-051 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.10985 | 117.1294 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-051 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.12508 | 118.0094 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-051 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.10985 | 118.9455 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-051 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.12425 | 119.5678 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-051 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.12425 | 120.8848 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-051 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.12443 | 121.2729 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-051 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.12443 | 121.3014 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-051 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.1253 | 121.5027 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-051 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.12443 | 122.5957 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-051 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.12443 | 122.6148 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-051 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.1253 | 122.8495 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-051 | TO->FROM | 645454 S3454 3 345 650185 WAGENER 3 345 1 | B | 982 | 0.25169 | 124.4523 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | Rebuild line 645454 S3454 3 345 650185 WAGENER 3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-051 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.10445 | 125.7992 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-051 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.10445 | 128.7149 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-051 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.12462 | 130.4818 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-051 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.12462 | 132.0705 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-051 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.12414 | 146.377 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-051 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.10992 | 148.4763 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-051 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.12434 | 148.5944 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-051 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.12434 | 148.6147 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-051 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.12522 | 148.9728 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-051 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.12414 | 149.1688 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-051 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.12434 | 151.4021 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-051 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.12434 | 151.42 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-051 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.12522 | 151.7992 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-051 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.10992 | 152.3912 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-051 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.12459 | 159.9633 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-051 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.12459 | 163.2816 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 03ALL | 1 | 29WP | JTIQ - Expanded Scope Analysis | GEN-2024-054 | TO->FROM | 345072 5MCBAINE 161 345411 5OVERTON 2 161 1 | B | 355 | 0.12865 | 100.48 | P23:345:AECI:7MCCRED:352::: | TDF Impact | Rebuild the 5MCBAINE to 5OVERTON 2 115kV Line 1
Thermal | 03ALL | 1 | 26SP | T1 | GEN-2024-054 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.050262 | 105.0133 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-054 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.05078 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-054 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.05078 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-054 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.05078 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-055 | TO->FROM | 541199 ST JOE 7 345 541400 EASTOWN7 345 1 | B | 1185 | 0.06844 | 100.396 | Single 541199 STJOE7 345 761383 G17-183-TAP 345 1 | Cumulative Impact | Rebuild line 541199 ST JOE 7 345 541400 EASTOWN7 345 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-055 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.059575 | 101.6955 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-055 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.059575 | 101.6955 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-055 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.059575 | 101.6955 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29WP | T1 | GEN-2024-055 | TO->FROM | 301402 5LOSTVALY 161 505502 TRUMAN 5 161 1 | A | 278 | 0.030007 | 103.0727 | System Intact | TDF Impact | Rebuild line 301402 5LOSTVALY 161 505502 TRUMAN 5 161 1
Thermal | 03ALL | 1 | 26SP | T1 | GEN-2024-055 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.062831 | 105.0133 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-055 | TO->FROM | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | B | 1195 | 0.07561 | 107.005 | Single 541199 STJOE7 345 761383 G17-183-TAP 345 1 | Cumulative Impact | Rebuild line 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-055 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | A | 311 | 0.03952 | 111.039 | System Intact | TDF Impact | Rebuild line 300071 5CLINTN 161 761278 G17-108-TAP 161 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-055 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.06118 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-055 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.06118 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-055 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.06118 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-055 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.05346 | 117.7598 | P55:345:OPPD:S3458 3::FN13:EHV: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-055 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | A | 311 | 0.039364 | 121.8886 | System Intact | TDF Impact | Rebuild line 300071 5CLINTN 161 761278 G17-108-TAP 161 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-055 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | A | 334 | 0.03949 | 145.0684 | System Intact | TDF Impact | Rebuild line 300071 5CLINTN 161 761278 G17-108-TAP 161 1
Thermal | 04ALL | 1 | 29SP | T1 | GEN-2024-056 | TO->FROM | 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | A | 1076 | 0.030791 | 100.9112 | System Intact | TDF Impact | Rebuild line 532774 SWISVAL7 345 776380 G23-220-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T1 | GEN-2024-056 | TO->FROM | 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1 | A | 1076 | 0.030791 | 100.9112 | System Intact | TDF Impact | Rebuild line 776380 G23-220-TAP 345 776400 G23-221-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-056 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | A | 901 | 0.039013 | 101.5467 | System Intact | TDF Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-056 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | A | 901 | 0.040305 | 102.5076 | System Intact | TDF Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-056 | TO->FROM | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | A | 1806 | 0.077397 | 104.7272 | System Intact | TDF Impact | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-056 | TO->FROM | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | A | 1806 | 0.083226 | 104.7927 | System Intact | TDF Impact | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-056 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1011 | 0.039653 | 106.9293 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-056 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1011 | 0.036254 | 107.7039 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-056 | TO->FROM | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | A | 827 | 0.041998 | 107.8643 | System Intact | TDF Impact | Rebuild line 532791 BENTON 7 345 532794 ROSEHIL7 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-056 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1187 | 0.048972 | 112.2151 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-056 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.053877 | 112.5233 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-056 | TO->FROM | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | A | 827 | 0.043879 | 113.506 | System Intact | TDF Impact | Rebuild line 532791 BENTON 7 345 532794 ROSEHIL7 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-056 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.064228 | 113.7225 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-056 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.053587 | 114.0272 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-056 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.0559 | 114.0895 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-056 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.078816 | 114.4362 | System Intact | TDF Impact | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-056 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.073426 | 114.6025 | System Intact | TDF Impact | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-056 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.06357 | 115.4477 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-056 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.0559 | 115.647 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-056 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.06357 | 117.1553 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-056 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.06357 | 117.1572 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-056 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.06357 | 119.7129 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-056 | TO->FROM | 514804 MIDLTNT4 138 515381 PECKHMT4 138 1 | A | 194 | 0.040966 | 122.5161 | System Intact | TDF Impact | Rebuild line 514804 MIDLTNT4 138 515381 PECKHMT4 138 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-056 | TO->FROM | 514804 MIDLTNT4 138 515381 PECKHMT4 138 1 | A | 194 | 0.041195 | 122.6094 | System Intact | TDF Impact | Rebuild line 514804 MIDLTNT4 138 515381 PECKHMT4 138 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-056 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.06357 | 124.3274 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-056 | TO->FROM | 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 | A | 194 | 0.040966 | 127.5435 | System Intact | TDF Impact | Rebuild line 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-056 | TO->FROM | 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1 | A | 194 | 0.041195 | 127.5714 | System Intact | TDF Impact | Rebuild line 514759 NEWKIRK4 138 514764 NWKRKAT4 138 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-056 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.040973 | 137.9906 | System Intact | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-056 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.037713 | 138.1985 | System Intact | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-056 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.053785 | 159.2546 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-056 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.053252 | 161.638 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-056 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.053252 | 164.1736 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-056 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.053252 | 164.1763 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-056 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.053252 | 167.9939 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-056 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.053252 | 175.0352 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 02ALL | 1 | 29WP | T0 | GEN-2024-065 | TO->FROM | 647976 S976 8 69 3WXFMR 640:FREMONT T4 115 1 | B | 56 | 0.18146 | 100.3132 | P13:069:OPPD:FREM 8G:::HV: | Cumulative Impact | Fremont_Add_transformer_fixed.idv :
Thermal | 02ALL | 1 | 29SP | T0 | GEN-2024-065 | TO->FROM | 647976 S976 8 69 3WXFMR 640:FREMONT T1 115 1 | B | 63 | 0.1998 | 101.4697 | GEN647418 8 | Cumulative Impact | Fremont_Add_transformer_fixed.idv :
Thermal | 02ALL | 1 | 29WP | T0 | GEN-2024-065 | TO->FROM | 647976 S976 8 69 3WXFMR 640:FREMONT T1 115 1 | B | 63 | 0.19966 | 102.1836 | P13:069:OPPD:FREM 8G:::HV: | Cumulative Impact | Fremont_Add_transformer_fixed.idv :
Thermal | 02ALL | 1 | 29WP | T0 | GEN-2024-065 | TO->FROM | 647976 S976 8 69 3WXFMR 640:FREMONT T4 115 1 | B | 56 | 0.18146 | 102.6328 | GEN647418 8 | Cumulative Impact | Fremont_Add_transformer_fixed.idv :
Thermal | 02ALL | 1 | 26SP | T0 | GEN-2024-065 | TO->FROM | 647424 FREM D 8 69 647976 S976 8 69 1 | B | 96 | 0.57706 | 102.6647 | Single 640173 FREMONT7 115 640409 WINSLOW7 115 1 | TDF Impact | Rebuild line 647424 FREM D 8 69 647976 S976 8 69 1
Thermal | 02ALL | 1 | 29SP | T0 | GEN-2024-065 | TO->FROM | 647424 FREM D 8 69 647976 S976 8 69 1 | B | 96 | 0.38116 | 102.848 | P22:345:OPPD:S3451-RAUN:::EHV: | TDF Impact | Rebuild line 647424 FREM D 8 69 647976 S976 8 69 1
Thermal | 02ALL | 1 | 29SP | T0 | GEN-2024-065 | TO->FROM | 647424 FREM D 8 69 647976 S976 8 69 1 | B | 96 | 0.38116 | 102.848 | Single 645551 S3451-RAUN3 345 762779 G18-043TAP 345 1 | TDF Impact | Rebuild line 647424 FREM D 8 69 647976 S976 8 69 1
Thermal | 02ALL | 1 | 29SP | T0 | GEN-2024-065 | TO->FROM | 647424 FREM D 8 69 647976 S976 8 69 1 | B | 96 | 0.38116 | 102.848 | P12:345:OPPD-MEC:S3451-RAUN:::EHV: | TDF Impact | Rebuild line 647424 FREM D 8 69 647976 S976 8 69 1
Thermal | 02ALL | 1 | 29WP | T0 | GEN-2024-065 | TO->FROM | 647424 FREM D 8 69 647976 S976 8 69 1 | B | 96 | 0.53008 | 103.1129 | Single 640281 N.BEND7 115 640336 SCHUYLR7 115 1 | TDF Impact | Rebuild line 647424 FREM D 8 69 647976 S976 8 69 1
Thermal | 02ALL | 1 | 29WP | T0 | GEN-2024-065 | TO->FROM | 647424 FREM D 8 69 647976 S976 8 69 1 | B | 96 | 0.38444 | 103.4071 | P12:230.0:UMZ:# N-1 #:: LINE TWIN CH4-SIOUXCY4-1 :HV: | TDF Impact | Rebuild line 647424 FREM D 8 69 647976 S976 8 69 1
Thermal | 02ALL | 1 | 29WP | T0 | GEN-2024-065 | TO->FROM | 647424 FREM D 8 69 647976 S976 8 69 1 | B | 96 | 0.38106 | 103.5421 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Rebuild line 647424 FREM D 8 69 647976 S976 8 69 1
Thermal | 02ALL | 1 | 26SP | T0 | GEN-2024-065 | TO->FROM | 647424 FREM D 8 69 647976 S976 8 69 1 | B | 96 | 0.38346 | 103.6602 | P12:345:OPPD-MEC:S3451-RAUN:::EHV: | TDF Impact | Rebuild line 647424 FREM D 8 69 647976 S976 8 69 1
Thermal | 02ALL | 1 | 26SP | T0 | GEN-2024-065 | TO->FROM | 647424 FREM D 8 69 647976 S976 8 69 1 | B | 96 | 0.38346 | 103.6602 | P22:345:OPPD:S3451-RAUN:::EHV: | TDF Impact | Rebuild line 647424 FREM D 8 69 647976 S976 8 69 1
Thermal | 02ALL | 1 | 26SP | T0 | GEN-2024-065 | TO->FROM | 647424 FREM D 8 69 647976 S976 8 69 1 | B | 96 | 0.38346 | 103.6602 | Single 645551 S3451-RAUN3 345 762779 G18-043TAP 345 1 | TDF Impact | Rebuild line 647424 FREM D 8 69 647976 S976 8 69 1
Thermal | 02ALL | 1 | 26SP | T0 | GEN-2024-065 | TO->FROM | 647424 FREM D 8 69 647976 S976 8 69 1 | B | 96 | 0.38346 | 103.6603 | Single 645451 S34513 345 645551 S3451-RAUN3 345 Z1 | TDF Impact | Rebuild line 647424 FREM D 8 69 647976 S976 8 69 1
Thermal | 02ALL | 1 | 29WP | T0 | GEN-2024-065 | TO->FROM | 647976 S976 8 69 3WXFMR 640:FREMONT T1 115 1 | B | 63 | 0.19966 | 104.7202 | GEN647418 8 | Cumulative Impact | Fremont_Add_transformer_fixed.idv :
Thermal | 02ALL | 1 | 29SP | T0 | GEN-2024-065 | TO->FROM | 647424 FREM D 8 69 647976 S976 8 69 1 | B | 96 | 0.57637 | 105.1151 | P12:115:NPPD:1160:OAKLAND7:FREMONT7 BTB | TDF Impact | Rebuild line 647424 FREM D 8 69 647976 S976 8 69 1
Thermal | 02ALL | 1 | 29SP | T0 | GEN-2024-065 | TO->FROM | 647424 FREM D 8 69 647976 S976 8 69 1 | B | 96 | 0.57637 | 105.1551 | Single 640173 FREMONT7 115 640409 WINSLOW7 115 1 | TDF Impact | Rebuild line 647424 FREM D 8 69 647976 S976 8 69 1
Thermal | 02ALL | 1 | 26SP | T0 | GEN-2024-065 | TO->FROM | 647424 FREM D 8 69 647976 S976 8 69 1 | B | 96 | 0.53324 | 105.8238 | Single 640173 FREMONT7 115 640281 N.BEND7 115 1 | TDF Impact | Rebuild line 647424 FREM D 8 69 647976 S976 8 69 1
Thermal | 02ALL | 1 | 26SP | T0 | GEN-2024-065 | TO->FROM | 647424 FREM D 8 69 647976 S976 8 69 1 | B | 96 | 0.53324 | 105.9012 | P12:115:NPPD:1151B:SCHUYLR7:FREMONT7 BTB | TDF Impact | Rebuild line 647424 FREM D 8 69 647976 S976 8 69 1
Thermal | 02ALL | 1 | 29SP | T0 | GEN-2024-065 | TO->FROM | 647424 FREM D 8 69 647976 S976 8 69 1 | B | 96 | 0.53024 | 106.147 | Single 640173 FREMONT7 115 640281 N.BEND7 115 1 | TDF Impact | Rebuild line 647424 FREM D 8 69 647976 S976 8 69 1
Thermal | 02ALL | 1 | 29SP | T0 | GEN-2024-065 | TO->FROM | 647424 FREM D 8 69 647976 S976 8 69 1 | B | 96 | 0.53024 | 106.2238 | P12:115:NPPD:1151B:SCHUYLR7:FREMONT7 BTB | TDF Impact | Rebuild line 647424 FREM D 8 69 647976 S976 8 69 1
Thermal | 02ALL | 1 | 29WP | T0 | GEN-2024-065 | TO->FROM | 647424 FREM D 8 69 647976 S976 8 69 1 | B | 96 | 0.57622 | 106.3337 | P12:115:NPPD:1160:OAKLAND7:FREMONT7 BTB | TDF Impact | Rebuild line 647424 FREM D 8 69 647976 S976 8 69 1
Thermal | 02ALL | 1 | 26SP | T0 | GEN-2024-065 | TO->FROM | 647424 FREM D 8 69 647976 S976 8 69 1 | B | 96 | 0.39547 | 106.3602 | P12:161:OPPD:TEKAMAH-S1226:::HV: | TDF Impact | Rebuild line 647424 FREM D 8 69 647976 S976 8 69 1
Thermal | 02ALL | 1 | 29WP | T0 | GEN-2024-065 | TO->FROM | 647424 FREM D 8 69 647976 S976 8 69 1 | B | 96 | 0.57622 | 106.3726 | Single 640173 FREMONT7 115 640409 WINSLOW7 115 1 | TDF Impact | Rebuild line 647424 FREM D 8 69 647976 S976 8 69 1
Thermal | 02ALL | 1 | 29SP | T0 | GEN-2024-065 | TO->FROM | 647424 FREM D 8 69 647976 S976 8 69 1 | B | 96 | 0.3926 | 106.8396 | P12:161:OPPD:TEKAMAH-S1226:::HV: | TDF Impact | Rebuild line 647424 FREM D 8 69 647976 S976 8 69 1
Thermal | 02ALL | 1 | 29WP | T0 | GEN-2024-065 | TO->FROM | 647424 FREM D 8 69 647976 S976 8 69 1 | B | 96 | 0.39237 | 107.8274 | P12:161:OPPD:TEKAMAH-S1226:::HV: | TDF Impact | Rebuild line 647424 FREM D 8 69 647976 S976 8 69 1
Thermal | 02ALL | 1 | 29WP | T0 | GEN-2024-065 | TO->FROM | 647424 FREM D 8 69 647976 S976 8 69 1 | B | 96 | 0.53008 | 109.1233 | Single 640173 FREMONT7 115 640281 N.BEND7 115 1 | TDF Impact | Rebuild line 647424 FREM D 8 69 647976 S976 8 69 1
Thermal | 02ALL | 1 | 29WP | T0 | GEN-2024-065 | TO->FROM | 647424 FREM D 8 69 647976 S976 8 69 1 | B | 96 | 0.53008 | 109.1791 | P12:115:NPPD:1151B:SCHUYLR7:FREMONT7 BTB | TDF Impact | Rebuild line 647424 FREM D 8 69 647976 S976 8 69 1
Thermal | 02ALL | 1 | 26SP | T0 | GEN-2024-065 | TO->FROM | 647424 FREM D 8 69 647976 S976 8 69 1 | B | 96 | 0.38335 | 112.1964 | P13:069:OPPD:FREM 8G:::HV: | TDF Impact | Rebuild line 647424 FREM D 8 69 647976 S976 8 69 1
Thermal | 02ALL | 1 | 29SP | T0 | GEN-2024-065 | TO->FROM | 647424 FREM D 8 69 647976 S976 8 69 1 | B | 96 | 0.38139 | 114.2267 | P13:069:OPPD:FREM 8G:::HV: | TDF Impact | Rebuild line 647424 FREM D 8 69 647976 S976 8 69 1
Thermal | 02ALL | 1 | 26SP | T0 | GEN-2024-065 | TO->FROM | 647424 FREM D 8 69 647976 S976 8 69 1 | B | 96 | 0.38335 | 115.287 | GEN647418 8 | TDF Impact | Rebuild line 647424 FREM D 8 69 647976 S976 8 69 1
Thermal | 02ALL | 1 | 29SP | T0 | GEN-2024-065 | TO->FROM | 647424 FREM D 8 69 647976 S976 8 69 1 | B | 96 | 0.38139 | 117.3606 | GEN647418 8 | TDF Impact | Rebuild line 647424 FREM D 8 69 647976 S976 8 69 1
Thermal | 02ALL | 1 | 29WP | T0 | GEN-2024-065 | TO->FROM | 647424 FREM D 8 69 647976 S976 8 69 1 | B | 96 | 0.38111 | 118.7967 | P13:069:OPPD:FREM 8G:::HV: | TDF Impact | Rebuild line 647424 FREM D 8 69 647976 S976 8 69 1
Thermal | 02ALL | 1 | 29WP | T0 | GEN-2024-065 | TO->FROM | 647424 FREM D 8 69 647976 S976 8 69 1 | B | 96 | 0.38111 | 122.214 | GEN647418 8 | TDF Impact | Rebuild line 647424 FREM D 8 69 647976 S976 8 69 1
Thermal | 02ALL | 1 | 26SP | T0 | GEN-2024-065 | TO->FROM | 647976 S976 8 69 3WXFMR 640:FREMONT T1 115 1 | B | 63 | 0.32848 | 123.0184 | P13:069-115:NPPD:FREMONT T4:::HV: | TDF Impact | Fremont_Add_transformer_fixed.idv :
Thermal | 02ALL | 1 | 29SP | T0 | GEN-2024-065 | TO->FROM | 647976 S976 8 69 3WXFMR 640:FREMONT T1 115 1 | B | 63 | 0.3266 | 125.7439 | P13:069-115:NPPD:FREMONT T4:::HV: | TDF Impact | Fremont_Add_transformer_fixed.idv :
Thermal | 02ALL | 1 | 29WP | T0 | GEN-2024-065 | TO->FROM | 647976 S976 8 69 3WXFMR 640:FREMONT T1 115 1 | B | 63 | 0.32642 | 129.1259 | P13:069-115:NPPD:FREMONT T4:::HV: | TDF Impact | Fremont_Add_transformer_fixed.idv :
Thermal | 02ALL | 1 | 26SP | T0 | GEN-2024-065 | TO->FROM | 647976 S976 8 69 3WXFMR 640:FREMONT T4 115 1 | B | 56 | 0.31874 | 131.2891 | Single 647976 S9768 69 640173 FREMONT7 115 643058 'FREMONT T1 9' 13 1 | TDF Impact | Fremont_Add_transformer_fixed.idv :
Thermal | 02ALL | 1 | 29SP | T0 | GEN-2024-065 | TO->FROM | 647976 S976 8 69 3WXFMR 640:FREMONT T4 115 1 | B | 56 | 0.3169 | 134.187 | Single 647976 S9768 69 640173 FREMONT7 115 643058 'FREMONT T1 9' 13 1 | TDF Impact | Fremont_Add_transformer_fixed.idv :
Thermal | 02ALL | 1 | 29WP | T0 | GEN-2024-065 | TO->FROM | 647976 S976 8 69 3WXFMR 640:FREMONT T4 115 1 | B | 56 | 0.31672 | 138.3493 | Single 647976 S9768 69 640173 FREMONT7 115 643058 'FREMONT T1 9' 13 1 | TDF Impact | Fremont_Add_transformer_fixed.idv :
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-067 | TO->FROM | 640277 MOORE 3 345 640525 TOBIAS 3 345 1 | B | 956 | 0.2575 | 100.5946 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | Rebuild line 640277 MOORE 3 345 640525 TOBIAS 3 345 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-067 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.057623 | 101.6955 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-067 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.057623 | 101.6955 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-067 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.057623 | 101.6955 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-067 | TO->FROM | 539656 CLIFTON3 115 539657 CONCORD3 115 1 | B | 113.9 | 0.043447 | 102.7717 | Single 539805 ELMCREEK7 345 640600 DAYKIN3 345 1 | TDF Impact | Rebuild line 539656 CLIFTON3 115 539657 CONCORD3 115 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-067 | TO->FROM | 645454 S3454 3 345 650185 WAGENER 3 345 1 | B | 982 | 0.055596 | 104.6262 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Rebuild line 645454 S3454 3 345 650185 WAGENER 3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-067 | TO->FROM | 650185 WAGENER 3 345 650189 103&ROKEBY3 345 1 | B | 1158 | 0.056605 | 105.9892 | P42:345:NPPD:BKR-MOR-3310:::: | TDF Impact | Rebuild line 650185 WAGENER 3 345 650189 103&ROKEBY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-067 | TO->FROM | 650185 WAGENER 3 345 650189 103&ROKEBY3 345 1 | B | 1158 | 0.056605 | 105.9892 | P42:345:NPPD:L3502A.MOORE.MCCOOL.CB3310:::: | TDF Impact | Rebuild line 650185 WAGENER 3 345 650189 103&ROKEBY3 345 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-067 | TO->FROM | 539657 CONCORD3 115 3WXFMR 534:CONCORD6 230 1 | B | 225.5 | 0.088333 | 106.7468 | Single 539805 ELMCREEK7 345 640600 DAYKIN3 345 1 | Cumulative Impact | Add 3-winding transformer 539657 CONCORD3 115 539658 CONCRD6 230 539904 CONCOD-1 13 M2
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-067 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.21301 | 106.8199 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-067 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.20534 | 108.3331 | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-067 | TO->FROM | 640277 MOORE 3 345 640525 TOBIAS 3 345 1 | B | 956 | 0.24548 | 109.5154 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | Rebuild line 640277 MOORE 3 345 640525 TOBIAS 3 345 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-067 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.059009 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-067 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.059009 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-067 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.059009 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-067 | TO->FROM | 645454 S3454 3 345 650185 WAGENER 3 345 1 | B | 982 | 0.068991 | 124.4523 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | Rebuild line 645454 S3454 3 345 650185 WAGENER 3 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-068 | TO->FROM | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | B | 1059 | 0.051338 | 100.2166 | P12:345:AEPW:R.S.S.-7:ONETA--7::: | Cumulative Impact | Rebuild line 509745 CLARKSV7 345 515224 MUSKOGE7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-068 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | A | 157 | 0.033716 | 148.4151 | System Intact | TDF Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-068 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | A | 157 | 0.034893 | 150.7438 | System Intact | TDF Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-068 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | A | 159 | 0.034981 | 153.3873 | System Intact | TDF Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-071 | TO->FROM | 508814 RODESSA2 69 783570 G24-220-TAP 69 1 | B | 65 | 0.10918 | 100.2123 | P23:345:AEPW:LONGWOOD CB 1N60 NBTB:::: | Cumulative Impact | Rebuild line 508814 RODESSA2 69 783570 G24-220-TAP 69 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-071 | TO->FROM | 508814 RODESSA2 69 783570 G24-220-TAP 69 1 | B | 53 | 0.1089 | 100.9169 | 267135_a | Cumulative Impact | Rebuild line 508814 RODESSA2 69 783570 G24-220-TAP 69 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-071 | TO->FROM | 508814 RODESSA2 69 783570 G24-220-TAP 69 1 | B | 53 | 0.10573 | 101.2934 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | Cumulative Impact | Rebuild line 508814 RODESSA2 69 783570 G24-220-TAP 69 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-071 | TO->FROM | 508804 HOSSTON2 69 508846 GODFREYRDTP2 69 1 | B | 53 | 0.10469 | 101.5037 | Single 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1 | Cumulative Impact | Rebuild line 508804 HOSSTON2 69 508846 GODFREYRDTP2 69 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-071 | TO->FROM | 508804 HOSSTON2 69 508846 GODFREYRDTP2 69 1 | B | 53 | 0.10469 | 101.54 | Single 508359 WELSH7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Rebuild line 508804 HOSSTON2 69 508846 GODFREYRDTP2 69 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-071 | TO->FROM | 508814 RODESSA2 69 783570 G24-220-TAP 69 1 | B | 53 | 0.1089 | 101.7098 | P12:345:AEPW:LONGWD7:WILKES7::: | Cumulative Impact | Rebuild line 508814 RODESSA2 69 783570 G24-220-TAP 69 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-071 | TO->FROM | 508814 RODESSA2 69 783570 G24-220-TAP 69 1 | B | 53 | 0.10974 | 102.1918 | P42:345:AEPW:WILKES CB 1W10 NBTB+FAULT:::: | Cumulative Impact | Rebuild line 508814 RODESSA2 69 783570 G24-220-TAP 69 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-071 | TO->FROM | 508814 RODESSA2 69 783570 G24-220-TAP 69 1 | B | 53 | 0.10923 | 102.2951 | P23:345:AEPW:LONGWOOD CB 1N60 NBTB:::: | Cumulative Impact | Rebuild line 508814 RODESSA2 69 783570 G24-220-TAP 69 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-071 | TO->FROM | 508804 HOSSTON2 69 508846 GODFREYRDTP2 69 1 | B | 53 | 0.10728 | 105.0581 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 508804 HOSSTON2 69 508846 GODFREYRDTP2 69 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-071 | TO->FROM | 508814 RODESSA2 69 783570 G24-220-TAP 69 1 | B | 53 | 0.10419 | 105.1089 | Single 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1 | Cumulative Impact | Rebuild line 508814 RODESSA2 69 783570 G24-220-TAP 69 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-071 | TO->FROM | 508814 RODESSA2 69 783570 G24-220-TAP 69 1 | B | 53 | 0.10419 | 105.1627 | Single 508359 WELSH7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Rebuild line 508814 RODESSA2 69 783570 G24-220-TAP 69 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-071 | TO->FROM | 508804 HOSSTON2 69 508846 GODFREYRDTP2 69 1 | B | 53 | 0.10508 | 105.59 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | Cumulative Impact | Rebuild line 508804 HOSSTON2 69 508846 GODFREYRDTP2 69 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-071 | TO->FROM | 508814 RODESSA2 69 783570 G24-220-TAP 69 1 | B | 65 | 0.1055 | 106.6412 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | Cumulative Impact | Rebuild line 508814 RODESSA2 69 783570 G24-220-TAP 69 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-071 | TO->FROM | 508814 RODESSA2 69 783570 G24-220-TAP 69 1 | B | 65 | 0.40366 | 107.1787 | Single 508089 WATLANT2 69 779100 G24-071-TAP 69 1 | TDF Impact | Rebuild line 508814 RODESSA2 69 783570 G24-220-TAP 69 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-071 | TO->FROM | 508814 RODESSA2 69 783570 G24-220-TAP 69 1 | B | 65 | 0.40372 | 107.6918 | P12:69:AEPW:WATLANT2:LINDEN 2::: | TDF Impact | Rebuild line 508814 RODESSA2 69 783570 G24-220-TAP 69 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-071 | TO->FROM | 508814 RODESSA2 69 783570 G24-220-TAP 69 1 | B | 53 | 0.10688 | 108.7199 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 508814 RODESSA2 69 783570 G24-220-TAP 69 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-071 | TO->FROM | 508804 HOSSTON2 69 508846 GODFREYRDTP2 69 1 | B | 53 | 0.10885 | 109.8273 | 267135_a | Cumulative Impact | Rebuild line 508804 HOSSTON2 69 508846 GODFREYRDTP2 69 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-071 | TO->FROM | 508804 HOSSTON2 69 508846 GODFREYRDTP2 69 1 | B | 53 | 0.10971 | 109.8956 | P42:345:AEPW:WILKES CB 1W10 NBTB+FAULT:::: | Cumulative Impact | Rebuild line 508804 HOSSTON2 69 508846 GODFREYRDTP2 69 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-071 | TO->FROM | 508804 HOSSTON2 69 508846 GODFREYRDTP2 69 1 | B | 53 | 0.40274 | 109.9041 | Single 508089 WATLANT2 69 779100 G24-071-TAP 69 1 | TDF Impact | Rebuild line 508804 HOSSTON2 69 508846 GODFREYRDTP2 69 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-071 | TO->FROM | 508804 HOSSTON2 69 508846 GODFREYRDTP2 69 1 | B | 53 | 0.10885 | 110.0283 | P12:345:AEPW:LONGWD7:WILKES7::: | Cumulative Impact | Rebuild line 508804 HOSSTON2 69 508846 GODFREYRDTP2 69 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-071 | TO->FROM | 508804 HOSSTON2 69 508846 GODFREYRDTP2 69 1 | B | 53 | 0.40279 | 110.5579 | P12:69:AEPW:WATLANT2:LINDEN 2::: | TDF Impact | Rebuild line 508804 HOSSTON2 69 508846 GODFREYRDTP2 69 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-071 | TO->FROM | 508814 RODESSA2 69 783570 G24-220-TAP 69 1 | B | 53 | 0.10844 | 110.561 | 267135_a | Cumulative Impact | Rebuild line 508814 RODESSA2 69 783570 G24-220-TAP 69 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-071 | TO->FROM | 508804 HOSSTON2 69 508846 GODFREYRDTP2 69 1 | B | 53 | 0.10918 | 110.8969 | P23:345:AEPW:LONGWOOD CB 1N60 NBTB:::: | Cumulative Impact | Rebuild line 508804 HOSSTON2 69 508846 GODFREYRDTP2 69 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-071 | TO->FROM | 508814 RODESSA2 69 783570 G24-220-TAP 69 1 | B | 53 | 0.10928 | 111.2974 | P42:345:AEPW:WILKES CB 1W10 NBTB+FAULT:::: | Cumulative Impact | Rebuild line 508814 RODESSA2 69 783570 G24-220-TAP 69 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-071 | TO->FROM | 508814 RODESSA2 69 783570 G24-220-TAP 69 1 | B | 53 | 0.10844 | 111.4001 | P12:345:AEPW:LONGWD7:WILKES7::: | Cumulative Impact | Rebuild line 508814 RODESSA2 69 783570 G24-220-TAP 69 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-071 | TO->FROM | 508814 RODESSA2 69 783570 G24-220-TAP 69 1 | B | 53 | 0.10877 | 111.5778 | P23:345:AEPW:LONGWOOD CB 1N60 NBTB:::: | Cumulative Impact | Rebuild line 508814 RODESSA2 69 783570 G24-220-TAP 69 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-071 | TO->FROM | 508814 RODESSA2 69 783570 G24-220-TAP 69 1 | B | 53 | 0.40377 | 111.5778 | Single 508089 WATLANT2 69 779100 G24-071-TAP 69 1 | TDF Impact | Rebuild line 508814 RODESSA2 69 783570 G24-220-TAP 69 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-071 | TO->FROM | 508814 RODESSA2 69 783570 G24-220-TAP 69 1 | B | 53 | 0.40382 | 112.112 | P12:69:AEPW:WATLANT2:LINDEN 2::: | TDF Impact | Rebuild line 508814 RODESSA2 69 783570 G24-220-TAP 69 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-071 | TO->FROM | 508804 HOSSTON2 69 508846 GODFREYRDTP2 69 1 | B | 53 | 0.1055 | 118.8031 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | Cumulative Impact | Rebuild line 508804 HOSSTON2 69 508846 GODFREYRDTP2 69 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-071 | TO->FROM | 508814 RODESSA2 69 783570 G24-220-TAP 69 1 | B | 53 | 0.10508 | 119.4276 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | Cumulative Impact | Rebuild line 508814 RODESSA2 69 783570 G24-220-TAP 69 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-071 | TO->FROM | 508804 HOSSTON2 69 508846 GODFREYRDTP2 69 1 | B | 53 | 0.40366 | 119.6096 | Single 508089 WATLANT2 69 779100 G24-071-TAP 69 1 | TDF Impact | Rebuild line 508804 HOSSTON2 69 508846 GODFREYRDTP2 69 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-071 | TO->FROM | 508804 HOSSTON2 69 508846 GODFREYRDTP2 69 1 | B | 53 | 0.40372 | 120.2355 | P12:69:AEPW:WATLANT2:LINDEN 2::: | TDF Impact | Rebuild line 508804 HOSSTON2 69 508846 GODFREYRDTP2 69 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-071 | TO->FROM | 508814 RODESSA2 69 783570 G24-220-TAP 69 1 | B | 53 | 0.40274 | 123.4859 | Single 508089 WATLANT2 69 779100 G24-071-TAP 69 1 | TDF Impact | Rebuild line 508814 RODESSA2 69 783570 G24-220-TAP 69 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-071 | TO->FROM | 508814 RODESSA2 69 783570 G24-220-TAP 69 1 | B | 53 | 0.40279 | 124.1415 | P12:69:AEPW:WATLANT2:LINDEN 2::: | TDF Impact | Rebuild line 508814 RODESSA2 69 783570 G24-220-TAP 69 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-071 | TO->FROM | 508806 LIEBERM4 138 780630 G24-122-TAP 138 1 | B | 183 | 0.053033 | 137.6957 | P42:345:AEPW:WILKES CB 1W10 NBTB+FAULT:::: | Cumulative Impact | Rebuild line 508806 LIEBERM4 138 780630 G24-122-TAP 138 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-071 | TO->FROM | 508806 LIEBERM4 138 780630 G24-122-TAP 138 1 | B | 162 | 0.053661 | 141.1802 | P42:345:AEPW:WILKES CB 1W10 NBTB+FAULT:::: | Cumulative Impact | Rebuild line 508806 LIEBERM4 138 780630 G24-122-TAP 138 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-071 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | A | 157 | 0.037398 | 148.4151 | System Intact | TDF Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-071 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | A | 157 | 0.038772 | 150.7438 | System Intact | TDF Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-071 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | A | 159 | 0.038783 | 153.3873 | System Intact | TDF Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-071 | TO->FROM | 508806 LIEBERM4 138 780630 G24-122-TAP 138 1 | B | 162 | 0.05336 | 160.6045 | P42:345:AEPW:WILKES CB 1W10 NBTB+FAULT:::: | Cumulative Impact | Rebuild line 508806 LIEBERM4 138 780630 G24-122-TAP 138 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-071 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | B | 157 | 0.053001 | 172.2965 | Single 508809 LONGWD7 345 788340 G24-379-TAP 345 1 | Cumulative Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-071 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | B | 157 | 0.053001 | 172.3873 | Single 337376 7SAREPTA% 345 788340 G24-379-TAP 345 1 | Cumulative Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-071 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | B | 157 | 0.054347 | 177.0636 | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | Cumulative Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-071 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | B | 159 | 0.054563 | 179.8598 | Single 337376 7SAREPTA% 345 788340 G24-379-TAP 345 1 | Cumulative Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-071 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | B | 159 | 0.054563 | 179.951 | Single 508809 LONGWD7 345 788340 G24-379-TAP 345 1 | Cumulative Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-071 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | B | 157 | 0.054427 | 180.7536 | Single 337376 7SAREPTA% 345 788340 G24-379-TAP 345 1 | Cumulative Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-071 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | B | 157 | 0.054427 | 180.8803 | Single 508809 LONGWD7 345 788340 G24-379-TAP 345 1 | Cumulative Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-071 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | B | 159 | 0.055925 | 184.4152 | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | Cumulative Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-071 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | B | 157 | 0.055786 | 185.7511 | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | Cumulative Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-074 | TO->FROM | 541199 ST JOE 7 345 541400 EASTOWN7 345 1 | B | 1185 | 0.084118 | 100.396 | Single 541199 STJOE7 345 761383 G17-183-TAP 345 1 | Cumulative Impact | Rebuild line 541199 ST JOE 7 345 541400 EASTOWN7 345 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-074 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.073831 | 101.6955 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-074 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.073831 | 101.6955 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-074 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.073831 | 101.6955 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 26SP | T1 | GEN-2024-074 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.072836 | 105.0133 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 29WP | T1 | GEN-2024-074 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.067527 | 106.2154 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-074 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.068106 | 106.5956 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-074 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.068106 | 106.5956 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-074 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.068106 | 106.5956 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-074 | TO->FROM | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | B | 1195 | 0.092722 | 107.005 | Single 541199 STJOE7 345 761383 G17-183-TAP 345 1 | Cumulative Impact | Rebuild line 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-074 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.075589 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-074 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.075589 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-074 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.075589 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-074 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.069389 | 117.7598 | P55:345:OPPD:S3458 3::FN13:EHV: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-076 | TO->FROM | 541199 ST JOE 7 345 541400 EASTOWN7 345 1 | B | 1185 | 0.062889 | 100.396 | Single 541199 STJOE7 345 761383 G17-183-TAP 345 1 | Cumulative Impact | Rebuild line 541199 ST JOE 7 345 541400 EASTOWN7 345 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-076 | TO->FROM | 532939 N345 4 5 161 3WXFMR 536:N345 TX-2 161 2 | B | 550 | 0.077001 | 100.4793 | Single 533021 NEOSHO4 138 533023 N34534 138 1 | TDF Impact | Add 3-winding transformer 532793 NEOSHO 7 345 532825 N345 2 1 13 532939 N345 4 5 161 M2
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-076 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.19003 | 101.6955 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-076 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.19003 | 101.6955 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-076 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.19003 | 101.6955 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-076 | TO->FROM | 532939 N345 4 5 161 3WXFMR 536:N345 TX-2 161 2 | B | 550 | 0.082919 | 103.5308 | Single 533021 NEOSHO4 138 533023 N34534 138 1 | TDF Impact | Add 3-winding transformer 532793 NEOSHO 7 345 532825 N345 2 1 13 532939 N345 4 5 161 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-076 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | B | 829 | 0.10932 | 103.7671 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | TDF Impact | Rebuild line 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1
Thermal | 03ALL | 1 | 26SP | T1 | GEN-2024-076 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.20214 | 105.0133 | P23:345:AECI:7BLACKBERRY:653::: | TDF Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 29WP | T1 | GEN-2024-076 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.21333 | 106.2154 | P23:345:AECI:7BLACKBERRY:653::: | TDF Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-076 | TO->FROM | 532937 NEOSHO 5 161 532939 N345 4 5 161 1 | B | 557 | 0.082767 | 106.5051 | Single 533021 NEOSHO4 138 533023 N34534 138 1 | TDF Impact | Rebuild line 532937 NEOSHO 5 161 532939 N345 4 5 161 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-076 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.21651 | 106.5956 | P23:345:AECI:7BLACKBERRY:653::: | TDF Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-076 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.21651 | 106.5956 | P23:345:AECI:7BLACKBERRY:653::: | TDF Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-076 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.21651 | 106.5956 | P23:345:AECI:7BLACKBERRY:653::: | TDF Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-076 | TO->FROM | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | B | 1195 | 0.069647 | 107.005 | Single 541199 STJOE7 345 761383 G17-183-TAP 345 1 | Cumulative Impact | Rebuild line 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-076 | TO->FROM | 532939 N345 4 5 161 3WXFMR 536:N345 TX-2 161 2 | B | 550 | 0.082767 | 111.179 | Single 533021 NEOSHO4 138 533023 N34534 138 1 | TDF Impact | Add 3-winding transformer 532793 NEOSHO 7 345 532825 N345 2 1 13 532939 N345 4 5 161 M2
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-076 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.19043 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-076 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.19043 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-076 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.19043 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | A | 600 | 0.20744 | 100.7847 | System Intact | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | A | 600 | 0.20744 | 100.7847 | System Intact | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | A | 600 | 0.20744 | 100.7847 | System Intact | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | 0.55175 | 100.9864 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-ROUNDUP_-BE3-1 :EHV: | TDF Impact | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.2042 | 101.1212 | 259421 | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.2042 | 101.1212 | 259421 | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.2042 | 101.1212 | 259421 | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | 0.55166 | 101.1602 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | TDF Impact | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.2042 | 101.5106 | 259422 | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.2042 | 101.5106 | 259698 | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.2042 | 101.5106 | 259422 | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.2042 | 101.5106 | 259698 | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.2042 | 101.5106 | 259422 | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.2042 | 101.5106 | 259698 | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.2042 | 101.5106 | P12:230:SASK:230KV-G1P-FUT:::HV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.2042 | 101.5106 | P12:230:SASK:230KV-G1P-FUT:::HV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.2042 | 101.5106 | P12:230:SASK:230KV-G1P-FUT:::HV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.2042 | 101.5249 | P11:13.8:SASK:CHNK #1 GT:::HV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.2042 | 101.5249 | P11:13.8:SASK:CHNK #1 GT:::HV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.2042 | 101.5249 | P11:13.8:SASK:CHNK #1 GT:::HV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.32319 | 102.1082 | 279736 | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.32319 | 102.1082 | 279736 | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.32319 | 102.1082 | 279736 | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1195 | 0.6622 | 103.6807 | P12:230.0:UMZ:# N-1 #:: LINE NESET___-BE4-TANDE___-BE4-1 :HV: | TDF Impact | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 659334 JUDSON__-BE4 230 3WXFMR 659:JUDSON KU3A 230 1 | B | 717 | 0.12894 | 104.5457 | Single 659333 JUDSON__-BE3 345 659334 JUDSON__-BE4 230 659329 'JDS.KUXA-BE9' 13 1 | Cumulative Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 659334 JUDSON__-BE4 230 3WXFMR 659:JUDSON KU3A 230 1 | B | 717 | 0.12894 | 104.5457 | Single 659333 JUDSON__-BE3 345 659334 JUDSON__-BE4 230 659329 'JDS.KUXA-BE9' 13 1 | Cumulative Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 659334 JUDSON__-BE4 230 3WXFMR 659:JUDSON KU3A 230 1 | B | 717 | 0.12894 | 104.5457 | Single 659333 JUDSON__-BE3 345 659334 JUDSON__-BE4 230 659329 'JDS.KUXA-BE9' 13 1 | Cumulative Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 659334 JUDSON__-BE4 230 3WXFMR 659:652: JUDSON KUXA 230 1 | B | 717 | 0.12894 | 104.5457 | P13:345-230.0:UMZ:# N-1 #:: 3WND JUDSON__-BE3-JUDSON__-BE4-JDS.KU6A-BE9-1 JUDSON KU3A:EHV: | Cumulative Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 659334 JUDSON__-BE4 230 3WXFMR 659:652: JUDSON KUXA 230 1 | B | 717 | 0.12894 | 104.5457 | P13:345-230.0:UMZ:# N-1 #:: 3WND JUDSON__-BE3-JUDSON__-BE4-JDS.KU6A-BE9-1 JUDSON KU3A:EHV: | Cumulative Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 659334 JUDSON__-BE4 230 3WXFMR 659:652: JUDSON KUXA 230 1 | B | 717 | 0.12894 | 104.5457 | P13:345-230.0:UMZ:# N-1 #:: 3WND JUDSON__-BE3-JUDSON__-BE4-JDS.KU6A-BE9-1 JUDSON KU3A:EHV: | Cumulative Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.22643 | 104.892 | P12:115.0:UMZ:# N-1 #:: LINE EASTFORK-MW7-SPRNGBRK-BE7-1 :HV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.22643 | 104.892 | P12:115.0:UMZ:# N-1 #:: LINE EASTFORK-MW7-SPRNGBRK-BE7-1 :HV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.22643 | 104.892 | P12:115.0:UMZ:# N-1 #:: LINE EASTFORK-MW7-SPRNGBRK-BE7-1 :HV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.22643 | 104.8922 | P13:345-115.0:UMZ:# N-1 #:: 3WND SPRNGBRK-BE3-SPRNGBRK-BE7-SPRNGBRK-BE9-1 652_ SPRNGBRK KUXA_:EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.22643 | 104.8922 | P13:345-115.0:UMZ:# N-1 #:: 3WND SPRNGBRK-BE3-SPRNGBRK-BE7-SPRNGBRK-BE9-1 652_ SPRNGBRK KUXA_:EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.22643 | 104.8922 | P13:345-115.0:UMZ:# N-1 #:: 3WND SPRNGBRK-BE3-SPRNGBRK-BE7-SPRNGBRK-BE9-1 652_ SPRNGBRK KUXA_:EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | TO->FROM | 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | A | 1087 | 0.5568 | 104.9308 | System Intact | TDF Impact | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 652400 WILISTN4 230 659334 JUDSON__-BE4 230 1 | B | 482 | 0.14793 | 105.161 | P12:230.0:UMZ:# N-1 #:: LINE OWAN -MW4-JUDSON__-BE4-Z :HV: | Cumulative Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 652400 WILISTN4 230 659334 JUDSON__-BE4 230 1 | B | 482 | 0.14793 | 105.161 | P12:230.0:UMZ:# N-1 #:: LINE OWAN -MW4-JUDSON__-BE4-Z :HV: | Cumulative Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 652400 WILISTN4 230 659334 JUDSON__-BE4 230 1 | B | 482 | 0.14793 | 105.161 | P12:230.0:UMZ:# N-1 #:: LINE OWAN -MW4-JUDSON__-BE4-Z :HV: | Cumulative Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | 0.57883 | 105.7 | P12:230.0:UMZ:# N-1 #:: LINE WHEELOCK-BE4-TIOGA4 4-1 :HV: | TDF Impact | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 29SP | T2 | GEN-2024-081 | TO->FROM | 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1 | B | 637 | 0.35033 | 106.461 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Rebuild line 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | A | 600 | 0.2042 | 106.9942 | System Intact | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | A | 600 | 0.2042 | 106.9942 | System Intact | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | A | 600 | 0.2042 | 106.9942 | System Intact | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | 0.62588 | 107.4493 | P12:230.0:UMZ:# N-1 #:: LINE NESET___-BE4-TIOGA4 4-Z :HV: | TDF Impact | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 652400 WILISTN4 230 659334 JUDSON__-BE4 230 1 | B | 482 | 0.34629 | 108.3751 | Single 659427 TN.LS-JD-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 652400 WILISTN4 230 659334 JUDSON__-BE4 230 1 | B | 482 | 0.34629 | 108.3751 | Single 659427 TN.LS-JD-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 652400 WILISTN4 230 659334 JUDSON__-BE4 230 1 | B | 482 | 0.34629 | 108.3751 | Single 659427 TN.LS-JD-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 652400 WILISTN4 230 659334 JUDSON__-BE4 230 1 | B | 482 | 0.34629 | 108.3754 | P12:345.0:UMZ:# N-1 #:: LINE TANDE___-BE3-TN.LS-JD-BE3-Z :EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 652400 WILISTN4 230 659334 JUDSON__-BE4 230 1 | B | 482 | 0.34629 | 108.3754 | P12:345.0:UMZ:# N-1 #:: LINE TANDE___-BE3-TN.LS-JD-BE3-Z :EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 652400 WILISTN4 230 659334 JUDSON__-BE4 230 1 | B | 482 | 0.34629 | 108.3754 | P12:345.0:UMZ:# N-1 #:: LINE TANDE___-BE3-TN.LS-JD-BE3-Z :EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.24707 | 108.6892 | P12:230.0:UMZ:# N-1 #:: LINE WILISTN4-JUDSON__-BE4-1 :HV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.24707 | 108.6892 | P12:230.0:UMZ:# N-1 #:: LINE WILISTN4-JUDSON__-BE4-1 :HV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.24707 | 108.6892 | P12:230.0:UMZ:# N-1 #:: LINE WILISTN4-JUDSON__-BE4-1 :HV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1 | B | 637 | 0.36398 | 109.1747 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1 | B | 637 | 0.36398 | 109.1747 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1 | B | 637 | 0.36398 | 109.1747 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | TO->FROM | 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | 0.62313 | 109.6836 | 279688 | TDF Impact | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 652400 WILISTN4 230 659334 JUDSON__-BE4 230 1 | B | 482 | 0.34356 | 110.5461 | P23:345:UMZB:# 7149 #:: TND IN ND. BREAKER FAULT (292):EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 652400 WILISTN4 230 659334 JUDSON__-BE4 230 1 | B | 482 | 0.34356 | 110.5461 | P23:345:UMZB:# 7149 #:: TND IN ND. BREAKER FAULT (292):EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 652400 WILISTN4 230 659334 JUDSON__-BE4 230 1 | B | 482 | 0.34356 | 110.5461 | P23:345:UMZB:# 7149 #:: TND IN ND. BREAKER FAULT (292):EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-081 | TO->FROM | 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1 | B | 506 | 0.34728 | 110.8229 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Rebuild line 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.22311 | 111.7104 | P12:115.0:UMZ:# N-1 #:: LINE EASTFORK-MW7-SPRNGBRK-BE7-1 :HV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.22311 | 111.7104 | P12:115.0:UMZ:# N-1 #:: LINE EASTFORK-MW7-SPRNGBRK-BE7-1 :HV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.22311 | 111.7104 | P12:115.0:UMZ:# N-1 #:: LINE EASTFORK-MW7-SPRNGBRK-BE7-1 :HV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.22311 | 111.7105 | P13:345-115.0:UMZ:# N-1 #:: 3WND SPRNGBRK-BE3-SPRNGBRK-BE7-SPRNGBRK-BE9-1 652_ SPRNGBRK KUXA_:EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.22311 | 111.7105 | P13:345-115.0:UMZ:# N-1 #:: 3WND SPRNGBRK-BE3-SPRNGBRK-BE7-SPRNGBRK-BE9-1 652_ SPRNGBRK KUXA_:EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.22311 | 111.7105 | P13:345-115.0:UMZ:# N-1 #:: 3WND SPRNGBRK-BE3-SPRNGBRK-BE7-SPRNGBRK-BE9-1 652_ SPRNGBRK KUXA_:EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29WP | T2 | GEN-2024-081 | TO->FROM | 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1 | B | 637 | 0.35174 | 111.713 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Rebuild line 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 652400 WILISTN4 230 659334 JUDSON__-BE4 230 1 | B | 482 | 0.21665 | 111.8239 | P13:345-230.0:UMZ:# N-1 #:: 3WND TANDE___-BE3-TANDE___-BE4-TND.KU3A-BE9-1 TANDE KU1A:EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 652400 WILISTN4 230 659334 JUDSON__-BE4 230 1 | B | 482 | 0.21665 | 111.8239 | P13:345-230.0:UMZ:# N-1 #:: 3WND TANDE___-BE3-TANDE___-BE4-TND.KU3A-BE9-1 TANDE KU1A:EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 652400 WILISTN4 230 659334 JUDSON__-BE4 230 1 | B | 482 | 0.21665 | 111.8239 | P13:345-230.0:UMZ:# N-1 #:: 3WND TANDE___-BE3-TANDE___-BE4-TND.KU3A-BE9-1 TANDE KU1A:EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | TO->FROM | 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | 0.54113 | 112.6506 | P12:230.0:UMZ:# N-1 #:: LINE WHEELOCK-BE4-TIOGA4 4-1 :HV: | TDF Impact | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | 0.64839 | 113.0149 | P12:230.0:UMZ:# N-1 #:: LINE NESET___-BE4-TANDE___-BE4-1 :HV: | TDF Impact | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | TO->FROM | 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | 0.62209 | 113.098 | 279736 | TDF Impact | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | TO->FROM | 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | 0.62715 | 114.4902 | P12:230.0:UMZ:# N-1 #:: LINE NESET___-BE4-TIOGA4 4-Z :HV: | TDF Impact | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.40604 | 115.1422 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.40604 | 115.1422 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.40604 | 115.1422 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1195 | 0.70189 | 115.2596 | P13:345-230.0:UMZ:# N-1 #:: 3WND TANDE___-BE3-TANDE___-BE4-TND.KU3A-BE9-1 TANDE KU1A:EHV: | TDF Impact | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 652400 WILISTN4 230 659334 JUDSON__-BE4 230 1 | B | 482 | 0.34408 | 115.4285 | P23:345:UMZB:# 7148 #:: TND IN ND. BREAKER FAULT (296):EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 652400 WILISTN4 230 659334 JUDSON__-BE4 230 1 | B | 482 | 0.34408 | 115.4285 | P23:345:UMZB:# 7148 #:: TND IN ND. BREAKER FAULT (296):EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 652400 WILISTN4 230 659334 JUDSON__-BE4 230 1 | B | 482 | 0.34408 | 115.4285 | P23:345:UMZB:# 7148 #:: TND IN ND. BREAKER FAULT (296):EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-081 | TO->FROM | 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1 | B | 506 | 0.31004 | 115.9626 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Rebuild line 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.24286 | 116.3034 | P12:230.0:UMZ:# N-1 #:: LINE WILISTN4-JUDSON__-BE4-1 :HV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.24286 | 116.3034 | P12:230.0:UMZ:# N-1 #:: LINE WILISTN4-JUDSON__-BE4-1 :HV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.24286 | 116.3034 | P12:230.0:UMZ:# N-1 #:: LINE WILISTN4-JUDSON__-BE4-1 :HV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 659362 WHEELOCK-BE4 230 661084 TIOGA4 4 230 1 | B | 526 | 0.21345 | 120.1453 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 659362 WHEELOCK-BE4 230 661084 TIOGA4 4 230 1 | B | 526 | 0.21345 | 120.1453 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 659362 WHEELOCK-BE4 230 661084 TIOGA4 4 230 1 | B | 526 | 0.21345 | 120.1453 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | TO->FROM | 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | 0.66219 | 121.1476 | P13:345-230.0:UMZ:# N-1 #:: 3WND TANDE___-BE3-TANDE___-BE4-TND.KU3A-BE9-1 TANDE KU1A:EHV: | TDF Impact | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | TO->FROM | 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | 0.66219 | 121.1484 | P12:230.0:UMZ:# N-1 #:: LINE NESET___-BE4-TANDE___-BE4-1 :HV: | TDF Impact | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1195 | 1 | 122.8003 | P12:345.0:UMZ:# N-1 #:: LINE TANDE___-BE3-TN.LS-JD-BE3-Z :EHV: | TDF Impact | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1195 | 1 | 122.9433 | Single 659427 TN.LS-JD-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1195 | 1 | 123.0553 | P23:345:UMZB:# 7149 #:: TND IN ND. BREAKER FAULT (292):EHV: | TDF Impact | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1195 | 1 | 123.2148 | P23:345:UMZB:# 7148 #:: TND IN ND. BREAKER FAULT (296):EHV: | TDF Impact | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-081 | TO->FROM | 659336 TANDE___-BE3 345 659427 TN.LS-JD-BE3 345 Z | B | 1195 | 1 | 124.5842 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Rebuild line 659336 TANDE___-BE3 345 659427 TN.LS-JD-BE3 345 Z
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 659362 WHEELOCK-BE4 230 661084 TIOGA4 4 230 1 | B | 506 | 0.20505 | 125.5606 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 659362 WHEELOCK-BE4 230 661084 TIOGA4 4 230 1 | B | 506 | 0.20505 | 125.5606 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 659362 WHEELOCK-BE4 230 661084 TIOGA4 4 230 1 | B | 506 | 0.20505 | 125.5606 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | 0.68962 | 125.907 | P13:345-230.0:UMZ:# N-1 #:: 3WND TANDE___-BE3-TANDE___-BE4-TND.KU3A-BE9-1 TANDE KU1A:EHV: | TDF Impact | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 659427 TN.LS-JD-BE3 345 779400 G24-081-TAP 345 1 | B | 1195 | 1 | 127.736 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Rebuild line 659427 TN.LS-JD-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 659336 TANDE___-BE3 345 659427 TN.LS-JD-BE3 345 Z | B | 1195 | 1 | 127.7361 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 659336 TANDE___-BE3 345 659427 TN.LS-JD-BE3 345 Z | B | 1195 | 1 | 127.7361 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 659336 TANDE___-BE3 345 659427 TN.LS-JD-BE3 345 Z | B | 1195 | 1 | 127.7361 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 659331 SPRNGBRK-BE7 115 3WXFMR 659:652: SPRNGBRK KUXA 115 1 | B | 416 | 0.25008 | 128.3005 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 659331 SPRNGBRK-BE7 115 3WXFMR 659:652: SPRNGBRK KUXA 115 1 | B | 416 | 0.25008 | 128.3005 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 659331 SPRNGBRK-BE7 115 3WXFMR 659:652: SPRNGBRK KUXA 115 1 | B | 416 | 0.25008 | 128.3005 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | TO->FROM | 659331 SPRNGBRK-BE7 115 3WXFMR 659:652: SPRNGBRK KUXA 115 1 | B | 416 | 0.24415 | 129.7201 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | TO->FROM | 659331 SPRNGBRK-BE7 115 3WXFMR 659:652: SPRNGBRK KUXA 115 1 | B | 416 | 0.24415 | 129.7201 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | TO->FROM | 659331 SPRNGBRK-BE7 115 3WXFMR 659:652: SPRNGBRK KUXA 115 1 | B | 416 | 0.24415 | 129.7201 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 655957 EASTFORK-MW7 115 659331 SPRNGBRK-BE7 115 1 | B | 415 | 0.25008 | 130.4722 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 655957 EASTFORK-MW7 115 659331 SPRNGBRK-BE7 115 1 | B | 415 | 0.25008 | 130.4722 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 655957 EASTFORK-MW7 115 659331 SPRNGBRK-BE7 115 1 | B | 415 | 0.25008 | 130.4722 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | TO->FROM | 659362 WHEELOCK-BE4 230 661084 TIOGA4 4 230 1 | B | 506 | 0.19572 | 130.9507 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | Cumulative Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | TO->FROM | 659362 WHEELOCK-BE4 230 661084 TIOGA4 4 230 1 | B | 506 | 0.19572 | 130.9507 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | Cumulative Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | TO->FROM | 659362 WHEELOCK-BE4 230 661084 TIOGA4 4 230 1 | B | 506 | 0.19572 | 130.9507 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | Cumulative Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 659331 SPRNGBRK-BE7 115 3WXFMR 659:652: SPRNGBRK KUXA 115 1 | B | 416 | 0.25434 | 132.4544 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 659331 SPRNGBRK-BE7 115 3WXFMR 659:652: SPRNGBRK KUXA 115 1 | B | 416 | 0.25434 | 132.4544 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 659331 SPRNGBRK-BE7 115 3WXFMR 659:652: SPRNGBRK KUXA 115 1 | B | 416 | 0.25434 | 132.4544 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-081 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.36634 | 132.5403 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Add 3-winding transformer 659336 TANDE___-BE3 345 659337 TANDE___-BE4 230 659338 TND.KU3A-BE9 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | TO->FROM | 655957 EASTFORK-MW7 115 659331 SPRNGBRK-BE7 115 1 | B | 415 | 0.24415 | 132.6347 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | TO->FROM | 655957 EASTFORK-MW7 115 659331 SPRNGBRK-BE7 115 1 | B | 415 | 0.24415 | 132.6347 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | TO->FROM | 655957 EASTFORK-MW7 115 659331 SPRNGBRK-BE7 115 1 | B | 415 | 0.24415 | 132.6347 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | TO->FROM | 652400 WILISTN4 230 659362 WHEELOCK-BE4 230 1 | B | 406 | 0.17607 | 133.1912 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | Cumulative Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | TO->FROM | 652400 WILISTN4 230 659362 WHEELOCK-BE4 230 1 | B | 406 | 0.17607 | 133.1912 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | Cumulative Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | TO->FROM | 652400 WILISTN4 230 659362 WHEELOCK-BE4 230 1 | B | 406 | 0.17607 | 133.1912 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | Cumulative Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1 | B | 506 | 0.35879 | 134.4545 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1 | B | 506 | 0.35879 | 134.4545 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1 | B | 506 | 0.35879 | 134.4545 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 655957 EASTFORK-MW7 115 659331 SPRNGBRK-BE7 115 1 | B | 415 | 0.25434 | 134.8503 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 655957 EASTFORK-MW7 115 659331 SPRNGBRK-BE7 115 1 | B | 415 | 0.25434 | 134.8503 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 655957 EASTFORK-MW7 115 659331 SPRNGBRK-BE7 115 1 | B | 415 | 0.25434 | 134.8503 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | 1 | 134.9437 | Single 659427 TN.LS-JD-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | 1 | 134.991 | P23:345:UMZB:# 7149 #:: TND IN ND. BREAKER FAULT (292):EHV: | TDF Impact | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | 1 | 135.0952 | P23:345:UMZB:# 7148 #:: TND IN ND. BREAKER FAULT (296):EHV: | TDF Impact | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | 1 | 135.101 | P12:345.0:UMZ:# N-1 #:: LINE TANDE___-BE3-TN.LS-JD-BE3-Z :EHV: | TDF Impact | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | TO->FROM | 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | 1 | 135.2094 | P12:345.0:UMZ:# N-1 #:: LINE TANDE___-BE3-TN.LS-JD-BE3-Z :EHV: | TDF Impact | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | TO->FROM | 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | 1 | 135.4088 | P23:345:UMZB:# 7149 #:: TND IN ND. BREAKER FAULT (292):EHV: | TDF Impact | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | TO->FROM | 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | 1 | 135.4128 | P23:345:UMZB:# 7148 #:: TND IN ND. BREAKER FAULT (296):EHV: | TDF Impact | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | TO->FROM | 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | 1 | 135.4147 | Single 659427 TN.LS-JD-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-081 | TO->FROM | 659336 TANDE___-BE3 345 659427 TN.LS-JD-BE3 345 Z | B | 1087 | 1 | 136.8399 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Rebuild line 659336 TANDE___-BE3 345 659427 TN.LS-JD-BE3 345 Z
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 655933 N.MISRDG-MW7 115 655957 EASTFORK-MW7 115 1 | B | 189 | 0.12707 | 137.3456 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | Cumulative Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 655933 N.MISRDG-MW7 115 655957 EASTFORK-MW7 115 1 | B | 189 | 0.12707 | 137.3456 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | Cumulative Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 655933 N.MISRDG-MW7 115 655957 EASTFORK-MW7 115 1 | B | 189 | 0.12707 | 137.3456 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | Cumulative Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 655933 N.MISRDG-MW7 115 655957 EASTFORK-MW7 115 1 | B | 189 | 0.12997 | 137.4246 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | Cumulative Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 655933 N.MISRDG-MW7 115 655957 EASTFORK-MW7 115 1 | B | 189 | 0.12997 | 137.4246 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | Cumulative Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 655933 N.MISRDG-MW7 115 655957 EASTFORK-MW7 115 1 | B | 189 | 0.12997 | 137.4246 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | Cumulative Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-081 | TO->FROM | 659336 TANDE___-BE3 345 659427 TN.LS-JD-BE3 345 Z | B | 1087 | 1 | 138.039 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Rebuild line 659336 TANDE___-BE3 345 659427 TN.LS-JD-BE3 345 Z
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-081 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.36527 | 138.2005 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Add 3-winding transformer 659336 TANDE___-BE3 345 659337 TANDE___-BE4 230 659338 TND.KU3A-BE9 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 659427 TN.LS-JD-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | 1 | 140.2416 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Rebuild line 659427 TN.LS-JD-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 659336 TANDE___-BE3 345 659427 TN.LS-JD-BE3 345 Z | B | 1087 | 1 | 140.2416 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 659336 TANDE___-BE3 345 659427 TN.LS-JD-BE3 345 Z | B | 1087 | 1 | 140.2416 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 659336 TANDE___-BE3 345 659427 TN.LS-JD-BE3 345 Z | B | 1087 | 1 | 140.2416 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | TO->FROM | 659427 TN.LS-JD-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | 1 | 141.3444 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Rebuild line 659427 TN.LS-JD-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | TO->FROM | 659336 TANDE___-BE3 345 659427 TN.LS-JD-BE3 345 Z | B | 1087 | 1 | 141.3444 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | TO->FROM | 659336 TANDE___-BE3 345 659427 TN.LS-JD-BE3 345 Z | B | 1087 | 1 | 141.3444 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | TO->FROM | 659336 TANDE___-BE3 345 659427 TN.LS-JD-BE3 345 Z | B | 1087 | 1 | 141.3444 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | TO->FROM | 655933 N.MISRDG-MW7 115 655957 EASTFORK-MW7 115 1 | B | 189 | 0.12584 | 142.6232 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | Cumulative Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | TO->FROM | 655933 N.MISRDG-MW7 115 655957 EASTFORK-MW7 115 1 | B | 189 | 0.12584 | 142.6232 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | Cumulative Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | TO->FROM | 655933 N.MISRDG-MW7 115 655957 EASTFORK-MW7 115 1 | B | 189 | 0.12584 | 142.6232 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | Cumulative Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | TO->FROM | 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1 | B | 506 | 0.40604 | 144.5546 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | TO->FROM | 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1 | B | 506 | 0.40604 | 144.5546 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | TO->FROM | 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1 | B | 506 | 0.40604 | 144.5546 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.42458 | 147.6215 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.42458 | 147.6215 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.42458 | 147.6215 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.42753 | 150.1034 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.42753 | 150.1034 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.42753 | 150.1034 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.58394 | 172.61 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.58394 | 172.61 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.58394 | 172.61 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1 | B | 637 | 0.54166 | 173.7597 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1 | B | 637 | 0.54166 | 173.7597 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1 | B | 637 | 0.54166 | 173.7597 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.60807 | 204.6432 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.60807 | 204.6432 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.60807 | 204.6432 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.61416 | 208.6129 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.61416 | 208.6129 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-081 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.61416 | 208.6129 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1 | B | 506 | 0.53355 | 213.4091 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1 | B | 506 | 0.53355 | 213.4091 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-081 | TO->FROM | 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1 | B | 506 | 0.53355 | 213.4091 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | TO->FROM | 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1 | B | 506 | 0.58394 | 227.6009 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | TO->FROM | 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1 | B | 506 | 0.58394 | 227.6009 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-081 | TO->FROM | 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1 | B | 506 | 0.58394 | 227.6009 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | A | 600 | 0.20744 | 100.7847 | System Intact | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | A | 600 | 0.20744 | 100.7847 | System Intact | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | A | 600 | 0.20744 | 100.7847 | System Intact | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | 0.55175 | 100.9864 | P12:345.0:UMZ:# N-1 #:: LINE ANTELOPE-BE3-ROUNDUP_-BE3-1 :EHV: | TDF Impact | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.2042 | 101.1212 | 259421 | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.2042 | 101.1212 | 259421 | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.2042 | 101.1212 | 259421 | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | 0.55166 | 101.1602 | P42:345:UMZB:# 2504 #:: AVS IN ND. STUCK BREAKER (4396):EHV: | TDF Impact | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.2042 | 101.5106 | 259422 | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.2042 | 101.5106 | 259698 | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.2042 | 101.5106 | 259422 | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.2042 | 101.5106 | 259698 | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.2042 | 101.5106 | 259422 | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.2042 | 101.5106 | 259698 | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.2042 | 101.5106 | P12:230:SASK:230KV-G1P-FUT:::HV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.2042 | 101.5106 | P12:230:SASK:230KV-G1P-FUT:::HV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.2042 | 101.5106 | P12:230:SASK:230KV-G1P-FUT:::HV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.2042 | 101.5249 | P11:13.8:SASK:CHNK #1 GT:::HV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.2042 | 101.5249 | P11:13.8:SASK:CHNK #1 GT:::HV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.2042 | 101.5249 | P11:13.8:SASK:CHNK #1 GT:::HV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.32319 | 102.1082 | 279736 | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.32319 | 102.1082 | 279736 | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.32319 | 102.1082 | 279736 | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1195 | 0.6622 | 103.6807 | P12:230.0:UMZ:# N-1 #:: LINE NESET___-BE4-TANDE___-BE4-1 :HV: | TDF Impact | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 659334 JUDSON__-BE4 230 3WXFMR 659:JUDSON KU3A 230 1 | B | 717 | 0.12894 | 104.5457 | Single 659333 JUDSON__-BE3 345 659334 JUDSON__-BE4 230 659329 'JDS.KUXA-BE9' 13 1 | Cumulative Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 659334 JUDSON__-BE4 230 3WXFMR 659:JUDSON KU3A 230 1 | B | 717 | 0.12894 | 104.5457 | Single 659333 JUDSON__-BE3 345 659334 JUDSON__-BE4 230 659329 'JDS.KUXA-BE9' 13 1 | Cumulative Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 659334 JUDSON__-BE4 230 3WXFMR 659:JUDSON KU3A 230 1 | B | 717 | 0.12894 | 104.5457 | Single 659333 JUDSON__-BE3 345 659334 JUDSON__-BE4 230 659329 'JDS.KUXA-BE9' 13 1 | Cumulative Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 659334 JUDSON__-BE4 230 3WXFMR 659:652: JUDSON KUXA 230 1 | B | 717 | 0.12894 | 104.5457 | P13:345-230.0:UMZ:# N-1 #:: 3WND JUDSON__-BE3-JUDSON__-BE4-JDS.KU6A-BE9-1 JUDSON KU3A:EHV: | Cumulative Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 659334 JUDSON__-BE4 230 3WXFMR 659:652: JUDSON KUXA 230 1 | B | 717 | 0.12894 | 104.5457 | P13:345-230.0:UMZ:# N-1 #:: 3WND JUDSON__-BE3-JUDSON__-BE4-JDS.KU6A-BE9-1 JUDSON KU3A:EHV: | Cumulative Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 659334 JUDSON__-BE4 230 3WXFMR 659:652: JUDSON KUXA 230 1 | B | 717 | 0.12894 | 104.5457 | P13:345-230.0:UMZ:# N-1 #:: 3WND JUDSON__-BE3-JUDSON__-BE4-JDS.KU6A-BE9-1 JUDSON KU3A:EHV: | Cumulative Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.22643 | 104.892 | P12:115.0:UMZ:# N-1 #:: LINE EASTFORK-MW7-SPRNGBRK-BE7-1 :HV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.22643 | 104.892 | P12:115.0:UMZ:# N-1 #:: LINE EASTFORK-MW7-SPRNGBRK-BE7-1 :HV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.22643 | 104.892 | P12:115.0:UMZ:# N-1 #:: LINE EASTFORK-MW7-SPRNGBRK-BE7-1 :HV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.22643 | 104.8922 | P13:345-115.0:UMZ:# N-1 #:: 3WND SPRNGBRK-BE3-SPRNGBRK-BE7-SPRNGBRK-BE9-1 652_ SPRNGBRK KUXA_:EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.22643 | 104.8922 | P13:345-115.0:UMZ:# N-1 #:: 3WND SPRNGBRK-BE3-SPRNGBRK-BE7-SPRNGBRK-BE9-1 652_ SPRNGBRK KUXA_:EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.22643 | 104.8922 | P13:345-115.0:UMZ:# N-1 #:: 3WND SPRNGBRK-BE3-SPRNGBRK-BE7-SPRNGBRK-BE9-1 652_ SPRNGBRK KUXA_:EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | TO->FROM | 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | A | 1087 | 0.5568 | 104.9308 | System Intact | TDF Impact | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 652400 WILISTN4 230 659334 JUDSON__-BE4 230 1 | B | 482 | 0.14793 | 105.161 | P12:230.0:UMZ:# N-1 #:: LINE OWAN -MW4-JUDSON__-BE4-Z :HV: | Cumulative Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 652400 WILISTN4 230 659334 JUDSON__-BE4 230 1 | B | 482 | 0.14793 | 105.161 | P12:230.0:UMZ:# N-1 #:: LINE OWAN -MW4-JUDSON__-BE4-Z :HV: | Cumulative Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 652400 WILISTN4 230 659334 JUDSON__-BE4 230 1 | B | 482 | 0.14793 | 105.161 | P12:230.0:UMZ:# N-1 #:: LINE OWAN -MW4-JUDSON__-BE4-Z :HV: | Cumulative Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | 0.57883 | 105.7 | P12:230.0:UMZ:# N-1 #:: LINE WHEELOCK-BE4-TIOGA4 4-1 :HV: | TDF Impact | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 29SP | T2 | GEN-2024-082 | TO->FROM | 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1 | B | 637 | 0.35033 | 106.461 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Rebuild line 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | A | 600 | 0.2042 | 106.9942 | System Intact | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | A | 600 | 0.2042 | 106.9942 | System Intact | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | A | 600 | 0.2042 | 106.9942 | System Intact | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | 0.62588 | 107.4493 | P12:230.0:UMZ:# N-1 #:: LINE NESET___-BE4-TIOGA4 4-Z :HV: | TDF Impact | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 652400 WILISTN4 230 659334 JUDSON__-BE4 230 1 | B | 482 | 0.34629 | 108.3751 | Single 659427 TN.LS-JD-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 652400 WILISTN4 230 659334 JUDSON__-BE4 230 1 | B | 482 | 0.34629 | 108.3751 | Single 659427 TN.LS-JD-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 652400 WILISTN4 230 659334 JUDSON__-BE4 230 1 | B | 482 | 0.34629 | 108.3751 | Single 659427 TN.LS-JD-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 652400 WILISTN4 230 659334 JUDSON__-BE4 230 1 | B | 482 | 0.34629 | 108.3754 | P12:345.0:UMZ:# N-1 #:: LINE TANDE___-BE3-TN.LS-JD-BE3-Z :EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 652400 WILISTN4 230 659334 JUDSON__-BE4 230 1 | B | 482 | 0.34629 | 108.3754 | P12:345.0:UMZ:# N-1 #:: LINE TANDE___-BE3-TN.LS-JD-BE3-Z :EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 652400 WILISTN4 230 659334 JUDSON__-BE4 230 1 | B | 482 | 0.34629 | 108.3754 | P12:345.0:UMZ:# N-1 #:: LINE TANDE___-BE3-TN.LS-JD-BE3-Z :EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.24707 | 108.6892 | P12:230.0:UMZ:# N-1 #:: LINE WILISTN4-JUDSON__-BE4-1 :HV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.24707 | 108.6892 | P12:230.0:UMZ:# N-1 #:: LINE WILISTN4-JUDSON__-BE4-1 :HV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.24707 | 108.6892 | P12:230.0:UMZ:# N-1 #:: LINE WILISTN4-JUDSON__-BE4-1 :HV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1 | B | 637 | 0.36398 | 109.1747 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1 | B | 637 | 0.36398 | 109.1747 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1 | B | 637 | 0.36398 | 109.1747 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | TO->FROM | 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | 0.62313 | 109.6836 | 279688 | TDF Impact | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 652400 WILISTN4 230 659334 JUDSON__-BE4 230 1 | B | 482 | 0.34356 | 110.5461 | P23:345:UMZB:# 7149 #:: TND IN ND. BREAKER FAULT (292):EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 652400 WILISTN4 230 659334 JUDSON__-BE4 230 1 | B | 482 | 0.34356 | 110.5461 | P23:345:UMZB:# 7149 #:: TND IN ND. BREAKER FAULT (292):EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 652400 WILISTN4 230 659334 JUDSON__-BE4 230 1 | B | 482 | 0.34356 | 110.5461 | P23:345:UMZB:# 7149 #:: TND IN ND. BREAKER FAULT (292):EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-082 | TO->FROM | 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1 | B | 506 | 0.34728 | 110.8229 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Rebuild line 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.22311 | 111.7104 | P12:115.0:UMZ:# N-1 #:: LINE EASTFORK-MW7-SPRNGBRK-BE7-1 :HV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.22311 | 111.7104 | P12:115.0:UMZ:# N-1 #:: LINE EASTFORK-MW7-SPRNGBRK-BE7-1 :HV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.22311 | 111.7104 | P12:115.0:UMZ:# N-1 #:: LINE EASTFORK-MW7-SPRNGBRK-BE7-1 :HV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.22311 | 111.7105 | P13:345-115.0:UMZ:# N-1 #:: 3WND SPRNGBRK-BE3-SPRNGBRK-BE7-SPRNGBRK-BE9-1 652_ SPRNGBRK KUXA_:EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.22311 | 111.7105 | P13:345-115.0:UMZ:# N-1 #:: 3WND SPRNGBRK-BE3-SPRNGBRK-BE7-SPRNGBRK-BE9-1 652_ SPRNGBRK KUXA_:EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.22311 | 111.7105 | P13:345-115.0:UMZ:# N-1 #:: 3WND SPRNGBRK-BE3-SPRNGBRK-BE7-SPRNGBRK-BE9-1 652_ SPRNGBRK KUXA_:EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29WP | T2 | GEN-2024-082 | TO->FROM | 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1 | B | 637 | 0.35174 | 111.713 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Rebuild line 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 652400 WILISTN4 230 659334 JUDSON__-BE4 230 1 | B | 482 | 0.21665 | 111.8239 | P13:345-230.0:UMZ:# N-1 #:: 3WND TANDE___-BE3-TANDE___-BE4-TND.KU3A-BE9-1 TANDE KU1A:EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 652400 WILISTN4 230 659334 JUDSON__-BE4 230 1 | B | 482 | 0.21665 | 111.8239 | P13:345-230.0:UMZ:# N-1 #:: 3WND TANDE___-BE3-TANDE___-BE4-TND.KU3A-BE9-1 TANDE KU1A:EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 652400 WILISTN4 230 659334 JUDSON__-BE4 230 1 | B | 482 | 0.21665 | 111.8239 | P13:345-230.0:UMZ:# N-1 #:: 3WND TANDE___-BE3-TANDE___-BE4-TND.KU3A-BE9-1 TANDE KU1A:EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | TO->FROM | 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | 0.54113 | 112.6506 | P12:230.0:UMZ:# N-1 #:: LINE WHEELOCK-BE4-TIOGA4 4-1 :HV: | TDF Impact | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | 0.64839 | 113.0149 | P12:230.0:UMZ:# N-1 #:: LINE NESET___-BE4-TANDE___-BE4-1 :HV: | TDF Impact | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | TO->FROM | 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | 0.62209 | 113.098 | 279736 | TDF Impact | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | TO->FROM | 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | 0.62715 | 114.4902 | P12:230.0:UMZ:# N-1 #:: LINE NESET___-BE4-TIOGA4 4-Z :HV: | TDF Impact | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.40604 | 115.1422 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.40604 | 115.1422 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.40604 | 115.1422 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1195 | 0.70189 | 115.2596 | P13:345-230.0:UMZ:# N-1 #:: 3WND TANDE___-BE3-TANDE___-BE4-TND.KU3A-BE9-1 TANDE KU1A:EHV: | TDF Impact | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 652400 WILISTN4 230 659334 JUDSON__-BE4 230 1 | B | 482 | 0.34408 | 115.4285 | P23:345:UMZB:# 7148 #:: TND IN ND. BREAKER FAULT (296):EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 652400 WILISTN4 230 659334 JUDSON__-BE4 230 1 | B | 482 | 0.34408 | 115.4285 | P23:345:UMZB:# 7148 #:: TND IN ND. BREAKER FAULT (296):EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 652400 WILISTN4 230 659334 JUDSON__-BE4 230 1 | B | 482 | 0.34408 | 115.4285 | P23:345:UMZB:# 7148 #:: TND IN ND. BREAKER FAULT (296):EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-082 | TO->FROM | 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1 | B | 506 | 0.31004 | 115.9626 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Rebuild line 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.24286 | 116.3034 | P12:230.0:UMZ:# N-1 #:: LINE WILISTN4-JUDSON__-BE4-1 :HV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.24286 | 116.3034 | P12:230.0:UMZ:# N-1 #:: LINE WILISTN4-JUDSON__-BE4-1 :HV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.24286 | 116.3034 | P12:230.0:UMZ:# N-1 #:: LINE WILISTN4-JUDSON__-BE4-1 :HV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 659362 WHEELOCK-BE4 230 661084 TIOGA4 4 230 1 | B | 526 | 0.21345 | 120.1453 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 659362 WHEELOCK-BE4 230 661084 TIOGA4 4 230 1 | B | 526 | 0.21345 | 120.1453 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 659362 WHEELOCK-BE4 230 661084 TIOGA4 4 230 1 | B | 526 | 0.21345 | 120.1453 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | TO->FROM | 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | 0.66219 | 121.1476 | P13:345-230.0:UMZ:# N-1 #:: 3WND TANDE___-BE3-TANDE___-BE4-TND.KU3A-BE9-1 TANDE KU1A:EHV: | TDF Impact | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | TO->FROM | 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | 0.66219 | 121.1484 | P12:230.0:UMZ:# N-1 #:: LINE NESET___-BE4-TANDE___-BE4-1 :HV: | TDF Impact | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1195 | 1 | 122.8003 | P12:345.0:UMZ:# N-1 #:: LINE TANDE___-BE3-TN.LS-JD-BE3-Z :EHV: | TDF Impact | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1195 | 1 | 122.9433 | Single 659427 TN.LS-JD-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1195 | 1 | 123.0553 | P23:345:UMZB:# 7149 #:: TND IN ND. BREAKER FAULT (292):EHV: | TDF Impact | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1195 | 1 | 123.2148 | P23:345:UMZB:# 7148 #:: TND IN ND. BREAKER FAULT (296):EHV: | TDF Impact | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-082 | TO->FROM | 659336 TANDE___-BE3 345 659427 TN.LS-JD-BE3 345 Z | B | 1195 | 1 | 124.5842 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Rebuild line 659336 TANDE___-BE3 345 659427 TN.LS-JD-BE3 345 Z
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 659362 WHEELOCK-BE4 230 661084 TIOGA4 4 230 1 | B | 506 | 0.20505 | 125.5606 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 659362 WHEELOCK-BE4 230 661084 TIOGA4 4 230 1 | B | 506 | 0.20505 | 125.5606 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 659362 WHEELOCK-BE4 230 661084 TIOGA4 4 230 1 | B | 506 | 0.20505 | 125.5606 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | 0.68962 | 125.907 | P13:345-230.0:UMZ:# N-1 #:: 3WND TANDE___-BE3-TANDE___-BE4-TND.KU3A-BE9-1 TANDE KU1A:EHV: | TDF Impact | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 659427 TN.LS-JD-BE3 345 779400 G24-081-TAP 345 1 | B | 1195 | 1 | 127.736 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Rebuild line 659427 TN.LS-JD-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 659336 TANDE___-BE3 345 659427 TN.LS-JD-BE3 345 Z | B | 1195 | 1 | 127.7361 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 659336 TANDE___-BE3 345 659427 TN.LS-JD-BE3 345 Z | B | 1195 | 1 | 127.7361 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 659336 TANDE___-BE3 345 659427 TN.LS-JD-BE3 345 Z | B | 1195 | 1 | 127.7361 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 659331 SPRNGBRK-BE7 115 3WXFMR 659:652: SPRNGBRK KUXA 115 1 | B | 416 | 0.25008 | 128.3005 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 659331 SPRNGBRK-BE7 115 3WXFMR 659:652: SPRNGBRK KUXA 115 1 | B | 416 | 0.25008 | 128.3005 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 659331 SPRNGBRK-BE7 115 3WXFMR 659:652: SPRNGBRK KUXA 115 1 | B | 416 | 0.25008 | 128.3005 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | TO->FROM | 659331 SPRNGBRK-BE7 115 3WXFMR 659:652: SPRNGBRK KUXA 115 1 | B | 416 | 0.24415 | 129.7201 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | TO->FROM | 659331 SPRNGBRK-BE7 115 3WXFMR 659:652: SPRNGBRK KUXA 115 1 | B | 416 | 0.24415 | 129.7201 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | TO->FROM | 659331 SPRNGBRK-BE7 115 3WXFMR 659:652: SPRNGBRK KUXA 115 1 | B | 416 | 0.24415 | 129.7201 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 655957 EASTFORK-MW7 115 659331 SPRNGBRK-BE7 115 1 | B | 415 | 0.25008 | 130.4722 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 655957 EASTFORK-MW7 115 659331 SPRNGBRK-BE7 115 1 | B | 415 | 0.25008 | 130.4722 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 655957 EASTFORK-MW7 115 659331 SPRNGBRK-BE7 115 1 | B | 415 | 0.25008 | 130.4722 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | TO->FROM | 659362 WHEELOCK-BE4 230 661084 TIOGA4 4 230 1 | B | 506 | 0.19572 | 130.9507 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | Cumulative Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | TO->FROM | 659362 WHEELOCK-BE4 230 661084 TIOGA4 4 230 1 | B | 506 | 0.19572 | 130.9507 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | Cumulative Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | TO->FROM | 659362 WHEELOCK-BE4 230 661084 TIOGA4 4 230 1 | B | 506 | 0.19572 | 130.9507 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | Cumulative Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 659331 SPRNGBRK-BE7 115 3WXFMR 659:652: SPRNGBRK KUXA 115 1 | B | 416 | 0.25434 | 132.4544 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 659331 SPRNGBRK-BE7 115 3WXFMR 659:652: SPRNGBRK KUXA 115 1 | B | 416 | 0.25434 | 132.4544 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 659331 SPRNGBRK-BE7 115 3WXFMR 659:652: SPRNGBRK KUXA 115 1 | B | 416 | 0.25434 | 132.4544 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-082 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.36634 | 132.5403 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Add 3-winding transformer 659336 TANDE___-BE3 345 659337 TANDE___-BE4 230 659338 TND.KU3A-BE9 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | TO->FROM | 655957 EASTFORK-MW7 115 659331 SPRNGBRK-BE7 115 1 | B | 415 | 0.24415 | 132.6347 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | TO->FROM | 655957 EASTFORK-MW7 115 659331 SPRNGBRK-BE7 115 1 | B | 415 | 0.24415 | 132.6347 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | TO->FROM | 655957 EASTFORK-MW7 115 659331 SPRNGBRK-BE7 115 1 | B | 415 | 0.24415 | 132.6347 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | TO->FROM | 652400 WILISTN4 230 659362 WHEELOCK-BE4 230 1 | B | 406 | 0.17607 | 133.1912 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | Cumulative Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | TO->FROM | 652400 WILISTN4 230 659362 WHEELOCK-BE4 230 1 | B | 406 | 0.17607 | 133.1912 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | Cumulative Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | TO->FROM | 652400 WILISTN4 230 659362 WHEELOCK-BE4 230 1 | B | 406 | 0.17607 | 133.1912 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | Cumulative Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1 | B | 506 | 0.35879 | 134.4545 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1 | B | 506 | 0.35879 | 134.4545 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1 | B | 506 | 0.35879 | 134.4545 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 655957 EASTFORK-MW7 115 659331 SPRNGBRK-BE7 115 1 | B | 415 | 0.25434 | 134.8503 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 655957 EASTFORK-MW7 115 659331 SPRNGBRK-BE7 115 1 | B | 415 | 0.25434 | 134.8503 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 655957 EASTFORK-MW7 115 659331 SPRNGBRK-BE7 115 1 | B | 415 | 0.25434 | 134.8503 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | 1 | 134.9437 | Single 659427 TN.LS-JD-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | 1 | 134.991 | P23:345:UMZB:# 7149 #:: TND IN ND. BREAKER FAULT (292):EHV: | TDF Impact | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | 1 | 135.0952 | P23:345:UMZB:# 7148 #:: TND IN ND. BREAKER FAULT (296):EHV: | TDF Impact | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | 1 | 135.101 | P12:345.0:UMZ:# N-1 #:: LINE TANDE___-BE3-TN.LS-JD-BE3-Z :EHV: | TDF Impact | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | TO->FROM | 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | 1 | 135.2094 | P12:345.0:UMZ:# N-1 #:: LINE TANDE___-BE3-TN.LS-JD-BE3-Z :EHV: | TDF Impact | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | TO->FROM | 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | 1 | 135.4088 | P23:345:UMZB:# 7149 #:: TND IN ND. BREAKER FAULT (292):EHV: | TDF Impact | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | TO->FROM | 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | 1 | 135.4128 | P23:345:UMZB:# 7148 #:: TND IN ND. BREAKER FAULT (296):EHV: | TDF Impact | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | TO->FROM | 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | 1 | 135.4147 | Single 659427 TN.LS-JD-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Rebuild line 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-082 | TO->FROM | 659336 TANDE___-BE3 345 659427 TN.LS-JD-BE3 345 Z | B | 1087 | 1 | 136.8399 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Rebuild line 659336 TANDE___-BE3 345 659427 TN.LS-JD-BE3 345 Z
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 655933 N.MISRDG-MW7 115 655957 EASTFORK-MW7 115 1 | B | 189 | 0.12707 | 137.3456 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | Cumulative Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 655933 N.MISRDG-MW7 115 655957 EASTFORK-MW7 115 1 | B | 189 | 0.12707 | 137.3456 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | Cumulative Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 655933 N.MISRDG-MW7 115 655957 EASTFORK-MW7 115 1 | B | 189 | 0.12707 | 137.3456 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | Cumulative Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 655933 N.MISRDG-MW7 115 655957 EASTFORK-MW7 115 1 | B | 189 | 0.12997 | 137.4246 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | Cumulative Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 655933 N.MISRDG-MW7 115 655957 EASTFORK-MW7 115 1 | B | 189 | 0.12997 | 137.4246 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | Cumulative Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 655933 N.MISRDG-MW7 115 655957 EASTFORK-MW7 115 1 | B | 189 | 0.12997 | 137.4246 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | Cumulative Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-082 | TO->FROM | 659336 TANDE___-BE3 345 659427 TN.LS-JD-BE3 345 Z | B | 1087 | 1 | 138.039 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Rebuild line 659336 TANDE___-BE3 345 659427 TN.LS-JD-BE3 345 Z
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-082 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.36527 | 138.2005 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Add 3-winding transformer 659336 TANDE___-BE3 345 659337 TANDE___-BE4 230 659338 TND.KU3A-BE9 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 659427 TN.LS-JD-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | 1 | 140.2416 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Rebuild line 659427 TN.LS-JD-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 659336 TANDE___-BE3 345 659427 TN.LS-JD-BE3 345 Z | B | 1087 | 1 | 140.2416 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 659336 TANDE___-BE3 345 659427 TN.LS-JD-BE3 345 Z | B | 1087 | 1 | 140.2416 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 659336 TANDE___-BE3 345 659427 TN.LS-JD-BE3 345 Z | B | 1087 | 1 | 140.2416 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | TO->FROM | 659427 TN.LS-JD-BE3 345 779400 G24-081-TAP 345 1 | B | 1087 | 1 | 141.3444 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | Rebuild line 659427 TN.LS-JD-BE3 345 779400 G24-081-TAP 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | TO->FROM | 659336 TANDE___-BE3 345 659427 TN.LS-JD-BE3 345 Z | B | 1087 | 1 | 141.3444 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | TO->FROM | 659336 TANDE___-BE3 345 659427 TN.LS-JD-BE3 345 Z | B | 1087 | 1 | 141.3444 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | TO->FROM | 659336 TANDE___-BE3 345 659427 TN.LS-JD-BE3 345 Z | B | 1087 | 1 | 141.3444 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | TO->FROM | 655933 N.MISRDG-MW7 115 655957 EASTFORK-MW7 115 1 | B | 189 | 0.12584 | 142.6232 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | Cumulative Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | TO->FROM | 655933 N.MISRDG-MW7 115 655957 EASTFORK-MW7 115 1 | B | 189 | 0.12584 | 142.6232 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | Cumulative Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | TO->FROM | 655933 N.MISRDG-MW7 115 655957 EASTFORK-MW7 115 1 | B | 189 | 0.12584 | 142.6232 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | Cumulative Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | TO->FROM | 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1 | B | 506 | 0.40604 | 144.5546 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | TO->FROM | 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1 | B | 506 | 0.40604 | 144.5546 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | TO->FROM | 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1 | B | 506 | 0.40604 | 144.5546 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.42458 | 147.6215 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.42458 | 147.6215 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.42458 | 147.6215 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.42753 | 150.1034 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.42753 | 150.1034 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.42753 | 150.1034 | P12:345.0:UMZ:# N-1 #:: LINE SPRNGBRK-BE3-JUDSON__-BE3-1 :EHV: | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.58394 | 172.61 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.58394 | 172.61 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.58394 | 172.61 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1 | B | 637 | 0.54166 | 173.7597 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1 | B | 637 | 0.54166 | 173.7597 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1 | B | 637 | 0.54166 | 173.7597 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.60807 | 204.6432 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.60807 | 204.6432 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.60807 | 204.6432 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.61416 | 208.6129 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.61416 | 208.6129 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-082 | TO->FROM | 659337 TANDE___-BE4 230 3WXFMR 659:TANDE KU1A 230 1 | B | 637 | 0.61416 | 208.6129 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1 | B | 506 | 0.53355 | 213.4091 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1 | B | 506 | 0.53355 | 213.4091 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-082 | TO->FROM | 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1 | B | 506 | 0.53355 | 213.4091 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | TO->FROM | 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1 | B | 506 | 0.58394 | 227.6009 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_multiLelandOldsFinstadTandeVanHook_GenRemoved.idv : 2021 ITP upgrade, PID : 92168, NTC, ISD : 11/30/2026
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | TO->FROM | 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1 | B | 506 | 0.58394 | 227.6009 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 652_newNEWillistonFolvagline.idv : 2021 ITP upgrade, PID : 92211, NTC, ISD : 12/3/2024
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-082 | TO->FROM | 659138 NESET___-BE4 230 659337 TANDE___-BE4 230 1 | B | 506 | 0.58394 | 227.6009 | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | NewLine_SpringBrook_TwelveMile_345.idv : 2024ITP upgrade, PID : 94673 , NTC, ISD : 4/1/2032
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-090 | TO->FROM | 541199 ST JOE 7 345 541400 EASTOWN7 345 1 | B | 1185 | 0.13308 | 100.396 | Single 541199 STJOE7 345 761383 G17-183-TAP 345 1 | Cumulative Impact | Rebuild line 541199 ST JOE 7 345 541400 EASTOWN7 345 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-090 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.073348 | 101.6955 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-090 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.073348 | 101.6955 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-090 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.073348 | 101.6955 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 26SP | T1 | GEN-2024-090 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.07115 | 105.0133 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 29WP | T1 | GEN-2024-090 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.066616 | 106.2154 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-090 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.067484 | 106.5956 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-090 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.067484 | 106.5956 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-090 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.067484 | 106.5956 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-090 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.052478 | 106.8199 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-090 | TO->FROM | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | B | 1195 | 0.14622 | 107.005 | Single 541199 STJOE7 345 761383 G17-183-TAP 345 1 | Cumulative Impact | Rebuild line 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-090 | TO->FROM | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | A | 274 | 0.81421 | 113.443 | System Intact | TDF Impact | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-090 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.075433 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-090 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.075433 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-090 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.075433 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-090 | TO->FROM | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | B | 297 | 0.82605 | 116.2822 | Single 301552 5PLATCTY 161 541221 PLTCTY5 161 Z1 | TDF Impact | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-090 | TO->FROM | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | B | 297 | 0.85427 | 117.7121 | Single 541230 RNRIDGE5 161 541318 NCONGRS5 161 1 | TDF Impact | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-090 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.084109 | 117.7598 | P55:345:OPPD:S3458 3::FN13:EHV: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-090 | TO->FROM | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | B | 297 | 0.85427 | 117.8533 | P12:161:GMO:TWA-NCONGRESS-ROANRIDGE_1 | TDF Impact | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-090 | TO->FROM | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | B | 297 | 0.85427 | 117.8533 | P12:161:GMO:TWA-NCONGRESS-ROANRID:::HV: | TDF Impact | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-090 | TO->FROM | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | B | 297 | 0.85427 | 117.8665 | Single 541214 TWA5 161 541318 NCONGRS5 161 1 | TDF Impact | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-090 | TO->FROM | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | B | 297 | 0.85427 | 119.9331 | Single 541213 FRLVW5 161 541214 TWA5 161 1 | TDF Impact | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-090 | TO->FROM | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | A | 233 | 0.81451 | 123.2184 | System Intact | TDF Impact | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-090 | TO->FROM | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | B | 261 | 0.82636 | 124.2094 | Single 301552 5PLATCTY 161 541221 PLTCTY5 161 Z1 | TDF Impact | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-090 | TO->FROM | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | B | 261 | 0.82636 | 124.2094 | Single 300307 2PLATCTY 69 301552 5PLATCTY 161 1 | TDF Impact | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-090 | TO->FROM | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | B | 261 | 1 | 124.8942 | Single 541204 SMTHVL5 161 541221 PLTCTY5 161 1 | TDF Impact | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-090 | TO->FROM | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | B | 297 | 0.85427 | 124.9432 | Single 541212 KCI5 161 541213 FRLVW5 161 1 | TDF Impact | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-090 | TO->FROM | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | B | 261 | 0.72879 | 125.6142 | Single 542980 NASHUA7 345 543028 NASHUA-5 161 543640 'NASH T11 ' 13 11 | TDF Impact | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-090 | TO->FROM | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | B | 261 | 0.83317 | 125.903 | Single 541214 TWA5 161 541318 NCONGRS5 161 1 | TDF Impact | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-090 | TO->FROM | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | B | 261 | 0.79575 | 126.3641 | Single 541400 EASTOWN7 345 542982 IATAN7 345 1 | TDF Impact | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-090 | TO->FROM | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | B | 261 | 0.79575 | 126.3694 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1 | TDF Impact | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-090 | TO->FROM | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | B | 261 | 0.79575 | 126.3694 | P23:345:GMO:EASTOWNE-R7-14:::EHV: | TDF Impact | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-090 | TO->FROM | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | A | 233 | 0.79368 | 126.423 | System Intact | TDF Impact | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-090 | TO->FROM | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | B | 297 | 0.85427 | 127.7794 | Single 541212 KCI5 161 541221 PLTCTY5 161 1 | TDF Impact | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-090 | TO->FROM | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | B | 261 | 0.81656 | 128.0574 | Single 541400 EASTOWN7 345 542982 IATAN7 345 1 | TDF Impact | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-090 | TO->FROM | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | B | 261 | 0.81655 | 128.0739 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1 | TDF Impact | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-090 | TO->FROM | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | B | 261 | 0.81655 | 128.0739 | P23:345:GMO:EASTOWNE-R7-14:::EHV: | TDF Impact | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-090 | TO->FROM | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | B | 261 | 0.8548 | 128.1307 | Single 541212 KCI5 161 541213 FRLVW5 161 1 | TDF Impact | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-090 | TO->FROM | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | B | 261 | 0.83317 | 128.1691 | Single 541213 FRLVW5 161 541214 TWA5 161 1 | TDF Impact | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-090 | TO->FROM | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | B | 297 | 0.79901 | 129.7876 | Single 542980 NASHUA7 345 542982 IATAN7 345 1 | TDF Impact | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-090 | TO->FROM | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | B | 261 | 0.8548 | 131.3808 | Single 541212 KCI5 161 541221 PLTCTY5 161 1 | TDF Impact | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-090 | TO->FROM | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | B | 261 | 0.78284 | 132.6973 | Single 542980 NASHUA7 345 542982 IATAN7 345 1 | TDF Impact | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-090 | TO->FROM | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | B | 261 | 0.79958 | 133.9227 | Single 542980 NASHUA7 345 542982 IATAN7 345 1 | TDF Impact | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-090 | TO->FROM | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | B | 261 | 0.83317 | 134.9833 | Single 541212 KCI5 161 541213 FRLVW5 161 1 | TDF Impact | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-090 | TO->FROM | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | B | 261 | 0.83317 | 138.1474 | Single 541212 KCI5 161 541221 PLTCTY5 161 1 | TDF Impact | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-090 | TO->FROM | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | B | 297 | 0.79579 | 175.5841 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-090 | TO->FROM | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | B | 261 | 0.78191 | 182.0098 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-090 | TO->FROM | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | B | 261 | 0.79673 | 196.2546 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-099 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.075865 | 100.0488 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-099 | TO->FROM | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | B | 997 | 0.1637 | 100.166 | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | Cumulative Impact | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-099 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.064964 | 100.533 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-099 | TO->FROM | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | B | 997 | 0.17143 | 100.7286 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-099 | TO->FROM | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | B | 997 | 0.17143 | 101.1047 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-099 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.066147 | 102.9616 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-099 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.066147 | 102.9634 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-099 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.066147 | 103.0288 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-099 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.066147 | 103.4739 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-099 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.079762 | 103.9266 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-099 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.066147 | 104.1493 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-099 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.078863 | 104.7552 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-099 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.078863 | 104.888 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-099 | TO->FROM | 531510 HARBNGR3 115 3WXFMR 534:HARBGR345 345 1 | B | 385 | 0.050125 | 105.7318 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Add 3-winding transformer 531510 HARBNGR3 115 531511 HARBNGR-1 13 531512 HARBNGR7 345 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-099 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.082699 | 107.2243 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-099 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.066147 | 107.2793 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-099 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.066147 | 107.2794 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-099 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.082699 | 107.2951 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-099 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.066147 | 107.3093 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-099 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.077147 | 107.5866 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-099 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.066147 | 107.7557 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-099 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.066147 | 108.1822 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-099 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.066147 | 108.2747 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-099 | TO->FROM | 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | B | 997 | 0.30966 | 109.7018 | Single 525832 TUCO_INT7 345 526000 CRAWFISH_DR 345 2 | TDF Impact | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-099 | TO->FROM | 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | B | 997 | 0.30438 | 111.09 | Single 525832 TUCO_INT7 345 526000 CRAWFISH_DR 345 2 | TDF Impact | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-099 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.066147 | 111.3621 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-099 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.080164 | 111.723 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-099 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.080164 | 111.8755 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-099 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.077147 | 115.0541 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-099 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.080164 | 118.9427 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-099 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.080164 | 119.313 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-099 | TO->FROM | 531405 WALKMYR3 115 531510 HARBNGR3 115 1 | B | 331.39 | 0.050125 | 122.4803 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild line 531405 WALKMYR3 115 531510 HARBNGR3 115 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-109 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.074578 | 100.0488 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-109 | TO->FROM | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | B | 997 | 0.16865 | 100.166 | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | Cumulative Impact | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-109 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063727 | 100.533 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-109 | TO->FROM | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | B | 997 | 0.17328 | 100.7286 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-109 | TO->FROM | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | B | 997 | 0.17328 | 101.1047 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-109 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.064596 | 102.9616 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-109 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.064596 | 102.9634 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-109 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.064596 | 103.0288 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-109 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.064596 | 103.4739 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-109 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.079085 | 103.9266 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-109 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.064596 | 104.1493 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-109 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.077559 | 104.7552 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-109 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.077559 | 104.888 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-109 | TO->FROM | 531510 HARBNGR3 115 3WXFMR 534:HARBGR345 345 1 | B | 385 | 0.050234 | 105.7318 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Add 3-winding transformer 531510 HARBNGR3 115 531511 HARBNGR-1 13 531512 HARBNGR7 345 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-109 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.082004 | 107.2243 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-109 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.064596 | 107.2793 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-109 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.064596 | 107.2794 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-109 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.082004 | 107.2951 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-109 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.064596 | 107.3093 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-109 | TO->FROM | 523959 POTTER_CO 6 230 3WXFMR 526:WAUK 90343-A 230 1 | B | 559 | 0.11281 | 107.3794 | P42:345:SPS:HITCHLAND-1R15:::EHV: | Cumulative Impact | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-109 | TO->FROM | 523959 POTTER_CO 6 230 3WXFMR 526:WAUK 90343-A 230 1 | B | 559 | 0.11281 | 107.3953 | Single 523097 HITCHLAND7 345 523961 POTTER_CO7 345 1 | Cumulative Impact | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-109 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.07562 | 107.5866 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-109 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.064596 | 107.7557 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-109 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.064596 | 108.1822 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-109 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.064596 | 108.2747 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-109 | TO->FROM | 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | B | 997 | 0.22554 | 109.7018 | Single 525832 TUCO_INT7 345 526000 CRAWFISH_DR 345 2 | TDF Impact | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-109 | TO->FROM | 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | B | 997 | 0.22564 | 111.09 | Single 525832 TUCO_INT7 345 526000 CRAWFISH_DR 345 2 | TDF Impact | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-109 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.064596 | 111.3621 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-109 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.078618 | 111.723 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-109 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.078618 | 111.8755 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-109 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.07562 | 115.0541 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29L | T0 | GEN-2024-109 | TO->FROM | 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | B | 997 | 0.18925 | 116.6859 | Single 525832 TUCO_INT7 345 526000 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-109 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.078618 | 118.9427 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-109 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.078618 | 119.313 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-109 | TO->FROM | 531405 WALKMYR3 115 531510 HARBNGR3 115 1 | B | 331.39 | 0.050234 | 122.4803 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild line 531405 WALKMYR3 115 531510 HARBNGR3 115 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-113 | TO->FROM | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | B | 1059 | 0.16962 | 100.2166 | P12:345:AEPW:R.S.S.-7:ONETA--7::: | Cumulative Impact | Rebuild line 509745 CLARKSV7 345 515224 MUSKOGE7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-113 | TO->FROM | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | B | 1059 | 0.27637 | 105.0001 | P42:345:OKGE:SB_FTTH7386:::EHV: | TDF Impact | Rebuild line 509745 CLARKSV7 345 515224 MUSKOGE7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-113 | TO->FROM | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | B | 1059 | 0.27635 | 105.0075 | Single 515012 RVRVALY7 345 515302 FTSMITH7 345 1 | TDF Impact | Rebuild line 509745 CLARKSV7 345 515224 MUSKOGE7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-113 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1011 | 0.051264 | 106.9293 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-113 | TO->FROM | 515227 5TRIBES2 69 516093 OKTAHA 2 69 1 | B | 111 | 0.030171 | 107.0862 | P22:345:EES:MUSKOGE7!:::EHV: | TDF Impact | Rebuild line 515227 5TRIBES2 69 516093 OKTAHA 2 69 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-113 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1011 | 0.045961 | 107.7039 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-113 | TO->FROM | 515305 FTSMITH8 500 3WXFMR 524:524:FTSMITH1 500 1 | B | 693 | 0.33292 | 108.5609 | P12:161:EES:FTSMTHW5%:FTSMITH7%:FTSMTH511:HV: | TDF Impact | Add 3-winding transformer 515302 FTSMITH7 345 515305 FTSMITH8 500 515726 FTSMTH11 13 M2
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-113 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1187 | 0.062342 | 112.2151 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-113 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.069672 | 112.5233 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-113 | TO->FROM | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | A | 827 | 0.031266 | 113.506 | System Intact | TDF Impact | Rebuild line 532791 BENTON 7 345 532794 ROSEHIL7 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-113 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.066451 | 113.7225 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-113 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.068019 | 114.0272 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-113 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.06163 | 114.0895 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-113 | TO->FROM | 515305 FTSMITH8 500 3WXFMR 524:524:FTSMITH1 500 1 | B | 693 | 0.22329 | 115.3188 | Single 515302 FTSMITH7 345 515305 FTSMITH8 500 519010 'FTSMITH71 ' 13 2 | TDF Impact | Add 3-winding transformer 515302 FTSMITH7 345 515305 FTSMITH8 500 515726 FTSMTH11 13 M2
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-113 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.065793 | 115.4477 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-113 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.06163 | 115.647 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-113 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.065793 | 117.1553 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-113 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.065793 | 117.1572 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-113 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.065793 | 119.7129 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-113 | TO->FROM | 515301 FTSMTHW5 161 3WXFMR 524:524:FTSMITH5 345 5 | B | 493 | 0.20353 | 120.3942 | P42:500:OKGE:SB_FTTH8585:::EHV: | TDF Impact | Add 3-winding transformer 515301 FTSMTHW5 161 515302 FTSMITH7 345 515728 FTSMTH51 13 M2
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-113 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.065793 | 124.3274 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-113 | TO->FROM | 515301 FTSMTHW5 161 3WXFMR 524:524:FTSMITH5 345 5 | B | 493 | 0.26036 | 126.769 | P12:345:EES:FTSMITH7%:FTSMITH8%:FTSMTH111:EHV: | TDF Impact | Add 3-winding transformer 515301 FTSMTHW5 161 515302 FTSMITH7 345 515728 FTSMTH51 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-113 | TO->FROM | 516093 OKTAHA 2 69 3WXFMR OKTAHA 5 69 7 | B | 112 | 0.036806 | 127.8893 | P22:345:EES:MUSKOGE7!:::EHV: | TDF Impact | Rebuild 3-winding transformer 516092 OKTAHA 5 161 516093 OKTAHA 2 69 516095 OKTAHA71 13 7
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-113 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.048447 | 137.9906 | System Intact | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-113 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.043381 | 138.1985 | System Intact | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-113 | TO->FROM | 516093 OKTAHA 2 69 3WXFMR OKTAHA 5 69 7 | B | 112 | 0.035995 | 146.2088 | P22:345:EES:MUSKOGE7!:::EHV: | TDF Impact | Rebuild 3-winding transformer 516092 OKTAHA 5 161 516093 OKTAHA 2 69 516095 OKTAHA71 13 7
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-113 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.052349 | 155.7991 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-113 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.052493 | 159.2546 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-113 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.056476 | 160.5677 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-113 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.05196 | 161.638 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-113 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.053786 | 161.7992 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-113 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051059 | 161.8408 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-113 | TO->FROM | 516093 OKTAHA 2 69 3WXFMR OKTAHA 5 69 7 | B | 112 | 0.037495 | 163.0673 | P22:345:EES:MUSKOGE7!:::EHV: | TDF Impact | Rebuild 3-winding transformer 516092 OKTAHA 5 161 516093 OKTAHA 2 69 516095 OKTAHA71 13 7
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-113 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.05196 | 164.1736 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-113 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.05196 | 164.1763 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-113 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.05196 | 167.9939 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-113 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.05196 | 175.0352 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-117 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | B | 829 | 0.060342 | 103.7671 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | TDF Impact | Rebuild line 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-117 | TO->FROM | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | A | 827 | 0.04852 | 107.8643 | System Intact | TDF Impact | Rebuild line 532791 BENTON 7 345 532794 ROSEHIL7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-117 | TO->FROM | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | A | 827 | 0.051157 | 113.506 | System Intact | TDF Impact | Rebuild line 532791 BENTON 7 345 532794 ROSEHIL7 345 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-117 | TO->FROM | 532937 NEOSHO 5 161 3WXFMR 536:NEOSHO TX-5 138 1 | B | 165 | 0.030993 | 125.6326 | Single 532937 NEOSHO5 161 532939 N34545 161 1 | TDF Impact | Add 3-winding transformer 532937 NEOSHO 5 161 532959 NEOSH5 1 13 533020 NEOSHOS4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-117 | TO->FROM | 532937 NEOSHO 5 161 3WXFMR 536:NEOSHO TX-5 138 1 | B | 165 | 0.030993 | 125.6401 | Single 532793 NEOSHO7 345 532939 N34545 161 532825 'N345 2 1 ' 13 2 | TDF Impact | Add 3-winding transformer 532937 NEOSHO 5 161 532959 NEOSH5 1 13 533020 NEOSHOS4 138 M2
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-117 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.073834 | 137.9906 | System Intact | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-117 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.068666 | 138.1985 | System Intact | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-117 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.076237 | 155.4006 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-117 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.19321 | 155.7991 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-117 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.18923 | 155.8883 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-117 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.069906 | 158.3302 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-117 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.074655 | 159.2546 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-117 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.06846 | 159.5575 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-117 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.07674 | 160.5677 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-117 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.074122 | 161.638 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-117 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.072144 | 161.7992 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-117 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.070851 | 161.8408 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-117 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.067871 | 162.2698 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-117 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.066428 | 163.3422 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-117 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.074122 | 164.1736 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-117 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.074122 | 164.1763 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-117 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.067871 | 164.8475 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-117 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.067871 | 164.8482 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-117 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.074122 | 167.9939 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-117 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.067871 | 169.069 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-117 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.074122 | 175.0352 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-117 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.067871 | 177.0235 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-118 | TO->FROM | 509770 LLAN WT4 138 509804 E 11TH ST 4 138 1 | B | 211 | 0.50237 | 103.0073 | Single 509790 CATOOSA4 138 509804 E11THST4 138 1 | TDF Impact | Rebuild line 509770 LLAN WT4 138 509804 E 11TH ST 4 138 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | TO->FROM | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | A | 1806 | 0.035989 | 104.7927 | System Intact | TDF Impact | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-118 | TO->FROM | 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1 | A | 293 | 0.59889 | 106.5586 | System Intact | TDF Impact | Rebuild line 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1011 | 0.075087 | 106.9293 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1011 | 0.069135 | 107.7039 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | TO->FROM | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | A | 827 | 0.045893 | 107.8643 | System Intact | TDF Impact | Rebuild line 532791 BENTON 7 345 532794 ROSEHIL7 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-118 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1187 | 0.10023 | 112.2151 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-118 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.11545 | 112.5233 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | TO->FROM | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | A | 827 | 0.048164 | 113.506 | System Intact | TDF Impact | Rebuild line 532791 BENTON 7 345 532794 ROSEHIL7 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-118 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.10627 | 113.7225 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-118 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.11341 | 114.0272 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-118 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.10128 | 114.0895 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | TO->FROM | 512638 CATSAGR5 161 3WXFMR 523:CATAUTO1 138 1 | B | 188 | 0.17417 | 114.3095 | P13:138-161:GRDA:CATAUTO2:::HV: | Cumulative Impact | Add 3-winding transformer 512623 CATSAGD4 138 512638 CATSAGR5 161 512833 CATTER1 1 13 M2
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | TO->FROM | 512638 CATSAGR5 161 3WXFMR 523:CATAUTO1 138 1 | B | 188 | 0.17417 | 114.3095 | Single 509790 CATOOSA4 138 512636 CATSAGR4 138 Z1 | Cumulative Impact | Add 3-winding transformer 512623 CATSAGD4 138 512638 CATSAGR5 161 512833 CATTER1 1 13 M2
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | TO->FROM | 512638 CATSAGR5 161 3WXFMR 523:CATAUTO2 138 2 | B | 188 | 0.17469 | 114.6349 | P13:138-161:GRDA:CATAUTO1:::HV: | Cumulative Impact | Add 3-winding transformer 512636 CATSAGR4 138 512638 CATSAGR5 161 512834 CATTER2 1 13 M2
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | TO->FROM | 512638 CATSAGR5 161 3WXFMR 523:CATAUTO2 138 2 | B | 188 | 0.17469 | 114.6349 | Single 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | Cumulative Impact | Add 3-winding transformer 512636 CATSAGR4 138 512638 CATSAGR5 161 512834 CATTER2 1 13 M2
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-118 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.10562 | 115.4477 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-118 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.10128 | 115.647 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | TO->FROM | 509792 DAWSON-4 138 509803 DAWSONT4 138 1 | B | 187 | 0.50238 | 116.7873 | Single 509790 CATOOSA4 138 509804 E11THST4 138 1 | TDF Impact | Rebuild line 509792 DAWSON-4 138 509803 DAWSONT4 138 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-118 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.10562 | 117.1553 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-118 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.10562 | 117.1572 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | TO->FROM | 509792 DAWSON-4 138 509803 DAWSONT4 138 1 | B | 187 | 0.49617 | 119.0915 | Single 509790 CATOOSA4 138 509804 E11THST4 138 1 | TDF Impact | Rebuild line 509792 DAWSON-4 138 509803 DAWSONT4 138 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-118 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.10562 | 119.7129 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-118 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.10562 | 124.3274 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-118 | TO->FROM | 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1 | B | 293 | 0.55153 | 125.8627 | Single 509760 MINGO-N4 138 509828 21STTAP4 138 1 | TDF Impact | Rebuild line 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-118 | TO->FROM | 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1 | B | 293 | 0.60214 | 125.8842 | P12:345:AEPW:ONETA--7:N.E.S.-7::: | TDF Impact | Rebuild line 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-118 | TO->FROM | 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1 | B | 293 | 0.60335 | 127.2165 | Single 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | TDF Impact | Rebuild line 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-118 | TO->FROM | 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1 | B | 293 | 0.60336 | 127.236 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | TDF Impact | Rebuild line 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-118 | TO->FROM | 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1 | B | 293 | 0.59921 | 127.735 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Rebuild line 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | TO->FROM | 512638 CATSAGR5 161 3WXFMR 523:CATAUTO2 138 2 | B | 188 | 0.16779 | 127.7708 | Single 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | Cumulative Impact | Add 3-winding transformer 512636 CATSAGR4 138 512638 CATSAGR5 161 512834 CATTER2 1 13 M2
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-118 | TO->FROM | 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1 | B | 293 | 0.60645 | 127.9513 | P22:345:EES:CLARKSV7!:::EHV: | TDF Impact | Rebuild line 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-118 | TO->FROM | 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1 | B | 293 | 0.55153 | 129.9561 | Single 509811 T.S.E.-4 138 509828 21STTAP4 138 1 | TDF Impact | Rebuild line 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-118 | TO->FROM | 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1 | B | 293 | 0.59921 | 130.3419 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Rebuild line 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | TO->FROM | 509770 LLAN WT4 138 509804 E 11TH ST 4 138 1 | B | 187 | 0.50238 | 133.1826 | Single 509790 CATOOSA4 138 509804 E11THST4 138 1 | TDF Impact | Rebuild line 509770 LLAN WT4 138 509804 E 11TH ST 4 138 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-118 | TO->FROM | 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1 | B | 293 | 0.59891 | 134.3622 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB:::: | TDF Impact | Rebuild line 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-118 | TO->FROM | 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1 | B | 293 | 0.59891 | 134.4196 | P12:345:EES:CHAMSPR7!:CLARKSV7!:1:EHV: | TDF Impact | Rebuild line 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | TO->FROM | 509770 LLAN WT4 138 509804 E 11TH ST 4 138 1 | B | 187 | 0.49617 | 135.7637 | Single 509790 CATOOSA4 138 509804 E11THST4 138 1 | TDF Impact | Rebuild line 509770 LLAN WT4 138 509804 E 11TH ST 4 138 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | TO->FROM | 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1 | A | 235 | 0.59505 | 137.3006 | System Intact | TDF Impact | Rebuild line 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.078865 | 137.9906 | System Intact | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.074405 | 138.1985 | System Intact | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | TO->FROM | 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1 | A | 235 | 0.59931 | 138.2768 | System Intact | TDF Impact | Rebuild line 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-118 | TO->FROM | 512638 CATSAGR5 161 3WXFMR 523:CATAUTO2 138 2 | B | 188 | 0.16643 | 143.3437 | Single 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | Cumulative Impact | Add 3-winding transformer 512636 CATSAGR4 138 512638 CATSAGR5 161 512834 CATTER2 1 13 M2
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.080167 | 155.4006 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.09002 | 155.7991 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.086024 | 155.8883 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.074726 | 158.3302 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | TO->FROM | 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1 | B | 235 | 0.71934 | 159.2158 | P12:138:AEPW:E 11TH ST 4:DAWSON-4::: | TDF Impact | Rebuild line 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.084708 | 159.2546 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.079403 | 159.5575 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | TO->FROM | 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1 | B | 235 | 0.72706 | 159.9672 | Single 509770 LLANWT4 138 509804 E11THST4 138 1 | TDF Impact | Rebuild line 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.095081 | 160.5677 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | TO->FROM | 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1 | B | 235 | 0.54338 | 160.8369 | Single 509760 MINGO-N4 138 509779 MAYO--N4 138 1 | TDF Impact | Rebuild line 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | TO->FROM | 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1 | B | 235 | 0.71934 | 161.0552 | Single 509770 LLANWT4 138 509804 E11THST4 138 1 | TDF Impact | Rebuild line 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | TO->FROM | 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1 | B | 235 | 0.60156 | 161.6241 | P23:345:AEPW:ONETA CB 3429B NBTB:::: | TDF Impact | Rebuild line 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | TO->FROM | 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1 | B | 235 | 0.60156 | 161.6264 | P12:345:AEPW:ONETA--7:N.E.S.-7::: | TDF Impact | Rebuild line 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | TO->FROM | 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1 | B | 235 | 0.59852 | 161.6333 | Single 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | TDF Impact | Rebuild line 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.084175 | 161.638 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.091685 | 161.7992 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.089969 | 161.8408 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | TO->FROM | 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1 | B | 235 | 0.55179 | 162.0446 | Single 509760 MINGO-N4 138 509779 MAYO--N4 138 1 | TDF Impact | Rebuild line 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.078814 | 162.2698 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.086693 | 163.3422 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | TO->FROM | 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1 | B | 235 | 0.54338 | 163.471 | Single 509760 MINGO-N4 138 509828 21STTAP4 138 1 | TDF Impact | Rebuild line 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | TO->FROM | 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1 | B | 235 | 0.59518 | 163.9081 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Rebuild line 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.084175 | 164.1736 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.084175 | 164.1763 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | TO->FROM | 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1 | B | 235 | 0.55179 | 164.5713 | Single 509760 MINGO-N4 138 509828 21STTAP4 138 1 | TDF Impact | Rebuild line 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.078814 | 164.8475 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.078814 | 164.8482 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | TO->FROM | 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1 | B | 235 | 0.59988 | 164.9055 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | TDF Impact | Rebuild line 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.084175 | 167.9939 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | TO->FROM | 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1 | B | 235 | 0.59988 | 168.7389 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Rebuild line 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.078814 | 169.069 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | TO->FROM | 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1 | B | 235 | 0.59518 | 170.8155 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Rebuild line 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | TO->FROM | 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1 | B | 235 | 0.54338 | 171.852 | Single 509811 T.S.E.-4 138 509828 21STTAP4 138 1 | TDF Impact | Rebuild line 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | TO->FROM | 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1 | B | 235 | 0.55179 | 172.5853 | Single 509811 T.S.E.-4 138 509828 21STTAP4 138 1 | TDF Impact | Rebuild line 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | TO->FROM | 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1 | B | 235 | 0.5953 | 174.4263 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB:::: | TDF Impact | Rebuild line 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | TO->FROM | 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1 | B | 235 | 0.5953 | 174.4925 | P12:345:EES:CHAMSPR7!:CLARKSV7!:1:EHV: | TDF Impact | Rebuild line 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.084175 | 175.0352 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | TO->FROM | 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1 | B | 235 | 0.59954 | 175.8532 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB:::: | TDF Impact | Rebuild line 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-118 | TO->FROM | 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1 | B | 235 | 0.59954 | 175.9265 | P12:345:EES:CHAMSPR7!:CLARKSV7!:1:EHV: | TDF Impact | Rebuild line 509790 CATOOSA4 138 509804 E 11TH ST 4 138 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-118 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.078814 | 177.0235 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-120 | TO->FROM | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 | B | 1015 | 0.07577 | 102.04 | P42:345:OKGE:SB_DGSE7313:::EHV: | Cumulative Impact | Rebuild line 514715 WOODRNG7 345 515875 REDNGTN7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-120 | TO->FROM | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 | B | 1015 | 0.089785 | 102.2256 | P42:345:OKGE:SB_DGSE7313:::EHV: | Cumulative Impact | Rebuild line 514715 WOODRNG7 345 515875 REDNGTN7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-120 | TO->FROM | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | A | 1806 | 0.043694 | 104.7272 | System Intact | TDF Impact | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-120 | TO->FROM | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | A | 1806 | 0.04927 | 104.7927 | System Intact | TDF Impact | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-120 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1011 | 0.040981 | 106.9293 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-120 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1011 | 0.038922 | 107.7039 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-120 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1187 | 0.048288 | 112.2151 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-120 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.053244 | 112.5233 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-120 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.057392 | 113.7225 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-120 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.052764 | 114.0272 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-120 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.052849 | 114.0895 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-120 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.062041 | 114.4362 | System Intact | TDF Impact | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-120 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.055135 | 114.6025 | System Intact | TDF Impact | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-120 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.056734 | 115.4477 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-120 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.052849 | 115.647 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-120 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.056734 | 117.1553 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-120 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.056734 | 117.1572 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-120 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.056734 | 119.7129 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-120 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.056734 | 124.3274 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-120 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.040064 | 137.9906 | System Intact | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-120 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.038013 | 138.1985 | System Intact | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-122 | TO->FROM | 508806 LIEBERM4 138 780630 G24-122-TAP 138 1 | A | 163 | 0.67739 | 107.0382 | System Intact | TDF Impact | Rebuild line 508806 LIEBERM4 138 780630 G24-122-TAP 138 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-122 | TO->FROM | 508806 LIEBERM4 138 780630 G24-122-TAP 138 1 | B | 183 | 0.67355 | 110.2948 | P23:345:AEPW:DIANA CB 12000 NBTB:::: | TDF Impact | Rebuild line 508806 LIEBERM4 138 780630 G24-122-TAP 138 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-122 | TO->FROM | 508806 LIEBERM4 138 780630 G24-122-TAP 138 1 | B | 183 | 0.67382 | 110.4795 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | TDF Impact | Rebuild line 508806 LIEBERM4 138 780630 G24-122-TAP 138 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-122 | TO->FROM | 508806 LIEBERM4 138 780630 G24-122-TAP 138 1 | B | 183 | 0.67964 | 111.1223 | Single 334197 7ROCKYCRK% 345 783930 G24-232-TAP 345 1 | TDF Impact | Rebuild line 508806 LIEBERM4 138 780630 G24-122-TAP 138 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-122 | TO->FROM | 508806 LIEBERM4 138 780630 G24-122-TAP 138 1 | B | 183 | 0.67964 | 111.1451 | P23:345:EES::7ROCKYCRK%:1:EHV: | TDF Impact | Rebuild line 508806 LIEBERM4 138 780630 G24-122-TAP 138 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-122 | TO->FROM | 508806 LIEBERM4 138 780630 G24-122-TAP 138 1 | B | 183 | 0.6729 | 112.3147 | P12:345:AEPW:SWSHV7:DIANA7::: | TDF Impact | Rebuild line 508806 LIEBERM4 138 780630 G24-122-TAP 138 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-122 | TO->FROM | 508806 LIEBERM4 138 780630 G24-122-TAP 138 1 | B | 162 | 0.67246 | 113.6652 | P23:345:AEPW:DIANA CB 12000 NBTB:::: | TDF Impact | Rebuild line 508806 LIEBERM4 138 780630 G24-122-TAP 138 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-122 | TO->FROM | 508806 LIEBERM4 138 780630 G24-122-TAP 138 1 | B | 162 | 0.67267 | 113.9454 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | TDF Impact | Rebuild line 508806 LIEBERM4 138 780630 G24-122-TAP 138 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-122 | TO->FROM | 508806 LIEBERM4 138 780630 G24-122-TAP 138 1 | B | 162 | 0.67182 | 115.7374 | P12:345:AEPW:SWSHV7:DIANA7::: | TDF Impact | Rebuild line 508806 LIEBERM4 138 780630 G24-122-TAP 138 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-122 | TO->FROM | 508806 LIEBERM4 138 780630 G24-122-TAP 138 1 | B | 162 | 0.67856 | 116.1765 | Single 334197 7ROCKYCRK% 345 783930 G24-232-TAP 345 1 | TDF Impact | Rebuild line 508806 LIEBERM4 138 780630 G24-122-TAP 138 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-122 | TO->FROM | 508806 LIEBERM4 138 780630 G24-122-TAP 138 1 | B | 162 | 0.67856 | 116.2093 | P23:345:EES::7ROCKYCRK%:1:EHV: | TDF Impact | Rebuild line 508806 LIEBERM4 138 780630 G24-122-TAP 138 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-122 | TO->FROM | 508806 LIEBERM4 138 780630 G24-122-TAP 138 1 | A | 137 | 0.67632 | 116.5092 | System Intact | TDF Impact | Rebuild line 508806 LIEBERM4 138 780630 G24-122-TAP 138 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-122 | TO->FROM | 508806 LIEBERM4 138 780630 G24-122-TAP 138 1 | B | 183 | 0.6717 | 121.8759 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | TDF Impact | Rebuild line 508806 LIEBERM4 138 780630 G24-122-TAP 138 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-122 | TO->FROM | 508806 LIEBERM4 138 780630 G24-122-TAP 138 1 | B | 162 | 0.67059 | 127.1399 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | TDF Impact | Rebuild line 508806 LIEBERM4 138 780630 G24-122-TAP 138 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-122 | TO->FROM | 508806 LIEBERM4 138 780630 G24-122-TAP 138 1 | B | 162 | 0.67214 | 130.1816 | P23:345:AEPW:DIANA CB 12000 NBTB:::: | TDF Impact | Rebuild line 508806 LIEBERM4 138 780630 G24-122-TAP 138 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-122 | TO->FROM | 508806 LIEBERM4 138 780630 G24-122-TAP 138 1 | B | 162 | 0.67229 | 131.5232 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | TDF Impact | Rebuild line 508806 LIEBERM4 138 780630 G24-122-TAP 138 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-122 | TO->FROM | 508806 LIEBERM4 138 780630 G24-122-TAP 138 1 | B | 162 | 0.67154 | 131.6128 | P12:345:AEPW:SWSHV7:DIANA7::: | TDF Impact | Rebuild line 508806 LIEBERM4 138 780630 G24-122-TAP 138 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-122 | TO->FROM | 508806 LIEBERM4 138 780630 G24-122-TAP 138 1 | A | 137 | 0.67606 | 132.6884 | System Intact | TDF Impact | Rebuild line 508806 LIEBERM4 138 780630 G24-122-TAP 138 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-122 | TO->FROM | 508806 LIEBERM4 138 780630 G24-122-TAP 138 1 | B | 162 | 0.67818 | 132.9902 | Single 334197 7ROCKYCRK% 345 783930 G24-232-TAP 345 1 | TDF Impact | Rebuild line 508806 LIEBERM4 138 780630 G24-122-TAP 138 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-122 | TO->FROM | 508806 LIEBERM4 138 780630 G24-122-TAP 138 1 | B | 162 | 0.67818 | 133.0226 | P23:345:EES::7ROCKYCRK%:1:EHV: | TDF Impact | Rebuild line 508806 LIEBERM4 138 780630 G24-122-TAP 138 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-122 | TO->FROM | 508806 LIEBERM4 138 780630 G24-122-TAP 138 1 | B | 183 | 0.68042 | 137.6957 | P42:345:AEPW:WILKES CB 1W10 NBTB+FAULT:::: | TDF Impact | Rebuild line 508806 LIEBERM4 138 780630 G24-122-TAP 138 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-122 | TO->FROM | 508806 LIEBERM4 138 780630 G24-122-TAP 138 1 | B | 183 | 0.66949 | 137.9155 | 267135_a | TDF Impact | Rebuild line 508806 LIEBERM4 138 780630 G24-122-TAP 138 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-122 | TO->FROM | 508806 LIEBERM4 138 780630 G24-122-TAP 138 1 | B | 183 | 0.66949 | 138.4317 | P12:345:AEPW:LONGWD7:WILKES7::: | TDF Impact | Rebuild line 508806 LIEBERM4 138 780630 G24-122-TAP 138 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-122 | TO->FROM | 508806 LIEBERM4 138 780630 G24-122-TAP 138 1 | B | 162 | 0.66817 | 139.3283 | 267135_a | TDF Impact | Rebuild line 508806 LIEBERM4 138 780630 G24-122-TAP 138 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-122 | TO->FROM | 508806 LIEBERM4 138 780630 G24-122-TAP 138 1 | B | 183 | 0.66771 | 141.0502 | P23:345:AEPW:LONGWOOD CB 1N60 NBTB:::: | TDF Impact | Rebuild line 508806 LIEBERM4 138 780630 G24-122-TAP 138 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-122 | TO->FROM | 508806 LIEBERM4 138 780630 G24-122-TAP 138 1 | B | 162 | 0.67966 | 141.1802 | P42:345:AEPW:WILKES CB 1W10 NBTB+FAULT:::: | TDF Impact | Rebuild line 508806 LIEBERM4 138 780630 G24-122-TAP 138 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-122 | TO->FROM | 508806 LIEBERM4 138 780630 G24-122-TAP 138 1 | B | 162 | 0.66817 | 141.6922 | P12:345:AEPW:LONGWD7:WILKES7::: | TDF Impact | Rebuild line 508806 LIEBERM4 138 780630 G24-122-TAP 138 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-122 | TO->FROM | 508806 LIEBERM4 138 780630 G24-122-TAP 138 1 | B | 162 | 0.66633 | 142.1541 | P23:345:AEPW:LONGWOOD CB 1N60 NBTB:::: | TDF Impact | Rebuild line 508806 LIEBERM4 138 780630 G24-122-TAP 138 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-122 | TO->FROM | 508806 LIEBERM4 138 780630 G24-122-TAP 138 1 | B | 162 | 0.67033 | 143.047 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | TDF Impact | Rebuild line 508806 LIEBERM4 138 780630 G24-122-TAP 138 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-122 | TO->FROM | 508806 LIEBERM4 138 780630 G24-122-TAP 138 1 | B | 162 | 0.6681 | 155.5457 | 267135_a | TDF Impact | Rebuild line 508806 LIEBERM4 138 780630 G24-122-TAP 138 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-122 | TO->FROM | 508806 LIEBERM4 138 780630 G24-122-TAP 138 1 | B | 162 | 0.6681 | 157.8493 | P12:345:AEPW:LONGWD7:WILKES7::: | TDF Impact | Rebuild line 508806 LIEBERM4 138 780630 G24-122-TAP 138 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-122 | TO->FROM | 508806 LIEBERM4 138 780630 G24-122-TAP 138 1 | B | 162 | 0.66628 | 159.6829 | P23:345:AEPW:LONGWOOD CB 1N60 NBTB:::: | TDF Impact | Rebuild line 508806 LIEBERM4 138 780630 G24-122-TAP 138 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-122 | TO->FROM | 508806 LIEBERM4 138 780630 G24-122-TAP 138 1 | B | 162 | 0.67947 | 160.6045 | P42:345:AEPW:WILKES CB 1W10 NBTB+FAULT:::: | TDF Impact | Rebuild line 508806 LIEBERM4 138 780630 G24-122-TAP 138 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-125 | TO->FROM | 532939 N345 4 5 161 3WXFMR 536:N345 TX-2 161 2 | B | 550 | 0.063411 | 100.4793 | Single 533021 NEOSHO4 138 533023 N34534 138 1 | TDF Impact | Add 3-winding transformer 532793 NEOSHO 7 345 532825 N345 2 1 13 532939 N345 4 5 161 M2
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-125 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.15495 | 101.6955 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-125 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.15495 | 101.6955 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-125 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.15495 | 101.6955 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-125 | TO->FROM | 532939 N345 4 5 161 3WXFMR 536:N345 TX-2 161 2 | B | 550 | 0.06975 | 103.5308 | Single 533021 NEOSHO4 138 533023 N34534 138 1 | TDF Impact | Add 3-winding transformer 532793 NEOSHO 7 345 532825 N345 2 1 13 532939 N345 4 5 161 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-125 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | B | 829 | 0.10627 | 103.7671 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | TDF Impact | Rebuild line 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1
Thermal | 03ALL | 1 | 26SP | T1 | GEN-2024-125 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.15728 | 105.0133 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 29WP | T1 | GEN-2024-125 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.17058 | 106.2154 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-125 | TO->FROM | 532937 NEOSHO 5 161 532939 N345 4 5 161 1 | B | 557 | 0.070113 | 106.5051 | Single 533021 NEOSHO4 138 533023 N34534 138 1 | TDF Impact | Rebuild line 532937 NEOSHO 5 161 532939 N345 4 5 161 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-125 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.17309 | 106.5956 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-125 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.17309 | 106.5956 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-125 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.17309 | 106.5956 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-125 | TO->FROM | 532777 NRSS7 345 780840 G24-129-TAP 345 1 | B | 1159 | 1 | 110.7526 | P12:345:WERE:CANR-LATH-345:EHV: | TDF Impact | Rebuild line 532777 NRSS7 345 780840 G24-129-TAP 345 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-125 | TO->FROM | 532777 NRSS7 345 780840 G24-129-TAP 345 1 | B | 1159 | 1 | 110.759 | P23:345:WERE:LATH-BKRS:EHV: | TDF Impact | Rebuild line 532777 NRSS7 345 780840 G24-129-TAP 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-125 | TO->FROM | 532777 NRSS7 345 780840 G24-129-TAP 345 1 | B | 1159 | 1 | 110.8179 | P12:345:WERE:CANR-LATH-345:EHV: | TDF Impact | Rebuild line 532777 NRSS7 345 780840 G24-129-TAP 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-125 | TO->FROM | 532777 NRSS7 345 780840 G24-129-TAP 345 1 | B | 1159 | 1 | 110.8235 | P23:345:WERE:LATH-BKRS:EHV: | TDF Impact | Rebuild line 532777 NRSS7 345 780840 G24-129-TAP 345 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-125 | TO->FROM | 532777 NRSS7 345 780840 G24-129-TAP 345 1 | B | 1159 | 1 | 110.941 | Single 532780 CANEYRV7 345 780720 G24-125-TAP 345 1 | TDF Impact | Rebuild line 532777 NRSS7 345 780840 G24-129-TAP 345 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-125 | TO->FROM | 532777 NRSS7 345 780840 G24-129-TAP 345 1 | B | 1159 | 1 | 110.9432 | P23:345:WERE:CANR-BKRS:EHV: | TDF Impact | Rebuild line 532777 NRSS7 345 780840 G24-129-TAP 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-125 | TO->FROM | 532777 NRSS7 345 780840 G24-129-TAP 345 1 | B | 1159 | 1 | 110.9831 | Single 532780 CANEYRV7 345 780720 G24-125-TAP 345 1 | TDF Impact | Rebuild line 532777 NRSS7 345 780840 G24-129-TAP 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-125 | TO->FROM | 532777 NRSS7 345 780840 G24-129-TAP 345 1 | B | 1159 | 1 | 110.9857 | P23:345:WERE:CANR-BKRS:EHV: | TDF Impact | Rebuild line 532777 NRSS7 345 780840 G24-129-TAP 345 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-125 | TO->FROM | 532939 N345 4 5 161 3WXFMR 536:N345 TX-2 161 2 | B | 550 | 0.070113 | 111.179 | Single 533021 NEOSHO4 138 533023 N34534 138 1 | TDF Impact | Add 3-winding transformer 532793 NEOSHO 7 345 532825 N345 2 1 13 532939 N345 4 5 161 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-125 | TO->FROM | 532777 NRSS7 345 780840 G24-129-TAP 345 1 | B | 1159 | 0.99864 | 111.3269 | P12:345:WERE:LATH-ROSE-345:EHV: | TDF Impact | Rebuild line 532777 NRSS7 345 780840 G24-129-TAP 345 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-125 | TO->FROM | 532777 NRSS7 345 780840 G24-129-TAP 345 1 | B | 1159 | 1 | 111.4446 | Single 532780 CANEYRV7 345 780720 G24-125-TAP 345 1 | TDF Impact | Rebuild line 532777 NRSS7 345 780840 G24-129-TAP 345 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-125 | TO->FROM | 532777 NRSS7 345 780840 G24-129-TAP 345 1 | B | 1159 | 1 | 111.4535 | P23:345:WERE:CANR-BKRS:EHV: | TDF Impact | Rebuild line 532777 NRSS7 345 780840 G24-129-TAP 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-125 | TO->FROM | 532777 NRSS7 345 780840 G24-129-TAP 345 1 | B | 1159 | 0.99854 | 111.4772 | P12:345:WERE:LATH-ROSE-345:EHV: | TDF Impact | Rebuild line 532777 NRSS7 345 780840 G24-129-TAP 345 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-125 | TO->FROM | 532777 NRSS7 345 780840 G24-129-TAP 345 1 | B | 1159 | 1 | 113.2779 | P12:345:WERE:CANR-LATH-345:EHV: | TDF Impact | Rebuild line 532777 NRSS7 345 780840 G24-129-TAP 345 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-125 | TO->FROM | 532777 NRSS7 345 780840 G24-129-TAP 345 1 | B | 1159 | 1 | 113.2864 | P23:345:WERE:LATH-BKRS:EHV: | TDF Impact | Rebuild line 532777 NRSS7 345 780840 G24-129-TAP 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-125 | TO->FROM | 532780 CANEYRV7 345 780720 G24-125-TAP 345 1 | B | 1159 | 1 | 113.6032 | Single 532777 NRSS7 345 780840 G24-129-TAP 345 1 | TDF Impact | Rebuild line 532780 CANEYRV7 345 780720 G24-125-TAP 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-125 | TO->FROM | 532780 CANEYRV7 345 780720 G24-125-TAP 345 1 | B | 1159 | 1 | 113.622 | P52:345:WERE:NRSS7:EHV: | TDF Impact | Rebuild line 532780 CANEYRV7 345 780720 G24-125-TAP 345 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-125 | TO->FROM | 532780 CANEYRV7 345 780720 G24-125-TAP 345 1 | B | 1159 | 1 | 114.0092 | Single 532777 NRSS7 345 780840 G24-129-TAP 345 1 | TDF Impact | Rebuild line 532780 CANEYRV7 345 780720 G24-125-TAP 345 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-125 | TO->FROM | 532780 CANEYRV7 345 780720 G24-125-TAP 345 1 | B | 1159 | 1 | 114.029 | P52:345:WERE:NRSS7:EHV: | TDF Impact | Rebuild line 532780 CANEYRV7 345 780720 G24-125-TAP 345 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-125 | TO->FROM | 532780 CANEYRV7 345 780720 G24-125-TAP 345 1 | B | 1159 | 1 | 114.3072 | Single 532777 NRSS7 345 780840 G24-129-TAP 345 1 | TDF Impact | Rebuild line 532780 CANEYRV7 345 780720 G24-125-TAP 345 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-125 | TO->FROM | 532780 CANEYRV7 345 780720 G24-125-TAP 345 1 | B | 1159 | 1 | 114.3281 | P52:345:WERE:NRSS7:EHV: | TDF Impact | Rebuild line 532780 CANEYRV7 345 780720 G24-125-TAP 345 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-125 | TO->FROM | 532777 NRSS7 345 780840 G24-129-TAP 345 1 | B | 1159 | 0.99718 | 114.3329 | P12:345:WERE:LATH-ROSE-345:EHV: | TDF Impact | Rebuild line 532777 NRSS7 345 780840 G24-129-TAP 345 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-125 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.15494 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-125 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.15494 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-125 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.15494 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-125 | TO->FROM | 532780 CANEYRV7 345 780720 G24-125-TAP 345 1 | B | 1159 | 0.99089 | 118.4516 | P12:345:WERE:NRSS-N345-345:EHV: | TDF Impact | Rebuild line 532780 CANEYRV7 345 780720 G24-125-TAP 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-125 | TO->FROM | 532780 CANEYRV7 345 780720 G24-125-TAP 345 1 | B | 1159 | 0.99089 | 118.4554 | P23:345:WERE:N345-345-20:EHV: | TDF Impact | Rebuild line 532780 CANEYRV7 345 780720 G24-125-TAP 345 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-125 | TO->FROM | 532780 CANEYRV7 345 780720 G24-125-TAP 345 1 | B | 1159 | 0.99044 | 119.3022 | P12:345:WERE:NRSS-N345-345:EHV: | TDF Impact | Rebuild line 532780 CANEYRV7 345 780720 G24-125-TAP 345 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-125 | TO->FROM | 532780 CANEYRV7 345 780720 G24-125-TAP 345 1 | B | 1159 | 0.99044 | 119.3033 | P23:345:WERE:N345-345-20:EHV: | TDF Impact | Rebuild line 532780 CANEYRV7 345 780720 G24-125-TAP 345 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-125 | TO->FROM | 532780 CANEYRV7 345 780720 G24-125-TAP 345 1 | B | 1159 | 0.97949 | 122.9229 | P12:345:WERE:NRSS-N345-345:EHV: | TDF Impact | Rebuild line 532780 CANEYRV7 345 780720 G24-125-TAP 345 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-125 | TO->FROM | 532780 CANEYRV7 345 780720 G24-125-TAP 345 1 | B | 1159 | 0.97949 | 122.9304 | P23:345:WERE:N345-345-20:EHV: | TDF Impact | Rebuild line 532780 CANEYRV7 345 780720 G24-125-TAP 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-128 | TO->FROM | 511467 L.E.S.-4 138 3WXFMR 520:LES 5 345 2 | B | 515 | 0.19605 | 101.3128 | P42:345:OKGE:SB_GRNT7313:::EHV: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-128 | TO->FROM | 511468 L.E.S.-7 345 764550 G20-087-TAP 345 1 | B | 1324 | 1 | 102.0233 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Rebuild line 511468 L.E.S.-7 345 764550 G20-087-TAP 345 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-128 | TO->FROM | 511468 L.E.S.-7 345 764550 G20-087-TAP 345 1 | B | 1324 | 1 | 102.0233 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | TDF Impact | Rebuild line 511468 L.E.S.-7 345 764550 G20-087-TAP 345 1
Thermal | 00NR | 1 | 29SP | T1 | GEN-2024-128 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | B | 211 | 0.070093 | 104.1932 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Rebuild line 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1
Thermal | 00NR | 1 | 29SP | T1 | GEN-2024-128 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | B | 211 | 0.070572 | 104.436 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | TDF Impact | Rebuild line 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-128 | TO->FROM | 515802 GRACMNT4 138 3WXFMR 524:524:GRACMNT3 345 3 | B | 478 | 0.36629 | 105.3618 | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | Add 3-winding transformer 515800 GRACMNT7 345 515801 GRCMNT11 13 515802 GRACMNT4 138 M2
Thermal | 00NR | 1 | 26SP | T1 | GEN-2024-128 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | B | 211 | 0.07028 | 105.7881 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Rebuild line 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1
Thermal | 00NR | 1 | 26SP | T1 | GEN-2024-128 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | B | 211 | 0.070763 | 106.2632 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | TDF Impact | Rebuild line 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-128 | TO->FROM | 515802 GRACMNT4 138 3WXFMR 524:524:GRACMNT3 345 3 | B | 478 | 0.36401 | 111.6521 | P42:345:OKGE:SB_GRNT7381:::EHV: | TDF Impact | Add 3-winding transformer 515800 GRACMNT7 345 515801 GRCMNT11 13 515802 GRACMNT4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-128 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | B | 171 | 0.061956 | 111.797 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Rebuild line 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-128 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | B | 171 | 0.062292 | 111.9445 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | TDF Impact | Rebuild line 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-128 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | B | 171 | 0.062115 | 113.6342 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Rebuild line 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-128 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | B | 171 | 0.06245 | 113.9786 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | TDF Impact | Rebuild line 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-128 | TO->FROM | 511467 L.E.S.-4 138 3WXFMR 520:LES 5 345 2 | B | 515 | 0.20582 | 114.4267 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-128 | TO->FROM | 511467 L.E.S.-4 138 3WXFMR 520:LES 5 345 2 | B | 515 | 0.20715 | 114.7092 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-128 | TO->FROM | 511468 L.E.S.-7 345 764550 G20-087-TAP 345 1 | B | 1176 | 1 | 114.9842 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Rebuild line 511468 L.E.S.-7 345 764550 G20-087-TAP 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-128 | TO->FROM | 511468 L.E.S.-7 345 764550 G20-087-TAP 345 1 | B | 1176 | 1 | 114.9872 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | TDF Impact | Rebuild line 511468 L.E.S.-7 345 764550 G20-087-TAP 345 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-128 | TO->FROM | 511468 L.E.S.-7 345 764550 G20-087-TAP 345 1 | B | 1176 | 1 | 115.0779 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Rebuild line 511468 L.E.S.-7 345 764550 G20-087-TAP 345 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-128 | TO->FROM | 511468 L.E.S.-7 345 764550 G20-087-TAP 345 1 | B | 1176 | 1 | 115.0941 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | TDF Impact | Rebuild line 511468 L.E.S.-7 345 764550 G20-087-TAP 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-128 | TO->FROM | 511467 L.E.S.-4 138 3WXFMR 520:LES 5 345 2 | B | 515 | 0.21237 | 115.4941 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | TDF Impact | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-128 | TO->FROM | 511467 L.E.S.-4 138 3WXFMR 520:LES 5 345 2 | B | 515 | 0.21381 | 117.1585 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | TDF Impact | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-128 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | B | 106 | 0.046806 | 124.9388 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Line - Duncan - Duncan Tap - Duncan Eastside - Rush Springs Tap - Marlow 138 kV Rebuild.idv : 2025 ITP, PID: 900298, NTC, ISD: Unknown
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-128 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | B | 106 | 0.047152 | 125.1801 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | TDF Impact | Line - Duncan - Duncan Tap - Duncan Eastside - Rush Springs Tap - Marlow 138 kV Rebuild.idv : 2025 ITP, PID: 900298, NTC, ISD: Unknown
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-128 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | B | 106 | 0.046897 | 126.104 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Line - Duncan - Duncan Tap - Duncan Eastside - Rush Springs Tap - Marlow 138 kV Rebuild.idv : 2025 ITP, PID: 900298, NTC, ISD: Unknown
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-128 | TO->FROM | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | B | 106 | 0.047245 | 126.6716 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | TDF Impact | Line - Duncan - Duncan Tap - Duncan Eastside - Rush Springs Tap - Marlow 138 kV Rebuild.idv : 2025 ITP, PID: 900298, NTC, ISD: Unknown
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-129 | TO->FROM | 532939 N345 4 5 161 3WXFMR 536:N345 TX-2 161 2 | B | 550 | 0.092767 | 100.4793 | Single 533021 NEOSHO4 138 533023 N34534 138 1 | TDF Impact | Add 3-winding transformer 532793 NEOSHO 7 345 532825 N345 2 1 13 532939 N345 4 5 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-129 | TO->FROM | 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 | B | 956 | 0.99778 | 102.5387 | Single 532777 NRSS7 345 780840 G24-129-TAP 345 1 | TDF Impact | Rebuild line 532794 ROSEHIL7 345 532800 LATHAMS7 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-129 | TO->FROM | 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 | B | 956 | 0.99772 | 102.5849 | P52:345:WERE:NRSS7:EHV: | TDF Impact | Rebuild line 532794 ROSEHIL7 345 532800 LATHAMS7 345 1
Thermal | 00NR | 1 | 29SP | T1 | GEN-2024-129 | TO->FROM | 532911 MUSTNG5 161 532937 NEOSHO 5 161 1 | B | 148 | 0.03376 | 102.6985 | P23:345:AECI:7BLACKBERRY:6_2::: | TDF Impact | Rebuild line 532911 MUSTNG5 161 532937 NEOSHO 5 161 1
Thermal | 00NR | 1 | 29SP | T1 | GEN-2024-129 | TO->FROM | 532911 MUSTNG5 161 532937 NEOSHO 5 161 1 | B | 148 | 0.03376 | 102.701 | P23:345:AECI:7BLACKBERRY:6_3::: | TDF Impact | Rebuild line 532911 MUSTNG5 161 532937 NEOSHO 5 161 1
Thermal | 00NR | 1 | 29SP | T1 | GEN-2024-129 | TO->FROM | 532911 MUSTNG5 161 532937 NEOSHO 5 161 1 | B | 148 | 0.033684 | 103.3719 | P23:345:AECI:7BLACKBERRY:656::: | TDF Impact | Rebuild line 532911 MUSTNG5 161 532937 NEOSHO 5 161 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-129 | TO->FROM | 532939 N345 4 5 161 3WXFMR 536:N345 TX-2 161 2 | B | 550 | 0.09931 | 103.5308 | Single 533021 NEOSHO4 138 533023 N34534 138 1 | TDF Impact | Add 3-winding transformer 532793 NEOSHO 7 345 532825 N345 2 1 13 532939 N345 4 5 161 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-129 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | B | 829 | 0.13881 | 103.7671 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | TDF Impact | Rebuild line 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1
Thermal | 00NR | 1 | 29SP | T1 | GEN-2024-129 | TO->FROM | 532911 MUSTNG5 161 532937 NEOSHO 5 161 1 | B | 148 | 0.030521 | 106.4728 | Single 532937 NEOSHO5 161 764310 G20-079-TAP 161 1 | TDF Impact | Rebuild line 532911 MUSTNG5 161 532937 NEOSHO 5 161 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-129 | TO->FROM | 532937 NEOSHO 5 161 532939 N345 4 5 161 1 | B | 557 | 0.099768 | 106.5051 | Single 533021 NEOSHO4 138 533023 N34534 138 1 | TDF Impact | Rebuild line 532937 NEOSHO 5 161 532939 N345 4 5 161 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-129 | TO->FROM | 532777 NRSS7 345 780840 G24-129-TAP 345 1 | B | 1159 | 1 | 110.7526 | P12:345:WERE:CANR-LATH-345:EHV: | TDF Impact | Rebuild line 532777 NRSS7 345 780840 G24-129-TAP 345 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-129 | TO->FROM | 532777 NRSS7 345 780840 G24-129-TAP 345 1 | B | 1159 | 1 | 110.759 | P23:345:WERE:LATH-BKRS:EHV: | TDF Impact | Rebuild line 532777 NRSS7 345 780840 G24-129-TAP 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-129 | TO->FROM | 532777 NRSS7 345 780840 G24-129-TAP 345 1 | B | 1159 | 1 | 110.8179 | P12:345:WERE:CANR-LATH-345:EHV: | TDF Impact | Rebuild line 532777 NRSS7 345 780840 G24-129-TAP 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-129 | TO->FROM | 532777 NRSS7 345 780840 G24-129-TAP 345 1 | B | 1159 | 1 | 110.8235 | P23:345:WERE:LATH-BKRS:EHV: | TDF Impact | Rebuild line 532777 NRSS7 345 780840 G24-129-TAP 345 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-129 | TO->FROM | 532777 NRSS7 345 780840 G24-129-TAP 345 1 | B | 1159 | 1 | 110.941 | Single 532780 CANEYRV7 345 780720 G24-125-TAP 345 1 | TDF Impact | Rebuild line 532777 NRSS7 345 780840 G24-129-TAP 345 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-129 | TO->FROM | 532777 NRSS7 345 780840 G24-129-TAP 345 1 | B | 1159 | 1 | 110.9432 | P23:345:WERE:CANR-BKRS:EHV: | TDF Impact | Rebuild line 532777 NRSS7 345 780840 G24-129-TAP 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-129 | TO->FROM | 532777 NRSS7 345 780840 G24-129-TAP 345 1 | B | 1159 | 1 | 110.9831 | Single 532780 CANEYRV7 345 780720 G24-125-TAP 345 1 | TDF Impact | Rebuild line 532777 NRSS7 345 780840 G24-129-TAP 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-129 | TO->FROM | 532777 NRSS7 345 780840 G24-129-TAP 345 1 | B | 1159 | 1 | 110.9857 | P23:345:WERE:CANR-BKRS:EHV: | TDF Impact | Rebuild line 532777 NRSS7 345 780840 G24-129-TAP 345 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-129 | TO->FROM | 532939 N345 4 5 161 3WXFMR 536:N345 TX-2 161 2 | B | 550 | 0.099768 | 111.179 | Single 533021 NEOSHO4 138 533023 N34534 138 1 | TDF Impact | Add 3-winding transformer 532793 NEOSHO 7 345 532825 N345 2 1 13 532939 N345 4 5 161 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-129 | TO->FROM | 532777 NRSS7 345 780840 G24-129-TAP 345 1 | B | 1159 | 0.99864 | 111.3269 | P12:345:WERE:LATH-ROSE-345:EHV: | TDF Impact | Rebuild line 532777 NRSS7 345 780840 G24-129-TAP 345 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-129 | TO->FROM | 532777 NRSS7 345 780840 G24-129-TAP 345 1 | B | 1159 | 1 | 111.4446 | Single 532780 CANEYRV7 345 780720 G24-125-TAP 345 1 | TDF Impact | Rebuild line 532777 NRSS7 345 780840 G24-129-TAP 345 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-129 | TO->FROM | 532777 NRSS7 345 780840 G24-129-TAP 345 1 | B | 1159 | 1 | 111.4535 | P23:345:WERE:CANR-BKRS:EHV: | TDF Impact | Rebuild line 532777 NRSS7 345 780840 G24-129-TAP 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-129 | TO->FROM | 532777 NRSS7 345 780840 G24-129-TAP 345 1 | B | 1159 | 0.99854 | 111.4772 | P12:345:WERE:LATH-ROSE-345:EHV: | TDF Impact | Rebuild line 532777 NRSS7 345 780840 G24-129-TAP 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-129 | TO->FROM | 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 | B | 956 | 0.97109 | 112.4273 | P12:345:WERE:NRSS-N345-345:EHV: | TDF Impact | Rebuild line 532794 ROSEHIL7 345 532800 LATHAMS7 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-129 | TO->FROM | 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 | B | 956 | 0.97109 | 112.4564 | P23:345:WERE:N345-345-20:EHV: | TDF Impact | Rebuild line 532794 ROSEHIL7 345 532800 LATHAMS7 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-129 | TO->FROM | 533023 N345 3 4 138 3WXFMR 536:N345 TX-1 138 1 | B | 400 | 0.095642 | 112.5071 | Single 532793 NEOSHO7 345 532939 N34545 161 532825 'N345 2 1 ' 13 2 | Cumulative Impact | Add 3-winding transformer 532793 NEOSHO 7 345 532824 N345 1 1 13 533023 N345 3 4 138 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-129 | TO->FROM | 533023 N345 3 4 138 3WXFMR 536:N345 TX-1 138 1 | B | 400 | 0.095642 | 112.6182 | Single 532937 NEOSHO5 161 532939 N34545 161 1 | Cumulative Impact | Add 3-winding transformer 532793 NEOSHO 7 345 532824 N345 1 1 13 533023 N345 3 4 138 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-129 | TO->FROM | 532777 NRSS7 345 780840 G24-129-TAP 345 1 | B | 1159 | 1 | 113.2779 | P12:345:WERE:CANR-LATH-345:EHV: | TDF Impact | Rebuild line 532777 NRSS7 345 780840 G24-129-TAP 345 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-129 | TO->FROM | 532777 NRSS7 345 780840 G24-129-TAP 345 1 | B | 1159 | 1 | 113.2864 | P23:345:WERE:LATH-BKRS:EHV: | TDF Impact | Rebuild line 532777 NRSS7 345 780840 G24-129-TAP 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-129 | TO->FROM | 532780 CANEYRV7 345 780720 G24-125-TAP 345 1 | B | 1159 | 1 | 113.6032 | Single 532777 NRSS7 345 780840 G24-129-TAP 345 1 | TDF Impact | Rebuild line 532780 CANEYRV7 345 780720 G24-125-TAP 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-129 | TO->FROM | 532780 CANEYRV7 345 780720 G24-125-TAP 345 1 | B | 1159 | 1 | 113.622 | P52:345:WERE:NRSS7:EHV: | TDF Impact | Rebuild line 532780 CANEYRV7 345 780720 G24-125-TAP 345 1
Thermal | 00NR | 1 | 29SP | T1 | GEN-2024-129 | TO->FROM | 532911 MUSTNG5 161 532937 NEOSHO 5 161 1 | B | 148 | 0.030521 | 113.9313 | Single 547469 RIV4525 161 764310 G20-079-TAP 161 1 | TDF Impact | Rebuild line 532911 MUSTNG5 161 532937 NEOSHO 5 161 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-129 | TO->FROM | 532780 CANEYRV7 345 780720 G24-125-TAP 345 1 | B | 1159 | 1 | 114.0092 | Single 532777 NRSS7 345 780840 G24-129-TAP 345 1 | TDF Impact | Rebuild line 532780 CANEYRV7 345 780720 G24-125-TAP 345 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-129 | TO->FROM | 532780 CANEYRV7 345 780720 G24-125-TAP 345 1 | B | 1159 | 1 | 114.029 | P52:345:WERE:NRSS7:EHV: | TDF Impact | Rebuild line 532780 CANEYRV7 345 780720 G24-125-TAP 345 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-129 | TO->FROM | 533021 NEOSHO 4 138 533023 N345 3 4 138 1 | B | 478 | 0.10554 | 114.1602 | P23:345:AECI:7BLACKBERRY:656::: | Cumulative Impact | Rebuild line 533021 NEOSHO 4 138 533023 N345 3 4 138 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-129 | TO->FROM | 532937 NEOSHO 5 161 3WXFMR 536:NEOSHO TX-5 138 1 | B | 165 | 0.03672 | 114.2107 | Single 532937 NEOSHO5 161 532939 N34545 161 1 | TDF Impact | Add 3-winding transformer 532937 NEOSHO 5 161 532959 NEOSH5 1 13 533020 NEOSHOS4 138 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-129 | TO->FROM | 532937 NEOSHO 5 161 3WXFMR 536:NEOSHO TX-5 138 1 | B | 165 | 0.03672 | 114.2181 | Single 532793 NEOSHO7 345 532939 N34545 161 532825 'N345 2 1 ' 13 2 | TDF Impact | Add 3-winding transformer 532937 NEOSHO 5 161 532959 NEOSH5 1 13 533020 NEOSHOS4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-129 | TO->FROM | 532780 CANEYRV7 345 780720 G24-125-TAP 345 1 | B | 1159 | 1 | 114.3072 | Single 532777 NRSS7 345 780840 G24-129-TAP 345 1 | TDF Impact | Rebuild line 532780 CANEYRV7 345 780720 G24-125-TAP 345 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-129 | TO->FROM | 532780 CANEYRV7 345 780720 G24-125-TAP 345 1 | B | 1159 | 1 | 114.3281 | P52:345:WERE:NRSS7:EHV: | TDF Impact | Rebuild line 532780 CANEYRV7 345 780720 G24-125-TAP 345 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-129 | TO->FROM | 532777 NRSS7 345 780840 G24-129-TAP 345 1 | B | 1159 | 0.99718 | 114.3329 | P12:345:WERE:LATH-ROSE-345:EHV: | TDF Impact | Rebuild line 532777 NRSS7 345 780840 G24-129-TAP 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-129 | TO->FROM | 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 | B | 956 | 0.9982 | 115.0534 | Single 532777 NRSS7 345 780840 G24-129-TAP 345 1 | TDF Impact | Rebuild line 532794 ROSEHIL7 345 532800 LATHAMS7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-129 | TO->FROM | 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 | B | 956 | 0.99816 | 115.0781 | P52:345:WERE:NRSS7:EHV: | TDF Impact | Rebuild line 532794 ROSEHIL7 345 532800 LATHAMS7 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-129 | TO->FROM | 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 | B | 956 | 0.99784 | 116.0644 | Single 532777 NRSS7 345 780840 G24-129-TAP 345 1 | TDF Impact | Rebuild line 532794 ROSEHIL7 345 532800 LATHAMS7 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-129 | TO->FROM | 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 | B | 956 | 0.99778 | 116.0914 | P52:345:WERE:NRSS7:EHV: | TDF Impact | Rebuild line 532794 ROSEHIL7 345 532800 LATHAMS7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-129 | TO->FROM | 533023 N345 3 4 138 3WXFMR 536:N345 TX-1 138 1 | B | 400 | 0.095013 | 117.0122 | Single 532937 NEOSHO5 161 532939 N34545 161 1 | Cumulative Impact | Add 3-winding transformer 532793 NEOSHO 7 345 532824 N345 1 1 13 533023 N345 3 4 138 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-129 | TO->FROM | 533023 N345 3 4 138 3WXFMR 536:N345 TX-1 138 1 | B | 400 | 0.095013 | 117.0158 | Single 532793 NEOSHO7 345 532939 N34545 161 532825 'N345 2 1 ' 13 2 | Cumulative Impact | Add 3-winding transformer 532793 NEOSHO 7 345 532824 N345 1 1 13 533023 N345 3 4 138 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-129 | TO->FROM | 533021 NEOSHO 4 138 533023 N345 3 4 138 1 | B | 478 | 0.1146 | 117.9873 | Single 532937 NEOSHO5 161 532939 N34545 161 1 | Cumulative Impact | Rebuild line 533021 NEOSHO 4 138 533023 N345 3 4 138 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-129 | TO->FROM | 533021 NEOSHO 4 138 533023 N345 3 4 138 1 | B | 478 | 0.1146 | 117.99 | Single 532793 NEOSHO7 345 532939 N34545 161 532825 'N345 2 1 ' 13 2 | Cumulative Impact | Rebuild line 533021 NEOSHO 4 138 533023 N345 3 4 138 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-129 | TO->FROM | 532780 CANEYRV7 345 780720 G24-125-TAP 345 1 | B | 1159 | 0.99089 | 118.4516 | P12:345:WERE:NRSS-N345-345:EHV: | TDF Impact | Rebuild line 532780 CANEYRV7 345 780720 G24-125-TAP 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-129 | TO->FROM | 532780 CANEYRV7 345 780720 G24-125-TAP 345 1 | B | 1159 | 0.99089 | 118.4554 | P23:345:WERE:N345-345-20:EHV: | TDF Impact | Rebuild line 532780 CANEYRV7 345 780720 G24-125-TAP 345 1
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-129 | TO->FROM | 533021 NEOSHO 4 138 533023 N345 3 4 138 1 | B | 478 | 0.11546 | 118.739 | Single 532793 NEOSHO7 345 532939 N34545 161 532825 'N345 2 1 ' 13 2 | Cumulative Impact | Rebuild line 533021 NEOSHO 4 138 533023 N345 3 4 138 1
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-129 | TO->FROM | 533021 NEOSHO 4 138 533023 N345 3 4 138 1 | B | 478 | 0.11546 | 118.9931 | Single 532937 NEOSHO5 161 532939 N34545 161 1 | Cumulative Impact | Rebuild line 533021 NEOSHO 4 138 533023 N345 3 4 138 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-129 | TO->FROM | 532780 CANEYRV7 345 780720 G24-125-TAP 345 1 | B | 1159 | 0.99044 | 119.3022 | P12:345:WERE:NRSS-N345-345:EHV: | TDF Impact | Rebuild line 532780 CANEYRV7 345 780720 G24-125-TAP 345 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-129 | TO->FROM | 532780 CANEYRV7 345 780720 G24-125-TAP 345 1 | B | 1159 | 0.99044 | 119.3033 | P23:345:WERE:N345-345-20:EHV: | TDF Impact | Rebuild line 532780 CANEYRV7 345 780720 G24-125-TAP 345 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-129 | TO->FROM | 533021 NEOSHO 4 138 533023 N345 3 4 138 1 | B | 478 | 0.10633 | 120.3264 | P23:345:AECI:7BLACKBERRY:6_2::: | Cumulative Impact | Rebuild line 533021 NEOSHO 4 138 533023 N345 3 4 138 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-129 | TO->FROM | 533021 NEOSHO 4 138 533023 N345 3 4 138 1 | B | 478 | 0.10633 | 120.3274 | P23:345:AECI:7BLACKBERRY:6_3::: | Cumulative Impact | Rebuild line 533021 NEOSHO 4 138 533023 N345 3 4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-129 | TO->FROM | 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 | B | 956 | 0.97646 | 121.554 | P12:345:WERE:NRSS-N345-345:EHV: | TDF Impact | Rebuild line 532794 ROSEHIL7 345 532800 LATHAMS7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-129 | TO->FROM | 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 | B | 956 | 0.97646 | 121.5852 | P23:345:WERE:N345-345-20:EHV: | TDF Impact | Rebuild line 532794 ROSEHIL7 345 532800 LATHAMS7 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-129 | TO->FROM | 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 | B | 956 | 0.97036 | 122.6591 | P12:345:WERE:NRSS-N345-345:EHV: | TDF Impact | Rebuild line 532794 ROSEHIL7 345 532800 LATHAMS7 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-129 | TO->FROM | 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 | B | 956 | 0.97036 | 122.6952 | P23:345:WERE:N345-345-20:EHV: | TDF Impact | Rebuild line 532794 ROSEHIL7 345 532800 LATHAMS7 345 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-129 | TO->FROM | 532780 CANEYRV7 345 780720 G24-125-TAP 345 1 | B | 1159 | 0.97949 | 122.9229 | P12:345:WERE:NRSS-N345-345:EHV: | TDF Impact | Rebuild line 532780 CANEYRV7 345 780720 G24-125-TAP 345 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-129 | TO->FROM | 532780 CANEYRV7 345 780720 G24-125-TAP 345 1 | B | 1159 | 0.97949 | 122.9304 | P23:345:WERE:N345-345-20:EHV: | TDF Impact | Rebuild line 532780 CANEYRV7 345 780720 G24-125-TAP 345 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-129 | TO->FROM | 532937 NEOSHO 5 161 3WXFMR 536:NEOSHO TX-5 138 1 | B | 165 | 0.037516 | 125.6326 | Single 532937 NEOSHO5 161 532939 N34545 161 1 | TDF Impact | Add 3-winding transformer 532937 NEOSHO 5 161 532959 NEOSH5 1 13 533020 NEOSHOS4 138 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-129 | TO->FROM | 532937 NEOSHO 5 161 3WXFMR 536:NEOSHO TX-5 138 1 | B | 165 | 0.037516 | 125.6401 | Single 532793 NEOSHO7 345 532939 N34545 161 532825 'N345 2 1 ' 13 2 | TDF Impact | Add 3-winding transformer 532937 NEOSHO 5 161 532959 NEOSH5 1 13 533020 NEOSHOS4 138 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-129 | TO->FROM | 533023 N345 3 4 138 3WXFMR 536:N345 TX-1 138 1 | B | 400 | 0.098814 | 127.6223 | Single 532937 NEOSHO5 161 532939 N34545 161 1 | Cumulative Impact | Add 3-winding transformer 532793 NEOSHO 7 345 532824 N345 1 1 13 533023 N345 3 4 138 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-129 | TO->FROM | 533023 N345 3 4 138 3WXFMR 536:N345 TX-1 138 1 | B | 400 | 0.098814 | 127.6279 | Single 532793 NEOSHO7 345 532939 N34545 161 532825 'N345 2 1 ' 13 2 | Cumulative Impact | Add 3-winding transformer 532793 NEOSHO 7 345 532824 N345 1 1 13 533023 N345 3 4 138 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-129 | TO->FROM | 532937 NEOSHO 5 161 3WXFMR 536:NEOSHO TX-5 138 1 | B | 165 | 0.033451 | 130.1747 | Single 532793 NEOSHO7 345 532939 N34545 161 532825 'N345 2 1 ' 13 2 | TDF Impact | Add 3-winding transformer 532937 NEOSHO 5 161 532959 NEOSH5 1 13 533020 NEOSHOS4 138 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-129 | TO->FROM | 532937 NEOSHO 5 161 3WXFMR 536:NEOSHO TX-5 138 1 | B | 165 | 0.033451 | 130.1983 | Single 532937 NEOSHO5 161 532939 N34545 161 1 | TDF Impact | Add 3-winding transformer 532937 NEOSHO 5 161 532959 NEOSH5 1 13 533020 NEOSHOS4 138 M2
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-129 | TO->FROM | 533021 NEOSHO 4 138 533023 N345 3 4 138 1 | B | 478 | 0.11778 | 134.24 | Single 532937 NEOSHO5 161 532939 N34545 161 1 | Cumulative Impact | Rebuild line 533021 NEOSHO 4 138 533023 N345 3 4 138 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-129 | TO->FROM | 533021 NEOSHO 4 138 533023 N345 3 4 138 1 | B | 478 | 0.11778 | 134.2441 | Single 532793 NEOSHO7 345 532939 N34545 161 532825 'N345 2 1 ' 13 2 | Cumulative Impact | Rebuild line 533021 NEOSHO 4 138 533023 N345 3 4 138 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-139 | TO->FROM | 541199 ST JOE 7 345 541400 EASTOWN7 345 1 | B | 1185 | 0.060314 | 100.396 | Single 541199 STJOE7 345 761383 G17-183-TAP 345 1 | Cumulative Impact | Rebuild line 541199 ST JOE 7 345 541400 EASTOWN7 345 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-139 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.11364 | 101.6955 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-139 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.11364 | 101.6955 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-139 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.11364 | 101.6955 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-139 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | B | 829 | 0.033914 | 103.7671 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | TDF Impact | Rebuild line 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1
Thermal | 03ALL | 1 | 26SP | T1 | GEN-2024-139 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.10901 | 105.0133 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 29WP | T1 | GEN-2024-139 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.11648 | 106.2154 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-139 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.11794 | 106.5956 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-139 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.11794 | 106.5956 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-139 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.11794 | 106.5956 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-139 | TO->FROM | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | B | 1195 | 0.066913 | 107.005 | Single 541199 STJOE7 345 761383 G17-183-TAP 345 1 | Cumulative Impact | Rebuild line 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-139 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.11416 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-139 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.11416 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-139 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.11416 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-140 | TO->FROM | 640149 CREITON7 115 640521 ANTELOPE 7 115 1 | B | 143 | 0.062189 | 101.3014 | Single 640226 HOSKINS3 345 763443 G18-131-TAP 345 1 | TDF Impact | Rebuild line 640149 CREITON7 115 640521 ANTELOPE 7 115 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-140 | TO->FROM | 640228 HOSKINS7 115 3WXFMR 640:HOSKINS T1 230 1 | B | 187 | 0.031401 | 101.793 | P13:115-345:NPPD:HOSKINS3:T4::: | TDF Impact | Add 3-winding transformer 640227 HOSKINS4 230 640228 HOSKINS7 115 643083 HOSKINS T1 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-140 | TO->FROM | 640149 CREITON7 115 640521 ANTELOPE 7 115 1 | B | 143 | 0.061968 | 103.6591 | P42:345:NPPD:BKR-HOS-3308:::: | TDF Impact | Rebuild line 640149 CREITON7 115 640521 ANTELOPE 7 115 1
Thermal | 02ALL | 1 | 26SP | T0 | GEN-2024-140 | TO->FROM | 640113 CLRWATR7 115 640293 NELIGH 7 115 1 | B | 120 | 0.16986 | 106.785 | Single 640226 HOSKINS3 345 763443 G18-131-TAP 345 1 | Cumulative Impact | 640_NPPD_NewBranch_Holt-Antilope3_345.idv : 2024 ITP, PID: 94842, NTC, ISD: 12/31/2029
Thermal | 02ALL | 1 | 26SP | T0 | GEN-2024-140 | TO->FROM | 640113 CLRWATR7 115 640293 NELIGH 7 115 1 | B | 120 | 0.1712 | 107.9844 | P42:345:NPPD:BKR-HOS-3308:::: | Cumulative Impact | 640_NPPD_NewBranch_Holt-Antilope3_345.idv : 2024 ITP, PID: 94842, NTC, ISD: 12/31/2029
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-140 | TO->FROM | 640149 CREITON7 115 640521 ANTELOPE 7 115 1 | B | 143 | 0.055859 | 110.9949 | Single 640226 HOSKINS3 345 763443 G18-131-TAP 345 1 | TDF Impact | Rebuild line 640149 CREITON7 115 640521 ANTELOPE 7 115 1
Thermal | 02ALL | 1 | 26SP | T0 | GEN-2024-140 | TO->FROM | 640149 CREITON7 115 640521 ANTELOPE 7 115 1 | B | 143 | 0.20496 | 112.9996 | P42:345:NPPD:BKR-HOS-3308:::: | TDF Impact | 640_NPPD_NewBranch_Holt-Antilope3_345.idv : 2024 ITP, PID: 94842, NTC, ISD: 12/31/2029
Thermal | 02ALL | 1 | 26SP | T0 | GEN-2024-140 | TO->FROM | 640149 CREITON7 115 640521 ANTELOPE 7 115 1 | B | 143 | 0.20503 | 113.1478 | Single 640226 HOSKINS3 345 763443 G18-131-TAP 345 1 | TDF Impact | 640_NPPD_NewBranch_Holt-Antilope3_345.idv : 2024 ITP, PID: 94842, NTC, ISD: 12/31/2029
Thermal | 02ALL | 1 | 26SP | T0 | GEN-2024-140 | TO->FROM | 640072 BATTLCR7 115 640115 CO.LINE7 115 1 | B | 193 | 0.3847 | 113.7251 | P42:345:NPPD:BKR-HOS-3308:::: | TDF Impact | 640_NPPD_NewBranch_Holt-Antilope3_345.idv : 2024 ITP, PID: 94842, NTC, ISD: 12/31/2029
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-140 | TO->FROM | 640149 CREITON7 115 640521 ANTELOPE 7 115 1 | B | 143 | 0.055726 | 114.0717 | P42:345:NPPD:BKR-HOS-3308:::: | TDF Impact | Rebuild line 640149 CREITON7 115 640521 ANTELOPE 7 115 1
Thermal | 02ALL | 1 | 26SP | T0 | GEN-2024-140 | TO->FROM | 640115 CO.LINE7 115 640521 ANTELOPE 7 115 1 | B | 193 | 0.3847 | 116.9814 | P42:345:NPPD:BKR-HOS-3308:::: | TDF Impact | 640_NPPD_NewBranch_Holt-Antilope3_345.idv : 2024 ITP, PID: 94842, NTC, ISD: 12/31/2029
Thermal | 02ALL | 1 | 26SP | T0 | GEN-2024-140 | TO->FROM | 640072 BATTLCR7 115 640115 CO.LINE7 115 1 | B | 193 | 0.39194 | 118.2169 | Single 640226 HOSKINS3 345 763443 G18-131-TAP 345 1 | TDF Impact | 640_NPPD_NewBranch_Holt-Antilope3_345.idv : 2024 ITP, PID: 94842, NTC, ISD: 12/31/2029
Thermal | 02ALL | 1 | 26SP | T0 | GEN-2024-140 | TO->FROM | 640054 ALBION 7 115 640318 PETRSBG7 115 1 | B | 137 | 0.23133 | 120.1247 | Single 640226 HOSKINS3 345 763443 G18-131-TAP 345 1 | TDF Impact | 640_NPPD_NewBranch_Holt-Antilope3_345.idv : 2024 ITP, PID: 94842, NTC, ISD: 12/31/2029
Thermal | 02ALL | 1 | 26SP | T0 | GEN-2024-140 | TO->FROM | 640115 CO.LINE7 115 640521 ANTELOPE 7 115 1 | B | 193 | 0.39194 | 121.4834 | Single 640226 HOSKINS3 345 763443 G18-131-TAP 345 1 | TDF Impact | 640_NPPD_NewBranch_Holt-Antilope3_345.idv : 2024 ITP, PID: 94842, NTC, ISD: 12/31/2029
Thermal | 02ALL | 1 | 26SP | T0 | GEN-2024-140 | TO->FROM | 640318 PETRSBG7 115 640444 PETERSBRG.N7 115 Z1 | B | 137 | 0.23133 | 124.1705 | Single 640226 HOSKINS3 345 763443 G18-131-TAP 345 1 | TDF Impact | 640_NPPD_NewBranch_Holt-Antilope3_345.idv : 2024 ITP, PID: 94842, NTC, ISD: 12/31/2029
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-140 | TO->FROM | 645454 S3454 3 345 650185 WAGENER 3 345 1 | B | 982 | 0.057128 | 124.4523 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | Rebuild line 645454 S3454 3 345 650185 WAGENER 3 345 1
Thermal | 02ALL | 1 | 26SP | T0 | GEN-2024-140 | TO->FROM | 640054 ALBION 7 115 640318 PETRSBG7 115 1 | B | 137 | 0.2373 | 124.7531 | P42:345:NPPD:BKR-HOS-3308:::: | TDF Impact | 640_NPPD_NewBranch_Holt-Antilope3_345.idv : 2024 ITP, PID: 94842, NTC, ISD: 12/31/2029
Thermal | 02ALL | 1 | 26SP | T0 | GEN-2024-140 | TO->FROM | 640318 PETRSBG7 115 640444 PETERSBRG.N7 115 Z1 | B | 137 | 0.2373 | 128.8228 | P42:345:NPPD:BKR-HOS-3308:::: | TDF Impact | 640_NPPD_NewBranch_Holt-Antilope3_345.idv : 2024 ITP, PID: 94842, NTC, ISD: 12/31/2029
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-143 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.075571 | 100.0488 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-143 | TO->FROM | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | B | 997 | 0.1262 | 100.166 | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | Cumulative Impact | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-143 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.06169 | 100.533 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-143 | TO->FROM | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | B | 997 | 0.13654 | 100.7286 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-143 | TO->FROM | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | B | 997 | 0.13654 | 101.1047 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-143 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063077 | 102.9616 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-143 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063077 | 102.9634 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-143 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063077 | 103.0288 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-143 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063077 | 103.4739 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-143 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.079609 | 103.9266 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-143 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063077 | 104.1493 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-143 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.077927 | 104.7552 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-143 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.077927 | 104.888 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-143 | TO->FROM | 531510 HARBNGR3 115 3WXFMR 534:HARBGR345 345 1 | B | 385 | 0.057704 | 105.7318 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Add 3-winding transformer 531510 HARBNGR3 115 531511 HARBNGR-1 13 531512 HARBNGR7 345 M2
Thermal | 05ALL | 1 | 26SP | T1 | GEN-2024-143 | TO->FROM | 523216 RB-HOGUE 3 115 523246 DALHART 3 115 1 | B | 82 | 0.080252 | 106.1269 | Single 523228 DALLAM3 115 523235 HILMRCHZ_TP3 115 1 | Cumulative Impact | Rebuild line 523216 RB-HOGUE 3 115 523246 DALHART 3 115 1
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-143 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.081907 | 107.2243 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-143 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063077 | 107.2793 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-143 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063077 | 107.2794 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-143 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.081907 | 107.2951 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-143 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063077 | 107.3093 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-143 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.077008 | 107.5866 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-143 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063077 | 107.7557 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-143 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063077 | 108.1822 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-143 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063077 | 108.2747 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T1 | GEN-2024-143 | TO->FROM | 523216 RB-HOGUE 3 115 523246 DALHART 3 115 1 | B | 82 | 0.080094 | 108.5963 | Single 523228 DALLAM3 115 523235 HILMRCHZ_TP3 115 1 | Cumulative Impact | Rebuild line 523216 RB-HOGUE 3 115 523246 DALHART 3 115 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-143 | TO->FROM | 523308 MOORE_E 3 115 3WXFMR 526:ENRCO 136402 115 1 | B | 239 | 0.12016 | 109.5161 | P12:115:SPS:W80.1.XIT.DALM:::HV: | Cumulative Impact | 526_New_MooreCounty_2ndTransformer_230_115.idv : PID: 220817, 2024 ITP, NTC, ISD: 5/15/2029
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-143 | TO->FROM | 523308 MOORE_E 3 115 3WXFMR 526:ENRCO 136402 115 1 | B | 239 | 0.12016 | 109.5161 | Single 523220 XIT_INTG3 115 523228 DALLAM3 115 1 | Cumulative Impact | 526_New_MooreCounty_2ndTransformer_230_115.idv : PID: 220817, 2024 ITP, NTC, ISD: 5/15/2029
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-143 | TO->FROM | 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | B | 997 | 0.15023 | 109.7018 | Single 525832 TUCO_INT7 345 526000 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-143 | TO->FROM | 523220 XIT_INTG 3 115 3WXFMR 526:SIEM_T126401 115 1 | B | 284 | 0.37348 | 110.6438 | Single 523221 XIT_INTG6 230 523309 MOORE_CNTY6 230 1 | TDF Impact | Add 3-winding transformer 523219 XIT_INTG TR1 13 523220 XIT_INTG 3 115 523221 XIT_INTG 6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-143 | TO->FROM | 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | B | 997 | 0.14059 | 111.09 | Single 525832 TUCO_INT7 345 526000 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-143 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063077 | 111.3621 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-143 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.079378 | 111.723 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-143 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.079378 | 111.8755 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-143 | TO->FROM | 523308 MOORE_E 3 115 3WXFMR 526:ENRCO 136402 115 1 | B | 239 | 0.12016 | 114.1569 | Single 523221 XIT_INTG6 230 523220 XIT_INTG3 115 523219 'XIT_INTG TR1' 13 1 | Cumulative Impact | 526_New_MooreCounty_2ndTransformer_230_115.idv : PID: 220817, 2024 ITP, NTC, ISD: 5/15/2029
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-143 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.077008 | 115.0541 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29L | T0 | GEN-2024-143 | TO->FROM | 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | B | 997 | 0.10423 | 116.6859 | Single 525832 TUCO_INT7 345 526000 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-143 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.079378 | 118.9427 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-143 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.079378 | 119.313 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-143 | TO->FROM | 523308 MOORE_E 3 115 3WXFMR 526:ENRCO 136402 115 1 | B | 239 | 0.19816 | 120.7667 | P12:230:SPS:K98:1:XITINTG_CHAN+TASCOS___:HV: | Cumulative Impact | 526_New_MooreCounty_2ndTransformer_230_115.idv : PID: 220817, 2024 ITP, NTC, ISD: 5/15/2029
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-143 | TO->FROM | 531405 WALKMYR3 115 531510 HARBNGR3 115 1 | B | 331.39 | 0.057704 | 122.4803 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild line 531405 WALKMYR3 115 531510 HARBNGR3 115 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-145 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.075571 | 100.0488 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-145 | TO->FROM | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | B | 997 | 0.1262 | 100.166 | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | Cumulative Impact | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-145 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.06169 | 100.533 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-145 | TO->FROM | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | B | 997 | 0.13654 | 100.7286 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-145 | TO->FROM | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | B | 997 | 0.13654 | 101.1047 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-145 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063077 | 102.9616 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-145 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063077 | 102.9634 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-145 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063077 | 103.0288 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-145 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063077 | 103.4739 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-145 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.079609 | 103.9266 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-145 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063077 | 104.1493 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-145 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.077927 | 104.7552 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-145 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.077927 | 104.888 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-145 | TO->FROM | 531510 HARBNGR3 115 3WXFMR 534:HARBGR345 345 1 | B | 385 | 0.057704 | 105.7318 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Add 3-winding transformer 531510 HARBNGR3 115 531511 HARBNGR-1 13 531512 HARBNGR7 345 M2
Thermal | 05ALL | 1 | 26SP | T1 | GEN-2024-145 | TO->FROM | 523216 RB-HOGUE 3 115 523246 DALHART 3 115 1 | B | 82 | 0.080252 | 106.1269 | Single 523228 DALLAM3 115 523235 HILMRCHZ_TP3 115 1 | Cumulative Impact | Rebuild line 523216 RB-HOGUE 3 115 523246 DALHART 3 115 1
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-145 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.081907 | 107.2243 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-145 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063077 | 107.2793 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-145 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063077 | 107.2794 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-145 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.081907 | 107.2951 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-145 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063077 | 107.3093 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-145 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.077008 | 107.5866 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-145 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063077 | 107.7557 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-145 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063077 | 108.1822 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-145 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063077 | 108.2747 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T1 | GEN-2024-145 | TO->FROM | 523216 RB-HOGUE 3 115 523246 DALHART 3 115 1 | B | 82 | 0.080094 | 108.5963 | Single 523228 DALLAM3 115 523235 HILMRCHZ_TP3 115 1 | Cumulative Impact | Rebuild line 523216 RB-HOGUE 3 115 523246 DALHART 3 115 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-145 | TO->FROM | 523308 MOORE_E 3 115 3WXFMR 526:ENRCO 136402 115 1 | B | 239 | 0.12016 | 109.5161 | P12:115:SPS:W80.1.XIT.DALM:::HV: | Cumulative Impact | 526_New_MooreCounty_2ndTransformer_230_115.idv : PID: 220817, 2024 ITP, NTC, ISD: 5/15/2029
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-145 | TO->FROM | 523308 MOORE_E 3 115 3WXFMR 526:ENRCO 136402 115 1 | B | 239 | 0.12016 | 109.5161 | Single 523220 XIT_INTG3 115 523228 DALLAM3 115 1 | Cumulative Impact | 526_New_MooreCounty_2ndTransformer_230_115.idv : PID: 220817, 2024 ITP, NTC, ISD: 5/15/2029
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-145 | TO->FROM | 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | B | 997 | 0.15023 | 109.7018 | Single 525832 TUCO_INT7 345 526000 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-145 | TO->FROM | 523220 XIT_INTG 3 115 3WXFMR 526:SIEM_T126401 115 1 | B | 284 | 0.37348 | 110.6438 | Single 523221 XIT_INTG6 230 523309 MOORE_CNTY6 230 1 | TDF Impact | Add 3-winding transformer 523219 XIT_INTG TR1 13 523220 XIT_INTG 3 115 523221 XIT_INTG 6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-145 | TO->FROM | 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | B | 997 | 0.14059 | 111.09 | Single 525832 TUCO_INT7 345 526000 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-145 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063077 | 111.3621 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-145 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.079378 | 111.723 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-145 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.079378 | 111.8755 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-145 | TO->FROM | 523308 MOORE_E 3 115 3WXFMR 526:ENRCO 136402 115 1 | B | 239 | 0.12016 | 114.1569 | Single 523221 XIT_INTG6 230 523220 XIT_INTG3 115 523219 'XIT_INTG TR1' 13 1 | Cumulative Impact | 526_New_MooreCounty_2ndTransformer_230_115.idv : PID: 220817, 2024 ITP, NTC, ISD: 5/15/2029
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-145 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.077008 | 115.0541 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29L | T0 | GEN-2024-145 | TO->FROM | 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | B | 997 | 0.10423 | 116.6859 | Single 525832 TUCO_INT7 345 526000 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-145 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.079378 | 118.9427 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-145 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.079378 | 119.313 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-145 | TO->FROM | 523308 MOORE_E 3 115 3WXFMR 526:ENRCO 136402 115 1 | B | 239 | 0.19816 | 120.7667 | P12:230:SPS:K98:1:XITINTG_CHAN+TASCOS___:HV: | Cumulative Impact | 526_New_MooreCounty_2ndTransformer_230_115.idv : PID: 220817, 2024 ITP, NTC, ISD: 5/15/2029
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-145 | TO->FROM | 531405 WALKMYR3 115 531510 HARBNGR3 115 1 | B | 331.39 | 0.057704 | 122.4803 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild line 531405 WALKMYR3 115 531510 HARBNGR3 115 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-154 | TO->FROM | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 | B | 1015 | 0.098277 | 102.04 | P42:345:OKGE:SB_DGSE7313:::EHV: | Cumulative Impact | Rebuild line 514715 WOODRNG7 345 515875 REDNGTN7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-154 | TO->FROM | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 | B | 1015 | 0.097989 | 102.2256 | P42:345:OKGE:SB_DGSE7313:::EHV: | Cumulative Impact | Rebuild line 514715 WOODRNG7 345 515875 REDNGTN7 345 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-159 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.073955 | 100.0488 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-159 | TO->FROM | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | B | 997 | 0.17098 | 100.166 | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | Cumulative Impact | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-159 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063708 | 100.533 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-159 | TO->FROM | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | B | 997 | 0.17619 | 100.7286 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-159 | TO->FROM | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | B | 997 | 0.17619 | 101.1047 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-159 | TO->FROM | 524875 OASIS 6 230 781740 G24-159-TAP 230 1 | B | 319 | 0.79904 | 101.2294 | P12:345:SPS:J15:1:TOLK_CROSSROADS___:EHV: | TDF Impact | Rebuild line 524875 OASIS 6 230 781740 G24-159-TAP 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-159 | TO->FROM | 524875 OASIS 6 230 781740 G24-159-TAP 230 1 | B | 319 | 0.79904 | 101.2294 | Single 525549 TOLK7 345 780240 G24-109-TAP 345 1 | TDF Impact | Rebuild line 524875 OASIS 6 230 781740 G24-159-TAP 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-159 | TO->FROM | 524875 OASIS 6 230 781740 G24-159-TAP 230 1 | B | 319 | 0.81541 | 101.8343 | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | Rebuild line 524875 OASIS 6 230 781740 G24-159-TAP 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-159 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.064675 | 102.9616 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-159 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.064675 | 102.9634 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-159 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.064675 | 103.0288 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-159 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.064675 | 103.4739 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-159 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.077999 | 103.9266 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-159 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.064675 | 104.1493 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-159 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.076993 | 104.7552 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-159 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.076993 | 104.888 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-159 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.080976 | 107.2243 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-159 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.064675 | 107.2793 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-159 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.064675 | 107.2794 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-159 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.080976 | 107.2951 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-159 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.064675 | 107.3093 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-159 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.075075 | 107.5866 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-159 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.064675 | 107.7557 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-159 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.064675 | 108.1822 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-159 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.064675 | 108.2747 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-159 | TO->FROM | 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | B | 997 | 0.26878 | 109.7018 | Single 525832 TUCO_INT7 345 526000 CRAWFISH_DR 345 2 | TDF Impact | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-159 | TO->FROM | 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | B | 997 | 0.26766 | 111.09 | Single 525832 TUCO_INT7 345 526000 CRAWFISH_DR 345 2 | TDF Impact | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-159 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.064675 | 111.3621 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-159 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.07813 | 111.723 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-159 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.07813 | 111.8755 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-159 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.075075 | 115.0541 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-159 | TO->FROM | 524875 OASIS 6 230 781740 G24-159-TAP 230 1 | B | 319 | 0.90413 | 117.1851 | Single 527799 EDDY_NORTH6 230 786270 G24-310-TAP 230 1 | TDF Impact | Rebuild line 524875 OASIS 6 230 781740 G24-159-TAP 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-159 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.07813 | 118.9427 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-159 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.07813 | 119.313 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-159 | TO->FROM | 524875 OASIS 6 230 781740 G24-159-TAP 230 1 | B | 319 | 0.90346 | 120.7292 | Single 527799 EDDY_NORTH6 230 786270 G24-310-TAP 230 1 | TDF Impact | Rebuild line 524875 OASIS 6 230 781740 G24-159-TAP 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-159 | TO->FROM | 524875 OASIS 6 230 781740 G24-159-TAP 230 1 | B | 319 | 0.90292 | 125.4479 | Single 527799 EDDY_NORTH6 230 786270 G24-310-TAP 230 1 | TDF Impact | Rebuild line 524875 OASIS 6 230 781740 G24-159-TAP 230 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-166 | TO->FROM | 640277 MOORE 3 345 640525 TOBIAS 3 345 1 | B | 956 | 0.050258 | 100.5946 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640525 TOBIAS 3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-166 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | B | 829 | 0.035348 | 103.7671 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | TDF Impact | Rebuild line 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-168 | TO->FROM | 645454 S3454 3 345 650185 WAGENER 3 345 1 | B | 982 | 0.12861 | 104.6262 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Rebuild line 645454 S3454 3 345 650185 WAGENER 3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-168 | TO->FROM | 650185 WAGENER 3 345 650189 103&ROKEBY3 345 1 | B | 1158 | 0.056209 | 105.9892 | P42:345:NPPD:BKR-MOR-3310:::: | TDF Impact | Rebuild line 650185 WAGENER 3 345 650189 103&ROKEBY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-168 | TO->FROM | 650185 WAGENER 3 345 650189 103&ROKEBY3 345 1 | B | 1158 | 0.056209 | 105.9892 | P42:345:NPPD:L3502A.MOORE.MCCOOL.CB3310:::: | TDF Impact | Rebuild line 650185 WAGENER 3 345 650189 103&ROKEBY3 345 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-168 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.033007 | 106.6762 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-168 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.033039 | 108.9935 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-168 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.033039 | 109.0153 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-168 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.032839 | 109.4444 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-168 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.033217 | 118.0094 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-168 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.032868 | 119.5678 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-168 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.032868 | 120.8848 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-168 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.032905 | 121.2729 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-168 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.032905 | 121.3014 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-168 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.032686 | 121.5027 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-168 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.032905 | 122.5957 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-168 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.032905 | 122.6148 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-168 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.032686 | 122.8495 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-168 | TO->FROM | 645454 S3454 3 345 650185 WAGENER 3 345 1 | B | 982 | 0.18718 | 124.4523 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | Rebuild line 645454 S3454 3 345 650185 WAGENER 3 345 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-168 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.033152 | 130.4818 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-168 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.033152 | 132.0705 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-168 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.032571 | 146.377 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-168 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.032621 | 148.5944 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-168 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.03262 | 148.6147 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-168 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.032404 | 148.9728 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-168 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.032571 | 149.1688 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-168 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.032621 | 151.4021 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-168 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.03262 | 151.42 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-168 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.032404 | 151.7992 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-168 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.032916 | 159.9633 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-168 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.032916 | 163.2816 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-170 | TO->FROM | 541199 ST JOE 7 345 541400 EASTOWN7 345 1 | B | 1185 | 0.085676 | 100.396 | Single 541199 STJOE7 345 761383 G17-183-TAP 345 1 | Cumulative Impact | Rebuild line 541199 ST JOE 7 345 541400 EASTOWN7 345 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-170 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.081411 | 101.6955 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-170 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.081411 | 101.6955 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-170 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.081411 | 101.6955 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 26SP | T1 | GEN-2024-170 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.080386 | 105.0133 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 29WP | T1 | GEN-2024-170 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.07672 | 106.2154 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-170 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.077608 | 106.5956 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-170 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.077608 | 106.5956 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-170 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.077608 | 106.5956 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-170 | TO->FROM | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | B | 1195 | 0.094539 | 107.005 | Single 541199 STJOE7 345 761383 G17-183-TAP 345 1 | Cumulative Impact | Rebuild line 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-170 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | A | 311 | 0.054358 | 111.039 | System Intact | TDF Impact | Rebuild line 300071 5CLINTN 161 761278 G17-108-TAP 161 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-170 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.08303 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-170 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.08303 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-170 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.08303 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-170 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.065723 | 117.7598 | P55:345:OPPD:S3458 3::FN13:EHV: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-170 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | A | 311 | 0.054327 | 121.8886 | System Intact | TDF Impact | Rebuild line 300071 5CLINTN 161 761278 G17-108-TAP 161 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-170 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | A | 334 | 0.053498 | 145.0684 | System Intact | TDF Impact | Rebuild line 300071 5CLINTN 161 761278 G17-108-TAP 161 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-171 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.16367 | 100.4398 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-171 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.16986 | 100.451 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-171 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1182 | 0.18415 | 100.7686 | Single 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-171 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1182 | 0.18423 | 100.7917 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | Cumulative Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-171 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.1824 | 101.1642 | Single 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-171 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | A | 901 | 0.17064 | 101.5467 | System Intact | TDF Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-171 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.18402 | 101.7923 | Single 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-171 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.17425 | 101.9139 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-171 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.16986 | 101.9296 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-171 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | A | 901 | 0.16597 | 102.5076 | System Intact | TDF Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-171 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.18749 | 102.6355 | Single 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Cumulative Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-171 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.1824 | 102.8031 | Single 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Cumulative Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-171 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.16957 | 102.8233 | P22:345:EES:CLARKSV7!:::EHV: | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-171 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.18402 | 103.1009 | Single 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-171 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.1824 | 103.3738 | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-171 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.18465 | 103.4829 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-171 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.18402 | 103.5409 | Single 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-171 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.18965 | 103.7549 | Single 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-171 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.17392 | 104.0394 | P22:345:EES:CLARKSV7!:::EHV: | Cumulative Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-171 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.1626 | 104.6561 | P22:345:EES:CLARKSV7!:::EHV: | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-171 | TO->FROM | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | A | 1806 | 0.04459 | 104.7272 | System Intact | TDF Impact | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-171 | TO->FROM | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | A | 1806 | 0.049503 | 104.7927 | System Intact | TDF Impact | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-171 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.16957 | 104.8397 | P22:345:EES:CLARKSV7!:::EHV: | Cumulative Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-171 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.18402 | 104.9783 | Single 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-171 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.18749 | 105.1591 | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | Cumulative Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-171 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.1824 | 105.2013 | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | Cumulative Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-171 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.18965 | 105.3089 | Single 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-171 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.18465 | 105.3978 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | Cumulative Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-171 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.16554 | 105.4314 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB:::: | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-171 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.16555 | 105.47 | P12:345:EES:CHAMSPR7!:CLARKSV7!:1:EHV: | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-171 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.15927 | 105.6463 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB:::: | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-171 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.15927 | 105.6708 | P12:345:EES:CHAMSPR7!:CLARKSV7!:1:EHV: | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-171 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.19016 | 105.6815 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | Cumulative Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-171 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.18151 | 106.3738 | P23:345:WERE:N345-345-20:EHV: | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-171 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1011 | 0.10838 | 106.9293 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-171 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.1701 | 107.3179 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB:::: | Cumulative Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-171 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.17011 | 107.3846 | P12:345:EES:CHAMSPR7!:CLARKSV7!:1:EHV: | Cumulative Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-171 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.18415 | 107.6019 | Single 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-171 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1011 | 0.10844 | 107.7039 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-171 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.16554 | 107.8076 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB:::: | Cumulative Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-171 | TO->FROM | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | A | 827 | 0.052052 | 107.8643 | System Intact | TDF Impact | Rebuild line 532791 BENTON 7 345 532794 ROSEHIL7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-171 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.16555 | 107.867 | P12:345:EES:CHAMSPR7!:CLARKSV7!:1:EHV: | Cumulative Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-171 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.18151 | 108.4042 | P23:345:WERE:N345-345-20:EHV: | Cumulative Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-171 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.18644 | 108.8315 | P23:345:WERE:N345-345-20:EHV: | Cumulative Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-171 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.18415 | 109.031 | Single 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-171 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.18423 | 109.0559 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-171 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.17425 | 109.2662 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-171 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.18749 | 109.6648 | Single 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-171 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.18965 | 110.6179 | Single 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-171 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.17392 | 110.6357 | P22:345:EES:CLARKSV7!:::EHV: | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-171 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.18749 | 112.0601 | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-171 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.18965 | 112.0812 | Single 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-171 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1187 | 0.14128 | 112.2151 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-171 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.19016 | 112.433 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-171 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.15509 | 112.5233 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-171 | TO->FROM | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | A | 827 | 0.053787 | 113.506 | System Intact | TDF Impact | Rebuild line 532791 BENTON 7 345 532794 ROSEHIL7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-171 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.1701 | 113.5635 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB:::: | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-171 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.17011 | 113.5961 | P12:345:EES:CHAMSPR7!:CLARKSV7!:1:EHV: | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-171 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.14969 | 113.7225 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-171 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.15321 | 114.0272 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-171 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.17148 | 114.0895 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-171 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.14903 | 115.4477 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-171 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.17148 | 115.647 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-171 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.18644 | 115.6656 | P23:345:WERE:N345-345-20:EHV: | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-171 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.14903 | 117.1553 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-171 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.14903 | 117.1572 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-171 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.14903 | 119.7129 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-171 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.14903 | 124.3274 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-171 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.10388 | 137.9906 | System Intact | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-171 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.1027 | 138.1985 | System Intact | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-171 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.12687 | 155.4006 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-171 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.11281 | 155.7991 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-171 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.11082 | 155.8883 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-171 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.12747 | 158.3302 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-171 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.11172 | 159.2546 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-171 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.10994 | 159.5575 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-171 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.11857 | 160.5677 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-171 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.11118 | 161.638 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-171 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.11539 | 161.7992 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-171 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.11679 | 161.8408 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-171 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.10935 | 162.2698 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-171 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.11376 | 163.3422 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-171 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.11118 | 164.1736 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-171 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.11118 | 164.1763 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-171 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.10935 | 164.8475 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-171 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.10935 | 164.8482 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-171 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.11118 | 167.9939 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-171 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.10935 | 169.069 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-171 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.11118 | 175.0352 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-171 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.10935 | 177.0235 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-173 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.058593 | 101.6704 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-173 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.058593 | 103.1149 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-173 | TO->FROM | 645454 S3454 3 345 650185 WAGENER 3 345 1 | B | 982 | 0.16928 | 104.6262 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Rebuild line 645454 S3454 3 345 650185 WAGENER 3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-173 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | A | 110 | 0.059859 | 105.8619 | System Intact | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-173 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.064764 | 106.3207 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-173 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.076201 | 106.6762 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-173 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.0763 | 108.9935 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-173 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.0763 | 109.0153 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-173 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.075908 | 109.4444 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-173 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.062894 | 110.3426 | P42:345:LES:L1485::NW68&HOLDREGE.WAGENER.CB3006:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-173 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.060535 | 111.0459 | P13:161-345:OPPD:TX01::S3454.CKT1:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-173 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.060535 | 111.0459 | P13:161-345:OPPD:S1254 T1:::HV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-173 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.062894 | 112.4118 | P42:345:LES:L1485::NW68&HOLDREGE.WAGENER.CB3006:: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-173 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.060535 | 112.9897 | P13:161-345:OPPD:TX01::S3454.CKT1:: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-173 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.060535 | 112.9897 | P13:161-345:OPPD:S1254 T1:::HV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-173 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.064329 | 117.1294 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-173 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.076455 | 118.0094 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-173 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.064329 | 118.9455 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-173 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.075817 | 119.5678 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-173 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.075817 | 120.8848 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-173 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.075914 | 121.2729 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-173 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.075914 | 121.3014 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-173 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.075503 | 121.5027 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-173 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.075914 | 122.5957 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-173 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.075914 | 122.6148 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-173 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.075503 | 122.8495 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-173 | TO->FROM | 645454 S3454 3 345 650185 WAGENER 3 345 1 | B | 982 | 0.22857 | 124.4523 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | Rebuild line 645454 S3454 3 345 650185 WAGENER 3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-173 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.058631 | 125.7992 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-173 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.058631 | 128.7149 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-173 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.076126 | 130.4818 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-173 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.076126 | 132.0705 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-173 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.075616 | 146.377 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-173 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.064296 | 148.4763 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-173 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.075731 | 148.5944 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-173 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.075731 | 148.6147 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-173 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.075325 | 148.9728 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-173 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.075616 | 149.1688 | P23:345:OPPD:S3454-S3451&WAGNER:::EHV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-173 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.075731 | 151.4021 | P12:345:OPPD-LES:L3472::S3454.WAGENER.CKT1:: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-173 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.075731 | 151.42 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-173 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.075325 | 151.7992 | P42:345:LES:L1485::WAGENER.NW68&HOLDREGE.CB3006:: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-173 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.064296 | 152.3912 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-173 | TO->FROM | 650169 70&BLUFF 5 161 3WXFMR 650:T691 161 1 | B | 120 | 0.075999 | 159.9633 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Add 3-winding transformer 650169 70&BLUFF 5 161 650269 70&BLUFF 7 115 650369 70&BLUFF 9 13 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-173 | TO->FROM | 646214 S1214 5 161 650169 70&BLUFF 5 161 1 | B | 116 | 0.075999 | 163.2816 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Rebuild line 646214 S1214 5 161 650169 70&BLUFF 5 161 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-204 | TO->FROM | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | B | 1059 | 0.053592 | 100.2166 | P12:345:AEPW:R.S.S.-7:ONETA--7::: | Cumulative Impact | Rebuild line 509745 CLARKSV7 345 515224 MUSKOGE7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-204 | TO->FROM | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | B | 1059 | 0.056511 | 100.8866 | Single 515231 KEEFTON7 345 780360 G24-113-TAP 345 1 | Cumulative Impact | Rebuild line 509745 CLARKSV7 345 515224 MUSKOGE7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-204 | TO->FROM | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 | B | 1015 | 0.061865 | 102.04 | P42:345:OKGE:SB_DGSE7313:::EHV: | Cumulative Impact | Rebuild line 514715 WOODRNG7 345 515875 REDNGTN7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-204 | TO->FROM | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 | B | 1015 | 0.068809 | 102.2256 | P42:345:OKGE:SB_DGSE7313:::EHV: | Cumulative Impact | Rebuild line 514715 WOODRNG7 345 515875 REDNGTN7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-204 | TO->FROM | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | A | 1806 | 0.032587 | 104.7927 | System Intact | TDF Impact | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-204 | TO->FROM | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | B | 1059 | 0.056513 | 105.0001 | P42:345:OKGE:SB_FTTH7386:::EHV: | Cumulative Impact | Rebuild line 509745 CLARKSV7 345 515224 MUSKOGE7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-204 | TO->FROM | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | B | 1059 | 0.056511 | 105.0075 | Single 515012 RVRVALY7 345 515302 FTSMITH7 345 1 | Cumulative Impact | Rebuild line 509745 CLARKSV7 345 515224 MUSKOGE7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-204 | TO->FROM | 505600 TUPELO 4 138 505602 S BROWN4 138 1 | B | 147 | 0.24721 | 105.0878 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | TDF Impact | Rebuild line 505600 TUPELO 4 138 505602 S BROWN4 138 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-204 | TO->FROM | 505600 TUPELO 4 138 505602 S BROWN4 138 1 | B | 147 | 0.28361 | 105.5558 | Single 520918 FROGVIL4 138 520948 HUGOPP4 138 1 | TDF Impact | Rebuild line 505600 TUPELO 4 138 505602 S BROWN4 138 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-204 | TO->FROM | 505600 TUPELO 4 138 505602 S BROWN4 138 1 | B | 147 | 0.28361 | 106.4089 | Single 520918 FROGVIL4 138 773820 G23-092-TAP 138 1 | TDF Impact | Rebuild line 505600 TUPELO 4 138 505602 S BROWN4 138 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-204 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1011 | 0.036779 | 106.9293 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-204 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1011 | 0.033121 | 107.7039 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-204 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1187 | 0.04257 | 112.2151 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-204 | TO->FROM | 511467 L.E.S.-4 138 3WXFMR 520:LES 5 345 2 | B | 515 | 0.03699 | 114.4267 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-204 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.041393 | 114.4362 | System Intact | TDF Impact | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-204 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.035245 | 114.6025 | System Intact | TDF Impact | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-204 | TO->FROM | 511467 L.E.S.-4 138 3WXFMR 520:LES 5 345 2 | B | 515 | 0.037462 | 114.7092 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-204 | TO->FROM | 511467 L.E.S.-4 138 3WXFMR 520:LES 5 345 2 | B | 515 | 0.035346 | 115.4941 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | TDF Impact | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-204 | TO->FROM | 511467 L.E.S.-4 138 3WXFMR 520:LES 5 345 2 | B | 515 | 0.035969 | 117.1585 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | TDF Impact | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-204 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.035378 | 137.9906 | System Intact | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-204 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.031824 | 138.1985 | System Intact | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-205 | TO->FROM | 530679 SEWRDMW3 115 539692 SEWARD 3 115 1 | B | 40 | 0.089958 | 100.1735 | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | Rebuild line 530679 SEWRDMW3 115 539692 SEWARD 3 115 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-205 | TO->FROM | 640277 MOORE 3 345 640525 TOBIAS 3 345 1 | B | 956 | 0.083567 | 100.5946 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild line 640277 MOORE 3 345 640525 TOBIAS 3 345 1
Thermal | 00NR | 1 | 29SP | T1 | GEN-2024-205 | TO->FROM | 530565 SEWARD 2 69 3WXFMR 531:SEWARD T1 69 1 | B | 53 | 0.23451 | 101.4947 | Single 539666 GBENDTP3 115 539692 SEWARD3 115 1 | TDF Impact | Rebuild 3-winding transformer 530565 SEWARD 2 69 530631 SWRD1 1 12 530679 SEWRDMW3 115 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-205 | TO->FROM | 530679 SEWRDMW3 115 539692 SEWARD 3 115 1 | B | 40 | 0.12399 | 105.8181 | P12:115:SUNC:SAINTJOHN-SAINTJOHN(MIDWEST):::HV: | TDF Impact | Rebuild line 530679 SEWRDMW3 115 539692 SEWARD 3 115 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-205 | TO->FROM | 530565 SEWARD 2 69 3WXFMR 531:SEWARD T1 69 1 | B | 44.79 | 0.23265 | 105.8778 | Single 539666 GBENDTP3 115 539692 SEWARD3 115 1 | TDF Impact | Rebuild 3-winding transformer 530565 SEWARD 2 69 530631 SWRD1 1 12 530679 SEWRDMW3 115 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-205 | TO->FROM | 530565 SEWARD 2 69 3WXFMR 531:SEWARD T1 69 1 | B | 44.79 | 0.23312 | 106.4389 | Single 539666 GBENDTP3 115 539692 SEWARD3 115 1 | TDF Impact | Rebuild 3-winding transformer 530565 SEWARD 2 69 530631 SWRD1 1 12 530679 SEWRDMW3 115 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-205 | TO->FROM | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | B | 101 | 0.59505 | 110.8057 | P12:115:SUNC:SAINTJOHN-SAINTJOHN(MIDWEST):::HV: | TDF Impact | Rebuild line 539692 SEWARD 3 115 539696 ST-JOHN3 115 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-205 | TO->FROM | 530679 SEWRDMW3 115 539692 SEWARD 3 115 1 | B | 40 | 0.23312 | 112.2153 | Single 539666 GBENDTP3 115 539692 SEWARD3 115 1 | TDF Impact | Rebuild line 530679 SEWRDMW3 115 539692 SEWARD 3 115 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-205 | TO->FROM | 530679 SEWRDMW3 115 539692 SEWARD 3 115 1 | B | 40 | 0.23265 | 115.3002 | Single 539666 GBENDTP3 115 539692 SEWARD3 115 1 | TDF Impact | Rebuild line 530679 SEWRDMW3 115 539692 SEWARD 3 115 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-205 | TO->FROM | 530565 SEWARD 2 69 3WXFMR 531:SEWARD T1 69 1 | B | 44.79 | 0.23274 | 117.8065 | Single 539666 GBENDTP3 115 539692 SEWARD3 115 1 | TDF Impact | Rebuild 3-winding transformer 530565 SEWARD 2 69 530631 SWRD1 1 12 530679 SEWRDMW3 115 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-205 | TO->FROM | 539692 SEWARD 3 115 539696 ST-JOHN3 115 1 | B | 101 | 0.59506 | 121.4881 | P12:115:SUNC:SAINTJOHN-SAINTJOHN(MIDWEST):::HV: | TDF Impact | Rebuild line 539692 SEWARD 3 115 539696 ST-JOHN3 115 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-205 | TO->FROM | 530679 SEWRDMW3 115 539692 SEWARD 3 115 1 | B | 40 | 0.23274 | 128.1998 | Single 539666 GBENDTP3 115 539692 SEWARD3 115 1 | TDF Impact | Rebuild line 530679 SEWRDMW3 115 539692 SEWARD 3 115 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | B | 956 | 0.055167 | 100.2221 | P42:345:NPPD:BKR-TOB-3304:::: | Cumulative Impact | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | B | 227 | 0.096538 | 100.4948 | P12:345:NPPD:3517:COOPER 3:ST JOE 3 BTB | Cumulative Impact | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | B | 227 | 0.096538 | 100.4949 | P12:345:AECI-KCPL:FRPRT:STJ:CPR:: | Cumulative Impact | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | B | 227 | 0.096426 | 100.6093 | Single 300076 5FAIRPTB2 161 301559 5FAIRPTXF3 161 1 | Cumulative Impact | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | B | 227 | 0.096426 | 100.6094 | Single 301559 5FAIRPTXF3 161 300039 7FAIRPT 345 3 | Cumulative Impact | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.065135 | 102.136 | P12:161:INDN-KCPL:ECKLES-SIBLEYPL:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | B | 956 | 0.053101 | 102.2146 | P42:345:NPPD:BKR-MOR-3312:::: | Cumulative Impact | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 548802 SUB H 69 548815 SUB M 69 1 | B | 96 | 0.081169 | 102.4189 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | Cumulative Impact | Rebuild line 548802 SUB H 69 548815 SUB M 69 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | B | 227 | 0.11102 | 102.5967 | Single 541205 BLSPE5 161 541235 DUNCAN5 161 1 | Cumulative Impact | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | B | 277 | 0.21515 | 102.9044 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | TDF Impact | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 542987 GRAND 5 161 543666 NEASTN5 161 1 | B | 259 | 0.089345 | 104.1256 | P12:161:KCPL:NORTHEAST-GRANDAVEW-NAV:::HV: | Cumulative Impact | Line - Crosstown - Blue Valley Station 161 kV New Line.idv : 2025 ITP upgrade, PID : 900341, NO NTC
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-206 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.37101 | 104.3265 | Single 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-206 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.37101 | 104.3267 | P12:161:INDN:BLUVLY-ECKLES:::HV: | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 542987 GRAND 5 161 543666 NEASTN5 161 1 | B | 259 | 0.0895 | 104.5774 | P12:161:KCPL:NRTHST-GRANDAVE-NTHEASTCAP:::HV: | Cumulative Impact | Line - Crosstown - Blue Valley Station 161 kV New Line.idv : 2025 ITP upgrade, PID : 900341, NO NTC
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 542987 GRAND 5 161 543666 NEASTN5 161 1 | B | 259 | 0.0895 | 104.5925 | Single 542985 NEASTS5 161 542988 GRANDW5 161 1 | Cumulative Impact | Line - Crosstown - Blue Valley Station 161 kV New Line.idv : 2025 ITP upgrade, PID : 900341, NO NTC
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | B | 277 | 0.21488 | 105.0593 | P12:161:INDN:BLUVLY-SUB M:::HV: | TDF Impact | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 543085 COURTNY2 69 548802 SUB H 69 1 | B | 58 | 0.056474 | 105.2667 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | Cumulative Impact | Rebuild line 543085 COURTNY2 69 548802 SUB H 69 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.056998 | 106.9865 | Single 548815 SUBM 69 548814 SUBM-161 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 543085 COURTNY2 69 548802 SUB H 69 1 | B | 58 | 0.056723 | 107.2237 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | Cumulative Impact | Rebuild line 543085 COURTNY2 69 548802 SUB H 69 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | B | 227 | 0.09692 | 107.6209 | Single 300076 5FAIRPTB2 161 301559 5FAIRPTXF3 161 1 | Cumulative Impact | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | B | 227 | 0.09692 | 107.621 | Single 301559 5FAIRPTXF3 161 300039 7FAIRPT 345 3 | Cumulative Impact | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | B | 227 | 0.097024 | 107.6485 | P12:345:NPPD:3517:COOPER 3:ST JOE 3 BTB | Cumulative Impact | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | B | 227 | 0.097024 | 107.6487 | P12:345:AECI-KCPL:FRPRT:STJ:CPR:: | Cumulative Impact | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 543164 SUGRCK_TP_W2 69 543165 SUGRCK_TP_E2 69 1 | B | 53 | 0.070773 | 108.8766 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | Cumulative Impact | Rebuild line 543164 SUGRCK_TP_W2 69 543165 SUGRCK_TP_E2 69 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.05856 | 109.9155 | Single 548815 SUBM 69 548814 SUBM-161 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 543164 SUGRCK_TP_W2 69 543165 SUGRCK_TP_E2 69 1 | B | 53 | 0.070754 | 110.2063 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | Cumulative Impact | Rebuild line 543164 SUGRCK_TP_W2 69 543165 SUGRCK_TP_E2 69 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | A | 112 | 0.052403 | 110.7651 | System Intact | TDF Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | A | 112 | 0.052247 | 111.8723 | System Intact | TDF Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 | B | 334 | 0.44448 | 112.1602 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | TDF Impact | Rebuild line 541250 SIBLEYPL 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | B | 309 | 0.3912 | 113.6383 | Single 543004 BLUMILS5 161 769861 GEN-2022-144 161 1 | TDF Impact | Rebuild line 543004 BLUMILS5 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | B | 309 | 0.3912 | 113.6383 | Single 769861 GEN-2022-144 161 769862 G22-144XFMR1 34 1 | TDF Impact | Rebuild line 543004 BLUMILS5 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | B | 309 | 0.3912 | 113.6383 | GEN-2022-144_POI_543004_Generator_outage | TDF Impact | Rebuild line 543004 BLUMILS5 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | A | 112 | 0.053839 | 113.7975 | System Intact | TDF Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 548802 SUB H 69 548815 SUB M 69 1 | B | 79 | 0.079776 | 114.1517 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | Cumulative Impact | Rebuild line 548802 SUB H 69 548815 SUB M 69 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.054555 | 114.3171 | P12:161:AECI-INDN:ECKLES-5MOCITYB1:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | A | 112 | 0.053678 | 114.9351 | System Intact | TDF Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 | B | 334 | 0.4446 | 115.0181 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | TDF Impact | Rebuild line 541250 SIBLEYPL 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.054399 | 115.7468 | P12:161:AECI-INDN:ECKLES-5MOCITYB1:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | B | 309 | 0.39142 | 116.001 | GEN-2022-144_POI_543004_Generator_outage | TDF Impact | Rebuild line 543004 BLUMILS5 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | B | 309 | 0.39142 | 116.001 | Single 769861 GEN-2022-144 161 769862 G22-144XFMR1 34 1 | TDF Impact | Rebuild line 543004 BLUMILS5 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | B | 309 | 0.39142 | 116.001 | Single 543004 BLUMILS5 161 769861 GEN-2022-144 161 1 | TDF Impact | Rebuild line 543004 BLUMILS5 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | B | 334 | 0.3906 | 116.7516 | GEN-2022-144_POI_543004_Generator_outage | TDF Impact | Rebuild line 543004 BLUMILS5 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | B | 334 | 0.3906 | 116.7516 | Single 543004 BLUMILS5 161 769861 GEN-2022-144 161 1 | TDF Impact | Rebuild line 543004 BLUMILS5 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | B | 334 | 0.3906 | 116.7516 | Single 769861 GEN-2022-144 161 769862 G22-144XFMR1 34 1 | TDF Impact | Rebuild line 543004 BLUMILS5 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.062185 | 116.8959 | P12:161:INDN-KCPL:ECKLES-SIBLEYPL:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | B | 227 | 0.22 | 116.9935 | P12:161:INDN-KCPL:ECKLES-SIBLEYPL:::HV: | TDF Impact | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.05605 | 117.4467 | P12:161:AECI-INDN:ECKLES-5MOCITYB1:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 548802 SUB H 69 548815 SUB M 69 1 | B | 79 | 0.080265 | 117.5648 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | Cumulative Impact | Rebuild line 548802 SUB H 69 548815 SUB M 69 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.089697 | 117.8053 | Single 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.062007 | 118.1547 | P12:161:INDN-KCPL:ECKLES-SIBLEYPL:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.089697 | 118.3509 | P12:161:INDN:BLUVLY-ECKLES:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.055889 | 118.9156 | P12:161:AECI-INDN:ECKLES-5MOCITYB1:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.063889 | 120.0962 | P12:161:INDN-KCPL:ECKLES-SIBLEYPL:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.092154 | 121.0304 | Single 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.063706 | 121.3894 | P12:161:INDN-KCPL:ECKLES-SIBLEYPL:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 | B | 334 | 0.44243 | 121.4264 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | TDF Impact | Rebuild line 541250 SIBLEYPL 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 | B | 334 | 0.45024 | 121.4761 | P12:161:INDN:BLUVLY-SUB M:::HV: | TDF Impact | Rebuild line 541250 SIBLEYPL 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.092154 | 121.591 | P12:161:INDN:BLUVLY-ECKLES:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 | B | 334 | 0.45067 | 122.1591 | P12:161:INDN:BLUVLY-SUB M:::HV: | TDF Impact | Rebuild line 541250 SIBLEYPL 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 543164 SUGRCK_TP_W2 69 543165 SUGRCK_TP_E2 69 1 | B | 53 | 0.071642 | 125.9223 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | Cumulative Impact | Rebuild line 543164 SUGRCK_TP_W2 69 543165 SUGRCK_TP_E2 69 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 | B | 334 | 0.4472 | 126.3305 | P12:161:INDN:BLUVLY-SUB M:::HV: | TDF Impact | Rebuild line 541250 SIBLEYPL 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | B | 227 | 0.22045 | 126.5957 | P12:161:INDN-KCPL:ECKLES-SIBLEYPL:::HV: | TDF Impact | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.089714 | 126.6455 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.073926 | 127.5873 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | B | 227 | 0.21653 | 129.594 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | TDF Impact | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.075184 | 129.7506 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.055926 | 129.8128 | Single 548815 SUBM 69 548814 SUBM-161 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.092172 | 130.1126 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.05583 | 131.1303 | Single 548815 SUBM 69 548814 SUBM-161 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.088089 | 132.5565 | Single 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.088089 | 133.1083 | P12:161:INDN:BLUVLY-ECKLES:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.089697 | 133.146 | Single 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.057458 | 133.3666 | Single 548815 SUBM 69 548814 SUBM-161 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.087841 | 134.0414 | Single 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.087841 | 134.5876 | P12:161:INDN:BLUVLY-ECKLES:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.05736 | 134.7203 | Single 548815 SUBM 69 548814 SUBM-161 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | B | 227 | 0.21685 | 136.1003 | P12:161:INDN:BLUVLY-SUB M:::HV: | TDF Impact | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 548815 SUB M 69 548814 SUB M-161 161 1 | B | 112 | 0.096046 | 136.1066 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548814 SUB M-161 161 548815 SUB M 69 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.090502 | 136.1855 | Single 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.090502 | 136.7525 | P12:161:INDN:BLUVLY-ECKLES:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.092154 | 136.7911 | Single 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 548802 SUB H 69 548806 BLUVLY 69 1 | B | 72 | 0.084945 | 136.8184 | P12:161:INDN:BLUVLY-SUB M:::HV: | Cumulative Impact | Rebuild line 548802 SUB H 69 548806 BLUVLY 69 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.090247 | 137.711 | Single 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.090247 | 138.2722 | P12:161:INDN:BLUVLY-ECKLES:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | B | 227 | 0.2167 | 139.2489 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | TDF Impact | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.088821 | 143.4912 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | B | 227 | 0.21717 | 143.8483 | P12:161:INDN:BLUVLY-SUB M:::HV: | TDF Impact | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.08839 | 144.9665 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.091255 | 147.4196 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.088089 | 147.573 | Single 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 548815 SUB M 69 548814 SUB M-161 161 1 | B | 112 | 0.093952 | 147.8714 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548814 SUB M-161 161 548815 SUB M 69 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.087841 | 148.8633 | Single 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.090812 | 148.9352 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 548815 SUB M 69 548814 SUB M-161 161 1 | B | 112 | 0.094967 | 150.5222 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548814 SUB M-161 161 548815 SUB M 69 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.49814 | 150.933 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.49809 | 151.0379 | Single 300098 5MOCITYB2 161 301563 5MOCITYB1 161 Z1 | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | A | 334 | 0.48675 | 151.0615 | System Intact | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.49852 | 151.2045 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.090502 | 151.6131 | Single 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.48775 | 152.1075 | GEN542951 5 | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.072118 | 152.4638 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.090247 | 152.9387 | Single 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.49745 | 153.2977 | Single 541205 BLSPE5 161 541235 DUNCAN5 161 1 | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.071783 | 153.6184 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.4979 | 153.9755 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.49442 | 154.1261 | Single 548815 SUBM 69 548814 SUBM-161 161 1 | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.49827 | 154.2455 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | A | 311 | 0.48818 | 154.3906 | System Intact | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.073358 | 155.0815 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.49713 | 155.3564 | Single 541205 BLSPE5 161 541235 DUNCAN5 161 1 | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.073022 | 156.2682 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.51164 | 156.5884 | P12:161:AECI-INDN:ECKLES-5MOCITYB1:::HV: | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.4932 | 156.8353 | P12:161:AECI-INDN:ECKLES-5LEVASY:::HV: | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.4932 | 156.8373 | P12:161:AECI:PITTSVIL:ECKLES:1:: | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.49437 | 157.5714 | Single 548815 SUBM 69 548814 SUBM-161 161 1 | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | A | 311 | 0.48798 | 157.7045 | System Intact | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.49667 | 158.547 | Single 300098 5MOCITYB2 161 301563 5MOCITYB1 161 Z1 | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.4929 | 159.244 | Single 548815 SUBM 69 548814 SUBM-161 161 1 | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.56183 | 159.8592 | P12:161:INDN-KCPL:ECKLES-SIBLEYPL:::HV: | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.49597 | 160.5088 | Single 541205 BLSPE5 161 541235 DUNCAN5 161 1 | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.51151 | 161.0318 | P12:161:AECI-INDN:ECKLES-5MOCITYB1:::HV: | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.51009 | 162.7484 | P12:161:AECI-INDN:ECKLES-5MOCITYB1:::HV: | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.56173 | 163.4226 | P12:161:INDN-KCPL:ECKLES-SIBLEYPL:::HV: | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.56015 | 169.0404 | P12:161:INDN-KCPL:ECKLES-SIBLEYPL:::HV: | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 548802 SUB H 69 548806 BLUVLY 69 1 | B | 58 | 0.083037 | 171.565 | P12:161:INDN:BLUVLY-SUB M:::HV: | Cumulative Impact | Rebuild line 548802 SUB H 69 548806 BLUVLY 69 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.13492 | 173.2062 | P12:161:INDN:BLUVLY-SUB M:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 548802 SUB H 69 548806 BLUVLY 69 1 | B | 58 | 0.083072 | 173.8468 | P12:161:INDN:BLUVLY-SUB M:::HV: | Cumulative Impact | Rebuild line 548802 SUB H 69 548806 BLUVLY 69 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.13862 | 177.948 | P12:161:INDN:BLUVLY-SUB M:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.13199 | 191.6339 | P12:161:INDN:BLUVLY-SUB M:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.13217 | 191.8914 | P12:161:INDN:BLUVLY-SUB M:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | B | 309 | 0.72597 | 193.674 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | TDF Impact | Rebuild line 543004 BLUMILS5 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.038325 | 194.842 | System Intact | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | B | 334 | 0.72207 | 195.8245 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | TDF Impact | Rebuild line 543004 BLUMILS5 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.1356 | 196.8803 | P12:161:INDN:BLUVLY-SUB M:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.13579 | 197.1448 | P12:161:INDN:BLUVLY-SUB M:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | B | 309 | 0.72583 | 198.5193 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | TDF Impact | Rebuild line 543004 BLUMILS5 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | B | 334 | 0.72646 | 202.7077 | P12:161:INDN:BLUVLY-SUB M:::HV: | TDF Impact | Rebuild line 543004 BLUMILS5 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.040526 | 202.7501 | System Intact | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.79537 | 207.1634 | P12:161:INDN:BLUVLY-ECKLES:::HV: | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.79537 | 207.562 | Single 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | B | 309 | 0.73205 | 209.2685 | P12:161:INDN:BLUVLY-SUB M:::HV: | TDF Impact | Rebuild line 543004 BLUMILS5 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | B | 309 | 0.73241 | 210.1332 | P12:161:INDN:BLUVLY-SUB M:::HV: | TDF Impact | Rebuild line 543004 BLUMILS5 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.79538 | 211.9817 | P12:161:INDN:BLUVLY-ECKLES:::HV: | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.79538 | 212.3817 | Single 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.79228 | 223.448 | P12:161:INDN:BLUVLY-ECKLES:::HV: | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.79228 | 223.8368 | Single 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.053288 | 242.4879 | System Intact | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.051701 | 247.7008 | Single 640600 DAYKIN3 345 771999 G23-222-POI 345 1 | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.059212 | 250.2801 | P55:345:MEC:NORTHBORO | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.059212 | 250.2801 | P23:345:MEC:NORTHBORO:901::EHV: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.054212 | 250.332 | Single 640076 BEATRCE7 115 640208 HARBINE7 115 1 | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.79537 | 251.3484 | Single 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.059212 | 251.4352 | P12:345:MEC:ORIENT:NORTHBORO:1 | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.059217 | 251.4821 | P23:345:MEC:ORIENT:902::EHV: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.059236 | 251.8126 | P55:345:MEC:ORIENT | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-206 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.79538 | 256.1148 | Single 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-206 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.052871 | 260.7181 | Single 640088 BPSSUB7 115 771999 G23-222-POI 345 771998 'NEW_TER_BPS ' 13 1 | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-206 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.79228 | 267.3731 | Single 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | B | 956 | 0.055172 | 100.2221 | P42:345:NPPD:BKR-TOB-3304:::: | Cumulative Impact | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | B | 227 | 0.099057 | 100.4948 | P12:345:NPPD:3517:COOPER 3:ST JOE 3 BTB | Cumulative Impact | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | B | 227 | 0.099057 | 100.4949 | P12:345:AECI-KCPL:FRPRT:STJ:CPR:: | Cumulative Impact | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | B | 227 | 0.098946 | 100.6093 | Single 300076 5FAIRPTB2 161 301559 5FAIRPTXF3 161 1 | Cumulative Impact | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | B | 227 | 0.098946 | 100.6094 | Single 301559 5FAIRPTXF3 161 300039 7FAIRPT 345 3 | Cumulative Impact | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.064587 | 102.136 | P12:161:INDN-KCPL:ECKLES-SIBLEYPL:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | B | 956 | 0.053109 | 102.2146 | P42:345:NPPD:BKR-MOR-3312:::: | Cumulative Impact | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 548802 SUB H 69 548815 SUB M 69 1 | B | 96 | 0.080081 | 102.4189 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | Cumulative Impact | Rebuild line 548802 SUB H 69 548815 SUB M 69 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | B | 227 | 0.11372 | 102.5967 | Single 541205 BLSPE5 161 541235 DUNCAN5 161 1 | Cumulative Impact | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | B | 277 | 0.21628 | 102.9044 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | TDF Impact | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 542987 GRAND 5 161 543666 NEASTN5 161 1 | B | 259 | 0.088827 | 104.1256 | P12:161:KCPL:NORTHEAST-GRANDAVEW-NAV:::HV: | Cumulative Impact | Line - Crosstown - Blue Valley Station 161 kV New Line.idv : 2025 ITP upgrade, PID : 900341, NO NTC
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-207 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.37101 | 104.3265 | Single 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-207 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.37101 | 104.3267 | P12:161:INDN:BLUVLY-ECKLES:::HV: | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 542987 GRAND 5 161 543666 NEASTN5 161 1 | B | 259 | 0.088981 | 104.5774 | P12:161:KCPL:NRTHST-GRANDAVE-NTHEASTCAP:::HV: | Cumulative Impact | Line - Crosstown - Blue Valley Station 161 kV New Line.idv : 2025 ITP upgrade, PID : 900341, NO NTC
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 542987 GRAND 5 161 543666 NEASTN5 161 1 | B | 259 | 0.088981 | 104.5925 | Single 542985 NEASTS5 161 542988 GRANDW5 161 1 | Cumulative Impact | Line - Crosstown - Blue Valley Station 161 kV New Line.idv : 2025 ITP upgrade, PID : 900341, NO NTC
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | B | 277 | 0.216 | 105.0593 | P12:161:INDN:BLUVLY-SUB M:::HV: | TDF Impact | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 543085 COURTNY2 69 548802 SUB H 69 1 | B | 58 | 0.055633 | 105.2667 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | Cumulative Impact | Rebuild line 543085 COURTNY2 69 548802 SUB H 69 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.056219 | 106.9865 | Single 548815 SUBM 69 548814 SUBM-161 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 543085 COURTNY2 69 548802 SUB H 69 1 | B | 58 | 0.055882 | 107.2237 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | Cumulative Impact | Rebuild line 543085 COURTNY2 69 548802 SUB H 69 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | B | 227 | 0.099439 | 107.6209 | Single 300076 5FAIRPTB2 161 301559 5FAIRPTXF3 161 1 | Cumulative Impact | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | B | 227 | 0.099439 | 107.621 | Single 301559 5FAIRPTXF3 161 300039 7FAIRPT 345 3 | Cumulative Impact | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | B | 227 | 0.099544 | 107.6485 | P12:345:NPPD:3517:COOPER 3:ST JOE 3 BTB | Cumulative Impact | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | B | 227 | 0.099544 | 107.6487 | P12:345:AECI-KCPL:FRPRT:STJ:CPR:: | Cumulative Impact | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 543164 SUGRCK_TP_W2 69 543165 SUGRCK_TP_E2 69 1 | B | 53 | 0.069926 | 108.8766 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | Cumulative Impact | Rebuild line 543164 SUGRCK_TP_W2 69 543165 SUGRCK_TP_E2 69 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.05776 | 109.9155 | Single 548815 SUBM 69 548814 SUBM-161 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 543164 SUGRCK_TP_W2 69 543165 SUGRCK_TP_E2 69 1 | B | 53 | 0.069906 | 110.2063 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | Cumulative Impact | Rebuild line 543164 SUGRCK_TP_W2 69 543165 SUGRCK_TP_E2 69 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | A | 112 | 0.051695 | 110.7651 | System Intact | TDF Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | A | 112 | 0.051541 | 111.8723 | System Intact | TDF Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | B | 277 | 0.30112 | 111.917 | Single 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | TDF Impact | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 | B | 334 | 0.44674 | 112.1602 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | TDF Impact | Rebuild line 541250 SIBLEYPL 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | B | 309 | 0.39896 | 113.6383 | Single 543004 BLUMILS5 161 769861 GEN-2022-144 161 1 | TDF Impact | Rebuild line 543004 BLUMILS5 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | B | 309 | 0.39896 | 113.6383 | Single 769861 GEN-2022-144 161 769862 G22-144XFMR1 34 1 | TDF Impact | Rebuild line 543004 BLUMILS5 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | B | 309 | 0.39896 | 113.6383 | GEN-2022-144_POI_543004_Generator_outage | TDF Impact | Rebuild line 543004 BLUMILS5 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | A | 112 | 0.053111 | 113.7975 | System Intact | TDF Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 548802 SUB H 69 548815 SUB M 69 1 | B | 79 | 0.078705 | 114.1517 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | Cumulative Impact | Rebuild line 548802 SUB H 69 548815 SUB M 69 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.053902 | 114.3171 | P12:161:AECI-INDN:ECKLES-5MOCITYB1:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | A | 112 | 0.052953 | 114.9351 | System Intact | TDF Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 | B | 334 | 0.44686 | 115.0181 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | TDF Impact | Rebuild line 541250 SIBLEYPL 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.053748 | 115.7468 | P12:161:AECI-INDN:ECKLES-5MOCITYB1:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | B | 309 | 0.39918 | 116.001 | GEN-2022-144_POI_543004_Generator_outage | TDF Impact | Rebuild line 543004 BLUMILS5 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | B | 309 | 0.39918 | 116.001 | Single 769861 GEN-2022-144 161 769862 G22-144XFMR1 34 1 | TDF Impact | Rebuild line 543004 BLUMILS5 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | B | 309 | 0.39918 | 116.001 | Single 543004 BLUMILS5 161 769861 GEN-2022-144 161 1 | TDF Impact | Rebuild line 543004 BLUMILS5 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | B | 334 | 0.39837 | 116.7516 | GEN-2022-144_POI_543004_Generator_outage | TDF Impact | Rebuild line 543004 BLUMILS5 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | B | 334 | 0.39837 | 116.7516 | Single 543004 BLUMILS5 161 769861 GEN-2022-144 161 1 | TDF Impact | Rebuild line 543004 BLUMILS5 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | B | 334 | 0.39837 | 116.7516 | Single 769861 GEN-2022-144 161 769862 G22-144XFMR1 34 1 | TDF Impact | Rebuild line 543004 BLUMILS5 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.061662 | 116.8959 | P12:161:INDN-KCPL:ECKLES-SIBLEYPL:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | B | 227 | 0.22484 | 116.9935 | P12:161:INDN-KCPL:ECKLES-SIBLEYPL:::HV: | TDF Impact | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.055379 | 117.4467 | P12:161:AECI-INDN:ECKLES-5MOCITYB1:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 548802 SUB H 69 548815 SUB M 69 1 | B | 79 | 0.079188 | 117.5648 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | Cumulative Impact | Rebuild line 548802 SUB H 69 548815 SUB M 69 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.089697 | 117.8053 | Single 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.061486 | 118.1547 | P12:161:INDN-KCPL:ECKLES-SIBLEYPL:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.089697 | 118.3509 | P12:161:INDN:BLUVLY-ECKLES:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.055221 | 118.9156 | P12:161:AECI-INDN:ECKLES-5MOCITYB1:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.063352 | 120.0962 | P12:161:INDN-KCPL:ECKLES-SIBLEYPL:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.092154 | 121.0304 | Single 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.063171 | 121.3894 | P12:161:INDN-KCPL:ECKLES-SIBLEYPL:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 | B | 334 | 0.44472 | 121.4264 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | TDF Impact | Rebuild line 541250 SIBLEYPL 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 | B | 334 | 0.4524 | 121.4761 | P12:161:INDN:BLUVLY-SUB M:::HV: | TDF Impact | Rebuild line 541250 SIBLEYPL 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.092154 | 121.591 | P12:161:INDN:BLUVLY-ECKLES:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 | B | 334 | 0.45283 | 122.1591 | P12:161:INDN:BLUVLY-SUB M:::HV: | TDF Impact | Rebuild line 541250 SIBLEYPL 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 543164 SUGRCK_TP_W2 69 543165 SUGRCK_TP_E2 69 1 | B | 53 | 0.070783 | 125.9223 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | Cumulative Impact | Rebuild line 543164 SUGRCK_TP_W2 69 543165 SUGRCK_TP_E2 69 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 | B | 334 | 0.4494 | 126.3305 | P12:161:INDN:BLUVLY-SUB M:::HV: | TDF Impact | Rebuild line 541250 SIBLEYPL 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | B | 227 | 0.22529 | 126.5957 | P12:161:INDN-KCPL:ECKLES-SIBLEYPL:::HV: | TDF Impact | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.08854 | 126.6455 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.072929 | 127.5873 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | B | 227 | 0.21764 | 129.594 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | TDF Impact | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.074169 | 129.7506 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.055161 | 129.8128 | Single 548815 SUBM 69 548814 SUBM-161 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.090965 | 130.1126 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | A | 334 | 0.60163 | 130.375 | System Intact | TDF Impact | Add line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.055067 | 131.1303 | Single 548815 SUBM 69 548814 SUBM-161 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.088089 | 132.5565 | Single 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.088089 | 133.1083 | P12:161:INDN:BLUVLY-ECKLES:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.089697 | 133.146 | Single 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.056672 | 133.3666 | Single 548815 SUBM 69 548814 SUBM-161 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.087841 | 134.0414 | Single 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.087841 | 134.5876 | P12:161:INDN:BLUVLY-ECKLES:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.056576 | 134.7203 | Single 548815 SUBM 69 548814 SUBM-161 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | B | 227 | 0.21794 | 136.1003 | P12:161:INDN:BLUVLY-SUB M:::HV: | TDF Impact | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 548815 SUB M 69 548814 SUB M-161 161 1 | B | 112 | 0.094795 | 136.1066 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548814 SUB M-161 161 548815 SUB M 69 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.090502 | 136.1855 | Single 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.090502 | 136.7525 | P12:161:INDN:BLUVLY-ECKLES:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.092154 | 136.7911 | Single 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 548802 SUB H 69 548806 BLUVLY 69 1 | B | 72 | 0.083855 | 136.8184 | P12:161:INDN:BLUVLY-SUB M:::HV: | Cumulative Impact | Rebuild line 548802 SUB H 69 548806 BLUVLY 69 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.090247 | 137.711 | Single 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.090247 | 138.2722 | P12:161:INDN:BLUVLY-ECKLES:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 334 | 0.60951 | 138.394 | Single 541205 BLSPE5 161 541235 DUNCAN5 161 1 | TDF Impact | Add line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | B | 227 | 0.21781 | 139.2489 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | TDF Impact | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 334 | 0.6143 | 139.5581 | Single 300098 5MOCITYB2 161 301563 5MOCITYB1 161 Z1 | TDF Impact | Add line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 | B | 334 | 0.61778 | 141.2841 | Single 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | TDF Impact | Rebuild line 541250 SIBLEYPL 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 334 | 0.60163 | 141.6936 | Single 548807 BLUVLY-161 161 762669 GEN-2018-031 161 1 | TDF Impact | Add line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 | B | 334 | 0.61744 | 142.1462 | Single 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | TDF Impact | Rebuild line 541250 SIBLEYPL 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 541250 SIBLEYPL 161 548808 ECKLES-161 161 1 | B | 334 | 0.61764 | 142.2515 | Single 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | TDF Impact | Rebuild line 541250 SIBLEYPL 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.087659 | 143.4912 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | B | 227 | 0.21827 | 143.8483 | P12:161:INDN:BLUVLY-SUB M:::HV: | TDF Impact | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 334 | 0.63066 | 144.4894 | P12:161:AECI-INDN:ECKLES-5MOCITYB1:::HV: | TDF Impact | Add line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.087233 | 144.9665 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.09006 | 147.4196 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.088089 | 147.573 | Single 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 548815 SUB M 69 548814 SUB M-161 161 1 | B | 112 | 0.092727 | 147.8714 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548814 SUB M-161 161 548815 SUB M 69 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.087841 | 148.8633 | Single 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.089623 | 148.9352 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | B | 227 | 0.30124 | 149.0441 | Single 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | TDF Impact | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 548815 SUB M 69 548814 SUB M-161 161 1 | B | 112 | 0.09373 | 150.5222 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548814 SUB M-161 161 548815 SUB M 69 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.49191 | 150.933 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.49243 | 151.0379 | Single 300098 5MOCITYB2 161 301563 5MOCITYB1 161 Z1 | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | A | 334 | 0.48067 | 151.0615 | System Intact | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.49228 | 151.2045 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.090502 | 151.6131 | Single 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.48165 | 152.1075 | GEN542951 5 | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.071144 | 152.4638 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.090247 | 152.9387 | Single 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.49147 | 153.2977 | Single 541205 BLSPE5 161 541235 DUNCAN5 161 1 | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.070814 | 153.6184 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.49167 | 153.9755 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 334 | 0.70067 | 153.99 | P12:161:INDN-KCPL:ECKLES-SIBLEYPL:::HV: | TDF Impact | Add line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.48823 | 154.1261 | Single 548815 SUBM 69 548814 SUBM-161 161 1 | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.49204 | 154.2455 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | A | 311 | 0.48209 | 154.3906 | System Intact | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.072367 | 155.0815 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.49115 | 155.3564 | Single 541205 BLSPE5 161 541235 DUNCAN5 161 1 | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 334 | 0.60163 | 155.9387 | Single 548807 BLUVLY-161 161 783151 GEN-2024-206 161 1 | TDF Impact | Add line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.072035 | 156.2682 | Single 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 334 | 0.60163 | 156.323 | GEN-2024-206_POI_548807_Generator_outage | TDF Impact | Add line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | B | 227 | 0.30146 | 156.472 | Single 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | TDF Impact | Rebuild line 301563 5MOCITYB1 161 548808 ECKLES-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.50615 | 156.5884 | P12:161:AECI-INDN:ECKLES-5MOCITYB1:::HV: | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.48719 | 156.8353 | P12:161:AECI-INDN:ECKLES-5LEVASY:::HV: | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.48719 | 156.8373 | P12:161:AECI:PITTSVIL:ECKLES:1:: | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.48817 | 157.5714 | Single 548815 SUBM 69 548814 SUBM-161 161 1 | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | A | 311 | 0.48189 | 157.7045 | System Intact | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.49102 | 158.547 | Single 300098 5MOCITYB2 161 301563 5MOCITYB1 161 Z1 | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.48672 | 159.244 | Single 548815 SUBM 69 548814 SUBM-161 161 1 | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.55713 | 159.8592 | P12:161:INDN-KCPL:ECKLES-SIBLEYPL:::HV: | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 309 | 0.61355 | 159.9654 | Single 300098 5MOCITYB2 161 301563 5MOCITYB1 161 Z1 | TDF Impact | Add line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 309 | 0.60866 | 160.2452 | Single 541205 BLSPE5 161 541235 DUNCAN5 161 1 | TDF Impact | Add line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.49 | 160.5088 | Single 541205 BLSPE5 161 541235 DUNCAN5 161 1 | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.50602 | 161.0318 | P12:161:AECI-INDN:ECKLES-5MOCITYB1:::HV: | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.50462 | 162.7484 | P12:161:AECI-INDN:ECKLES-5MOCITYB1:::HV: | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.55703 | 163.4226 | P12:161:INDN-KCPL:ECKLES-SIBLEYPL:::HV: | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 309 | 0.60898 | 163.6397 | Single 541205 BLSPE5 161 541235 DUNCAN5 161 1 | TDF Impact | Add line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 309 | 0.61367 | 164.3883 | Single 300098 5MOCITYB2 161 301563 5MOCITYB1 161 Z1 | TDF Impact | Add line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 309 | 0.60082 | 164.9327 | Single 548807 BLUVLY-161 161 762669 GEN-2018-031 161 1 | TDF Impact | Add line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 309 | 0.60104 | 167.2899 | Single 548807 BLUVLY-161 161 762669 GEN-2018-031 161 1 | TDF Impact | Add line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | A | 281 | 0.60082 | 167.6873 | System Intact | TDF Impact | Add line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.55546 | 169.0404 | P12:161:INDN-KCPL:ECKLES-SIBLEYPL:::HV: | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | A | 281 | 0.60104 | 170.2736 | System Intact | TDF Impact | Add line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 309 | 0.62998 | 171.0079 | P12:161:AECI-INDN:ECKLES-5MOCITYB1:::HV: | TDF Impact | Add line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 548802 SUB H 69 548806 BLUVLY 69 1 | B | 58 | 0.081972 | 171.565 | P12:161:INDN:BLUVLY-SUB M:::HV: | Cumulative Impact | Rebuild line 548802 SUB H 69 548806 BLUVLY 69 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 309 | 0.63011 | 171.5975 | P12:161:AECI-INDN:ECKLES-5MOCITYB1:::HV: | TDF Impact | Add line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.13318 | 173.2062 | P12:161:INDN:BLUVLY-SUB M:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 548802 SUB H 69 548806 BLUVLY 69 1 | B | 58 | 0.082006 | 173.8468 | P12:161:INDN:BLUVLY-SUB M:::HV: | Cumulative Impact | Rebuild line 548802 SUB H 69 548806 BLUVLY 69 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 309 | 0.6999 | 175.8771 | P12:161:INDN-KCPL:ECKLES-SIBLEYPL:::HV: | TDF Impact | Add line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 309 | 0.7 | 177.5131 | P12:161:INDN-KCPL:ECKLES-SIBLEYPL:::HV: | TDF Impact | Add line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.13683 | 177.948 | P12:161:INDN:BLUVLY-SUB M:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 309 | 0.60082 | 180.7944 | Single 548807 BLUVLY-161 161 783151 GEN-2024-206 161 1 | TDF Impact | Add line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 309 | 0.60082 | 181.2476 | GEN-2024-206_POI_548807_Generator_outage | TDF Impact | Add line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 309 | 0.60104 | 183.1612 | Single 548807 BLUVLY-161 161 783151 GEN-2024-206 161 1 | TDF Impact | Add line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 309 | 0.60104 | 183.6144 | GEN-2024-206_POI_548807_Generator_outage | TDF Impact | Add line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.13028 | 191.6339 | P12:161:INDN:BLUVLY-SUB M:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 1 | B | 112 | 0.13045 | 191.8914 | P12:161:INDN:BLUVLY-SUB M:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | B | 309 | 0.72955 | 193.674 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | TDF Impact | Rebuild line 543004 BLUMILS5 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.038303 | 194.842 | System Intact | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | B | 334 | 0.7257 | 195.8245 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | TDF Impact | Rebuild line 543004 BLUMILS5 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.13385 | 196.8803 | P12:161:INDN:BLUVLY-SUB M:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 548806 BLUVLY 69 548807 BLUVLY-161 161 2 | B | 112 | 0.13403 | 197.1448 | P12:161:INDN:BLUVLY-SUB M:::HV: | Cumulative Impact | Rebuild 2-winding transformer 548806 BLUVLY 69 548807 BLUVLY-161 161 2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | B | 309 | 0.72941 | 198.5193 | P12:161:INDN-KCPL:SUB M-HAWTHRN5:::HV: | TDF Impact | Rebuild line 543004 BLUMILS5 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | B | 334 | 0.73 | 202.7077 | P12:161:INDN:BLUVLY-SUB M:::HV: | TDF Impact | Rebuild line 543004 BLUMILS5 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.040504 | 202.7501 | System Intact | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.79537 | 207.1634 | P12:161:INDN:BLUVLY-ECKLES:::HV: | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.79537 | 207.562 | Single 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | B | 309 | 0.73552 | 209.2685 | P12:161:INDN:BLUVLY-SUB M:::HV: | TDF Impact | Rebuild line 543004 BLUMILS5 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | B | 309 | 0.73587 | 210.1332 | P12:161:INDN:BLUVLY-SUB M:::HV: | TDF Impact | Rebuild line 543004 BLUMILS5 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.79538 | 211.9817 | P12:161:INDN:BLUVLY-ECKLES:::HV: | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.79538 | 212.3817 | Single 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 334 | 1 | 222.7205 | Single 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | TDF Impact | Add line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 334 | 1 | 222.8307 | P12:161:INDN:BLUVLY-ECKLES:::HV: | TDF Impact | Add line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.79228 | 223.448 | P12:161:INDN:BLUVLY-ECKLES:::HV: | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.79228 | 223.8368 | Single 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | B | 334 | 1 | 224.2817 | Single 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | TDF Impact | Rebuild line 543004 BLUMILS5 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 309 | 1 | 242.2056 | Single 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | TDF Impact | Add line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 309 | 1 | 242.2499 | Single 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | TDF Impact | Add line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 309 | 1 | 242.3134 | P12:161:INDN:BLUVLY-ECKLES:::HV: | TDF Impact | Add line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 309 | 1 | 242.3556 | P12:161:INDN:BLUVLY-ECKLES:::HV: | TDF Impact | Add line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.053278 | 242.4879 | System Intact | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | B | 309 | 1 | 242.7652 | Single 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | TDF Impact | Rebuild line 543004 BLUMILS5 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 543004 BLUMILS5 161 783180 G24-207-TAP 161 1 | B | 309 | 1 | 242.7931 | Single 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | TDF Impact | Rebuild line 543004 BLUMILS5 161 783180 G24-207-TAP 161 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.051692 | 247.7008 | Single 640600 DAYKIN3 345 771999 G23-222-POI 345 1 | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.059196 | 250.2801 | P55:345:MEC:NORTHBORO | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.059196 | 250.2801 | P23:345:MEC:NORTHBORO:901::EHV: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.054205 | 250.332 | Single 640076 BEATRCE7 115 640208 HARBINE7 115 1 | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.79537 | 251.3484 | Single 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.059196 | 251.4352 | P12:345:MEC:ORIENT:NORTHBORO:1 | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.059201 | 251.4821 | P23:345:MEC:ORIENT:902::EHV: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.05922 | 251.8126 | P55:345:MEC:ORIENT | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.79538 | 256.1148 | Single 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.052863 | 260.7181 | Single 640088 BPSSUB7 115 771999 G23-222-POI 345 771998 'NEW_TER_BPS ' 13 1 | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 542973 HAWTHS5 161 548814 SUB M-161 161 1 | B | 334 | 0.79228 | 267.3731 | Single 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | TDF Impact | Add line and rebuild line 542973 HAWTHS5 161 548814 SUB M-161 161 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-207 | TO->FROM | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 334 | 1 | 277.815 | Single 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | TDF Impact | Add line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-207 | TO->FROM | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 309 | 1 | 302.1205 | Single 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | TDF Impact | Add line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-207 | TO->FROM | 548807 BLUVLY-161 161 783180 G24-207-TAP 161 1 | B | 309 | 1 | 302.2631 | Single 543004 BLUMILS5 161 548808 ECKLES-161 161 1 | TDF Impact | Add line 548807 BLUVLY-161 161 783180 G24-207-TAP 161 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-211 | TO->FROM | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | B | 956 | 0.11018 | 100.2221 | P42:345:NPPD:BKR-TOB-3304:::: | Cumulative Impact | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-211 | TO->FROM | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | B | 956 | 0.078451 | 100.3823 | P42:345:NPPD:BKR-TOB-3304:::: | Cumulative Impact | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-211 | TO->FROM | 645454 S3454 3 345 645740 S3740 3 345 1 | B | 1792 | 0.57989 | 100.7287 | P12:345:OPPD:S3455-S3740:::EHV: | TDF Impact | Rebuild line 645454 S3454 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-211 | TO->FROM | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | B | 956 | 0.075801 | 101.3156 | Single 640312 PAULINE3 345 640525 TOBIAS3 345 1 | Cumulative Impact | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-211 | TO->FROM | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | B | 956 | 0.11294 | 102.2146 | P42:345:NPPD:BKR-MOR-3312:::: | Cumulative Impact | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-211 | TO->FROM | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | B | 956 | 0.082328 | 102.6296 | P42:345:NPPD:BKR-TOB-3304:::: | Cumulative Impact | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-211 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | A | 1195 | 0.29088 | 103.713 | System Intact | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-211 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | A | 1195 | 0.29135 | 104.0836 | System Intact | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-211 | TO->FROM | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | B | 956 | 0.079674 | 104.1025 | Single 640312 PAULINE3 345 640525 TOBIAS3 345 1 | Cumulative Impact | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-211 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.2958 | 104.614 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-211 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.28836 | 105.026 | P12:345:OPPD:LX004::S3454.S3455.CKT1:: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-211 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.27024 | 105.343 | P23:345:OPPD:S3456-S3458&CB:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-211 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.28728 | 105.6441 | P12:345:OPPD:LX007::S3458.S3456.CKT1:: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-211 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.298 | 106.113 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-211 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.29053 | 106.3263 | P12:345:OPPD:LX004::S3454.S3455.CKT1:: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-211 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.29868 | 106.5333 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-211 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.29116 | 106.7885 | P12:345:OPPD:LX004::S3454.S3455.CKT1:: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-211 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.34309 | 107.6426 | P12:345:OPPD:LX007::S3458.S3456.CKT1:: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-211 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.27096 | 109.6596 | P23:345:OPPD:S3456-S3458&CB:::EHV: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-211 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.28905 | 109.6889 | P12:345:OPPD:LX007::S3458.S3456.CKT1:: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-211 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.27152 | 109.8739 | P23:345:OPPD:S3456-S3458&CB:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-211 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.28972 | 110.0566 | P12:345:OPPD:LX007::S3458.S3456.CKT1:: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-211 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.38949 | 110.6628 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-211 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.36399 | 111.4422 | P12:345:OPPD:LX004::S3454.S3455.CKT1:: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-211 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.52993 | 114.4569 | P12:345:OPPD:LX008::S3458.S3740.CKT1:: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-211 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.52176 | 115.3799 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-211 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.52169 | 115.4582 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-211 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.29747 | 116.2686 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-211 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.29812 | 116.8671 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-211 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.29004 | 116.9566 | P12:345:OPPD:LX004::S3454.S3455.CKT1:: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-211 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.52222 | 117.0346 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-211 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.52233 | 117.1341 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-211 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.29065 | 117.6224 | P12:345:OPPD:LX004::S3454.S3455.CKT1:: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-211 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.2717 | 119.2334 | P23:345:OPPD:S3456-S3458&CB:::EHV: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-211 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.27226 | 119.5938 | P23:345:OPPD:S3456-S3458&CB:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-211 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.2892 | 119.7072 | P12:345:OPPD:LX007::S3458.S3456.CKT1:: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-211 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.28986 | 120.2549 | P12:345:OPPD:LX007::S3458.S3456.CKT1:: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-211 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.52245 | 120.9642 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-211 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.52258 | 121.0293 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-211 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.4568 | 137.4937 | P23:345:OPPD:S3740-S3454&CC2:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-211 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.42855 | 138.637 | P23:345:OPPD:S3454-S3455&S3740:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-211 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.42855 | 138.637 | P42:345:OPPD:S3454-S3740&S3455:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-211 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.45644 | 141.6018 | P12:345:OPPD:S3454-S3740:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-211 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.43032 | 144.3167 | P42:345:OPPD:S3454-S3740&S3455:::EHV: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-211 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.43032 | 144.3167 | P23:345:OPPD:S3454-S3455&S3740:::EHV: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-211 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.431 | 144.6751 | P42:345:OPPD:S3454-S3740&S3455:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-211 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.431 | 144.6751 | P23:345:OPPD:S3454-S3455&S3740:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-211 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.45815 | 144.7416 | P23:345:OPPD:S3740-S3454&CC2:::EHV: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-211 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.45878 | 145.0088 | P23:345:OPPD:S3740-S3454&CC2:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-211 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.45778 | 148.9384 | P12:345:OPPD:S3454-S3740:::EHV: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-211 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.4584 | 149.2059 | P12:345:OPPD:S3454-S3740:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-211 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.41707 | 150.0028 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-211 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.45869 | 152.3003 | P23:345:OPPD:S3740-S3454&CC2:::EHV: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-211 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.45932 | 152.7184 | P23:345:OPPD:S3740-S3454&CC2:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-211 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.43055 | 153.5033 | P42:345:OPPD:S3454-S3740&S3455:::EHV: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-211 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.43055 | 153.5033 | P23:345:OPPD:S3454-S3455&S3740:::EHV: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-211 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.60106 | 153.5075 | P23:345:OPPD:S3740-S3454&CC2:::EHV: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-211 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.43122 | 154.0422 | P23:345:OPPD:S3454-S3455&S3740:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-211 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.43122 | 154.0422 | P42:345:OPPD:S3454-S3740&S3455:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-211 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.41963 | 155.7815 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-211 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.57484 | 156.0768 | P23:345:OPPD:S3454-S3455&S3740:::EHV: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-211 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.57484 | 156.0768 | P42:345:OPPD:S3454-S3740&S3455:::EHV: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-211 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.42054 | 156.3479 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-211 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.45838 | 156.4592 | P12:345:OPPD:S3454-S3740:::EHV: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-211 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.45901 | 156.8769 | P12:345:OPPD:S3454-S3740:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-211 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.60058 | 158.8538 | P12:345:OPPD:S3454-S3740:::EHV: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-211 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.56181 | 164.1197 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-211 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.41962 | 167.3859 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-211 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.42051 | 168.2571 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-212 | TO->FROM | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | B | 956 | 0.11018 | 100.2221 | P42:345:NPPD:BKR-TOB-3304:::: | Cumulative Impact | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-212 | TO->FROM | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | B | 956 | 0.078451 | 100.3823 | P42:345:NPPD:BKR-TOB-3304:::: | Cumulative Impact | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-212 | TO->FROM | 645454 S3454 3 345 645740 S3740 3 345 1 | B | 1792 | 0.57989 | 100.7287 | P12:345:OPPD:S3455-S3740:::EHV: | TDF Impact | Rebuild line 645454 S3454 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-212 | TO->FROM | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | B | 956 | 0.075801 | 101.3156 | Single 640312 PAULINE3 345 640525 TOBIAS3 345 1 | Cumulative Impact | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-212 | TO->FROM | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | B | 956 | 0.11294 | 102.2146 | P42:345:NPPD:BKR-MOR-3312:::: | Cumulative Impact | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-212 | TO->FROM | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | B | 956 | 0.082328 | 102.6296 | P42:345:NPPD:BKR-TOB-3304:::: | Cumulative Impact | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-212 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | A | 1195 | 0.29088 | 103.713 | System Intact | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-212 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | A | 1195 | 0.29135 | 104.0836 | System Intact | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-212 | TO->FROM | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | B | 956 | 0.079674 | 104.1025 | Single 640312 PAULINE3 345 640525 TOBIAS3 345 1 | Cumulative Impact | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-212 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.2958 | 104.614 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-212 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.28836 | 105.026 | P12:345:OPPD:LX004::S3454.S3455.CKT1:: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-212 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.27024 | 105.343 | P23:345:OPPD:S3456-S3458&CB:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-212 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.28728 | 105.6441 | P12:345:OPPD:LX007::S3458.S3456.CKT1:: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-212 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.298 | 106.113 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-212 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.29053 | 106.3263 | P12:345:OPPD:LX004::S3454.S3455.CKT1:: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-212 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.29868 | 106.5333 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-212 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.29116 | 106.7885 | P12:345:OPPD:LX004::S3454.S3455.CKT1:: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-212 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.34309 | 107.6426 | P12:345:OPPD:LX007::S3458.S3456.CKT1:: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-212 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.27096 | 109.6596 | P23:345:OPPD:S3456-S3458&CB:::EHV: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-212 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.28905 | 109.6889 | P12:345:OPPD:LX007::S3458.S3456.CKT1:: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-212 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.27152 | 109.8739 | P23:345:OPPD:S3456-S3458&CB:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-212 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.28972 | 110.0566 | P12:345:OPPD:LX007::S3458.S3456.CKT1:: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-212 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.38949 | 110.6628 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-212 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.36399 | 111.4422 | P12:345:OPPD:LX004::S3454.S3455.CKT1:: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-212 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.52993 | 114.4569 | P12:345:OPPD:LX008::S3458.S3740.CKT1:: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-212 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.52176 | 115.3799 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-212 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.52169 | 115.4582 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-212 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.29747 | 116.2686 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-212 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.29812 | 116.8671 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-212 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.29004 | 116.9566 | P12:345:OPPD:LX004::S3454.S3455.CKT1:: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-212 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.52222 | 117.0346 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-212 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.52233 | 117.1341 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-212 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.29065 | 117.6224 | P12:345:OPPD:LX004::S3454.S3455.CKT1:: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-212 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.2717 | 119.2334 | P23:345:OPPD:S3456-S3458&CB:::EHV: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-212 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.27226 | 119.5938 | P23:345:OPPD:S3456-S3458&CB:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-212 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.2892 | 119.7072 | P12:345:OPPD:LX007::S3458.S3456.CKT1:: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-212 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.28986 | 120.2549 | P12:345:OPPD:LX007::S3458.S3456.CKT1:: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-212 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.52245 | 120.9642 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-212 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.52258 | 121.0293 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-212 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.4568 | 137.4937 | P23:345:OPPD:S3740-S3454&CC2:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-212 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.42855 | 138.637 | P23:345:OPPD:S3454-S3455&S3740:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-212 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.42855 | 138.637 | P42:345:OPPD:S3454-S3740&S3455:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-212 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.45644 | 141.6018 | P12:345:OPPD:S3454-S3740:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-212 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.43032 | 144.3167 | P42:345:OPPD:S3454-S3740&S3455:::EHV: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-212 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.43032 | 144.3167 | P23:345:OPPD:S3454-S3455&S3740:::EHV: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-212 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.431 | 144.6751 | P42:345:OPPD:S3454-S3740&S3455:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-212 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.431 | 144.6751 | P23:345:OPPD:S3454-S3455&S3740:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-212 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.45815 | 144.7416 | P23:345:OPPD:S3740-S3454&CC2:::EHV: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-212 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.45878 | 145.0088 | P23:345:OPPD:S3740-S3454&CC2:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-212 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.45778 | 148.9384 | P12:345:OPPD:S3454-S3740:::EHV: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-212 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.4584 | 149.2059 | P12:345:OPPD:S3454-S3740:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-212 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.41707 | 150.0028 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-212 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.45869 | 152.3003 | P23:345:OPPD:S3740-S3454&CC2:::EHV: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-212 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.45932 | 152.7184 | P23:345:OPPD:S3740-S3454&CC2:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-212 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.43055 | 153.5033 | P42:345:OPPD:S3454-S3740&S3455:::EHV: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-212 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.43055 | 153.5033 | P23:345:OPPD:S3454-S3455&S3740:::EHV: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-212 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.60106 | 153.5075 | P23:345:OPPD:S3740-S3454&CC2:::EHV: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-212 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.43122 | 154.0422 | P23:345:OPPD:S3454-S3455&S3740:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-212 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.43122 | 154.0422 | P42:345:OPPD:S3454-S3740&S3455:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-212 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.41963 | 155.7815 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-212 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.57484 | 156.0768 | P23:345:OPPD:S3454-S3455&S3740:::EHV: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-212 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.57484 | 156.0768 | P42:345:OPPD:S3454-S3740&S3455:::EHV: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-212 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.42054 | 156.3479 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-212 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.45838 | 156.4592 | P12:345:OPPD:S3454-S3740:::EHV: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-212 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.45901 | 156.8769 | P12:345:OPPD:S3454-S3740:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-212 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.60058 | 158.8538 | P12:345:OPPD:S3454-S3740:::EHV: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-212 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.56181 | 164.1197 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-212 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.41962 | 167.3859 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-212 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.42051 | 168.2571 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-213 | TO->FROM | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | B | 956 | 0.11018 | 100.2221 | P42:345:NPPD:BKR-TOB-3304:::: | Cumulative Impact | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-213 | TO->FROM | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | B | 956 | 0.078451 | 100.3823 | P42:345:NPPD:BKR-TOB-3304:::: | Cumulative Impact | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-213 | TO->FROM | 645454 S3454 3 345 645740 S3740 3 345 1 | B | 1792 | 0.57989 | 100.7287 | P12:345:OPPD:S3455-S3740:::EHV: | TDF Impact | Rebuild line 645454 S3454 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-213 | TO->FROM | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | B | 956 | 0.075801 | 101.3156 | Single 640312 PAULINE3 345 640525 TOBIAS3 345 1 | Cumulative Impact | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-213 | TO->FROM | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | B | 956 | 0.11294 | 102.2146 | P42:345:NPPD:BKR-MOR-3312:::: | Cumulative Impact | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-213 | TO->FROM | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | B | 956 | 0.082328 | 102.6296 | P42:345:NPPD:BKR-TOB-3304:::: | Cumulative Impact | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-213 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | A | 1195 | 0.29088 | 103.713 | System Intact | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-213 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | A | 1195 | 0.29135 | 104.0836 | System Intact | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-213 | TO->FROM | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | B | 956 | 0.079674 | 104.1025 | Single 640312 PAULINE3 345 640525 TOBIAS3 345 1 | Cumulative Impact | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-213 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.2958 | 104.614 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-213 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.28836 | 105.026 | P12:345:OPPD:LX004::S3454.S3455.CKT1:: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-213 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.27024 | 105.343 | P23:345:OPPD:S3456-S3458&CB:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-213 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.28728 | 105.6441 | P12:345:OPPD:LX007::S3458.S3456.CKT1:: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-213 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.298 | 106.113 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-213 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.29053 | 106.3263 | P12:345:OPPD:LX004::S3454.S3455.CKT1:: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-213 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.29868 | 106.5333 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-213 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.29116 | 106.7885 | P12:345:OPPD:LX004::S3454.S3455.CKT1:: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-213 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.34309 | 107.6426 | P12:345:OPPD:LX007::S3458.S3456.CKT1:: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-213 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.27096 | 109.6596 | P23:345:OPPD:S3456-S3458&CB:::EHV: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-213 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.28905 | 109.6889 | P12:345:OPPD:LX007::S3458.S3456.CKT1:: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-213 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.27152 | 109.8739 | P23:345:OPPD:S3456-S3458&CB:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-213 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.28972 | 110.0566 | P12:345:OPPD:LX007::S3458.S3456.CKT1:: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-213 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.38949 | 110.6628 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-213 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.36399 | 111.4422 | P12:345:OPPD:LX004::S3454.S3455.CKT1:: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-213 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.52993 | 114.4569 | P12:345:OPPD:LX008::S3458.S3740.CKT1:: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-213 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.52176 | 115.3799 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-213 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.52169 | 115.4582 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-213 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.29747 | 116.2686 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-213 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.29812 | 116.8671 | P23:345:OPPD:S3454-S3455&WAGNER:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-213 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.29004 | 116.9566 | P12:345:OPPD:LX004::S3454.S3455.CKT1:: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-213 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.52222 | 117.0346 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-213 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.52233 | 117.1341 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-213 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.29065 | 117.6224 | P12:345:OPPD:LX004::S3454.S3455.CKT1:: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-213 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.2717 | 119.2334 | P23:345:OPPD:S3456-S3458&CB:::EHV: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-213 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.27226 | 119.5938 | P23:345:OPPD:S3456-S3458&CB:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-213 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.2892 | 119.7072 | P12:345:OPPD:LX007::S3458.S3456.CKT1:: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-213 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.28986 | 120.2549 | P12:345:OPPD:LX007::S3458.S3456.CKT1:: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-213 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.52245 | 120.9642 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-213 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.52258 | 121.0293 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-213 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.4568 | 137.4937 | P23:345:OPPD:S3740-S3454&CC2:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-213 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.42855 | 138.637 | P23:345:OPPD:S3454-S3455&S3740:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-213 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.42855 | 138.637 | P42:345:OPPD:S3454-S3740&S3455:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-213 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.45644 | 141.6018 | P12:345:OPPD:S3454-S3740:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-213 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.43032 | 144.3167 | P42:345:OPPD:S3454-S3740&S3455:::EHV: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-213 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.43032 | 144.3167 | P23:345:OPPD:S3454-S3455&S3740:::EHV: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-213 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.431 | 144.6751 | P42:345:OPPD:S3454-S3740&S3455:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-213 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.431 | 144.6751 | P23:345:OPPD:S3454-S3455&S3740:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-213 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.45815 | 144.7416 | P23:345:OPPD:S3740-S3454&CC2:::EHV: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-213 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.45878 | 145.0088 | P23:345:OPPD:S3740-S3454&CC2:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-213 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.45778 | 148.9384 | P12:345:OPPD:S3454-S3740:::EHV: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-213 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.4584 | 149.2059 | P12:345:OPPD:S3454-S3740:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-213 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.41707 | 150.0028 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-213 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.45869 | 152.3003 | P23:345:OPPD:S3740-S3454&CC2:::EHV: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-213 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.45932 | 152.7184 | P23:345:OPPD:S3740-S3454&CC2:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-213 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.43055 | 153.5033 | P42:345:OPPD:S3454-S3740&S3455:::EHV: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-213 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.43055 | 153.5033 | P23:345:OPPD:S3454-S3455&S3740:::EHV: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-213 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.60106 | 153.5075 | P23:345:OPPD:S3740-S3454&CC2:::EHV: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-213 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.43122 | 154.0422 | P23:345:OPPD:S3454-S3455&S3740:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-213 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.43122 | 154.0422 | P42:345:OPPD:S3454-S3740&S3455:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-213 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.41963 | 155.7815 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-213 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.57484 | 156.0768 | P23:345:OPPD:S3454-S3455&S3740:::EHV: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-213 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.57484 | 156.0768 | P42:345:OPPD:S3454-S3740&S3455:::EHV: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-213 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.42054 | 156.3479 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-213 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.45838 | 156.4592 | P12:345:OPPD:S3454-S3740:::EHV: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-213 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.45901 | 156.8769 | P12:345:OPPD:S3454-S3740:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-213 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.60058 | 158.8538 | P12:345:OPPD:S3454-S3740:::EHV: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-213 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.56181 | 164.1197 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-213 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.41962 | 167.3859 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | NewBranch_S3458_S3740_ckt2_345.idv : 2024 ITP upgrade, PID : 94788 , NTC, ISD : 12/31/2030
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-213 | TO->FROM | 645455 S3455 3 345 645740 S3740 3 345 1 | B | 1195 | 0.42051 | 168.2571 | P23:345:OPPD:S3454-S3740&WAGNER:::EHV: | TDF Impact | Rebuild line 645455 S3455 3 345 645740 S3740 3 345 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-215 | TO->FROM | 640277 MOORE 3 345 640525 TOBIAS 3 345 1 | B | 956 | 0.27659 | 100.5946 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | Rebuild line 640277 MOORE 3 345 640525 TOBIAS 3 345 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-215 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.057386 | 101.6955 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-215 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.057386 | 101.6955 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-215 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.057386 | 101.6955 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-215 | TO->FROM | 539656 CLIFTON3 115 539657 CONCORD3 115 1 | B | 113.9 | 0.047166 | 102.7717 | Single 539805 ELMCREEK7 345 640600 DAYKIN3 345 1 | TDF Impact | Rebuild line 539656 CLIFTON3 115 539657 CONCORD3 115 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-215 | TO->FROM | 645454 S3454 3 345 650185 WAGENER 3 345 1 | B | 982 | 0.059941 | 104.6262 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Rebuild line 645454 S3454 3 345 650185 WAGENER 3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-215 | TO->FROM | 650185 WAGENER 3 345 650189 103&ROKEBY3 345 1 | B | 1158 | 0.061769 | 105.9892 | P42:345:NPPD:BKR-MOR-3310:::: | TDF Impact | Rebuild line 650185 WAGENER 3 345 650189 103&ROKEBY3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-215 | TO->FROM | 650185 WAGENER 3 345 650189 103&ROKEBY3 345 1 | B | 1158 | 0.061769 | 105.9892 | P42:345:NPPD:L3502A.MOORE.MCCOOL.CB3310:::: | TDF Impact | Rebuild line 650185 WAGENER 3 345 650189 103&ROKEBY3 345 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-215 | TO->FROM | 539657 CONCORD3 115 3WXFMR 534:CONCORD6 230 1 | B | 225.5 | 0.096151 | 106.7468 | Single 539805 ELMCREEK7 345 640600 DAYKIN3 345 1 | Cumulative Impact | Add 3-winding transformer 539657 CONCORD3 115 539658 CONCRD6 230 539904 CONCOD-1 13 M2
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-215 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.22875 | 106.8199 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-215 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.22024 | 108.3331 | P42:345:NPPD:BKR-TOB-3304:::: | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-215 | TO->FROM | 640277 MOORE 3 345 640525 TOBIAS 3 345 1 | B | 956 | 0.26441 | 109.5154 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | Rebuild line 640277 MOORE 3 345 640525 TOBIAS 3 345 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-215 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.05882 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-215 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.05882 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-215 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.05882 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-215 | TO->FROM | 645454 S3454 3 345 650185 WAGENER 3 345 1 | B | 982 | 0.074428 | 124.4523 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | Rebuild line 645454 S3454 3 345 650185 WAGENER 3 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-219 | TO->FROM | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | B | 1059 | 0.054394 | 100.8866 | Single 515231 KEEFTON7 345 780360 G24-113-TAP 345 1 | Cumulative Impact | Rebuild line 509745 CLARKSV7 345 515224 MUSKOGE7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-219 | TO->FROM | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 | B | 1015 | 0.074173 | 102.04 | P42:345:OKGE:SB_DGSE7313:::EHV: | Cumulative Impact | Rebuild line 514715 WOODRNG7 345 515875 REDNGTN7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-219 | TO->FROM | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 | B | 1015 | 0.081497 | 102.2256 | P42:345:OKGE:SB_DGSE7313:::EHV: | Cumulative Impact | Rebuild line 514715 WOODRNG7 345 515875 REDNGTN7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-219 | TO->FROM | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | A | 1806 | 0.030993 | 104.7272 | System Intact | TDF Impact | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-219 | TO->FROM | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | A | 1806 | 0.036856 | 104.7927 | System Intact | TDF Impact | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-219 | TO->FROM | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | B | 1059 | 0.0544 | 105.0001 | P42:345:OKGE:SB_FTTH7386:::EHV: | Cumulative Impact | Rebuild line 509745 CLARKSV7 345 515224 MUSKOGE7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-219 | TO->FROM | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | B | 1059 | 0.054394 | 105.0075 | Single 515012 RVRVALY7 345 515302 FTSMITH7 345 1 | Cumulative Impact | Rebuild line 509745 CLARKSV7 345 515224 MUSKOGE7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-219 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1011 | 0.038149 | 106.9293 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-219 | TO->FROM | 515055 MAUD 4 138 787770 G24-360-TAP 138 1 | B | 287 | 0.054415 | 107.4306 | P12:138:OKGE:BKRBKR2170:::HV: | Cumulative Impact | Rebuild line 515055 MAUD 4 138 787770 G24-360-TAP 138 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-219 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1011 | 0.034829 | 107.7039 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-219 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1187 | 0.044236 | 112.2151 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-219 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.051055 | 113.7225 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-219 | TO->FROM | 515055 MAUD 4 138 787770 G24-360-TAP 138 1 | B | 287 | 0.064946 | 114.0688 | P12:138:OKGE:BKRBKR2170:::HV: | Cumulative Impact | Rebuild line 515055 MAUD 4 138 787770 G24-360-TAP 138 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-219 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.047345 | 114.4362 | System Intact | TDF Impact | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-219 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.041238 | 114.6025 | System Intact | TDF Impact | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-219 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.050398 | 115.4477 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-219 | TO->FROM | 515055 MAUD 4 138 787770 G24-360-TAP 138 1 | B | 287 | 0.054648 | 115.6328 | P12:138:OKGE:BKRBKR2170:::HV: | Cumulative Impact | Rebuild line 515055 MAUD 4 138 787770 G24-360-TAP 138 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-219 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.050398 | 117.1553 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-219 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.050398 | 117.1572 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-219 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.050398 | 119.7129 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-219 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.050398 | 124.3274 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-219 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.036807 | 137.9906 | System Intact | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-219 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.033568 | 138.1985 | System Intact | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-220 | TO->FROM | 508814 RODESSA2 69 783570 G24-220-TAP 69 1 | B | 65 | 0.29132 | 100.2123 | P23:345:AEPW:LONGWOOD CB 1N60 NBTB:::: | TDF Impact | Rebuild line 508814 RODESSA2 69 783570 G24-220-TAP 69 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-220 | TO->FROM | 508814 RODESSA2 69 783570 G24-220-TAP 69 1 | B | 53 | 0.29117 | 100.9169 | 267135_a | TDF Impact | Rebuild line 508814 RODESSA2 69 783570 G24-220-TAP 69 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-220 | TO->FROM | 508814 RODESSA2 69 783570 G24-220-TAP 69 1 | B | 53 | 0.28934 | 101.2934 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | Rebuild line 508814 RODESSA2 69 783570 G24-220-TAP 69 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-220 | TO->FROM | 508804 HOSSTON2 69 508846 GODFREYRDTP2 69 1 | B | 53 | 0.28843 | 101.5037 | Single 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1 | TDF Impact | Rebuild line 508804 HOSSTON2 69 508846 GODFREYRDTP2 69 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-220 | TO->FROM | 508804 HOSSTON2 69 508846 GODFREYRDTP2 69 1 | B | 53 | 0.28843 | 101.54 | Single 508359 WELSH7 345 776060 G23-204-TAP 345 1 | TDF Impact | Rebuild line 508804 HOSSTON2 69 508846 GODFREYRDTP2 69 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-220 | TO->FROM | 508055 BLOOMBG2 69 783570 G24-220-TAP 69 1 | B | 53 | 1 | 101.6574 | P12:69:AEPW:HOSSTON2:BLOOMBG2::: | TDF Impact | Rebuild line 508055 BLOOMBG2 69 783570 G24-220-TAP 69 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-220 | TO->FROM | 508055 BLOOMBG2 69 783570 G24-220-TAP 69 1 | B | 53 | 1 | 101.6598 | Single 508814 RODESSA2 69 783570 G24-220-TAP 69 1 | TDF Impact | Rebuild line 508055 BLOOMBG2 69 783570 G24-220-TAP 69 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-220 | TO->FROM | 508814 RODESSA2 69 783570 G24-220-TAP 69 1 | B | 53 | 0.29117 | 101.7098 | P12:345:AEPW:LONGWD7:WILKES7::: | TDF Impact | Rebuild line 508814 RODESSA2 69 783570 G24-220-TAP 69 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-220 | TO->FROM | 508814 RODESSA2 69 783570 G24-220-TAP 69 1 | B | 53 | 1 | 101.8422 | Single 508055 BLOOMBG2 69 783570 G24-220-TAP 69 1 | TDF Impact | Rebuild line 508814 RODESSA2 69 783570 G24-220-TAP 69 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-220 | TO->FROM | 508055 BLOOMBG2 69 783570 G24-220-TAP 69 1 | B | 53 | 1 | 101.9258 | P12:69:AEPW:HOSSTON2:BLOOMBG2::: | TDF Impact | Rebuild line 508055 BLOOMBG2 69 783570 G24-220-TAP 69 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-220 | TO->FROM | 508055 BLOOMBG2 69 783570 G24-220-TAP 69 1 | B | 53 | 1 | 101.9287 | Single 508814 RODESSA2 69 783570 G24-220-TAP 69 1 | TDF Impact | Rebuild line 508055 BLOOMBG2 69 783570 G24-220-TAP 69 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-220 | TO->FROM | 508814 RODESSA2 69 783570 G24-220-TAP 69 1 | B | 53 | 0.29164 | 102.1918 | P42:345:AEPW:WILKES CB 1W10 NBTB+FAULT:::: | TDF Impact | Rebuild line 508814 RODESSA2 69 783570 G24-220-TAP 69 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-220 | TO->FROM | 508814 RODESSA2 69 783570 G24-220-TAP 69 1 | B | 53 | 0.2914 | 102.2951 | P23:345:AEPW:LONGWOOD CB 1N60 NBTB:::: | TDF Impact | Rebuild line 508814 RODESSA2 69 783570 G24-220-TAP 69 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-220 | TO->FROM | 508804 HOSSTON2 69 508846 GODFREYRDTP2 69 1 | B | 53 | 0.29007 | 105.0581 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | TDF Impact | Rebuild line 508804 HOSSTON2 69 508846 GODFREYRDTP2 69 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-220 | TO->FROM | 508814 RODESSA2 69 783570 G24-220-TAP 69 1 | B | 53 | 0.2875 | 105.1089 | Single 776060 G23-204-TAP 345 779010 G24-068-TAP 345 1 | TDF Impact | Rebuild line 508814 RODESSA2 69 783570 G24-220-TAP 69 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-220 | TO->FROM | 508814 RODESSA2 69 783570 G24-220-TAP 69 1 | B | 53 | 0.2875 | 105.1627 | Single 508359 WELSH7 345 776060 G23-204-TAP 345 1 | TDF Impact | Rebuild line 508814 RODESSA2 69 783570 G24-220-TAP 69 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-220 | TO->FROM | 508804 HOSSTON2 69 508846 GODFREYRDTP2 69 1 | B | 53 | 0.28824 | 105.59 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | Rebuild line 508804 HOSSTON2 69 508846 GODFREYRDTP2 69 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-220 | TO->FROM | 508814 RODESSA2 69 783570 G24-220-TAP 69 1 | B | 65 | 0.2891 | 106.6412 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | Rebuild line 508814 RODESSA2 69 783570 G24-220-TAP 69 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-220 | TO->FROM | 508814 RODESSA2 69 783570 G24-220-TAP 69 1 | B | 65 | 0.42719 | 107.1787 | Single 508089 WATLANT2 69 779100 G24-071-TAP 69 1 | TDF Impact | Rebuild line 508814 RODESSA2 69 783570 G24-220-TAP 69 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-220 | TO->FROM | 508814 RODESSA2 69 783570 G24-220-TAP 69 1 | B | 65 | 0.42724 | 107.6918 | P12:69:AEPW:WATLANT2:LINDEN 2::: | TDF Impact | Rebuild line 508814 RODESSA2 69 783570 G24-220-TAP 69 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-220 | TO->FROM | 508814 RODESSA2 69 783570 G24-220-TAP 69 1 | B | 53 | 0.28923 | 108.7199 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | TDF Impact | Rebuild line 508814 RODESSA2 69 783570 G24-220-TAP 69 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-220 | TO->FROM | 508804 HOSSTON2 69 508846 GODFREYRDTP2 69 1 | B | 53 | 0.29109 | 109.8273 | 267135_a | TDF Impact | Rebuild line 508804 HOSSTON2 69 508846 GODFREYRDTP2 69 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-220 | TO->FROM | 508804 HOSSTON2 69 508846 GODFREYRDTP2 69 1 | B | 53 | 0.29157 | 109.8956 | P42:345:AEPW:WILKES CB 1W10 NBTB+FAULT:::: | TDF Impact | Rebuild line 508804 HOSSTON2 69 508846 GODFREYRDTP2 69 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-220 | TO->FROM | 508804 HOSSTON2 69 508846 GODFREYRDTP2 69 1 | B | 53 | 0.42622 | 109.9041 | Single 508089 WATLANT2 69 779100 G24-071-TAP 69 1 | TDF Impact | Rebuild line 508804 HOSSTON2 69 508846 GODFREYRDTP2 69 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-220 | TO->FROM | 508804 HOSSTON2 69 508846 GODFREYRDTP2 69 1 | B | 53 | 0.29109 | 110.0283 | P12:345:AEPW:LONGWD7:WILKES7::: | TDF Impact | Rebuild line 508804 HOSSTON2 69 508846 GODFREYRDTP2 69 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-220 | TO->FROM | 508804 HOSSTON2 69 508846 GODFREYRDTP2 69 1 | B | 53 | 0.42627 | 110.5579 | P12:69:AEPW:WATLANT2:LINDEN 2::: | TDF Impact | Rebuild line 508804 HOSSTON2 69 508846 GODFREYRDTP2 69 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-220 | TO->FROM | 508814 RODESSA2 69 783570 G24-220-TAP 69 1 | B | 53 | 0.29024 | 110.561 | 267135_a | TDF Impact | Rebuild line 508814 RODESSA2 69 783570 G24-220-TAP 69 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-220 | TO->FROM | 508804 HOSSTON2 69 508846 GODFREYRDTP2 69 1 | B | 53 | 0.29132 | 110.8969 | P23:345:AEPW:LONGWOOD CB 1N60 NBTB:::: | TDF Impact | Rebuild line 508804 HOSSTON2 69 508846 GODFREYRDTP2 69 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-220 | TO->FROM | 508814 RODESSA2 69 783570 G24-220-TAP 69 1 | B | 53 | 0.29071 | 111.2974 | P42:345:AEPW:WILKES CB 1W10 NBTB+FAULT:::: | TDF Impact | Rebuild line 508814 RODESSA2 69 783570 G24-220-TAP 69 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-220 | TO->FROM | 508814 RODESSA2 69 783570 G24-220-TAP 69 1 | B | 53 | 0.29024 | 111.4001 | P12:345:AEPW:LONGWD7:WILKES7::: | TDF Impact | Rebuild line 508814 RODESSA2 69 783570 G24-220-TAP 69 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-220 | TO->FROM | 508814 RODESSA2 69 783570 G24-220-TAP 69 1 | B | 53 | 0.29048 | 111.5778 | P23:345:AEPW:LONGWOOD CB 1N60 NBTB:::: | TDF Impact | Rebuild line 508814 RODESSA2 69 783570 G24-220-TAP 69 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-220 | TO->FROM | 508814 RODESSA2 69 783570 G24-220-TAP 69 1 | B | 53 | 0.4273 | 111.5778 | Single 508089 WATLANT2 69 779100 G24-071-TAP 69 1 | TDF Impact | Rebuild line 508814 RODESSA2 69 783570 G24-220-TAP 69 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-220 | TO->FROM | 508814 RODESSA2 69 783570 G24-220-TAP 69 1 | B | 53 | 0.42735 | 112.112 | P12:69:AEPW:WATLANT2:LINDEN 2::: | TDF Impact | Rebuild line 508814 RODESSA2 69 783570 G24-220-TAP 69 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-220 | TO->FROM | 508804 HOSSTON2 69 508846 GODFREYRDTP2 69 1 | B | 53 | 0.2891 | 118.8031 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | Rebuild line 508804 HOSSTON2 69 508846 GODFREYRDTP2 69 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-220 | TO->FROM | 508814 RODESSA2 69 783570 G24-220-TAP 69 1 | B | 53 | 0.28824 | 119.4276 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | Rebuild line 508814 RODESSA2 69 783570 G24-220-TAP 69 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-220 | TO->FROM | 508804 HOSSTON2 69 508846 GODFREYRDTP2 69 1 | B | 53 | 0.42719 | 119.6096 | Single 508089 WATLANT2 69 779100 G24-071-TAP 69 1 | TDF Impact | Rebuild line 508804 HOSSTON2 69 508846 GODFREYRDTP2 69 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-220 | TO->FROM | 508804 HOSSTON2 69 508846 GODFREYRDTP2 69 1 | B | 53 | 0.42724 | 120.2355 | P12:69:AEPW:WATLANT2:LINDEN 2::: | TDF Impact | Rebuild line 508804 HOSSTON2 69 508846 GODFREYRDTP2 69 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-220 | TO->FROM | 508814 RODESSA2 69 783570 G24-220-TAP 69 1 | B | 53 | 0.42622 | 123.4859 | Single 508089 WATLANT2 69 779100 G24-071-TAP 69 1 | TDF Impact | Rebuild line 508814 RODESSA2 69 783570 G24-220-TAP 69 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-220 | TO->FROM | 508814 RODESSA2 69 783570 G24-220-TAP 69 1 | B | 53 | 0.42627 | 124.1415 | P12:69:AEPW:WATLANT2:LINDEN 2::: | TDF Impact | Rebuild line 508814 RODESSA2 69 783570 G24-220-TAP 69 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-220 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | A | 157 | 0.038837 | 148.4151 | System Intact | TDF Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-220 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | A | 157 | 0.040242 | 150.7438 | System Intact | TDF Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-220 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | A | 159 | 0.040258 | 153.3873 | System Intact | TDF Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-220 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | B | 157 | 0.054526 | 172.2965 | Single 508809 LONGWD7 345 788340 G24-379-TAP 345 1 | Cumulative Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-220 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | B | 157 | 0.054526 | 172.3873 | Single 337376 7SAREPTA% 345 788340 G24-379-TAP 345 1 | Cumulative Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-220 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | B | 157 | 0.055665 | 177.0636 | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | Cumulative Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-220 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | B | 159 | 0.056119 | 179.8598 | Single 337376 7SAREPTA% 345 788340 G24-379-TAP 345 1 | Cumulative Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-220 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | B | 159 | 0.056119 | 179.951 | Single 508809 LONGWD7 345 788340 G24-379-TAP 345 1 | Cumulative Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-220 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | B | 157 | 0.055983 | 180.7536 | Single 337376 7SAREPTA% 345 788340 G24-379-TAP 345 1 | Cumulative Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-220 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | B | 157 | 0.055983 | 180.8803 | Single 508809 LONGWD7 345 788340 G24-379-TAP 345 1 | Cumulative Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-220 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | B | 159 | 0.057269 | 184.4152 | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | Cumulative Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-220 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | B | 157 | 0.057132 | 185.7511 | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | Cumulative Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-221 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.073449 | 100.0488 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-221 | TO->FROM | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | B | 997 | 0.172 | 100.166 | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | Cumulative Impact | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-221 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063087 | 100.533 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-221 | TO->FROM | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | B | 997 | 0.17586 | 100.7286 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-221 | TO->FROM | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | B | 997 | 0.17586 | 101.1047 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-221 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063915 | 102.9616 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-221 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063915 | 102.9634 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-221 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063915 | 103.0288 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-221 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063915 | 103.4739 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-221 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.0778 | 103.9266 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-221 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063915 | 104.1493 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-221 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.076457 | 104.7552 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-221 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.076457 | 104.888 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-221 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.080747 | 107.2243 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-221 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063915 | 107.2793 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-221 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063915 | 107.2794 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-221 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.080747 | 107.2951 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-221 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063915 | 107.3093 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-221 | TO->FROM | 523959 POTTER_CO 6 230 3WXFMR 526:WAUK 90343-A 230 1 | B | 559 | 0.14621 | 107.3794 | P42:345:SPS:HITCHLAND-1R15:::EHV: | Cumulative Impact | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-221 | TO->FROM | 523959 POTTER_CO 6 230 3WXFMR 526:WAUK 90343-A 230 1 | B | 559 | 0.14621 | 107.3953 | Single 523097 HITCHLAND7 345 523961 POTTER_CO7 345 1 | Cumulative Impact | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-221 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.074461 | 107.5866 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-221 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063915 | 107.7557 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-221 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063915 | 108.1822 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-221 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063915 | 108.2747 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-221 | TO->FROM | 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | B | 997 | 0.17157 | 109.7018 | Single 525832 TUCO_INT7 345 526000 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-221 | TO->FROM | 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | B | 997 | 0.17247 | 111.09 | Single 525832 TUCO_INT7 345 526000 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-221 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063915 | 111.3621 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-221 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.077486 | 111.723 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-221 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.077486 | 111.8755 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-221 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.074461 | 115.0541 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29L | T0 | GEN-2024-221 | TO->FROM | 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | B | 997 | 0.13609 | 116.6859 | Single 525832 TUCO_INT7 345 526000 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-221 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.077486 | 118.9427 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-221 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.077486 | 119.313 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-232 | TO->FROM | 334197 7ROCKYCRK% 345 783930 G24-232-TAP 345 1 | B | 1193 | 0.39294 | 101.2 | P11:18:EES:1J472MCPS G2:1::EHV: | TDF Impact | Rebuild line 334197 7ROCKYCRK% 345 783930 G24-232-TAP 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-234 | TO->FROM | 652552 SIOUXCY2 230 3WXFMR 652:652: SC2 KU1B 230 1 | B | 750 | 0.034756 | 100.7724 | P23:345:XEL:396 BKR SPK:::EHV: | TDF Impact | Add 3-winding transformer 652305 SIOUXC29 13 652552 SIOUXCY2 230 652564 SIOUXCY3 345 M2
Thermal | 02ALL | 1 | 29SP | T0 | GEN-2024-234 | TO->FROM | 640377 TEKAMAH5 161 646300 S1300 5 161 1 | B | 217 | 0.6403 | 101.1323 | Single 645451 S34513 345 645551 S3451-RAUN3 345 Z1 | TDF Impact | Rebuild line 640377 TEKAMAH5 161 646300 S1300 5 161 1
Thermal | 02ALL | 1 | 29SP | T0 | GEN-2024-234 | TO->FROM | 640377 TEKAMAH5 161 646300 S1300 5 161 1 | B | 217 | 0.6403 | 101.1332 | Single 645551 S3451-RAUN3 345 762779 G18-043TAP 345 1 | TDF Impact | Rebuild line 640377 TEKAMAH5 161 646300 S1300 5 161 1
Thermal | 02ALL | 1 | 29SP | T0 | GEN-2024-234 | TO->FROM | 640377 TEKAMAH5 161 646300 S1300 5 161 1 | B | 217 | 0.6403 | 101.1332 | P22:345:OPPD:S3451-RAUN:::EHV: | TDF Impact | Rebuild line 640377 TEKAMAH5 161 646300 S1300 5 161 1
Thermal | 02ALL | 1 | 29SP | T0 | GEN-2024-234 | TO->FROM | 640377 TEKAMAH5 161 646300 S1300 5 161 1 | B | 217 | 0.6403 | 101.1332 | P12:345:OPPD-MEC:S3451-RAUN:::EHV: | TDF Impact | Rebuild line 640377 TEKAMAH5 161 646300 S1300 5 161 1
Thermal | 02ALL | 1 | 26SP | T0 | GEN-2024-234 | TO->FROM | 647424 FREM D 8 69 647976 S976 8 69 1 | B | 96 | 0.084153 | 106.3602 | P12:161:OPPD:TEKAMAH-S1226:::HV: | Cumulative Impact | Rebuild line 647424 FREM D 8 69 647976 S976 8 69 1
Thermal | 02ALL | 1 | 29SP | T0 | GEN-2024-234 | TO->FROM | 647424 FREM D 8 69 647976 S976 8 69 1 | B | 96 | 0.080678 | 106.8396 | P12:161:OPPD:TEKAMAH-S1226:::HV: | Cumulative Impact | Rebuild line 647424 FREM D 8 69 647976 S976 8 69 1
Thermal | 02ALL | 1 | 29WP | T0 | GEN-2024-234 | TO->FROM | 647424 FREM D 8 69 647976 S976 8 69 1 | B | 96 | 0.080382 | 107.8274 | P12:161:OPPD:TEKAMAH-S1226:::HV: | Cumulative Impact | Rebuild line 647424 FREM D 8 69 647976 S976 8 69 1
Thermal | 02ALL | 1 | 26SP | T0 | GEN-2024-234 | TO->FROM | 640377 TEKAMAH5 161 646300 S1300 5 161 1 | B | 217 | 0.6411 | 109.2055 | P12:345:OPPD-MEC:S3451-RAUN:::EHV: | TDF Impact | Rebuild line 640377 TEKAMAH5 161 646300 S1300 5 161 1
Thermal | 02ALL | 1 | 26SP | T0 | GEN-2024-234 | TO->FROM | 640377 TEKAMAH5 161 646300 S1300 5 161 1 | B | 217 | 0.6411 | 109.2055 | P22:345:OPPD:S3451-RAUN:::EHV: | TDF Impact | Rebuild line 640377 TEKAMAH5 161 646300 S1300 5 161 1
Thermal | 02ALL | 1 | 26SP | T0 | GEN-2024-234 | TO->FROM | 640377 TEKAMAH5 161 646300 S1300 5 161 1 | B | 217 | 0.6411 | 109.2055 | Single 645551 S3451-RAUN3 345 762779 G18-043TAP 345 1 | TDF Impact | Rebuild line 640377 TEKAMAH5 161 646300 S1300 5 161 1
Thermal | 02ALL | 1 | 26SP | T0 | GEN-2024-234 | TO->FROM | 640377 TEKAMAH5 161 646300 S1300 5 161 1 | B | 217 | 0.6411 | 109.2059 | Single 645451 S34513 345 645551 S3451-RAUN3 345 Z1 | TDF Impact | Rebuild line 640377 TEKAMAH5 161 646300 S1300 5 161 1
Thermal | 02ALL | 1 | 26SP | T0 | GEN-2024-234 | TO->FROM | 640377 TEKAMAH5 161 646300 S1300 5 161 1 | B | 217 | 1 | 123.6499 | P12:161:OPPD:S1300-RAUN:::HV: | TDF Impact | Rebuild line 640377 TEKAMAH5 161 646300 S1300 5 161 1
Thermal | 02ALL | 1 | 26SP | T0 | GEN-2024-234 | TO->FROM | 635201 RAUN 5 161 646300 S1300 5 161 1 | B | 217 | 1 | 123.8066 | P12:161:OPPD:S1300-TEKAMAH:::HV: | TDF Impact | Rebuild line 635201 RAUN 5 161 646300 S1300 5 161 1
Thermal | 02ALL | 1 | 29SP | T0 | GEN-2024-234 | TO->FROM | 640377 TEKAMAH5 161 646300 S1300 5 161 1 | B | 217 | 1 | 123.8434 | P12:161:OPPD:S1300-RAUN:::HV: | TDF Impact | Rebuild line 640377 TEKAMAH5 161 646300 S1300 5 161 1
Thermal | 02ALL | 1 | 29SP | T0 | GEN-2024-234 | TO->FROM | 635201 RAUN 5 161 646300 S1300 5 161 1 | B | 217 | 1 | 123.8554 | P12:161:OPPD:S1300-TEKAMAH:::HV: | TDF Impact | Rebuild line 635201 RAUN 5 161 646300 S1300 5 161 1
Thermal | 02ALL | 1 | 29WP | T0 | GEN-2024-234 | TO->FROM | 635201 RAUN 5 161 646300 S1300 5 161 1 | B | 217 | 1 | 123.9016 | P12:161:OPPD:S1300-TEKAMAH:::HV: | TDF Impact | Rebuild line 635201 RAUN 5 161 646300 S1300 5 161 1
Thermal | 02ALL | 1 | 29WP | T0 | GEN-2024-234 | TO->FROM | 640377 TEKAMAH5 161 646300 S1300 5 161 1 | B | 217 | 1 | 124.0466 | P12:161:OPPD:S1300-RAUN:::HV: | TDF Impact | Rebuild line 640377 TEKAMAH5 161 646300 S1300 5 161 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-235 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.066345 | 100.4398 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.071087 | 100.451 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-235 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1182 | 0.070463 | 100.7686 | Single 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-235 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1182 | 0.070531 | 100.7917 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | Cumulative Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.071003 | 101.1642 | Single 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | A | 901 | 0.062004 | 101.5467 | System Intact | TDF Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.071769 | 101.7923 | Single 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.071162 | 101.9139 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.071087 | 101.9296 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | A | 901 | 0.061784 | 102.5076 | System Intact | TDF Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.071128 | 102.6355 | Single 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Cumulative Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.071003 | 102.8031 | Single 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Cumulative Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.067082 | 102.8233 | P22:345:EES:CLARKSV7!:::EHV: | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.071769 | 103.1009 | Single 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.071003 | 103.3738 | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.072168 | 103.4829 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.071769 | 103.5409 | Single 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.072094 | 103.7549 | Single 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.06705 | 104.0394 | P22:345:EES:CLARKSV7!:::EHV: | Cumulative Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-235 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.061642 | 104.6561 | P22:345:EES:CLARKSV7!:::EHV: | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | TO->FROM | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | A | 1806 | 0.11293 | 104.7272 | System Intact | TDF Impact | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | TO->FROM | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | A | 1806 | 0.11848 | 104.7927 | System Intact | TDF Impact | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.067082 | 104.8397 | P22:345:EES:CLARKSV7!:::EHV: | Cumulative Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.071769 | 104.9783 | Single 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.071128 | 105.1591 | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | Cumulative Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.071003 | 105.2013 | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | Cumulative Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.072094 | 105.3089 | Single 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.072168 | 105.3978 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | Cumulative Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.064431 | 105.4314 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB:::: | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.064435 | 105.47 | P12:345:EES:CHAMSPR7!:CLARKSV7!:1:EHV: | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-235 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.059424 | 105.6463 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB:::: | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-235 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.059427 | 105.6708 | P12:345:EES:CHAMSPR7!:CLARKSV7!:1:EHV: | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.07242 | 105.6815 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | Cumulative Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.072173 | 106.3738 | P23:345:WERE:N345-345-20:EHV: | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1011 | 0.05998 | 106.9293 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.064565 | 107.3179 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB:::: | Cumulative Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.064569 | 107.3846 | P12:345:EES:CHAMSPR7!:CLARKSV7!:1:EHV: | Cumulative Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-235 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.070463 | 107.6019 | Single 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1011 | 0.057546 | 107.7039 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.064431 | 107.8076 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB:::: | Cumulative Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | TO->FROM | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | A | 827 | 0.065639 | 107.8643 | System Intact | TDF Impact | Rebuild line 532791 BENTON 7 345 532794 ROSEHIL7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.064435 | 107.867 | P12:345:EES:CHAMSPR7!:CLARKSV7!:1:EHV: | Cumulative Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.072173 | 108.4042 | P23:345:WERE:N345-345-20:EHV: | Cumulative Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.072181 | 108.8315 | P23:345:WERE:N345-345-20:EHV: | Cumulative Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-235 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.070463 | 109.031 | Single 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-235 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.070531 | 109.0559 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.071162 | 109.2662 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.071128 | 109.6648 | Single 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.072094 | 110.6179 | Single 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.06705 | 110.6357 | P22:345:EES:CLARKSV7!:::EHV: | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.071128 | 112.0601 | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.072094 | 112.0812 | Single 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-235 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1187 | 0.076477 | 112.2151 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.07242 | 112.433 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-235 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.083201 | 112.5233 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | TO->FROM | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | A | 827 | 0.067755 | 113.506 | System Intact | TDF Impact | Rebuild line 532791 BENTON 7 345 532794 ROSEHIL7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.064565 | 113.5635 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB:::: | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.064569 | 113.5961 | P12:345:EES:CHAMSPR7!:CLARKSV7!:1:EHV: | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-235 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.097904 | 113.7225 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-235 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.082547 | 114.0272 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-235 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.087323 | 114.0895 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.05617 | 114.4362 | System Intact | TDF Impact | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.050465 | 114.6025 | System Intact | TDF Impact | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-235 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.097247 | 115.4477 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-235 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.087323 | 115.647 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.072181 | 115.6656 | P23:345:WERE:N345-345-20:EHV: | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-235 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.097247 | 117.1553 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-235 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.097247 | 117.1572 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-235 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.097247 | 119.7129 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-235 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.097247 | 124.3274 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.058301 | 137.9906 | System Intact | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.055608 | 138.1985 | System Intact | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.066858 | 155.4006 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.06367 | 155.7991 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.060555 | 155.8883 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.06461 | 158.3302 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.076315 | 159.2546 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.073049 | 159.5575 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.065546 | 160.5677 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.075782 | 161.638 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.064477 | 161.7992 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.062258 | 161.8408 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.07246 | 162.2698 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.061346 | 163.3422 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.075782 | 164.1736 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.075782 | 164.1763 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.07246 | 164.8475 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.07246 | 164.8482 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.075782 | 167.9939 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.07246 | 169.069 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-235 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.075782 | 175.0352 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-235 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.07246 | 177.0235 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-236 | TO->FROM | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | B | 1059 | 0.11224 | 100.2166 | P12:345:AEPW:R.S.S.-7:ONETA--7::: | Cumulative Impact | Rebuild line 509745 CLARKSV7 345 515224 MUSKOGE7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-236 | TO->FROM | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | B | 1059 | 0.13263 | 100.8866 | Single 515231 KEEFTON7 345 780360 G24-113-TAP 345 1 | Cumulative Impact | Rebuild line 509745 CLARKSV7 345 515224 MUSKOGE7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-236 | TO->FROM | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 | B | 1015 | 0.054458 | 102.04 | P42:345:OKGE:SB_DGSE7313:::EHV: | Cumulative Impact | Rebuild line 514715 WOODRNG7 345 515875 REDNGTN7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-236 | TO->FROM | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 | B | 1015 | 0.062664 | 102.2256 | P42:345:OKGE:SB_DGSE7313:::EHV: | Cumulative Impact | Rebuild line 514715 WOODRNG7 345 515875 REDNGTN7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-236 | TO->FROM | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | A | 1806 | 0.031882 | 104.7272 | System Intact | TDF Impact | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-236 | TO->FROM | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | A | 1806 | 0.037185 | 104.7927 | System Intact | TDF Impact | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-236 | TO->FROM | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | B | 1059 | 0.13264 | 105.0001 | P42:345:OKGE:SB_FTTH7386:::EHV: | Cumulative Impact | Rebuild line 509745 CLARKSV7 345 515224 MUSKOGE7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-236 | TO->FROM | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | B | 1059 | 0.13263 | 105.0075 | Single 515012 RVRVALY7 345 515302 FTSMITH7 345 1 | Cumulative Impact | Rebuild line 509745 CLARKSV7 345 515224 MUSKOGE7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-236 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1011 | 0.048027 | 106.9293 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-236 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1011 | 0.045786 | 107.7039 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-236 | TO->FROM | 515305 FTSMITH8 500 3WXFMR 524:524:FTSMITH1 500 1 | B | 693 | 0.07105 | 108.5609 | P12:161:EES:FTSMTHW5%:FTSMITH7%:FTSMTH511:HV: | Cumulative Impact | Add 3-winding transformer 515302 FTSMITH7 345 515305 FTSMITH8 500 515726 FTSMTH11 13 M2
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-236 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1187 | 0.057556 | 112.2151 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-236 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.063785 | 112.5233 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-236 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.064302 | 113.7225 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-236 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.062814 | 114.0272 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-236 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.059799 | 114.0895 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-236 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.043807 | 114.4362 | System Intact | TDF Impact | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-236 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.037957 | 114.6025 | System Intact | TDF Impact | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-236 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.063644 | 115.4477 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-236 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.059799 | 115.647 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-236 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.063644 | 117.1553 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-236 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.063644 | 117.1572 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-236 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.063644 | 119.7129 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-236 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.063644 | 124.3274 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-236 | TO->FROM | 515301 FTSMTHW5 161 3WXFMR 524:524:FTSMITH5 345 5 | B | 493 | 0.054263 | 126.769 | P12:345:EES:FTSMITH7%:FTSMITH8%:FTSMTH111:EHV: | Cumulative Impact | Add 3-winding transformer 515301 FTSMTHW5 161 515302 FTSMITH7 345 515728 FTSMTH51 13 M2
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-236 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.045977 | 137.9906 | System Intact | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-236 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.043758 | 138.1985 | System Intact | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-236 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051996 | 159.2546 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-236 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.052767 | 160.5677 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-236 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051463 | 161.638 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-236 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051241 | 161.7992 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-236 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.050166 | 161.8408 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-236 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051463 | 164.1736 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-236 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051463 | 164.1763 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-236 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051463 | 167.9939 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-236 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051463 | 175.0352 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-239 | TO->FROM | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 | B | 1015 | 0.14839 | 102.04 | P42:345:OKGE:SB_DGSE7313:::EHV: | Cumulative Impact | Rebuild line 514715 WOODRNG7 345 515875 REDNGTN7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-239 | TO->FROM | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 | B | 1015 | 0.14745 | 102.2256 | P42:345:OKGE:SB_DGSE7313:::EHV: | Cumulative Impact | Rebuild line 514715 WOODRNG7 345 515875 REDNGTN7 345 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-239 | TO->FROM | 514898 CIMARON4 138 3WXFMR 524:524:CIMARON2 345 2 | B | 478 | 0.070638 | 102.3793 | P13:138:OKGE:BKRBKR_3W020:::HV: | TDF Impact | Add 3-winding transformer 514898 CIMARON4 138 514901 CIMARON7 345 515715 CIMARO21 13 M2
Thermal | 00NR | 1 | 26SP | T1 | GEN-2024-239 | TO->FROM | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | B | 444 | 0.030469 | 103.4096 | Single 514853 DVISION4 138 514863 HAYMAKR4 138 1 | TDF Impact | Rebuild line 514894 CZECHAL4 138 514898 CIMARON4 138 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-239 | TO->FROM | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | A | 1806 | 0.041876 | 104.7272 | System Intact | TDF Impact | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-239 | TO->FROM | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | A | 1806 | 0.047821 | 104.7927 | System Intact | TDF Impact | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1
Thermal | 00NR | 1 | 26SP | T1 | GEN-2024-239 | TO->FROM | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | B | 444 | 0.030469 | 105.2555 | P12:138:OKGE:BKRBKR1260:::HV: | TDF Impact | Rebuild line 514894 CZECHAL4 138 514898 CIMARON4 138 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-239 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1011 | 0.034037 | 106.9293 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 00NR | 1 | 26SP | T1 | GEN-2024-239 | TO->FROM | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | B | 444 | 0.030469 | 106.9994 | Single 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | TDF Impact | Rebuild line 514894 CZECHAL4 138 514898 CIMARON4 138 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-239 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1187 | 0.038358 | 112.2151 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-239 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.067317 | 114.4362 | System Intact | TDF Impact | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-239 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.062464 | 114.6025 | System Intact | TDF Impact | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-239 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.033193 | 137.9906 | System Intact | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-240 | TO->FROM | 532939 N345 4 5 161 3WXFMR 536:N345 TX-2 161 2 | B | 550 | 0.052242 | 100.4793 | Single 533021 NEOSHO4 138 533023 N34534 138 1 | TDF Impact | Add 3-winding transformer 532793 NEOSHO 7 345 532825 N345 2 1 13 532939 N345 4 5 161 M2
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-240 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.32782 | 101.903 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-240 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.33637 | 102.4032 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-240 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.38747 | 103.1002 | Single 510380 DELWARE7 345 580555 MONETT345 345 1 | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-240 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.097965 | 103.3738 | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-240 | TO->FROM | 532939 N345 4 5 161 3WXFMR 536:N345 TX-2 161 2 | B | 550 | 0.061457 | 103.5308 | Single 533021 NEOSHO4 138 533023 N34534 138 1 | TDF Impact | Add 3-winding transformer 532793 NEOSHO 7 345 532825 N345 2 1 13 532939 N345 4 5 161 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-240 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | B | 829 | 0.096399 | 103.7671 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | TDF Impact | Rebuild line 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-240 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.099708 | 105.1591 | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | Cumulative Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-240 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.097965 | 105.2013 | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | Cumulative Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-240 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.09668 | 106.3738 | P23:345:WERE:N345-345-20:EHV: | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-240 | TO->FROM | 532937 NEOSHO 5 161 532939 N345 4 5 161 1 | B | 557 | 0.062944 | 106.5051 | Single 533021 NEOSHO4 138 533023 N34534 138 1 | TDF Impact | Rebuild line 532937 NEOSHO 5 161 532939 N345 4 5 161 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-240 | TO->FROM | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | A | 827 | 0.062969 | 107.8643 | System Intact | TDF Impact | Rebuild line 532791 BENTON 7 345 532794 ROSEHIL7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-240 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.09668 | 108.4042 | P23:345:WERE:N345-345-20:EHV: | Cumulative Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-240 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.098236 | 108.8315 | P23:345:WERE:N345-345-20:EHV: | Cumulative Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-240 | TO->FROM | 532939 N345 4 5 161 3WXFMR 536:N345 TX-2 161 2 | B | 550 | 0.062944 | 111.179 | Single 533021 NEOSHO4 138 533023 N34534 138 1 | TDF Impact | Add 3-winding transformer 532793 NEOSHO 7 345 532825 N345 2 1 13 532939 N345 4 5 161 M2
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-240 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.099708 | 112.0601 | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-240 | TO->FROM | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | A | 827 | 0.065237 | 113.506 | System Intact | TDF Impact | Rebuild line 532791 BENTON 7 345 532794 ROSEHIL7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-240 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.098236 | 115.6656 | P23:345:WERE:N345-345-20:EHV: | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-240 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.45825 | 137.9906 | System Intact | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-240 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.45528 | 138.1985 | System Intact | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-240 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.46178 | 155.4006 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-240 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.46603 | 155.7991 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-240 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.46278 | 155.8883 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-240 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.45891 | 158.3302 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-240 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.45723 | 159.2546 | P42:345:OKGE:SB_RARD7311:::EHV: | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-240 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.45343 | 159.5575 | P42:345:OKGE:SB_RARD7311:::EHV: | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-240 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.45366 | 160.5677 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-240 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.4567 | 161.638 | P12:345:OKGE:BKRBKR3572:::EHV: | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-240 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.44672 | 161.7992 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-240 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.45002 | 161.8408 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-240 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.45284 | 162.2698 | P12:345:OKGE:BKRBKR3572:::EHV: | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-240 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.44325 | 163.3422 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-240 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.4567 | 164.1736 | P42:345:OKGE:SB_OPKY7388:::EHV: | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-240 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.4567 | 164.1763 | P42:345:OKGE:SB_OPKY7308:::EHV: | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-240 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.45284 | 164.8475 | P42:345:OKGE:SB_OPKY7388:::EHV: | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-240 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.45284 | 164.8482 | P42:345:OKGE:SB_OPKY7308:::EHV: | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-240 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.4567 | 167.9939 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-240 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.45284 | 169.069 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-240 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.4567 | 175.0352 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-240 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.45284 | 177.0235 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-241 | TO->FROM | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | B | 1059 | 0.052602 | 100.2166 | P12:345:AEPW:R.S.S.-7:ONETA--7::: | Cumulative Impact | Rebuild line 509745 CLARKSV7 345 515224 MUSKOGE7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-241 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | A | 157 | 0.035966 | 148.4151 | System Intact | TDF Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-241 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | A | 157 | 0.037145 | 150.7438 | System Intact | TDF Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-241 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | A | 159 | 0.037221 | 153.3873 | System Intact | TDF Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-241 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | B | 159 | 0.050823 | 184.4152 | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | Cumulative Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-241 | TO->FROM | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | B | 157 | 0.050683 | 185.7511 | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | Cumulative Impact | Rebuild line 338875 3PATMOS.W# 115 503912 FULTON 3 115 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-249 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.0394 | 194.842 | System Intact | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-249 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.041614 | 202.7501 | System Intact | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-249 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.07474 | 217.9772 | P42:345:NPPD:BKR-TOB-3304:::: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-249 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.080485 | 230.5239 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-249 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.078394 | 236.1008 | P42:345:NPPD:BKR-TOB-3304:::: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-249 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.084504 | 248.1828 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-252 | TO->FROM | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 | B | 1015 | 0.14839 | 102.04 | P42:345:OKGE:SB_DGSE7313:::EHV: | Cumulative Impact | Rebuild line 514715 WOODRNG7 345 515875 REDNGTN7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-252 | TO->FROM | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 | B | 1015 | 0.14745 | 102.2256 | P42:345:OKGE:SB_DGSE7313:::EHV: | Cumulative Impact | Rebuild line 514715 WOODRNG7 345 515875 REDNGTN7 345 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-252 | TO->FROM | 514898 CIMARON4 138 3WXFMR 524:524:CIMARON2 345 2 | B | 478 | 0.070638 | 102.3793 | P13:138:OKGE:BKRBKR_3W020:::HV: | TDF Impact | Add 3-winding transformer 514898 CIMARON4 138 514901 CIMARON7 345 515715 CIMARO21 13 M2
Thermal | 00NR | 1 | 26SP | T1 | GEN-2024-252 | TO->FROM | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | B | 444 | 0.030469 | 103.4096 | Single 514853 DVISION4 138 514863 HAYMAKR4 138 1 | TDF Impact | Rebuild line 514894 CZECHAL4 138 514898 CIMARON4 138 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-252 | TO->FROM | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | A | 1806 | 0.041876 | 104.7272 | System Intact | TDF Impact | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-252 | TO->FROM | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | A | 1806 | 0.047821 | 104.7927 | System Intact | TDF Impact | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1
Thermal | 00NR | 1 | 26SP | T1 | GEN-2024-252 | TO->FROM | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | B | 444 | 0.030469 | 105.2555 | P12:138:OKGE:BKRBKR1260:::HV: | TDF Impact | Rebuild line 514894 CZECHAL4 138 514898 CIMARON4 138 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-252 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1011 | 0.034037 | 106.9293 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 00NR | 1 | 26SP | T1 | GEN-2024-252 | TO->FROM | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | B | 444 | 0.030469 | 106.9994 | Single 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | TDF Impact | Rebuild line 514894 CZECHAL4 138 514898 CIMARON4 138 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-252 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1187 | 0.038358 | 112.2151 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-252 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.067317 | 114.4362 | System Intact | TDF Impact | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-252 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.062464 | 114.6025 | System Intact | TDF Impact | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-252 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.033193 | 137.9906 | System Intact | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-253 | TO->FROM | 640271 MCCOOL 3 345 640277 MOORE 3 345 1 | B | 956 | 0.051492 | 100.2221 | P42:345:NPPD:BKR-TOB-3304:::: | Cumulative Impact | Rebuild line 640271 MCCOOL 3 345 640277 MOORE 3 345 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-253 | TO->FROM | 541199 ST JOE 7 345 541400 EASTOWN7 345 1 | B | 1185 | 0.16145 | 100.396 | Single 541199 STJOE7 345 761383 G17-183-TAP 345 1 | Cumulative Impact | Rebuild line 541199 ST JOE 7 345 541400 EASTOWN7 345 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-253 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.078594 | 101.6955 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-253 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.078594 | 101.6955 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-253 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.078594 | 101.6955 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-253 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | A | 334 | 0.039414 | 103.3014 | System Intact | TDF Impact | Rebuild line 300071 5CLINTN 161 761278 G17-108-TAP 161 1
Thermal | 03ALL | 1 | 26SP | T1 | GEN-2024-253 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.074771 | 105.0133 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 29WP | T1 | GEN-2024-253 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.072657 | 106.2154 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-253 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.073602 | 106.5956 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-253 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.073602 | 106.5956 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-253 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.073602 | 106.5956 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-253 | TO->FROM | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | B | 1195 | 0.20325 | 106.5998 | Single 542980 NASHUA7 345 542982 IATAN7 345 1 | TDF Impact | Rebuild line 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-253 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.058956 | 106.8199 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-253 | TO->FROM | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | B | 1195 | 0.17733 | 107.005 | Single 541199 STJOE7 345 761383 G17-183-TAP 345 1 | Cumulative Impact | Rebuild line 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-253 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.052062 | 108.3331 | P42:345:NPPD:BKR-TOB-3304:::: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-253 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | A | 311 | 0.04157 | 111.039 | System Intact | TDF Impact | Rebuild line 300071 5CLINTN 161 761278 G17-108-TAP 161 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-253 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.080162 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-253 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.080162 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-253 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.080162 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-253 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.078018 | 117.7598 | P55:345:OPPD:S3458 3::FN13:EHV: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-253 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | A | 311 | 0.041628 | 121.8886 | System Intact | TDF Impact | Rebuild line 300071 5CLINTN 161 761278 G17-108-TAP 161 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-253 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | A | 334 | 0.040415 | 145.0684 | System Intact | TDF Impact | Rebuild line 300071 5CLINTN 161 761278 G17-108-TAP 161 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-253 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.043878 | 194.842 | System Intact | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-253 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.046073 | 202.7501 | System Intact | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-253 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.050321 | 205.4343 | P23:345:MEC:ORIENT:902::EHV: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-253 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.050339 | 205.5053 | P12:345:MEC:ORIENT:NORTHBORO:1 | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-253 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.050138 | 205.9776 | P55:345:MEC:ORIENT | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-253 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.052584 | 212.8881 | P55:345:MEC:NORTHBORO | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-253 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.052584 | 212.8881 | P23:345:MEC:NORTHBORO:901::EHV: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-253 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.052563 | 213.736 | P23:345:MEC:ORIENT:902::EHV: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-253 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.052411 | 213.7657 | P55:345:MEC:ORIENT | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-253 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.052584 | 213.7914 | P12:345:MEC:ORIENT:NORTHBORO:1 | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-253 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.056215 | 230.5239 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-253 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.051715 | 236.1008 | P42:345:NPPD:BKR-TOB-3304:::: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-253 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | A | 956 | 0.05303 | 242.4879 | System Intact | TDF Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-253 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.051341 | 247.7008 | Single 640600 DAYKIN3 345 771999 G23-222-POI 345 1 | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-253 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.059928 | 248.1828 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-253 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.060071 | 250.2801 | P55:345:MEC:NORTHBORO | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-253 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.060071 | 250.2801 | P23:345:MEC:NORTHBORO:901::EHV: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-253 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.052946 | 250.332 | Single 640076 BEATRCE7 115 640208 HARBINE7 115 1 | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-253 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.060071 | 251.4352 | P12:345:MEC:ORIENT:NORTHBORO:1 | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-253 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.060078 | 251.4821 | P23:345:MEC:ORIENT:902::EHV: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-253 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.060103 | 251.8126 | P55:345:MEC:ORIENT | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-253 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.051773 | 260.7181 | Single 640088 BPSSUB7 115 771999 G23-222-POI 345 771998 'NEW_TER_BPS ' 13 1 | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-254 | TO->FROM | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 | B | 1015 | 0.18007 | 102.04 | P42:345:OKGE:SB_DGSE7313:::EHV: | Cumulative Impact | Rebuild line 514715 WOODRNG7 345 515875 REDNGTN7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-254 | TO->FROM | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 | B | 1015 | 0.17474 | 102.2256 | P42:345:OKGE:SB_DGSE7313:::EHV: | Cumulative Impact | Rebuild line 514715 WOODRNG7 345 515875 REDNGTN7 345 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-254 | TO->FROM | 514898 CIMARON4 138 3WXFMR 524:524:CIMARON2 345 2 | B | 478 | 0.048347 | 102.3793 | P13:138:OKGE:BKRBKR_3W020:::HV: | TDF Impact | Add 3-winding transformer 514898 CIMARON4 138 514901 CIMARON7 345 515715 CIMARO21 13 M2
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-254 | TO->FROM | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | A | 1806 | 0.042071 | 104.7272 | System Intact | TDF Impact | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-254 | TO->FROM | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | A | 1806 | 0.048134 | 104.7927 | System Intact | TDF Impact | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-254 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1011 | 0.032842 | 106.9293 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-254 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1187 | 0.036671 | 112.2151 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-254 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.07251 | 114.4362 | System Intact | TDF Impact | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-254 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.068241 | 114.6025 | System Intact | TDF Impact | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-254 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.03208 | 137.9906 | System Intact | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-255 | TO->FROM | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 | B | 1015 | 0.10192 | 102.04 | P42:345:OKGE:SB_DGSE7313:::EHV: | Cumulative Impact | Rebuild line 514715 WOODRNG7 345 515875 REDNGTN7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-255 | TO->FROM | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 | B | 1015 | 0.10513 | 102.2256 | P42:345:OKGE:SB_DGSE7313:::EHV: | Cumulative Impact | Rebuild line 514715 WOODRNG7 345 515875 REDNGTN7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-255 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | A | 901 | 0.0303 | 102.5076 | System Intact | TDF Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-255 | TO->FROM | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | A | 1806 | 0.059478 | 104.7272 | System Intact | TDF Impact | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-255 | TO->FROM | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | A | 1806 | 0.06531 | 104.7927 | System Intact | TDF Impact | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-255 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1011 | 0.036249 | 106.9293 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-255 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1011 | 0.032746 | 107.7039 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-255 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1187 | 0.041988 | 112.2151 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-255 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.054077 | 113.7225 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-255 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.068359 | 114.4362 | System Intact | TDF Impact | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-255 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.062929 | 114.6025 | System Intact | TDF Impact | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-255 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.053419 | 115.4477 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-255 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.053419 | 117.1553 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-255 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.053419 | 117.1572 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-255 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.053419 | 119.7129 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-255 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.053419 | 124.3274 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-255 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.035412 | 137.9906 | System Intact | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-255 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.031938 | 138.1985 | System Intact | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-258 | TO->FROM | 541199 ST JOE 7 345 541400 EASTOWN7 345 1 | B | 1185 | 0.054215 | 100.396 | Single 541199 STJOE7 345 761383 G17-183-TAP 345 1 | Cumulative Impact | Rebuild line 541199 ST JOE 7 345 541400 EASTOWN7 345 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-258 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.14871 | 101.6955 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-258 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.14871 | 101.6955 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-258 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.14871 | 101.6955 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-258 | TO->FROM | 532939 N345 4 5 161 3WXFMR 536:N345 TX-2 161 2 | B | 550 | 0.030731 | 103.5308 | Single 533021 NEOSHO4 138 533023 N34534 138 1 | TDF Impact | Add 3-winding transformer 532793 NEOSHO 7 345 532825 N345 2 1 13 532939 N345 4 5 161 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-258 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | B | 829 | 0.033914 | 103.7671 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | TDF Impact | Rebuild line 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1
Thermal | 03ALL | 1 | 26SP | T1 | GEN-2024-258 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.15074 | 105.0133 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 29WP | T1 | GEN-2024-258 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.16088 | 106.2154 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-258 | TO->FROM | 532937 NEOSHO 5 161 532939 N345 4 5 161 1 | B | 557 | 0.030696 | 106.5051 | Single 533021 NEOSHO4 138 533023 N34534 138 1 | TDF Impact | Rebuild line 532937 NEOSHO 5 161 532939 N345 4 5 161 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-258 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.16311 | 106.5956 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-258 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.16311 | 106.5956 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-258 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.16311 | 106.5956 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-258 | TO->FROM | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | B | 1195 | 0.060201 | 107.005 | Single 541199 STJOE7 345 761383 G17-183-TAP 345 1 | Cumulative Impact | Rebuild line 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-258 | TO->FROM | 532939 N345 4 5 161 3WXFMR 536:N345 TX-2 161 2 | B | 550 | 0.030696 | 111.179 | Single 533021 NEOSHO4 138 533023 N34534 138 1 | TDF Impact | Add 3-winding transformer 532793 NEOSHO 7 345 532825 N345 2 1 13 532939 N345 4 5 161 M2
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-258 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.14906 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-258 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.14906 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-258 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.14906 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-259 | TO->FROM | 547485 CAR395 5 161 547491 PUR421 5 161 1 | B | 290 | 0.56525 | 100.088 | Single 547467 ORO1105 161 547490 FIR4175 161 1 | TDF Impact | Rebuild line 547485 CAR395 5 161 547491 PUR421 5 161 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-259 | TO->FROM | 505488 CARTHAG5 161 547485 CAR395 5 161 1 | B | 215 | 0.30621 | 100.118 | P23:345:AECI:7BLACKBERRY:6_2::: | TDF Impact | Rebuild line 505488 CARTHAG5 161 547485 CAR395 5 161 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-259 | TO->FROM | 505488 CARTHAG5 161 547485 CAR395 5 161 1 | B | 215 | 0.30621 | 100.1198 | P23:345:AECI:7BLACKBERRY:6_3::: | TDF Impact | Rebuild line 505488 CARTHAG5 161 547485 CAR395 5 161 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-259 | TO->FROM | 505488 CARTHAG5 161 547485 CAR395 5 161 1 | B | 215 | 0.30296 | 100.6261 | P12:345:AECI:BLCKBRRY:JSPR345:1:: | TDF Impact | Rebuild line 505488 CARTHAG5 161 547485 CAR395 5 161 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-259 | TO->FROM | 505488 CARTHAG5 161 547485 CAR395 5 161 1 | B | 215 | 0.30096 | 101.1594 | Single 505488 CARTHAG5 161 547466 ATL1095 161 1 | TDF Impact | Rebuild line 505488 CARTHAG5 161 547485 CAR395 5 161 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-259 | TO->FROM | 547467 ORO110 5 161 547490 FIR417 5 161 1 | B | 290 | 0.61775 | 101.3552 | Single 547476 ASB3495 161 547491 PUR4215 161 1 | TDF Impact | Rebuild line 547467 ORO110 5 161 547490 FIR417 5 161 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-259 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.067913 | 101.6955 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-259 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.067913 | 101.6955 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-259 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.067913 | 101.6955 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-259 | TO->FROM | 547467 ORO110 5 161 547490 FIR417 5 161 1 | B | 290 | 0.61185 | 102.0853 | Single 505488 CARTHAG5 161 547485 CAR3955 161 1 | TDF Impact | Rebuild line 547467 ORO110 5 161 547490 FIR417 5 161 1
Thermal | 03ALL | 1 | 29WP | T1 | GEN-2024-259 | TO->FROM | 505488 CARTHAG5 161 547485 CAR395 5 161 1 | B | 364 | 0.57765 | 102.5947 | Single 547477 CJ3665 161 547490 FIR4175 161 1 | TDF Impact | Rebuild line 505488 CARTHAG5 161 547485 CAR395 5 161 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-259 | TO->FROM | 505488 CARTHAG5 161 547485 CAR395 5 161 1 | B | 215 | 0.31342 | 102.8202 | Single 547466 ATL1095 161 547494 OAK4325 161 1 | TDF Impact | Rebuild line 505488 CARTHAG5 161 547485 CAR395 5 161 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-259 | TO->FROM | 505488 CARTHAG5 161 547485 CAR395 5 161 1 | B | 215 | 0.30571 | 102.9686 | P23:345:AECI:7BLACKBERRY:653::: | TDF Impact | Rebuild line 505488 CARTHAG5 161 547485 CAR395 5 161 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-259 | TO->FROM | 505490 CARTHG 2 69 3WXFMR 537:CRG X2 161 1 | B | 84 | 0.04632 | 103.1531 | Single 505490 CARTHG2 69 505488 CARTHAG5 161 505487 'CRG X1 1 ' 13 1 | TDF Impact | Carthage_Add_transformer_fixed.idv :
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-259 | TO->FROM | 505490 CARTHG 2 69 3WXFMR 300:CRG X1 161 1 | B | 84 | 0.046635 | 103.8455 | Single 505490 CARTHG2 69 505488 CARTHAG5 161 505489 'CRG X2 1 ' 13 1 | TDF Impact | Carthage_Add_transformer_fixed.idv :
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-259 | TO->FROM | 547485 CAR395 5 161 547491 PUR421 5 161 1 | B | 290 | 0.56525 | 103.9897 | Single 547477 CJ3665 161 547490 FIR4175 161 1 | TDF Impact | Rebuild line 547485 CAR395 5 161 547491 PUR421 5 161 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-259 | TO->FROM | 505488 CARTHAG5 161 547485 CAR395 5 161 1 | B | 215 | 0.30367 | 104.2906 | P23:345:AECI:7BLACKBERRY:6_2::: | TDF Impact | Rebuild line 505488 CARTHAG5 161 547485 CAR395 5 161 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-259 | TO->FROM | 505488 CARTHAG5 161 547485 CAR395 5 161 1 | B | 215 | 0.30367 | 104.297 | P23:345:AECI:7BLACKBERRY:6_3::: | TDF Impact | Rebuild line 505488 CARTHAG5 161 547485 CAR395 5 161 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-259 | TO->FROM | 505488 CARTHAG5 161 547485 CAR395 5 161 1 | B | 215 | 0.31342 | 104.3169 | Single 547467 ORO1105 161 547494 OAK4325 161 1 | TDF Impact | Rebuild line 505488 CARTHAG5 161 547485 CAR395 5 161 1
Thermal | 03ALL | 1 | 29WP | T1 | GEN-2024-259 | TO->FROM | 505488 CARTHAG5 161 547485 CAR395 5 161 1 | B | 364 | 0.57765 | 104.8704 | Single 547476 ASB3495 161 547477 CJ3665 161 1 | TDF Impact | Rebuild line 505488 CARTHAG5 161 547485 CAR395 5 161 1
Thermal | 03ALL | 1 | 26SP | T1 | GEN-2024-259 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.091714 | 105.0133 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-259 | TO->FROM | 547485 CAR395 5 161 547491 PUR421 5 161 1 | B | 290 | 0.55875 | 105.2314 | Single 547467 ORO1105 161 547490 FIR4175 161 1 | TDF Impact | Rebuild line 547485 CAR395 5 161 547491 PUR421 5 161 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-259 | TO->FROM | 547467 ORO110 5 161 547490 FIR417 5 161 1 | B | 290 | 0.61185 | 105.5535 | Single 547485 CAR3955 161 547491 PUR4215 161 1 | TDF Impact | Rebuild line 547467 ORO110 5 161 547490 FIR417 5 161 1
Thermal | 03ALL | 1 | 29WP | T1 | GEN-2024-259 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.075769 | 106.2154 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-259 | TO->FROM | 505488 CARTHAG5 161 547485 CAR395 5 161 1 | B | 215 | 0.31046 | 106.3682 | Single 547466 ATL1095 161 547494 OAK4325 161 1 | TDF Impact | Rebuild line 505488 CARTHAG5 161 547485 CAR395 5 161 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-259 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.071752 | 106.5956 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-259 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.071752 | 106.5956 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-259 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.071752 | 106.5956 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-259 | TO->FROM | 547485 CAR395 5 161 547491 PUR421 5 161 1 | B | 290 | 0.56525 | 106.6168 | Single 547476 ASB3495 161 547477 CJ3665 161 1 | TDF Impact | Rebuild line 547485 CAR395 5 161 547491 PUR421 5 161 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-259 | TO->FROM | 547467 ORO110 5 161 547490 FIR417 5 161 1 | B | 335 | 0.61764 | 107.0303 | Single 505488 CARTHAG5 161 547485 CAR3955 161 1 | TDF Impact | Rebuild line 547467 ORO110 5 161 547490 FIR417 5 161 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-259 | TO->FROM | 547467 ORO110 5 161 547490 FIR417 5 161 1 | B | 290 | 0.61185 | 107.1853 | Single 547476 ASB3495 161 547491 PUR4215 161 1 | TDF Impact | Rebuild line 547467 ORO110 5 161 547490 FIR417 5 161 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-259 | TO->FROM | 505488 CARTHAG5 161 547485 CAR395 5 161 1 | B | 215 | 0.3031 | 107.6914 | P23:345:AECI:7BLACKBERRY:653::: | TDF Impact | Rebuild line 505488 CARTHAG5 161 547485 CAR395 5 161 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-259 | TO->FROM | 505488 CARTHAG5 161 547485 CAR395 5 161 1 | B | 215 | 0.31046 | 107.8439 | Single 547467 ORO1105 161 547494 OAK4325 161 1 | TDF Impact | Rebuild line 505488 CARTHAG5 161 547485 CAR395 5 161 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-259 | TO->FROM | 547485 CAR395 5 161 547491 PUR421 5 161 1 | B | 290 | 0.55875 | 109.0445 | Single 547477 CJ3665 161 547490 FIR4175 161 1 | TDF Impact | Rebuild line 547485 CAR395 5 161 547491 PUR421 5 161 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-259 | TO->FROM | 547485 CAR395 5 161 547491 PUR421 5 161 1 | B | 335 | 0.56534 | 109.0981 | Single 547467 ORO1105 161 547490 FIR4175 161 1 | TDF Impact | Rebuild line 547485 CAR395 5 161 547491 PUR421 5 161 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-259 | TO->FROM | 547467 ORO110 5 161 547490 FIR417 5 161 1 | B | 335 | 0.61764 | 110.2044 | Single 547485 CAR3955 161 547491 PUR4215 161 1 | TDF Impact | Rebuild line 547467 ORO110 5 161 547490 FIR417 5 161 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-259 | TO->FROM | 547485 CAR395 5 161 547491 PUR421 5 161 1 | B | 290 | 0.55875 | 111.6106 | Single 547476 ASB3495 161 547477 CJ3665 161 1 | TDF Impact | Rebuild line 547485 CAR395 5 161 547491 PUR421 5 161 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-259 | TO->FROM | 547467 ORO110 5 161 547490 FIR417 5 161 1 | B | 335 | 0.61764 | 111.6996 | Single 547476 ASB3495 161 547491 PUR4215 161 1 | TDF Impact | Rebuild line 547467 ORO110 5 161 547490 FIR417 5 161 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-259 | TO->FROM | 547485 CAR395 5 161 547491 PUR421 5 161 1 | B | 335 | 0.56534 | 112.6041 | Single 547477 CJ3665 161 547490 FIR4175 161 1 | TDF Impact | Rebuild line 547485 CAR395 5 161 547491 PUR421 5 161 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-259 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.071524 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-259 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.071524 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-259 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.071524 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-259 | TO->FROM | 547485 CAR395 5 161 547491 PUR421 5 161 1 | B | 335 | 0.56534 | 114.965 | Single 547476 ASB3495 161 547477 CJ3665 161 1 | TDF Impact | Rebuild line 547485 CAR395 5 161 547491 PUR421 5 161 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-259 | TO->FROM | 505488 CARTHAG5 161 547485 CAR395 5 161 1 | B | 293 | 0.56534 | 119.6608 | Single 547467 ORO1105 161 547490 FIR4175 161 1 | TDF Impact | Rebuild line 505488 CARTHAG5 161 547485 CAR395 5 161 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-259 | TO->FROM | 505488 CARTHAG5 161 547485 CAR395 5 161 1 | B | 293 | 0.56534 | 123.6645 | Single 547477 CJ3665 161 547490 FIR4175 161 1 | TDF Impact | Rebuild line 505488 CARTHAG5 161 547485 CAR395 5 161 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-259 | TO->FROM | 505488 CARTHAG5 161 547485 CAR395 5 161 1 | B | 293 | 0.56534 | 126.3605 | Single 547476 ASB3495 161 547477 CJ3665 161 1 | TDF Impact | Rebuild line 505488 CARTHAG5 161 547485 CAR395 5 161 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-259 | TO->FROM | 505488 CARTHAG5 161 547485 CAR395 5 161 1 | B | 215 | 0.56525 | 128.319 | Single 547467 ORO1105 161 547490 FIR4175 161 1 | TDF Impact | Rebuild line 505488 CARTHAG5 161 547485 CAR395 5 161 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-259 | TO->FROM | 505488 CARTHAG5 161 547485 CAR395 5 161 1 | B | 215 | 0.56525 | 133.5788 | Single 547477 CJ3665 161 547490 FIR4175 161 1 | TDF Impact | Rebuild line 505488 CARTHAG5 161 547485 CAR395 5 161 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-259 | TO->FROM | 505488 CARTHAG5 161 547485 CAR395 5 161 1 | B | 215 | 0.55875 | 135.3716 | Single 547467 ORO1105 161 547490 FIR4175 161 1 | TDF Impact | Rebuild line 505488 CARTHAG5 161 547485 CAR395 5 161 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-259 | TO->FROM | 505488 CARTHAG5 161 547485 CAR395 5 161 1 | B | 215 | 0.56525 | 137.1198 | Single 547476 ASB3495 161 547477 CJ3665 161 1 | TDF Impact | Rebuild line 505488 CARTHAG5 161 547485 CAR395 5 161 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-259 | TO->FROM | 505488 CARTHAG5 161 547485 CAR395 5 161 1 | B | 215 | 0.55875 | 140.5112 | Single 547477 CJ3665 161 547490 FIR4175 161 1 | TDF Impact | Rebuild line 505488 CARTHAG5 161 547485 CAR395 5 161 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-259 | TO->FROM | 505488 CARTHAG5 161 547485 CAR395 5 161 1 | B | 215 | 0.55875 | 143.9699 | Single 547476 ASB3495 161 547477 CJ3665 161 1 | TDF Impact | Rebuild line 505488 CARTHAG5 161 547485 CAR395 5 161 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-260 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.067628 | 101.6955 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-260 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.067628 | 101.6955 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-260 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.067628 | 101.6955 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 26SP | T1 | GEN-2024-260 | TO->FROM | 541369 MIDWAY_5 161 541394 AVENUECTY 5 161 1 | A | 161 | 0.066023 | 104.1401 | System Intact | TDF Impact | Rebuild line 541369 MIDWAY_5 161 541394 AVENUECTY 5 161 1
Thermal | 03ALL | 1 | 26SP | T1 | GEN-2024-260 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.063653 | 105.0133 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 29WP | T1 | GEN-2024-260 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.059503 | 106.2154 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-260 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.060519 | 106.5956 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-260 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.060519 | 106.5956 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-260 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.060519 | 106.5956 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-260 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.063008 | 106.8199 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-260 | TO->FROM | 541254 EAST 5 161 541401 EASTOWN5 161 1 | B | 334 | 0.33521 | 108.1532 | P23:345:GMO-AECI:STJOE_R3-14::STJOE-EASTOWNE-FAIRPORT_1 | TDF Impact | Rebuild line 541254 EAST 5 161 541401 EASTOWN5 161 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-260 | TO->FROM | 541254 EAST 5 161 541401 EASTOWN5 161 1 | B | 334 | 0.33521 | 108.1532 | P23:345:GMO-AECI:STJOE-R3-14:::EHV: | TDF Impact | Rebuild line 541254 EAST 5 161 541401 EASTOWN5 161 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-260 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.053111 | 108.3331 | P42:345:NPPD:BKR-TOB-3304:::: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-260 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.06942 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-260 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.06942 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-260 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.06942 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-260 | TO->FROM | 541254 EAST 5 161 541401 EASTOWN5 161 1 | B | 334 | 0.3435 | 117.1628 | Single 541199 STJOE7 345 541400 EASTOWN7 345 1 | TDF Impact | Rebuild line 541254 EAST 5 161 541401 EASTOWN5 161 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-260 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.11531 | 117.7598 | P55:345:OPPD:S3458 3::FN13:EHV: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 03ALL | 1 | 29SP | T1 | GEN-2024-260 | TO->FROM | 541251 MARYVLE5 161 541369 MIDWAY_5 161 1 | A | 161 | 0.066323 | 118.7915 | System Intact | TDF Impact | Rebuild line 541251 MARYVLE5 161 541369 MIDWAY_5 161 1
Thermal | 03ALL | 1 | 29SP | T1 | GEN-2024-260 | TO->FROM | 541369 MIDWAY_5 161 541394 AVENUECTY 5 161 1 | A | 161 | 0.066323 | 127.6857 | System Intact | TDF Impact | Rebuild line 541369 MIDWAY_5 161 541394 AVENUECTY 5 161 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-261 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.071579 | 100.0488 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-261 | TO->FROM | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | B | 997 | 0.17927 | 100.166 | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | Cumulative Impact | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-261 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.06252 | 100.533 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-261 | TO->FROM | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | B | 997 | 0.18292 | 100.7286 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-261 | TO->FROM | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | B | 997 | 0.18292 | 101.1047 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-261 | TO->FROM | 527891 HOBBS_INT 3 115 784800 G24-261-TAP 115 1 | B | 199 | 0.9977 | 101.7442 | Single 528333 LE-WEST_SUB3 115 528334 LE-NRTH_INT3 115 1 | TDF Impact | Rebuild line 527891 HOBBS_INT 3 115 784800 G24-261-TAP 115 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-261 | TO->FROM | 527891 HOBBS_INT 3 115 784800 G24-261-TAP 115 1 | B | 199 | 0.99794 | 101.8764 | Single 528333 LE-WEST_SUB3 115 528334 LE-NRTH_INT3 115 1 | TDF Impact | Rebuild line 527891 HOBBS_INT 3 115 784800 G24-261-TAP 115 1
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-261 | TO->FROM | 527891 HOBBS_INT 3 115 784800 G24-261-TAP 115 1 | B | 199 | 0.99783 | 102.1468 | Single 528333 LE-WEST_SUB3 115 528334 LE-NRTH_INT3 115 1 | TDF Impact | Rebuild line 527891 HOBBS_INT 3 115 784800 G24-261-TAP 115 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-261 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063415 | 102.9616 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-261 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063415 | 102.9634 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-261 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063415 | 103.0288 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-261 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063415 | 103.4739 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-261 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.075251 | 103.9266 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-261 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063415 | 104.1493 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-261 | TO->FROM | 528618 LE-LOVINTON2 69 528334 LE-NRTH_INT3 115 1 | B | 100 | 0.03841 | 104.5575 | Single 528348 BUCKEYE_TP3 115 528627 LE-TXACO_TP3 115 1 | TDF Impact | Rebuild 2-winding transformer 528334 LE-NRTH_INT3 115 528618 LE-LOVINTON2 69 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-261 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.074703 | 104.7552 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-261 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.074703 | 104.888 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-261 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.078317 | 107.2243 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-261 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063415 | 107.2793 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-261 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063415 | 107.2794 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-261 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.078317 | 107.2951 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-261 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063415 | 107.3093 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-261 | TO->FROM | 523959 POTTER_CO 6 230 3WXFMR 526:WAUK 90343-A 230 1 | B | 559 | 0.10911 | 107.3794 | P42:345:SPS:HITCHLAND-1R15:::EHV: | Cumulative Impact | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-261 | TO->FROM | 523959 POTTER_CO 6 230 3WXFMR 526:WAUK 90343-A 230 1 | B | 559 | 0.10911 | 107.3953 | Single 523097 HITCHLAND7 345 523961 POTTER_CO7 345 1 | Cumulative Impact | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-261 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.072667 | 107.5866 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-261 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063415 | 107.7557 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-261 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063415 | 108.1822 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-261 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063415 | 108.2747 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-261 | TO->FROM | 528618 LE-LOVINTON2 69 528334 LE-NRTH_INT3 115 1 | B | 100 | 0.03841 | 109.6229 | Single 527864 CUNNINHAM3 115 528348 BUCKEYE_TP3 115 1 | TDF Impact | Rebuild 2-winding transformer 528334 LE-NRTH_INT3 115 528618 LE-LOVINTON2 69 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-261 | TO->FROM | 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | B | 997 | 0.23996 | 109.7018 | Single 525832 TUCO_INT7 345 526000 CRAWFISH_DR 345 2 | TDF Impact | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-261 | TO->FROM | 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | B | 997 | 0.24186 | 111.09 | Single 525832 TUCO_INT7 345 526000 CRAWFISH_DR 345 2 | TDF Impact | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-261 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063415 | 111.3621 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-261 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.075808 | 111.723 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-261 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.075808 | 111.8755 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-261 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.072667 | 115.0541 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-261 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.075808 | 118.9427 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-261 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.075808 | 119.313 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-261 | TO->FROM | 528618 LE-LOVINTON2 69 528334 LE-NRTH_INT3 115 1 | B | 100 | 0.06996 | 126.5657 | Single 528626 LE-PLNSINT2 69 528709 LE-PLNSGOAB2 69 1 | TDF Impact | Rebuild 2-winding transformer 528334 LE-NRTH_INT3 115 528618 LE-LOVINTON2 69 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-265 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.071535 | 100.0488 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-265 | TO->FROM | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | B | 997 | 0.1795 | 100.166 | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | Cumulative Impact | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-265 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.062518 | 100.533 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-265 | TO->FROM | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | B | 997 | 0.18316 | 100.7286 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-265 | TO->FROM | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | B | 997 | 0.18316 | 101.1047 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-265 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063416 | 102.9616 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-265 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063416 | 102.9634 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-265 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063416 | 103.0288 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-265 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063416 | 103.4739 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-265 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.075186 | 103.9266 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-265 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063416 | 104.1493 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-265 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.074664 | 104.7552 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-265 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.074664 | 104.888 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-265 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.078256 | 107.2243 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-265 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063416 | 107.2793 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-265 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063416 | 107.2794 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-265 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.078256 | 107.2951 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-265 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063416 | 107.3093 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-265 | TO->FROM | 523959 POTTER_CO 6 230 3WXFMR 526:WAUK 90343-A 230 1 | B | 559 | 0.10698 | 107.3794 | P42:345:SPS:HITCHLAND-1R15:::EHV: | Cumulative Impact | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-265 | TO->FROM | 523959 POTTER_CO 6 230 3WXFMR 526:WAUK 90343-A 230 1 | B | 559 | 0.10698 | 107.3953 | Single 523097 HITCHLAND7 345 523961 POTTER_CO7 345 1 | Cumulative Impact | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-265 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.072627 | 107.5866 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-265 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063416 | 107.7557 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-265 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063416 | 108.1822 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-265 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063416 | 108.2747 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-265 | TO->FROM | 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | B | 997 | 0.2461 | 109.7018 | Single 525832 TUCO_INT7 345 526000 CRAWFISH_DR 345 2 | TDF Impact | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-265 | TO->FROM | 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | B | 997 | 0.24834 | 111.09 | Single 525832 TUCO_INT7 345 526000 CRAWFISH_DR 345 2 | TDF Impact | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-265 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063416 | 111.3621 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-265 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.075771 | 111.723 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-265 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.075771 | 111.8755 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-265 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.072627 | 115.0541 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-265 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.075771 | 118.9427 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-265 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.075771 | 119.313 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-268 | TO->FROM | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | B | 1059 | 0.22445 | 100.2166 | P12:345:AEPW:R.S.S.-7:ONETA--7::: | TDF Impact | Rebuild line 509745 CLARKSV7 345 515224 MUSKOGE7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-268 | TO->FROM | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | B | 1059 | 0.27635 | 100.8866 | Single 515231 KEEFTON7 345 780360 G24-113-TAP 345 1 | TDF Impact | Rebuild line 509745 CLARKSV7 345 515224 MUSKOGE7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-268 | TO->FROM | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | A | 1806 | 0.030236 | 104.7927 | System Intact | TDF Impact | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-268 | TO->FROM | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | B | 1059 | 0.27637 | 105.0001 | P42:345:OKGE:SB_FTTH7386:::EHV: | TDF Impact | Rebuild line 509745 CLARKSV7 345 515224 MUSKOGE7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-268 | TO->FROM | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | B | 1059 | 0.27635 | 105.0075 | Single 515012 RVRVALY7 345 515302 FTSMITH7 345 1 | TDF Impact | Rebuild line 509745 CLARKSV7 345 515224 MUSKOGE7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-268 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1011 | 0.062466 | 106.9293 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-268 | TO->FROM | 515227 5TRIBES2 69 516093 OKTAHA 2 69 1 | B | 111 | 0.041141 | 107.0862 | P22:345:EES:MUSKOGE7!:::EHV: | TDF Impact | Rebuild line 515227 5TRIBES2 69 516093 OKTAHA 2 69 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-268 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1011 | 0.061063 | 107.7039 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-268 | TO->FROM | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | A | 827 | 0.032748 | 107.8643 | System Intact | TDF Impact | Rebuild line 532791 BENTON 7 345 532794 ROSEHIL7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-268 | TO->FROM | 515305 FTSMITH8 500 3WXFMR 524:524:FTSMITH1 500 1 | B | 693 | 0.14687 | 108.5609 | P12:161:EES:FTSMTHW5%:FTSMITH7%:FTSMTH511:HV: | Cumulative Impact | Add 3-winding transformer 515302 FTSMITH7 345 515305 FTSMITH8 500 515726 FTSMTH11 13 M2
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-268 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1187 | 0.077086 | 112.2151 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-268 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.085573 | 112.5233 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-268 | TO->FROM | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | A | 827 | 0.034027 | 113.506 | System Intact | TDF Impact | Rebuild line 532791 BENTON 7 345 532794 ROSEHIL7 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-268 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.082325 | 113.7225 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-268 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.08397 | 114.0272 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-268 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.077531 | 114.0895 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-268 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.081668 | 115.4477 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-268 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.077531 | 115.647 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-268 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.081668 | 117.1553 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-268 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.081668 | 117.1572 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-268 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.081668 | 119.7129 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-268 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.081668 | 124.3274 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-268 | TO->FROM | 515301 FTSMTHW5 161 3WXFMR 524:524:FTSMITH5 345 5 | B | 493 | 0.11309 | 126.769 | P12:345:EES:FTSMITH7%:FTSMITH8%:FTSMTH111:EHV: | Cumulative Impact | Add 3-winding transformer 515301 FTSMTHW5 161 515302 FTSMITH7 345 515728 FTSMTH51 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-268 | TO->FROM | 516093 OKTAHA 2 69 3WXFMR OKTAHA 5 69 7 | B | 112 | 0.053035 | 127.8893 | P22:345:EES:MUSKOGE7!:::EHV: | TDF Impact | Rebuild 3-winding transformer 516092 OKTAHA 5 161 516093 OKTAHA 2 69 516095 OKTAHA71 13 7
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-268 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.059166 | 137.9906 | System Intact | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-268 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.057764 | 138.1985 | System Intact | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-268 | TO->FROM | 516093 OKTAHA 2 69 3WXFMR OKTAHA 5 69 7 | B | 112 | 0.052675 | 146.2088 | P22:345:EES:MUSKOGE7!:::EHV: | TDF Impact | Rebuild 3-winding transformer 516092 OKTAHA 5 161 516093 OKTAHA 2 69 516095 OKTAHA71 13 7
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-268 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.059823 | 155.4006 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-268 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.063869 | 155.7991 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-268 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.06238 | 155.8883 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-268 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.058239 | 158.3302 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-268 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.06416 | 159.2546 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-268 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.06215 | 159.5575 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-268 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.068374 | 160.5677 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-268 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.063627 | 161.638 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-268 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.065754 | 161.7992 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-268 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.06675 | 161.8408 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-268 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.061561 | 162.2698 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-268 | TO->FROM | 516093 OKTAHA 2 69 3WXFMR OKTAHA 5 69 7 | B | 112 | 0.053712 | 163.0673 | P22:345:EES:MUSKOGE7!:::EHV: | TDF Impact | Rebuild 3-winding transformer 516092 OKTAHA 5 161 516093 OKTAHA 2 69 516095 OKTAHA71 13 7
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-268 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.064246 | 163.3422 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-268 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.063627 | 164.1736 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-268 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.063627 | 164.1763 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-268 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.061561 | 164.8475 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-268 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.061561 | 164.8482 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-268 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.063627 | 167.9939 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-268 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.061561 | 169.069 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-268 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.063627 | 175.0352 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-268 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.061561 | 177.0235 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-276 | TO->FROM | 541199 ST JOE 7 345 541400 EASTOWN7 345 1 | B | 1185 | 0.092674 | 100.396 | Single 541199 STJOE7 345 761383 G17-183-TAP 345 1 | Cumulative Impact | Rebuild line 541199 ST JOE 7 345 541400 EASTOWN7 345 1
Thermal | 03ALL | 1 | 29SP | T1 | GEN-2024-276 | TO->FROM | 532857 TECHILL6 230 785250 G24-276-TAP 230 1 | B | 386 | 0.47304 | 100.5203 | P12:230:WERE:LAWH-SWIS-230:HV: | TDF Impact | Rebuild line 532857 TECHILL6 230 785250 G24-276-TAP 230 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-276 | TO->FROM | 533182 TECHILE3 115 3WXFMR 536:TECHILL TX-3 115 1 | B | 308 | 0.40613 | 100.9098 | P23:345:KCPL-WERE:241WGARDNER-R12-13:::EHV: | TDF Impact | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2
Thermal | 03ALL | 1 | 29SP | T1 | GEN-2024-276 | TO->FROM | 532857 TECHILL6 230 785250 G24-276-TAP 230 1 | B | 386 | 0.46189 | 100.9424 | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | Rebuild line 532857 TECHILL6 230 785250 G24-276-TAP 230 1
Thermal | 03ALL | 1 | 26SP | T1 | GEN-2024-276 | TO->FROM | 532857 TECHILL6 230 785250 G24-276-TAP 230 1 | B | 386 | 0.43053 | 101.1427 | Single 532765 HOYT7 345 533163 HOYT3 115 532804 'HOYT 1 ' 14 1 | TDF Impact | Rebuild line 532857 TECHILL6 230 785250 G24-276-TAP 230 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-276 | TO->FROM | 533182 TECHILE3 115 3WXFMR 536:TECHILL TX-3 115 1 | B | 308 | 0.40636 | 101.1762 | P12:345:WERE:SWIS-WGAR-345:::EHV: | TDF Impact | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-276 | TO->FROM | 532857 TECHILL6 230 785250 G24-276-TAP 230 1 | B | 318 | 0.38024 | 101.3216 | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | Rebuild line 532857 TECHILL6 230 785250 G24-276-TAP 230 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-276 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.07964 | 101.6955 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-276 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.07964 | 101.6955 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-276 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.07964 | 101.6955 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 26SP | T1 | GEN-2024-276 | TO->FROM | 532857 TECHILL6 230 785250 G24-276-TAP 230 1 | B | 386 | 0.45883 | 102.0917 | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | Rebuild line 532857 TECHILL6 230 785250 G24-276-TAP 230 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-276 | TO->FROM | 532857 TECHILL6 230 785250 G24-276-TAP 230 1 | B | 318 | 0.3936 | 102.1142 | P12:230:WERE:LAWH-SWIS-230:HV: | TDF Impact | Rebuild line 532857 TECHILL6 230 785250 G24-276-TAP 230 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-276 | TO->FROM | 533182 TECHILE3 115 3WXFMR 536:TECHILL TX-3 115 1 | B | 308 | 0.38024 | 102.3222 | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-276 | TO->FROM | 532857 TECHILL6 230 785250 G24-276-TAP 230 1 | B | 318 | 0.37824 | 102.3789 | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | Rebuild line 532857 TECHILL6 230 785250 G24-276-TAP 230 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-276 | TO->FROM | 533182 TECHILE3 115 3WXFMR 536:TECHILL TX-3 115 1 | A | 280 | 0.38057 | 103.0405 | System Intact | TDF Impact | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-276 | TO->FROM | 533182 TECHILE3 115 3WXFMR 536:TECHILL TX-3 115 1 | B | 308 | 0.3936 | 103.1556 | P12:230:WERE:LAWH-SWIS-230:HV: | TDF Impact | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-276 | TO->FROM | 532857 TECHILL6 230 785250 G24-276-TAP 230 1 | B | 318 | 0.35723 | 103.5245 | Single 532765 HOYT7 345 533163 HOYT3 115 532804 'HOYT 1 ' 14 1 | TDF Impact | Rebuild line 532857 TECHILL6 230 785250 G24-276-TAP 230 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-276 | TO->FROM | 533182 TECHILE3 115 3WXFMR 536:TECHILL TX-3 115 1 | B | 308 | 0.37824 | 103.7091 | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-276 | TO->FROM | 533182 TECHILE3 115 3WXFMR 536:TECHILL TX-3 115 1 | B | 308 | 0.35723 | 104.1314 | Single 532765 HOYT7 345 533163 HOYT3 115 532804 'HOYT 1 ' 14 1 | TDF Impact | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2
Thermal | 03ALL | 1 | 29SP | T1 | GEN-2024-276 | TO->FROM | 532857 TECHILL6 230 785250 G24-276-TAP 230 1 | B | 386 | 0.49147 | 104.5244 | P23:345:KCPL-WERE:241WGARDNER-R12-13:::EHV: | TDF Impact | Rebuild line 532857 TECHILL6 230 785250 G24-276-TAP 230 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-276 | TO->FROM | 532857 TECHILL6 230 785250 G24-276-TAP 230 1 | B | 318 | 0.37815 | 104.6533 | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | Rebuild line 532857 TECHILL6 230 785250 G24-276-TAP 230 1
Thermal | 03ALL | 1 | 29SP | T1 | GEN-2024-276 | TO->FROM | 532857 TECHILL6 230 785250 G24-276-TAP 230 1 | B | 386 | 0.49175 | 104.7827 | P12:345:WERE:SWIS-WGAR-345:::EHV: | TDF Impact | Rebuild line 532857 TECHILL6 230 785250 G24-276-TAP 230 1
Thermal | 03ALL | 1 | 26SP | T1 | GEN-2024-276 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.071589 | 105.0133 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 26SP | T1 | GEN-2024-276 | TO->FROM | 532857 TECHILL6 230 785250 G24-276-TAP 230 1 | B | 386 | 0.44084 | 105.4121 | Single 532851 AUBURN6 230 533151 AUBURN3 115 532880 'AUBURN 1 ' 14 1 | TDF Impact | Rebuild line 532857 TECHILL6 230 785250 G24-276-TAP 230 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-276 | TO->FROM | 533182 TECHILE3 115 3WXFMR 536:TECHILL TX-3 115 1 | B | 308 | 0.37815 | 105.5459 | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-276 | TO->FROM | 532857 TECHILL6 230 785250 G24-276-TAP 230 1 | B | 318 | 0.40654 | 105.8803 | P23:345:KCPL-WERE:241WGARDNER-R12-13:::EHV: | TDF Impact | Rebuild line 532857 TECHILL6 230 785250 G24-276-TAP 230 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-276 | TO->FROM | 532857 TECHILL6 230 785250 G24-276-TAP 230 1 | B | 318 | 0.40677 | 106.1459 | P12:345:WERE:SWIS-WGAR-345:::EHV: | TDF Impact | Rebuild line 532857 TECHILL6 230 785250 G24-276-TAP 230 1
Thermal | 03ALL | 1 | 29WP | T1 | GEN-2024-276 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.072261 | 106.2154 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-276 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.073711 | 106.5956 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-276 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.073711 | 106.5956 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-276 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.073711 | 106.5956 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-276 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.067819 | 106.8199 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-276 | TO->FROM | 533182 TECHILE3 115 3WXFMR 536:TECHILL TX-3 115 1 | B | 308 | 0.40654 | 106.9363 | P23:345:KCPL-WERE:241WGARDNER-R12-13:::EHV: | TDF Impact | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-276 | TO->FROM | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | B | 1195 | 0.10242 | 107.005 | Single 541199 STJOE7 345 761383 G17-183-TAP 345 1 | Cumulative Impact | Rebuild line 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-276 | TO->FROM | 533182 TECHILE3 115 3WXFMR 536:TECHILL TX-3 115 1 | B | 308 | 0.40677 | 107.1866 | P12:345:WERE:SWIS-WGAR-345:::EHV: | TDF Impact | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-276 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.062716 | 108.3331 | P42:345:NPPD:BKR-TOB-3304:::: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-276 | TO->FROM | 532857 TECHILL6 230 785250 G24-276-TAP 230 1 | B | 318 | 0.36951 | 108.8422 | Single 532851 AUBURN6 230 533151 AUBURN3 115 532880 'AUBURN 1 ' 14 1 | TDF Impact | Rebuild line 532857 TECHILL6 230 785250 G24-276-TAP 230 1
Thermal | 03ALL | 1 | 29SP | T1 | GEN-2024-276 | TO->FROM | 532857 TECHILL6 230 785250 G24-276-TAP 230 1 | B | 386 | 0.45943 | 109.6453 | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | Rebuild line 532857 TECHILL6 230 785250 G24-276-TAP 230 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-276 | TO->FROM | 533182 TECHILE3 115 3WXFMR 536:TECHILL TX-3 115 1 | B | 308 | 0.36951 | 109.6861 | Single 532851 AUBURN6 230 533151 AUBURN3 115 532880 'AUBURN 1 ' 14 1 | TDF Impact | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2
Thermal | 03ALL | 1 | 29SP | T1 | GEN-2024-276 | TO->FROM | 532857 TECHILL6 230 785250 G24-276-TAP 230 1 | B | 386 | 0.43093 | 109.8119 | Single 532765 HOYT7 345 533163 HOYT3 115 532804 'HOYT 1 ' 14 1 | TDF Impact | Rebuild line 532857 TECHILL6 230 785250 G24-276-TAP 230 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-276 | TO->FROM | 532857 TECHILL6 230 785250 G24-276-TAP 230 1 | B | 318 | 0.37866 | 110.4565 | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | Rebuild line 532857 TECHILL6 230 785250 G24-276-TAP 230 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-276 | TO->FROM | 533182 TECHILE3 115 3WXFMR 536:TECHILL TX-3 115 1 | B | 308 | 0.35756 | 110.9541 | Single 532765 HOYT7 345 533163 HOYT3 115 532804 'HOYT 1 ' 14 1 | TDF Impact | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-276 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | A | 311 | 0.035975 | 111.039 | System Intact | TDF Impact | Rebuild line 300071 5CLINTN 161 761278 G17-108-TAP 161 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-276 | TO->FROM | 533182 TECHILE3 115 3WXFMR 536:TECHILL TX-3 115 1 | B | 308 | 0.37866 | 111.1551 | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-276 | TO->FROM | 532857 TECHILL6 230 785250 G24-276-TAP 230 1 | B | 318 | 0.35756 | 111.1899 | Single 532765 HOYT7 345 533163 HOYT3 115 532804 'HOYT 1 ' 14 1 | TDF Impact | Rebuild line 532857 TECHILL6 230 785250 G24-276-TAP 230 1
Thermal | 03ALL | 1 | 29SP | T1 | GEN-2024-276 | TO->FROM | 532857 TECHILL6 230 785250 G24-276-TAP 230 1 | B | 386 | 0.45933 | 112.0505 | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | Rebuild line 532857 TECHILL6 230 785250 G24-276-TAP 230 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-276 | TO->FROM | 532857 TECHILL6 230 785250 G24-276-TAP 230 1 | B | 318 | 0.37857 | 112.9505 | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | Rebuild line 532857 TECHILL6 230 785250 G24-276-TAP 230 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-276 | TO->FROM | 533182 TECHILE3 115 3WXFMR 536:TECHILL TX-3 115 1 | B | 308 | 0.37857 | 113.0746 | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2
Thermal | 03ALL | 1 | 29SP | T1 | GEN-2024-276 | TO->FROM | 532857 TECHILL6 230 785250 G24-276-TAP 230 1 | B | 386 | 0.44127 | 114.6785 | Single 532851 AUBURN6 230 533151 AUBURN3 115 532880 'AUBURN 1 ' 14 1 | TDF Impact | Rebuild line 532857 TECHILL6 230 785250 G24-276-TAP 230 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-276 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.080915 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-276 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.080915 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-276 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.080915 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-276 | TO->FROM | 532857 TECHILL6 230 785250 G24-276-TAP 230 1 | B | 318 | 0.36987 | 117.2217 | Single 532851 AUBURN6 230 533151 AUBURN3 115 532880 'AUBURN 1 ' 14 1 | TDF Impact | Rebuild line 532857 TECHILL6 230 785250 G24-276-TAP 230 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-276 | TO->FROM | 533182 TECHILE3 115 3WXFMR 536:TECHILL TX-3 115 1 | B | 308 | 0.36987 | 117.3469 | Single 532851 AUBURN6 230 533151 AUBURN3 115 532880 'AUBURN 1 ' 14 1 | TDF Impact | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-276 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.062068 | 117.7598 | P55:345:OPPD:S3458 3::FN13:EHV: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-276 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | A | 311 | 0.036111 | 121.8886 | System Intact | TDF Impact | Rebuild line 300071 5CLINTN 161 761278 G17-108-TAP 161 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-276 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | A | 334 | 0.034537 | 145.0684 | System Intact | TDF Impact | Rebuild line 300071 5CLINTN 161 761278 G17-108-TAP 161 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-277 | TO->FROM | 541199 ST JOE 7 345 541400 EASTOWN7 345 1 | B | 1185 | 0.092674 | 100.396 | Single 541199 STJOE7 345 761383 G17-183-TAP 345 1 | Cumulative Impact | Rebuild line 541199 ST JOE 7 345 541400 EASTOWN7 345 1
Thermal | 03ALL | 1 | 29SP | T1 | GEN-2024-277 | TO->FROM | 532857 TECHILL6 230 785250 G24-276-TAP 230 1 | B | 386 | 0.47304 | 100.5203 | P12:230:WERE:LAWH-SWIS-230:HV: | TDF Impact | Rebuild line 532857 TECHILL6 230 785250 G24-276-TAP 230 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-277 | TO->FROM | 533182 TECHILE3 115 3WXFMR 536:TECHILL TX-3 115 1 | B | 308 | 0.40613 | 100.9098 | P23:345:KCPL-WERE:241WGARDNER-R12-13:::EHV: | TDF Impact | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2
Thermal | 03ALL | 1 | 29SP | T1 | GEN-2024-277 | TO->FROM | 532857 TECHILL6 230 785250 G24-276-TAP 230 1 | B | 386 | 0.46189 | 100.9424 | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | Rebuild line 532857 TECHILL6 230 785250 G24-276-TAP 230 1
Thermal | 03ALL | 1 | 26SP | T1 | GEN-2024-277 | TO->FROM | 532857 TECHILL6 230 785250 G24-276-TAP 230 1 | B | 386 | 0.43053 | 101.1427 | Single 532765 HOYT7 345 533163 HOYT3 115 532804 'HOYT 1 ' 14 1 | TDF Impact | Rebuild line 532857 TECHILL6 230 785250 G24-276-TAP 230 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-277 | TO->FROM | 533182 TECHILE3 115 3WXFMR 536:TECHILL TX-3 115 1 | B | 308 | 0.40636 | 101.1762 | P12:345:WERE:SWIS-WGAR-345:::EHV: | TDF Impact | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-277 | TO->FROM | 532857 TECHILL6 230 785250 G24-276-TAP 230 1 | B | 318 | 0.38024 | 101.3216 | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | Rebuild line 532857 TECHILL6 230 785250 G24-276-TAP 230 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-277 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.07964 | 101.6955 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-277 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.07964 | 101.6955 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-277 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.07964 | 101.6955 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 26SP | T1 | GEN-2024-277 | TO->FROM | 532857 TECHILL6 230 785250 G24-276-TAP 230 1 | B | 386 | 0.45883 | 102.0917 | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | Rebuild line 532857 TECHILL6 230 785250 G24-276-TAP 230 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-277 | TO->FROM | 532857 TECHILL6 230 785250 G24-276-TAP 230 1 | B | 318 | 0.3936 | 102.1142 | P12:230:WERE:LAWH-SWIS-230:HV: | TDF Impact | Rebuild line 532857 TECHILL6 230 785250 G24-276-TAP 230 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-277 | TO->FROM | 533182 TECHILE3 115 3WXFMR 536:TECHILL TX-3 115 1 | B | 308 | 0.38024 | 102.3222 | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-277 | TO->FROM | 532857 TECHILL6 230 785250 G24-276-TAP 230 1 | B | 318 | 0.37824 | 102.3789 | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | Rebuild line 532857 TECHILL6 230 785250 G24-276-TAP 230 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-277 | TO->FROM | 533182 TECHILE3 115 3WXFMR 536:TECHILL TX-3 115 1 | A | 280 | 0.38057 | 103.0405 | System Intact | TDF Impact | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-277 | TO->FROM | 533182 TECHILE3 115 3WXFMR 536:TECHILL TX-3 115 1 | B | 308 | 0.3936 | 103.1556 | P12:230:WERE:LAWH-SWIS-230:HV: | TDF Impact | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-277 | TO->FROM | 532857 TECHILL6 230 785250 G24-276-TAP 230 1 | B | 318 | 0.35723 | 103.5245 | Single 532765 HOYT7 345 533163 HOYT3 115 532804 'HOYT 1 ' 14 1 | TDF Impact | Rebuild line 532857 TECHILL6 230 785250 G24-276-TAP 230 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-277 | TO->FROM | 533182 TECHILE3 115 3WXFMR 536:TECHILL TX-3 115 1 | B | 308 | 0.37824 | 103.7091 | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-277 | TO->FROM | 533182 TECHILE3 115 3WXFMR 536:TECHILL TX-3 115 1 | B | 308 | 0.35723 | 104.1314 | Single 532765 HOYT7 345 533163 HOYT3 115 532804 'HOYT 1 ' 14 1 | TDF Impact | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2
Thermal | 03ALL | 1 | 29SP | T1 | GEN-2024-277 | TO->FROM | 532857 TECHILL6 230 785250 G24-276-TAP 230 1 | B | 386 | 0.49147 | 104.5244 | P23:345:KCPL-WERE:241WGARDNER-R12-13:::EHV: | TDF Impact | Rebuild line 532857 TECHILL6 230 785250 G24-276-TAP 230 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-277 | TO->FROM | 532857 TECHILL6 230 785250 G24-276-TAP 230 1 | B | 318 | 0.37815 | 104.6533 | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | Rebuild line 532857 TECHILL6 230 785250 G24-276-TAP 230 1
Thermal | 03ALL | 1 | 29SP | T1 | GEN-2024-277 | TO->FROM | 532857 TECHILL6 230 785250 G24-276-TAP 230 1 | B | 386 | 0.49175 | 104.7827 | P12:345:WERE:SWIS-WGAR-345:::EHV: | TDF Impact | Rebuild line 532857 TECHILL6 230 785250 G24-276-TAP 230 1
Thermal | 03ALL | 1 | 26SP | T1 | GEN-2024-277 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.071589 | 105.0133 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 26SP | T1 | GEN-2024-277 | TO->FROM | 532857 TECHILL6 230 785250 G24-276-TAP 230 1 | B | 386 | 0.44084 | 105.4121 | Single 532851 AUBURN6 230 533151 AUBURN3 115 532880 'AUBURN 1 ' 14 1 | TDF Impact | Rebuild line 532857 TECHILL6 230 785250 G24-276-TAP 230 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-277 | TO->FROM | 533182 TECHILE3 115 3WXFMR 536:TECHILL TX-3 115 1 | B | 308 | 0.37815 | 105.5459 | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-277 | TO->FROM | 532857 TECHILL6 230 785250 G24-276-TAP 230 1 | B | 318 | 0.40654 | 105.8803 | P23:345:KCPL-WERE:241WGARDNER-R12-13:::EHV: | TDF Impact | Rebuild line 532857 TECHILL6 230 785250 G24-276-TAP 230 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-277 | TO->FROM | 532857 TECHILL6 230 785250 G24-276-TAP 230 1 | B | 318 | 0.40677 | 106.1459 | P12:345:WERE:SWIS-WGAR-345:::EHV: | TDF Impact | Rebuild line 532857 TECHILL6 230 785250 G24-276-TAP 230 1
Thermal | 03ALL | 1 | 29WP | T1 | GEN-2024-277 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.072261 | 106.2154 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-277 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.073711 | 106.5956 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-277 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.073711 | 106.5956 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-277 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.073711 | 106.5956 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-277 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.067819 | 106.8199 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-277 | TO->FROM | 533182 TECHILE3 115 3WXFMR 536:TECHILL TX-3 115 1 | B | 308 | 0.40654 | 106.9363 | P23:345:KCPL-WERE:241WGARDNER-R12-13:::EHV: | TDF Impact | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-277 | TO->FROM | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | B | 1195 | 0.10242 | 107.005 | Single 541199 STJOE7 345 761383 G17-183-TAP 345 1 | Cumulative Impact | Rebuild line 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-277 | TO->FROM | 533182 TECHILE3 115 3WXFMR 536:TECHILL TX-3 115 1 | B | 308 | 0.40677 | 107.1866 | P12:345:WERE:SWIS-WGAR-345:::EHV: | TDF Impact | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-277 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.062716 | 108.3331 | P42:345:NPPD:BKR-TOB-3304:::: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-277 | TO->FROM | 532857 TECHILL6 230 785250 G24-276-TAP 230 1 | B | 318 | 0.36951 | 108.8422 | Single 532851 AUBURN6 230 533151 AUBURN3 115 532880 'AUBURN 1 ' 14 1 | TDF Impact | Rebuild line 532857 TECHILL6 230 785250 G24-276-TAP 230 1
Thermal | 03ALL | 1 | 29SP | T1 | GEN-2024-277 | TO->FROM | 532857 TECHILL6 230 785250 G24-276-TAP 230 1 | B | 386 | 0.45943 | 109.6453 | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | Rebuild line 532857 TECHILL6 230 785250 G24-276-TAP 230 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-277 | TO->FROM | 533182 TECHILE3 115 3WXFMR 536:TECHILL TX-3 115 1 | B | 308 | 0.36951 | 109.6861 | Single 532851 AUBURN6 230 533151 AUBURN3 115 532880 'AUBURN 1 ' 14 1 | TDF Impact | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2
Thermal | 03ALL | 1 | 29SP | T1 | GEN-2024-277 | TO->FROM | 532857 TECHILL6 230 785250 G24-276-TAP 230 1 | B | 386 | 0.43093 | 109.8119 | Single 532765 HOYT7 345 533163 HOYT3 115 532804 'HOYT 1 ' 14 1 | TDF Impact | Rebuild line 532857 TECHILL6 230 785250 G24-276-TAP 230 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-277 | TO->FROM | 532857 TECHILL6 230 785250 G24-276-TAP 230 1 | B | 318 | 0.37866 | 110.4565 | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | Rebuild line 532857 TECHILL6 230 785250 G24-276-TAP 230 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-277 | TO->FROM | 533182 TECHILE3 115 3WXFMR 536:TECHILL TX-3 115 1 | B | 308 | 0.35756 | 110.9541 | Single 532765 HOYT7 345 533163 HOYT3 115 532804 'HOYT 1 ' 14 1 | TDF Impact | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-277 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | A | 311 | 0.035975 | 111.039 | System Intact | TDF Impact | Rebuild line 300071 5CLINTN 161 761278 G17-108-TAP 161 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-277 | TO->FROM | 533182 TECHILE3 115 3WXFMR 536:TECHILL TX-3 115 1 | B | 308 | 0.37866 | 111.1551 | P23:345:WERE:JEC-345-16:EHV: | TDF Impact | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-277 | TO->FROM | 532857 TECHILL6 230 785250 G24-276-TAP 230 1 | B | 318 | 0.35756 | 111.1899 | Single 532765 HOYT7 345 533163 HOYT3 115 532804 'HOYT 1 ' 14 1 | TDF Impact | Rebuild line 532857 TECHILL6 230 785250 G24-276-TAP 230 1
Thermal | 03ALL | 1 | 29SP | T1 | GEN-2024-277 | TO->FROM | 532857 TECHILL6 230 785250 G24-276-TAP 230 1 | B | 386 | 0.45933 | 112.0505 | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | Rebuild line 532857 TECHILL6 230 785250 G24-276-TAP 230 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-277 | TO->FROM | 532857 TECHILL6 230 785250 G24-276-TAP 230 1 | B | 318 | 0.37857 | 112.9505 | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | Rebuild line 532857 TECHILL6 230 785250 G24-276-TAP 230 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-277 | TO->FROM | 533182 TECHILE3 115 3WXFMR 536:TECHILL TX-3 115 1 | B | 308 | 0.37857 | 113.0746 | P12:345:WERE:HOYT-JEC-345:EHV: | TDF Impact | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2
Thermal | 03ALL | 1 | 29SP | T1 | GEN-2024-277 | TO->FROM | 532857 TECHILL6 230 785250 G24-276-TAP 230 1 | B | 386 | 0.44127 | 114.6785 | Single 532851 AUBURN6 230 533151 AUBURN3 115 532880 'AUBURN 1 ' 14 1 | TDF Impact | Rebuild line 532857 TECHILL6 230 785250 G24-276-TAP 230 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-277 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.080915 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-277 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.080915 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-277 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.080915 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-277 | TO->FROM | 532857 TECHILL6 230 785250 G24-276-TAP 230 1 | B | 318 | 0.36987 | 117.2217 | Single 532851 AUBURN6 230 533151 AUBURN3 115 532880 'AUBURN 1 ' 14 1 | TDF Impact | Rebuild line 532857 TECHILL6 230 785250 G24-276-TAP 230 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-277 | TO->FROM | 533182 TECHILE3 115 3WXFMR 536:TECHILL TX-3 115 1 | B | 308 | 0.36987 | 117.3469 | Single 532851 AUBURN6 230 533151 AUBURN3 115 532880 'AUBURN 1 ' 14 1 | TDF Impact | Add 3-winding transformer 532857 TECHILL6 230 532886 TECHILL1 13 533182 TECHILE3 115 M2
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-277 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.062068 | 117.7598 | P55:345:OPPD:S3458 3::FN13:EHV: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-277 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | A | 311 | 0.036111 | 121.8886 | System Intact | TDF Impact | Rebuild line 300071 5CLINTN 161 761278 G17-108-TAP 161 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-277 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | A | 334 | 0.034537 | 145.0684 | System Intact | TDF Impact | Rebuild line 300071 5CLINTN 161 761278 G17-108-TAP 161 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-280 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.071916 | 100.0488 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-280 | TO->FROM | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | B | 997 | 0.1776 | 100.166 | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | Cumulative Impact | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-280 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.062525 | 100.533 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-280 | TO->FROM | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | B | 997 | 0.18115 | 100.7286 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-280 | TO->FROM | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | B | 997 | 0.18115 | 101.1047 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-280 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063383 | 102.9616 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-280 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063383 | 102.9634 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-280 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063383 | 103.0288 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-280 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063383 | 103.4739 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-280 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.075765 | 103.9266 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-280 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063383 | 104.1493 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-280 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.075004 | 104.7552 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-280 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.075004 | 104.888 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-280 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.078793 | 107.2243 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-280 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063383 | 107.2793 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-280 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063383 | 107.2794 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-280 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.078793 | 107.2951 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-280 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063383 | 107.3093 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-280 | TO->FROM | 523959 POTTER_CO 6 230 3WXFMR 526:WAUK 90343-A 230 1 | B | 559 | 0.12625 | 107.3794 | P42:345:SPS:HITCHLAND-1R15:::EHV: | Cumulative Impact | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-280 | TO->FROM | 523959 POTTER_CO 6 230 3WXFMR 526:WAUK 90343-A 230 1 | B | 559 | 0.12625 | 107.3953 | Single 523097 HITCHLAND7 345 523961 POTTER_CO7 345 1 | Cumulative Impact | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-280 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.072931 | 107.5866 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-280 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063383 | 107.7557 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-280 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063383 | 108.1822 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-280 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063383 | 108.2747 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-280 | TO->FROM | 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | B | 997 | 0.18982 | 109.7018 | Single 525832 TUCO_INT7 345 526000 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-280 | TO->FROM | 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | B | 997 | 0.18903 | 111.09 | Single 525832 TUCO_INT7 345 526000 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-280 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063383 | 111.3621 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-280 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.076038 | 111.723 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-280 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.076038 | 111.8755 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-280 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.072931 | 115.0541 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-280 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.076038 | 118.9427 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-280 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.076038 | 119.313 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-281 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.071795 | 100.0488 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-281 | TO->FROM | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | B | 997 | 0.17787 | 100.166 | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | Cumulative Impact | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-281 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.062481 | 100.533 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-281 | TO->FROM | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | B | 997 | 0.18141 | 100.7286 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-281 | TO->FROM | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | B | 997 | 0.18141 | 101.1047 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-281 | TO->FROM | 528540 WHITTEN 3 115 528547 S_JAL 3 115 1 | B | 239 | 0.9994 | 101.4619 | Single 528526 TEAGUE3 115 528596 CARDINAL3 115 1 | TDF Impact | Multi - Battle Axe - Wolfcamp Tap 115 kV DblCkt_Battle Axe - Ponderosa - Dollarhide 115 kV New Line.idv : PID : 900119, NTC, 2025 ITP, ISD: 6/1/2029
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-281 | TO->FROM | 528526 TEAGUE 3 115 785400 G24-281-TAP 115 1 | B | 154 | 0.61951 | 101.6002 | Single 528239 CUSTERMTN3 115 528240 PONDEROSA3 115 1 | TDF Impact | Multi - Battle Axe - Wolfcamp Tap 115 kV DblCkt_Battle Axe - Ponderosa - Dollarhide 115 kV New Line.idv : PID : 900119, NTC, 2025 ITP, ISD: 6/1/2029
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-281 | TO->FROM | 528526 TEAGUE 3 115 785400 G24-281-TAP 115 1 | B | 154 | 0.61951 | 101.6002 | P12:115:SPS:W81.1.CUSMTN.PONDEROSA:::HV: | TDF Impact | Multi - Battle Axe - Wolfcamp Tap 115 kV DblCkt_Battle Axe - Ponderosa - Dollarhide 115 kV New Line.idv : PID : 900119, NTC, 2025 ITP, ISD: 6/1/2029
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-281 | TO->FROM | 528540 WHITTEN 3 115 528547 S_JAL 3 115 1 | B | 239 | 0.99937 | 101.6164 | Single 528526 TEAGUE3 115 528596 CARDINAL3 115 1 | TDF Impact | Multi - Battle Axe - Wolfcamp Tap 115 kV DblCkt_Battle Axe - Ponderosa - Dollarhide 115 kV New Line.idv : PID : 900119, NTC, 2025 ITP, ISD: 6/1/2029
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-281 | TO->FROM | 528526 TEAGUE 3 115 785400 G24-281-TAP 115 1 | B | 154 | 0.5945 | 102.7438 | Single 527805 OXY_PALINDM3 115 527953 LIVSTNRIDGE3 115 1 | TDF Impact | Multi - Battle Axe - Wolfcamp Tap 115 kV DblCkt_Battle Axe - Ponderosa - Dollarhide 115 kV New Line.idv : PID : 900119, NTC, 2025 ITP, ISD: 6/1/2029
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-281 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063343 | 102.9616 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-281 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063343 | 102.9634 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-281 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063343 | 103.0288 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-281 | TO->FROM | 528526 TEAGUE 3 115 785400 G24-281-TAP 115 1 | A | 120 | 0.6071 | 103.4583 | System Intact | TDF Impact | Multi - Battle Axe - Wolfcamp Tap 115 kV DblCkt_Battle Axe - Ponderosa - Dollarhide 115 kV New Line.idv : PID : 900119, NTC, 2025 ITP, ISD: 6/1/2029
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-281 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063343 | 103.4739 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-281 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.075621 | 103.9266 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-281 | TO->FROM | 528540 WHITTEN 3 115 528547 S_JAL 3 115 1 | B | 239 | 0.9994 | 103.9331 | Single 528526 TEAGUE3 115 785400 G24-281-TAP 115 1 | TDF Impact | Multi - Battle Axe - Wolfcamp Tap 115 kV DblCkt_Battle Axe - Ponderosa - Dollarhide 115 kV New Line.idv : PID : 900119, NTC, 2025 ITP, ISD: 6/1/2029
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-281 | TO->FROM | 528540 WHITTEN 3 115 528547 S_JAL 3 115 1 | B | 239 | 0.99937 | 104.0301 | Single 528526 TEAGUE3 115 785400 G24-281-TAP 115 1 | TDF Impact | Multi - Battle Axe - Wolfcamp Tap 115 kV DblCkt_Battle Axe - Ponderosa - Dollarhide 115 kV New Line.idv : PID : 900119, NTC, 2025 ITP, ISD: 6/1/2029
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-281 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063343 | 104.1493 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-281 | TO->FROM | 528526 TEAGUE 3 115 785400 G24-281-TAP 115 1 | A | 120 | 0.60667 | 104.5513 | System Intact | TDF Impact | Multi - Battle Axe - Wolfcamp Tap 115 kV DblCkt_Battle Axe - Ponderosa - Dollarhide 115 kV New Line.idv : PID : 900119, NTC, 2025 ITP, ISD: 6/1/2029
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-281 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.074889 | 104.7552 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-281 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.074889 | 104.888 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-281 | TO->FROM | 528526 TEAGUE 3 115 785400 G24-281-TAP 115 1 | B | 154 | 0.76596 | 106.0832 | P12:115:SPS:W95.1.RDRN.CUSMTN:::HV: | TDF Impact | Multi - Battle Axe - Wolfcamp Tap 115 kV DblCkt_Battle Axe - Ponderosa - Dollarhide 115 kV New Line.idv : PID : 900119, NTC, 2025 ITP, ISD: 6/1/2029
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-281 | TO->FROM | 528526 TEAGUE 3 115 785400 G24-281-TAP 115 1 | B | 154 | 0.76596 | 106.0832 | Single 528025 RDRUNNER3 115 528239 CUSTERMTN3 115 1 | TDF Impact | Multi - Battle Axe - Wolfcamp Tap 115 kV DblCkt_Battle Axe - Ponderosa - Dollarhide 115 kV New Line.idv : PID : 900119, NTC, 2025 ITP, ISD: 6/1/2029
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-281 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.078655 | 107.2243 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-281 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063343 | 107.2793 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-281 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063343 | 107.2794 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-281 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.078655 | 107.2951 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-281 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063343 | 107.3093 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-281 | TO->FROM | 523959 POTTER_CO 6 230 3WXFMR 526:WAUK 90343-A 230 1 | B | 559 | 0.12526 | 107.3794 | P42:345:SPS:HITCHLAND-1R15:::EHV: | Cumulative Impact | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-281 | TO->FROM | 523959 POTTER_CO 6 230 3WXFMR 526:WAUK 90343-A 230 1 | B | 559 | 0.12526 | 107.3953 | Single 523097 HITCHLAND7 345 523961 POTTER_CO7 345 1 | Cumulative Impact | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-281 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.072838 | 107.5866 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-281 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063343 | 107.7557 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-281 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063343 | 108.1822 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-281 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063343 | 108.2747 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-281 | TO->FROM | 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | B | 997 | 0.18694 | 109.7018 | Single 525832 TUCO_INT7 345 526000 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-281 | TO->FROM | 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | B | 997 | 0.18922 | 111.09 | Single 525832 TUCO_INT7 345 526000 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-281 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063343 | 111.3621 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-281 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.075949 | 111.723 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-281 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.075949 | 111.8755 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-281 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.072838 | 115.0541 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-281 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.075949 | 118.9427 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-281 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.075949 | 119.313 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-281 | TO->FROM | 528526 TEAGUE 3 115 785400 G24-281-TAP 115 1 | A | 120 | 0.61951 | 120.8258 | System Intact | TDF Impact | Multi - Battle Axe - Wolfcamp Tap 115 kV DblCkt_Battle Axe - Ponderosa - Dollarhide 115 kV New Line.idv : PID : 900119, NTC, 2025 ITP, ISD: 6/1/2029
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-281 | TO->FROM | 528526 TEAGUE 3 115 785400 G24-281-TAP 115 1 | B | 154 | 0.76116 | 123.093 | Single 528239 CUSTERMTN3 115 528540 WHITTEN3 115 1 | TDF Impact | Multi - Battle Axe - Wolfcamp Tap 115 kV DblCkt_Battle Axe - Ponderosa - Dollarhide 115 kV New Line.idv : PID : 900119, NTC, 2025 ITP, ISD: 6/1/2029
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-281 | TO->FROM | 528526 TEAGUE 3 115 785400 G24-281-TAP 115 1 | B | 154 | 0.76116 | 123.093 | P12:115:SPS:W96.1.CUSMTN.WHITT:::HV: | TDF Impact | Multi - Battle Axe - Wolfcamp Tap 115 kV DblCkt_Battle Axe - Ponderosa - Dollarhide 115 kV New Line.idv : PID : 900119, NTC, 2025 ITP, ISD: 6/1/2029
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-281 | TO->FROM | 528526 TEAGUE 3 115 785400 G24-281-TAP 115 1 | B | 154 | 0.76089 | 125.7014 | P12:115:SPS:W96.1.CUSMTN.WHITT:::HV: | TDF Impact | Multi - Battle Axe - Wolfcamp Tap 115 kV DblCkt_Battle Axe - Ponderosa - Dollarhide 115 kV New Line.idv : PID : 900119, NTC, 2025 ITP, ISD: 6/1/2029
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-281 | TO->FROM | 528526 TEAGUE 3 115 785400 G24-281-TAP 115 1 | B | 154 | 0.76089 | 125.7014 | Single 528239 CUSTERMTN3 115 528540 WHITTEN3 115 1 | TDF Impact | Multi - Battle Axe - Wolfcamp Tap 115 kV DblCkt_Battle Axe - Ponderosa - Dollarhide 115 kV New Line.idv : PID : 900119, NTC, 2025 ITP, ISD: 6/1/2029
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-281 | TO->FROM | 528526 TEAGUE 3 115 785400 G24-281-TAP 115 1 | B | 154 | 0.76596 | 128.0523 | Single 528239 CUSTERMTN3 115 528540 WHITTEN3 115 1 | TDF Impact | Multi - Battle Axe - Wolfcamp Tap 115 kV DblCkt_Battle Axe - Ponderosa - Dollarhide 115 kV New Line.idv : PID : 900119, NTC, 2025 ITP, ISD: 6/1/2029
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-281 | TO->FROM | 528526 TEAGUE 3 115 785400 G24-281-TAP 115 1 | B | 154 | 0.76596 | 128.0523 | P12:115:SPS:W96.1.CUSMTN.WHITT:::HV: | TDF Impact | Multi - Battle Axe - Wolfcamp Tap 115 kV DblCkt_Battle Axe - Ponderosa - Dollarhide 115 kV New Line.idv : PID : 900119, NTC, 2025 ITP, ISD: 6/1/2029
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-281 | TO->FROM | 528547 S_JAL 3 115 785400 G24-281-TAP 115 1 | B | 154 | 1 | 153.5751 | Single 528526 TEAGUE3 115 528596 CARDINAL3 115 1 | TDF Impact | Rebuild line 528547 S_JAL 3 115 785400 G24-281-TAP 115 1
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-281 | TO->FROM | 528547 S_JAL 3 115 785400 G24-281-TAP 115 1 | B | 154 | 1 | 154.5991 | Single 528526 TEAGUE3 115 528596 CARDINAL3 115 1 | TDF Impact | Rebuild line 528547 S_JAL 3 115 785400 G24-281-TAP 115 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-281 | TO->FROM | 528547 S_JAL 3 115 785400 G24-281-TAP 115 1 | B | 154 | 1 | 154.6422 | Single 528526 TEAGUE3 115 528596 CARDINAL3 115 1 | TDF Impact | Rebuild line 528547 S_JAL 3 115 785400 G24-281-TAP 115 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-281 | TO->FROM | 528540 WHITTEN 3 115 528547 S_JAL 3 115 1 | B | 154 | 0.99933 | 156.2024 | Single 528526 TEAGUE3 115 528596 CARDINAL3 115 1 | TDF Impact | Multi - Battle Axe - Wolfcamp Tap 115 kV DblCkt_Battle Axe - Ponderosa - Dollarhide 115 kV New Line.idv : PID : 900119, NTC, 2025 ITP, ISD: 6/1/2029
Thermal | 05ALL | 1 | 29WP | T1 | GEN-2024-281 | TO->FROM | 528526 TEAGUE 3 115 785400 G24-281-TAP 115 1 | B | 154 | 1 | 157.8172 | Single 528547 S_JAL3 115 785400 G24-281-TAP 115 1 | TDF Impact | Rebuild line 528526 TEAGUE 3 115 785400 G24-281-TAP 115 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-281 | TO->FROM | 528547 S_JAL 3 115 785400 G24-281-TAP 115 1 | B | 154 | 1 | 157.9814 | Single 528526 TEAGUE3 115 785400 G24-281-TAP 115 1 | TDF Impact | Rebuild line 528547 S_JAL 3 115 785400 G24-281-TAP 115 1
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-281 | TO->FROM | 528526 TEAGUE 3 115 785400 G24-281-TAP 115 1 | B | 154 | 1 | 157.984 | Single 528547 S_JAL3 115 785400 G24-281-TAP 115 1 | TDF Impact | Multi - Battle Axe - Wolfcamp Tap 115 kV DblCkt_Battle Axe - Ponderosa - Dollarhide 115 kV New Line.idv : PID : 900119, NTC, 2025 ITP, ISD: 6/1/2029
Thermal | 05ALL | 1 | 29SP | T1 | GEN-2024-281 | TO->FROM | 528526 TEAGUE 3 115 785400 G24-281-TAP 115 1 | B | 154 | 1 | 158.0142 | Single 528547 S_JAL3 115 785400 G24-281-TAP 115 1 | TDF Impact | Rebuild line 528526 TEAGUE 3 115 785400 G24-281-TAP 115 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-281 | TO->FROM | 528526 TEAGUE 3 115 785400 G24-281-TAP 115 1 | B | 154 | 1 | 158.0402 | Single 528547 S_JAL3 115 785400 G24-281-TAP 115 1 | TDF Impact | Multi - Battle Axe - Wolfcamp Tap 115 kV DblCkt_Battle Axe - Ponderosa - Dollarhide 115 kV New Line.idv : PID : 900119, NTC, 2025 ITP, ISD: 6/1/2029
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-281 | TO->FROM | 528547 S_JAL 3 115 785400 G24-281-TAP 115 1 | B | 154 | 1 | 158.331 | Single 528526 TEAGUE3 115 785400 G24-281-TAP 115 1 | TDF Impact | Rebuild line 528547 S_JAL 3 115 785400 G24-281-TAP 115 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-281 | TO->FROM | 528547 S_JAL 3 115 785400 G24-281-TAP 115 1 | B | 154 | 1 | 158.4648 | Single 528526 TEAGUE3 115 785400 G24-281-TAP 115 1 | TDF Impact | Rebuild line 528547 S_JAL 3 115 785400 G24-281-TAP 115 1
Thermal | 05ALL | 1 | 26SP | T1 | GEN-2024-281 | TO->FROM | 528526 TEAGUE 3 115 785400 G24-281-TAP 115 1 | B | 154 | 1 | 159.172 | Single 528547 S_JAL3 115 785400 G24-281-TAP 115 1 | TDF Impact | Rebuild line 528526 TEAGUE 3 115 785400 G24-281-TAP 115 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-281 | TO->FROM | 528526 TEAGUE 3 115 785400 G24-281-TAP 115 1 | B | 154 | 1 | 159.2508 | Single 528547 S_JAL3 115 785400 G24-281-TAP 115 1 | TDF Impact | Multi - Battle Axe - Wolfcamp Tap 115 kV DblCkt_Battle Axe - Ponderosa - Dollarhide 115 kV New Line.idv : PID : 900119, NTC, 2025 ITP, ISD: 6/1/2029
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-281 | TO->FROM | 528540 WHITTEN 3 115 528547 S_JAL 3 115 1 | B | 154 | 0.99933 | 160.627 | Single 528526 TEAGUE3 115 785400 G24-281-TAP 115 1 | TDF Impact | Multi - Battle Axe - Wolfcamp Tap 115 kV DblCkt_Battle Axe - Ponderosa - Dollarhide 115 kV New Line.idv : PID : 900119, NTC, 2025 ITP, ISD: 6/1/2029
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-281 | TO->FROM | 528526 TEAGUE 3 115 785400 G24-281-TAP 115 1 | B | 154 | 0.9994 | 160.9054 | Single 528540 WHITTEN3 115 528547 S_JAL3 115 1 | TDF Impact | Multi - Battle Axe - Wolfcamp Tap 115 kV DblCkt_Battle Axe - Ponderosa - Dollarhide 115 kV New Line.idv : PID : 900119, NTC, 2025 ITP, ISD: 6/1/2029
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-281 | TO->FROM | 528526 TEAGUE 3 115 785400 G24-281-TAP 115 1 | B | 154 | 0.99937 | 161.1693 | Single 528540 WHITTEN3 115 528547 S_JAL3 115 1 | TDF Impact | Multi - Battle Axe - Wolfcamp Tap 115 kV DblCkt_Battle Axe - Ponderosa - Dollarhide 115 kV New Line.idv : PID : 900119, NTC, 2025 ITP, ISD: 6/1/2029
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-281 | TO->FROM | 528526 TEAGUE 3 115 785400 G24-281-TAP 115 1 | B | 154 | 0.99933 | 162.1558 | Single 528540 WHITTEN3 115 528547 S_JAL3 115 1 | TDF Impact | Multi - Battle Axe - Wolfcamp Tap 115 kV DblCkt_Battle Axe - Ponderosa - Dollarhide 115 kV New Line.idv : PID : 900119, NTC, 2025 ITP, ISD: 6/1/2029
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-286 | TO->FROM | 514934 DRAPER 7 345 515045 SEMINOL7 345 2 | B | 717 | 0.064076 | 104.675 | P42:345:OKGE:SB_SEOL7385:::EHV: | Cumulative Impact | Rebuild line 514934 DRAPER 7 345 515045 SEMINOL7 345 2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-286 | TO->FROM | 514934 DRAPER 7 345 515045 SEMINOL7 345 2 | B | 717 | 0.067318 | 109.0105 | P42:345:OKGE:SB_SEOL7385:::EHV: | Cumulative Impact | Rebuild line 514934 DRAPER 7 345 515045 SEMINOL7 345 2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-286 | TO->FROM | 515339 VBI 5 161 515406 ADABELL5 161 1 | B | 223 | 0.081134 | 128.9573 | Single 515231 KEEFTON7 345 780360 G24-113-TAP 345 1 | Cumulative Impact | Rebuild line 515339 VBI 5 161 515406 ADABELL5 161 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-287 | TO->FROM | 532939 N345 4 5 161 3WXFMR 536:N345 TX-2 161 2 | B | 550 | 0.036056 | 100.4793 | Single 533021 NEOSHO4 138 533023 N34534 138 1 | TDF Impact | Add 3-winding transformer 532793 NEOSHO 7 345 532825 N345 2 1 13 532939 N345 4 5 161 M2
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-287 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.1782 | 101.6955 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-287 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.1782 | 101.6955 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-287 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.1782 | 101.6955 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-287 | TO->FROM | 532939 N345 4 5 161 3WXFMR 536:N345 TX-2 161 2 | B | 550 | 0.040304 | 103.5308 | Single 533021 NEOSHO4 138 533023 N34534 138 1 | TDF Impact | Add 3-winding transformer 532793 NEOSHO 7 345 532825 N345 2 1 13 532939 N345 4 5 161 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-287 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | B | 829 | 0.033914 | 103.7671 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | TDF Impact | Rebuild line 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1
Thermal | 03ALL | 1 | 26SP | T1 | GEN-2024-287 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.18582 | 105.0133 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 29WP | T1 | GEN-2024-287 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.1982 | 106.2154 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-287 | TO->FROM | 532937 NEOSHO 5 161 532939 N345 4 5 161 1 | B | 557 | 0.040376 | 106.5051 | Single 533021 NEOSHO4 138 533023 N34534 138 1 | TDF Impact | Rebuild line 532937 NEOSHO 5 161 532939 N345 4 5 161 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-287 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.20108 | 106.5956 | P23:345:AECI:7BLACKBERRY:653::: | TDF Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-287 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.20108 | 106.5956 | P23:345:AECI:7BLACKBERRY:653::: | TDF Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-287 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.20108 | 106.5956 | P23:345:AECI:7BLACKBERRY:653::: | TDF Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-287 | TO->FROM | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | B | 1195 | 0.054558 | 107.005 | Single 541199 STJOE7 345 761383 G17-183-TAP 345 1 | Cumulative Impact | Rebuild line 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-287 | TO->FROM | 532939 N345 4 5 161 3WXFMR 536:N345 TX-2 161 2 | B | 550 | 0.040376 | 111.179 | Single 533021 NEOSHO4 138 533023 N34534 138 1 | TDF Impact | Add 3-winding transformer 532793 NEOSHO 7 345 532825 N345 2 1 13 532939 N345 4 5 161 M2
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-287 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.17841 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-287 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.17841 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-287 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.17841 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-293 | TO->FROM | 515301 FTSMTHW5 161 3WXFMR 524:524:FTSMITH5 345 5 | B | 493 | 0.060592 | 103.9313 | P42:500:OKGE:SB_FTTH8585:::EHV: | Cumulative Impact | Add 3-winding transformer 515301 FTSMTHW5 161 515302 FTSMITH7 345 515728 FTSMTH51 13 M2
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-293 | TO->FROM | 514934 DRAPER 7 345 515045 SEMINOL7 345 2 | B | 717 | 0.064495 | 104.675 | P42:345:OKGE:SB_SEOL7385:::EHV: | Cumulative Impact | Rebuild line 514934 DRAPER 7 345 515045 SEMINOL7 345 2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-293 | TO->FROM | 514934 DRAPER 7 345 515045 SEMINOL7 345 2 | B | 717 | 0.067083 | 109.0105 | P42:345:OKGE:SB_SEOL7385:::EHV: | Cumulative Impact | Rebuild line 514934 DRAPER 7 345 515045 SEMINOL7 345 2
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-294 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.48241 | 100.4398 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-294 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.48498 | 100.451 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-294 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1182 | 0.49425 | 100.7686 | Single 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | TDF Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-294 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1182 | 0.49428 | 100.7917 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | TDF Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-294 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.49216 | 101.1642 | Single 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | TDF Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-294 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | A | 901 | 0.48307 | 101.5467 | System Intact | TDF Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-294 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.49299 | 101.7923 | Single 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | TDF Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-294 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.485 | 101.9139 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-294 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.48498 | 101.9296 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-294 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | A | 901 | 0.48267 | 102.5076 | System Intact | TDF Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-294 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.49247 | 102.6355 | Single 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | TDF Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-294 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.49216 | 102.8031 | Single 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | TDF Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-294 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.47558 | 102.8233 | P22:345:EES:CLARKSV7!:::EHV: | TDF Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-294 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.49299 | 103.1009 | Single 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | TDF Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-294 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.49216 | 103.3738 | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-294 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.49339 | 103.4829 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | TDF Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-294 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.49299 | 103.5409 | Single 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | TDF Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-294 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.49356 | 103.7549 | Single 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | TDF Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-294 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.47521 | 104.0394 | P22:345:EES:CLARKSV7!:::EHV: | TDF Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-294 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.47376 | 104.6561 | P22:345:EES:CLARKSV7!:::EHV: | TDF Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-294 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.47558 | 104.8397 | P22:345:EES:CLARKSV7!:::EHV: | TDF Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-294 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.49299 | 104.9783 | Single 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | TDF Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-294 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.49247 | 105.1591 | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-294 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.49216 | 105.2013 | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-294 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.49356 | 105.3089 | Single 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | TDF Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-294 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.49339 | 105.3978 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | TDF Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-294 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.47239 | 105.4314 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB:::: | TDF Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-294 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.47239 | 105.47 | P12:345:EES:CHAMSPR7!:CLARKSV7!:1:EHV: | TDF Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-294 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.47106 | 105.6463 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB:::: | TDF Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-294 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.47107 | 105.6708 | P12:345:EES:CHAMSPR7!:CLARKSV7!:1:EHV: | TDF Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-294 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.49387 | 105.6815 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | TDF Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-294 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.49002 | 106.3738 | P23:345:WERE:N345-345-20:EHV: | TDF Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-294 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1011 | 0.062007 | 106.9293 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-294 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.47218 | 107.3179 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB:::: | TDF Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-294 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.47219 | 107.3846 | P12:345:EES:CHAMSPR7!:CLARKSV7!:1:EHV: | TDF Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-294 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.49425 | 107.6019 | Single 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | TDF Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-294 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1011 | 0.059867 | 107.7039 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-294 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.47239 | 107.8076 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB:::: | TDF Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-294 | TO->FROM | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | A | 827 | 0.048155 | 107.8643 | System Intact | TDF Impact | Rebuild line 532791 BENTON 7 345 532794 ROSEHIL7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-294 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.47239 | 107.867 | P12:345:EES:CHAMSPR7!:CLARKSV7!:1:EHV: | TDF Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-294 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.49002 | 108.4042 | P23:345:WERE:N345-345-20:EHV: | TDF Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-294 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.4901 | 108.8315 | P23:345:WERE:N345-345-20:EHV: | TDF Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-294 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.49425 | 109.031 | Single 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | TDF Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-294 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.49428 | 109.0559 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | TDF Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-294 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.485 | 109.2662 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-294 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.49247 | 109.6648 | Single 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | TDF Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-294 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.49356 | 110.6179 | Single 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | TDF Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-294 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.47521 | 110.6357 | P22:345:EES:CLARKSV7!:::EHV: | TDF Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-294 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.49247 | 112.0601 | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | TDF Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-294 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.49356 | 112.0812 | Single 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | TDF Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-294 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1187 | 0.081003 | 112.2151 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-294 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.49387 | 112.433 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | TDF Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-294 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.10887 | 112.5233 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-294 | TO->FROM | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | A | 827 | 0.050154 | 113.506 | System Intact | TDF Impact | Rebuild line 532791 BENTON 7 345 532794 ROSEHIL7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-294 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.47218 | 113.5635 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB:::: | TDF Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-294 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.47219 | 113.5961 | P12:345:EES:CHAMSPR7!:CLARKSV7!:1:EHV: | TDF Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-294 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.085857 | 113.7225 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-294 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.10659 | 114.0272 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-294 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.17148 | 114.0895 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-294 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.0852 | 115.4477 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-294 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.17148 | 115.647 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-294 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.4901 | 115.6656 | P23:345:WERE:N345-345-20:EHV: | TDF Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-294 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.0852 | 117.1553 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-294 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.0852 | 117.1572 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-294 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.0852 | 119.7129 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-294 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.0852 | 124.3274 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-294 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.060017 | 137.9906 | System Intact | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-294 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.057339 | 138.1985 | System Intact | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-294 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.12687 | 155.4006 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-294 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.066222 | 155.7991 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-294 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.063036 | 155.8883 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-294 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.12747 | 158.3302 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-294 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.064895 | 159.2546 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-294 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.061493 | 159.5575 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-294 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.089493 | 160.5677 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-294 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.064362 | 161.638 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-294 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.085694 | 161.7992 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-294 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.086305 | 161.8408 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-294 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.060904 | 162.2698 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-294 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.082631 | 163.3422 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-294 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.064362 | 164.1736 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-294 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.064362 | 164.1763 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-294 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.060904 | 164.8475 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-294 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.060904 | 164.8482 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-294 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.064362 | 167.9939 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-294 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.060904 | 169.069 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-294 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.064362 | 175.0352 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-294 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.060904 | 177.0235 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-295 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.071428 | 100.0488 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-295 | TO->FROM | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | B | 997 | 0.17824 | 100.166 | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | Cumulative Impact | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-295 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.062206 | 100.533 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-295 | TO->FROM | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | B | 997 | 0.18157 | 100.7286 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-295 | TO->FROM | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | B | 997 | 0.18157 | 101.1047 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-295 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063068 | 102.9616 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-295 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063068 | 102.9634 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-295 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063068 | 103.0288 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-295 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063068 | 103.4739 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-295 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.075201 | 103.9266 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-295 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063068 | 104.1493 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-295 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.074517 | 104.7552 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-295 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.074517 | 104.888 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-295 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.078232 | 107.2243 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-295 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063068 | 107.2793 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-295 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063068 | 107.2794 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-295 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.078232 | 107.2951 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-295 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063068 | 107.3093 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-295 | TO->FROM | 523959 POTTER_CO 6 230 3WXFMR 526:WAUK 90343-A 230 1 | B | 559 | 0.1342 | 107.3794 | P42:345:SPS:HITCHLAND-1R15:::EHV: | Cumulative Impact | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-295 | TO->FROM | 523959 POTTER_CO 6 230 3WXFMR 526:WAUK 90343-A 230 1 | B | 559 | 0.1342 | 107.3953 | Single 523097 HITCHLAND7 345 523961 POTTER_CO7 345 1 | Cumulative Impact | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-295 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.072475 | 107.5866 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-295 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063068 | 107.7557 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-295 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063068 | 108.1822 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-295 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063068 | 108.2747 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-295 | TO->FROM | 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | B | 997 | 0.12906 | 109.7018 | Single 525832 TUCO_INT7 345 526000 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-295 | TO->FROM | 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | B | 997 | 0.12884 | 111.09 | Single 525832 TUCO_INT7 345 526000 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-295 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063068 | 111.3621 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-295 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.075582 | 111.723 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-295 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.075582 | 111.8755 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-295 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.072475 | 115.0541 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-295 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.075582 | 118.9427 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-295 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.075582 | 119.313 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-296 | TO->FROM | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | B | 1059 | 0.14821 | 100.2166 | P12:345:AEPW:R.S.S.-7:ONETA--7::: | Cumulative Impact | Rebuild line 509745 CLARKSV7 345 515224 MUSKOGE7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-296 | TO->FROM | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | B | 1059 | 0.1749 | 100.8866 | Single 515231 KEEFTON7 345 780360 G24-113-TAP 345 1 | Cumulative Impact | Rebuild line 509745 CLARKSV7 345 515224 MUSKOGE7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-296 | TO->FROM | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | A | 1806 | 0.032274 | 104.7927 | System Intact | TDF Impact | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-296 | TO->FROM | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | B | 1059 | 0.17491 | 105.0001 | P42:345:OKGE:SB_FTTH7386:::EHV: | Cumulative Impact | Rebuild line 509745 CLARKSV7 345 515224 MUSKOGE7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-296 | TO->FROM | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | B | 1059 | 0.1749 | 105.0075 | Single 515012 RVRVALY7 345 515302 FTSMITH7 345 1 | Cumulative Impact | Rebuild line 509745 CLARKSV7 345 515224 MUSKOGE7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-296 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1011 | 0.051838 | 106.9293 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-296 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1011 | 0.049632 | 107.7039 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-296 | TO->FROM | 515305 FTSMITH8 500 3WXFMR 524:524:FTSMITH1 500 1 | B | 693 | 0.080261 | 108.5609 | P12:161:EES:FTSMTHW5%:FTSMITH7%:FTSMTH511:HV: | Cumulative Impact | Add 3-winding transformer 515302 FTSMITH7 345 515305 FTSMITH8 500 515726 FTSMTH11 13 M2
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-296 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1187 | 0.062853 | 112.2151 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-296 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.069779 | 112.5233 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-296 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.068612 | 113.7225 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-296 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.068535 | 114.0272 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-296 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.064137 | 114.0895 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-296 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.034766 | 114.4362 | System Intact | TDF Impact | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-296 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.067954 | 115.4477 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-296 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.064137 | 115.647 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-296 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.067954 | 117.1553 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-296 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.067954 | 117.1572 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-296 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.067954 | 119.7129 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-296 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.067954 | 124.3274 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-296 | TO->FROM | 515301 FTSMTHW5 161 3WXFMR 524:524:FTSMITH5 345 5 | B | 493 | 0.061469 | 126.769 | P12:345:EES:FTSMITH7%:FTSMITH8%:FTSMTH111:EHV: | Cumulative Impact | Add 3-winding transformer 515301 FTSMTHW5 161 515302 FTSMITH7 345 515728 FTSMTH51 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-296 | TO->FROM | 516093 OKTAHA 2 69 3WXFMR OKTAHA 5 69 7 | B | 112 | 0.038637 | 127.8893 | P22:345:EES:MUSKOGE7!:::EHV: | TDF Impact | Rebuild 3-winding transformer 516092 OKTAHA 5 161 516093 OKTAHA 2 69 516095 OKTAHA71 13 7
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-296 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.049365 | 137.9906 | System Intact | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-296 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.047193 | 138.1985 | System Intact | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-296 | TO->FROM | 516093 OKTAHA 2 69 3WXFMR OKTAHA 5 69 7 | B | 112 | 0.038657 | 146.2088 | P22:345:EES:MUSKOGE7!:::EHV: | TDF Impact | Rebuild 3-winding transformer 516092 OKTAHA 5 161 516093 OKTAHA 2 69 516095 OKTAHA71 13 7
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-296 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.050633 | 155.4006 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-296 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.053429 | 155.7991 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-296 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051096 | 155.8883 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-296 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.05466 | 159.2546 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-296 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051817 | 159.5575 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-296 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.056914 | 160.5677 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-296 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.054127 | 161.638 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-296 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.054917 | 161.7992 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-296 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.054395 | 161.8408 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-296 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051228 | 162.2698 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-296 | TO->FROM | 516093 OKTAHA 2 69 3WXFMR OKTAHA 5 69 7 | B | 112 | 0.039303 | 163.0673 | P22:345:EES:MUSKOGE7!:::EHV: | TDF Impact | Rebuild 3-winding transformer 516092 OKTAHA 5 161 516093 OKTAHA 2 69 516095 OKTAHA71 13 7
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-296 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.052519 | 163.3422 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-296 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.054127 | 164.1736 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-296 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.054127 | 164.1763 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-296 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051228 | 164.8475 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-296 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051228 | 164.8482 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-296 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.054127 | 167.9939 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-296 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051228 | 169.069 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-296 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.054127 | 175.0352 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-296 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051228 | 177.0235 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-297 | TO->FROM | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | B | 1059 | 0.14821 | 100.2166 | P12:345:AEPW:R.S.S.-7:ONETA--7::: | Cumulative Impact | Rebuild line 509745 CLARKSV7 345 515224 MUSKOGE7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-297 | TO->FROM | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | B | 1059 | 0.1749 | 100.8866 | Single 515231 KEEFTON7 345 780360 G24-113-TAP 345 1 | Cumulative Impact | Rebuild line 509745 CLARKSV7 345 515224 MUSKOGE7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-297 | TO->FROM | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | A | 1806 | 0.032274 | 104.7927 | System Intact | TDF Impact | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-297 | TO->FROM | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | B | 1059 | 0.17491 | 105.0001 | P42:345:OKGE:SB_FTTH7386:::EHV: | Cumulative Impact | Rebuild line 509745 CLARKSV7 345 515224 MUSKOGE7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-297 | TO->FROM | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | B | 1059 | 0.1749 | 105.0075 | Single 515012 RVRVALY7 345 515302 FTSMITH7 345 1 | Cumulative Impact | Rebuild line 509745 CLARKSV7 345 515224 MUSKOGE7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-297 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1011 | 0.051838 | 106.9293 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-297 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1011 | 0.049632 | 107.7039 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-297 | TO->FROM | 515305 FTSMITH8 500 3WXFMR 524:524:FTSMITH1 500 1 | B | 693 | 0.080261 | 108.5609 | P12:161:EES:FTSMTHW5%:FTSMITH7%:FTSMTH511:HV: | Cumulative Impact | Add 3-winding transformer 515302 FTSMITH7 345 515305 FTSMITH8 500 515726 FTSMTH11 13 M2
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-297 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1187 | 0.062853 | 112.2151 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-297 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.069779 | 112.5233 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-297 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.068612 | 113.7225 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-297 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.068535 | 114.0272 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-297 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.064137 | 114.0895 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-297 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.034766 | 114.4362 | System Intact | TDF Impact | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-297 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.067954 | 115.4477 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-297 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.064137 | 115.647 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-297 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.067954 | 117.1553 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-297 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.067954 | 117.1572 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-297 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.067954 | 119.7129 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-297 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.067954 | 124.3274 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-297 | TO->FROM | 515301 FTSMTHW5 161 3WXFMR 524:524:FTSMITH5 345 5 | B | 493 | 0.061469 | 126.769 | P12:345:EES:FTSMITH7%:FTSMITH8%:FTSMTH111:EHV: | Cumulative Impact | Add 3-winding transformer 515301 FTSMTHW5 161 515302 FTSMITH7 345 515728 FTSMTH51 13 M2
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-297 | TO->FROM | 516093 OKTAHA 2 69 3WXFMR OKTAHA 5 69 7 | B | 112 | 0.038637 | 127.8893 | P22:345:EES:MUSKOGE7!:::EHV: | TDF Impact | Rebuild 3-winding transformer 516092 OKTAHA 5 161 516093 OKTAHA 2 69 516095 OKTAHA71 13 7
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-297 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.049365 | 137.9906 | System Intact | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-297 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.047193 | 138.1985 | System Intact | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-297 | TO->FROM | 516093 OKTAHA 2 69 3WXFMR OKTAHA 5 69 7 | B | 112 | 0.038657 | 146.2088 | P22:345:EES:MUSKOGE7!:::EHV: | TDF Impact | Rebuild 3-winding transformer 516092 OKTAHA 5 161 516093 OKTAHA 2 69 516095 OKTAHA71 13 7
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-297 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.050633 | 155.4006 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-297 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.053429 | 155.7991 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-297 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051096 | 155.8883 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-297 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.05466 | 159.2546 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-297 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051817 | 159.5575 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-297 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.056914 | 160.5677 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-297 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.054127 | 161.638 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-297 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.054917 | 161.7992 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-297 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.054395 | 161.8408 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-297 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051228 | 162.2698 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-297 | TO->FROM | 516093 OKTAHA 2 69 3WXFMR OKTAHA 5 69 7 | B | 112 | 0.039303 | 163.0673 | P22:345:EES:MUSKOGE7!:::EHV: | TDF Impact | Rebuild 3-winding transformer 516092 OKTAHA 5 161 516093 OKTAHA 2 69 516095 OKTAHA71 13 7
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-297 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.052519 | 163.3422 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-297 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.054127 | 164.1736 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-297 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.054127 | 164.1763 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-297 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051228 | 164.8475 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-297 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051228 | 164.8482 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-297 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.054127 | 167.9939 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-297 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051228 | 169.069 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-297 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.054127 | 175.0352 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-297 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.051228 | 177.0235 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-299 | TO->FROM | 515339 VBI 5 161 515406 ADABELL5 161 1 | B | 223 | 0.073455 | 100.0239 | P22:345:EES:MUSKOGE7!:::EHV: | Cumulative Impact | Rebuild line 515339 VBI 5 161 515406 ADABELL5 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-299 | TO->FROM | 515301 FTSMTHW5 161 3WXFMR 524:524:FTSMITH5 345 5 | B | 493 | 0.25769 | 103.9313 | P42:500:OKGE:SB_FTTH8585:::EHV: | TDF Impact | Add 3-winding transformer 515301 FTSMTHW5 161 515302 FTSMITH7 345 515728 FTSMTH51 13 M2
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-299 | TO->FROM | 514934 DRAPER 7 345 515045 SEMINOL7 345 2 | B | 717 | 0.069347 | 104.675 | P42:345:OKGE:SB_SEOL7385:::EHV: | Cumulative Impact | Rebuild line 514934 DRAPER 7 345 515045 SEMINOL7 345 2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-299 | TO->FROM | 514934 DRAPER 7 345 515045 SEMINOL7 345 2 | B | 717 | 0.071688 | 109.0105 | P42:345:OKGE:SB_SEOL7385:::EHV: | Cumulative Impact | Rebuild line 514934 DRAPER 7 345 515045 SEMINOL7 345 2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-299 | TO->FROM | 515339 VBI 5 161 515406 ADABELL5 161 1 | B | 223 | 0.095906 | 110.333 | Single 515339 VBI5 161 515340 OAKGROV5 161 1 | Cumulative Impact | Rebuild line 515339 VBI 5 161 515406 ADABELL5 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-299 | TO->FROM | 515339 VBI 5 161 515406 ADABELL5 161 1 | B | 223 | 0.095906 | 114.5268 | P12:161:OKGE:BKRBKR3240:::HV: | Cumulative Impact | Rebuild line 515339 VBI 5 161 515406 ADABELL5 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-299 | TO->FROM | 515339 VBI 5 161 515406 ADABELL5 161 1 | B | 223 | 0.095906 | 115.4657 | Single 515340 OAKGROV5 161 515341 WHITESD5 161 1 | Cumulative Impact | Rebuild line 515339 VBI 5 161 515406 ADABELL5 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-299 | TO->FROM | 515339 VBI 5 161 515406 ADABELL5 161 1 | B | 223 | 0.08655 | 116.3693 | P22:345:EES:MUSKOGE7!:::EHV: | Cumulative Impact | Rebuild line 515339 VBI 5 161 515406 ADABELL5 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-299 | TO->FROM | 515339 VBI 5 161 515406 ADABELL5 161 1 | B | 223 | 0.095906 | 121.92 | Single 515341 WHITESD5 161 515343 MASSARD5 161 1 | Cumulative Impact | Rebuild line 515339 VBI 5 161 515406 ADABELL5 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-299 | TO->FROM | 515339 VBI 5 161 515406 ADABELL5 161 1 | B | 223 | 0.15844 | 128.9573 | Single 515231 KEEFTON7 345 780360 G24-113-TAP 345 1 | Cumulative Impact | Rebuild line 515339 VBI 5 161 515406 ADABELL5 161 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-303 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.073927 | 100.0488 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-303 | TO->FROM | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | B | 997 | 0.17037 | 100.166 | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | Cumulative Impact | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-303 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063268 | 100.533 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-303 | TO->FROM | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | B | 997 | 0.17432 | 100.7286 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-303 | TO->FROM | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | B | 997 | 0.17432 | 101.1047 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-303 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.064084 | 102.9616 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-303 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.064084 | 102.9634 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-303 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.064084 | 103.0288 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-303 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.064084 | 103.4739 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-303 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.078438 | 103.9266 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-303 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.064084 | 104.1493 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-303 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.076912 | 104.7552 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-303 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.076912 | 104.888 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-303 | TO->FROM | 531510 HARBNGR3 115 3WXFMR 534:HARBGR345 345 1 | B | 385 | 0.050041 | 105.7318 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Add 3-winding transformer 531510 HARBNGR3 115 531511 HARBNGR-1 13 531512 HARBNGR7 345 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-303 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.081361 | 107.2243 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-303 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.064084 | 107.2793 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-303 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.064084 | 107.2794 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-303 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.081361 | 107.2951 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-303 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.064084 | 107.3093 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-303 | TO->FROM | 523959 POTTER_CO 6 230 3WXFMR 526:WAUK 90343-A 230 1 | B | 559 | 0.15263 | 107.3794 | P42:345:SPS:HITCHLAND-1R15:::EHV: | Cumulative Impact | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-303 | TO->FROM | 523959 POTTER_CO 6 230 3WXFMR 526:WAUK 90343-A 230 1 | B | 559 | 0.15263 | 107.3953 | Single 523097 HITCHLAND7 345 523961 POTTER_CO7 345 1 | Cumulative Impact | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-303 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.074928 | 107.5866 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-303 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.064084 | 107.7557 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-303 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.064084 | 108.1822 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-303 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.064084 | 108.2747 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-303 | TO->FROM | 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | B | 997 | 0.17092 | 109.7018 | Single 525832 TUCO_INT7 345 526000 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-303 | TO->FROM | 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | B | 997 | 0.17176 | 111.09 | Single 525832 TUCO_INT7 345 526000 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-303 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.064084 | 111.3621 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-303 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.07793 | 111.723 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-303 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.07793 | 111.8755 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-303 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.074928 | 115.0541 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-303 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.07793 | 118.9427 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-303 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.07793 | 119.313 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-303 | TO->FROM | 531405 WALKMYR3 115 531510 HARBNGR3 115 1 | B | 331.39 | 0.050041 | 122.4803 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild line 531405 WALKMYR3 115 531510 HARBNGR3 115 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-304 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.073927 | 100.0488 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-304 | TO->FROM | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | B | 997 | 0.17037 | 100.166 | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | Cumulative Impact | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-304 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063268 | 100.533 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-304 | TO->FROM | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | B | 997 | 0.17432 | 100.7286 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-304 | TO->FROM | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | B | 997 | 0.17432 | 101.1047 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-304 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.064084 | 102.9616 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-304 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.064084 | 102.9634 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-304 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.064084 | 103.0288 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-304 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.064084 | 103.4739 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-304 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.078438 | 103.9266 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-304 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.064084 | 104.1493 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-304 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.076912 | 104.7552 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-304 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.076912 | 104.888 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-304 | TO->FROM | 531510 HARBNGR3 115 3WXFMR 534:HARBGR345 345 1 | B | 385 | 0.050041 | 105.7318 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Add 3-winding transformer 531510 HARBNGR3 115 531511 HARBNGR-1 13 531512 HARBNGR7 345 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-304 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.081361 | 107.2243 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-304 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.064084 | 107.2793 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-304 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.064084 | 107.2794 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-304 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.081361 | 107.2951 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-304 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.064084 | 107.3093 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-304 | TO->FROM | 523959 POTTER_CO 6 230 3WXFMR 526:WAUK 90343-A 230 1 | B | 559 | 0.15263 | 107.3794 | P42:345:SPS:HITCHLAND-1R15:::EHV: | Cumulative Impact | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-304 | TO->FROM | 523959 POTTER_CO 6 230 3WXFMR 526:WAUK 90343-A 230 1 | B | 559 | 0.15263 | 107.3953 | Single 523097 HITCHLAND7 345 523961 POTTER_CO7 345 1 | Cumulative Impact | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-304 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.074928 | 107.5866 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-304 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.064084 | 107.7557 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-304 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.064084 | 108.1822 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-304 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.064084 | 108.2747 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-304 | TO->FROM | 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | B | 997 | 0.17092 | 109.7018 | Single 525832 TUCO_INT7 345 526000 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-304 | TO->FROM | 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | B | 997 | 0.17176 | 111.09 | Single 525832 TUCO_INT7 345 526000 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-304 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.064084 | 111.3621 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-304 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.07793 | 111.723 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-304 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.07793 | 111.8755 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-304 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.074928 | 115.0541 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-304 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.07793 | 118.9427 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-304 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.07793 | 119.313 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-304 | TO->FROM | 531405 WALKMYR3 115 531510 HARBNGR3 115 1 | B | 331.39 | 0.050041 | 122.4803 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild line 531405 WALKMYR3 115 531510 HARBNGR3 115 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-310 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.072522 | 100.0488 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-310 | TO->FROM | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | B | 997 | 0.17537 | 100.166 | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | Cumulative Impact | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-310 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.062842 | 100.533 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-310 | TO->FROM | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | B | 997 | 0.17934 | 100.7286 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-310 | TO->FROM | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | B | 997 | 0.17934 | 101.1047 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-310 | TO->FROM | 524875 OASIS 6 230 781740 G24-159-TAP 230 1 | B | 319 | 0.2183 | 101.2294 | P12:345:SPS:J15:1:TOLK_CROSSROADS___:EHV: | TDF Impact | Rebuild line 524875 OASIS 6 230 781740 G24-159-TAP 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-310 | TO->FROM | 524875 OASIS 6 230 781740 G24-159-TAP 230 1 | B | 319 | 0.2183 | 101.2294 | Single 525549 TOLK7 345 780240 G24-109-TAP 345 1 | TDF Impact | Rebuild line 524875 OASIS 6 230 781740 G24-159-TAP 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-310 | TO->FROM | 524875 OASIS 6 230 781740 G24-159-TAP 230 1 | B | 319 | 0.225 | 101.8343 | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | Rebuild line 524875 OASIS 6 230 781740 G24-159-TAP 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-310 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063728 | 102.9616 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-310 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063728 | 102.9634 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-310 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063728 | 103.0288 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-310 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063728 | 103.4739 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-310 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.076461 | 103.9266 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-310 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063728 | 104.1493 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-310 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.07559 | 104.7552 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-310 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.07559 | 104.888 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-310 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.079469 | 107.2243 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-310 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063728 | 107.2793 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-310 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063728 | 107.2794 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-310 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.079469 | 107.2951 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-310 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063728 | 107.3093 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-310 | TO->FROM | 523959 POTTER_CO 6 230 3WXFMR 526:WAUK 90343-A 230 1 | B | 559 | 0.10959 | 107.3794 | P42:345:SPS:HITCHLAND-1R15:::EHV: | Cumulative Impact | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-310 | TO->FROM | 523959 POTTER_CO 6 230 3WXFMR 526:WAUK 90343-A 230 1 | B | 559 | 0.10959 | 107.3953 | Single 523097 HITCHLAND7 345 523961 POTTER_CO7 345 1 | Cumulative Impact | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-310 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.073588 | 107.5866 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-310 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063728 | 107.7557 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-310 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063728 | 108.1822 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-310 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063728 | 108.2747 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-310 | TO->FROM | 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | B | 997 | 0.19967 | 109.7018 | Single 525832 TUCO_INT7 345 526000 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-310 | TO->FROM | 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | B | 997 | 0.20101 | 111.09 | Single 525832 TUCO_INT7 345 526000 CRAWFISH_DR 345 2 | TDF Impact | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-310 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063728 | 111.3621 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-310 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.076673 | 111.723 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-310 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.076673 | 111.8755 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-310 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.073588 | 115.0541 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-310 | TO->FROM | 524875 OASIS 6 230 781740 G24-159-TAP 230 1 | B | 319 | 0.65534 | 117.1851 | Single 527799 EDDY_NORTH6 230 786270 G24-310-TAP 230 1 | TDF Impact | Rebuild line 524875 OASIS 6 230 781740 G24-159-TAP 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-310 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.076673 | 118.9427 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-310 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.076673 | 119.313 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-310 | TO->FROM | 524875 OASIS 6 230 781740 G24-159-TAP 230 1 | B | 319 | 0.65482 | 120.7292 | Single 527799 EDDY_NORTH6 230 786270 G24-310-TAP 230 1 | TDF Impact | Rebuild line 524875 OASIS 6 230 781740 G24-159-TAP 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-310 | TO->FROM | 524875 OASIS 6 230 781740 G24-159-TAP 230 1 | B | 319 | 0.65354 | 125.4479 | Single 527799 EDDY_NORTH6 230 786270 G24-310-TAP 230 1 | TDF Impact | Rebuild line 524875 OASIS 6 230 781740 G24-159-TAP 230 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-311 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.072522 | 100.0488 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-311 | TO->FROM | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | B | 997 | 0.17537 | 100.166 | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | Cumulative Impact | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-311 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.062842 | 100.533 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-311 | TO->FROM | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | B | 997 | 0.17934 | 100.7286 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-311 | TO->FROM | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | B | 997 | 0.17934 | 101.1047 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-311 | TO->FROM | 524875 OASIS 6 230 781740 G24-159-TAP 230 1 | B | 319 | 0.2183 | 101.2294 | P12:345:SPS:J15:1:TOLK_CROSSROADS___:EHV: | TDF Impact | Rebuild line 524875 OASIS 6 230 781740 G24-159-TAP 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-311 | TO->FROM | 524875 OASIS 6 230 781740 G24-159-TAP 230 1 | B | 319 | 0.2183 | 101.2294 | Single 525549 TOLK7 345 780240 G24-109-TAP 345 1 | TDF Impact | Rebuild line 524875 OASIS 6 230 781740 G24-159-TAP 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-311 | TO->FROM | 524875 OASIS 6 230 781740 G24-159-TAP 230 1 | B | 319 | 0.225 | 101.8343 | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | Rebuild line 524875 OASIS 6 230 781740 G24-159-TAP 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-311 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063728 | 102.9616 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-311 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063728 | 102.9634 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-311 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063728 | 103.0288 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-311 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063728 | 103.4739 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-311 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.076461 | 103.9266 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-311 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063728 | 104.1493 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-311 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.07559 | 104.7552 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-311 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.07559 | 104.888 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-311 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.079469 | 107.2243 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-311 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063728 | 107.2793 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-311 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063728 | 107.2794 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-311 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.079469 | 107.2951 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-311 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063728 | 107.3093 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-311 | TO->FROM | 523959 POTTER_CO 6 230 3WXFMR 526:WAUK 90343-A 230 1 | B | 559 | 0.10959 | 107.3794 | P42:345:SPS:HITCHLAND-1R15:::EHV: | Cumulative Impact | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-311 | TO->FROM | 523959 POTTER_CO 6 230 3WXFMR 526:WAUK 90343-A 230 1 | B | 559 | 0.10959 | 107.3953 | Single 523097 HITCHLAND7 345 523961 POTTER_CO7 345 1 | Cumulative Impact | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-311 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.073588 | 107.5866 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-311 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063728 | 107.7557 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-311 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063728 | 108.1822 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-311 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063728 | 108.2747 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-311 | TO->FROM | 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | B | 997 | 0.19967 | 109.7018 | Single 525832 TUCO_INT7 345 526000 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-311 | TO->FROM | 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | B | 997 | 0.20101 | 111.09 | Single 525832 TUCO_INT7 345 526000 CRAWFISH_DR 345 2 | TDF Impact | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-311 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063728 | 111.3621 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-311 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.076673 | 111.723 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-311 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.076673 | 111.8755 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-311 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.073588 | 115.0541 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-311 | TO->FROM | 524875 OASIS 6 230 781740 G24-159-TAP 230 1 | B | 319 | 0.65534 | 117.1851 | Single 527799 EDDY_NORTH6 230 786270 G24-310-TAP 230 1 | TDF Impact | Rebuild line 524875 OASIS 6 230 781740 G24-159-TAP 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-311 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.076673 | 118.9427 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-311 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.076673 | 119.313 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-311 | TO->FROM | 524875 OASIS 6 230 781740 G24-159-TAP 230 1 | B | 319 | 0.65482 | 120.7292 | Single 527799 EDDY_NORTH6 230 786270 G24-310-TAP 230 1 | TDF Impact | Rebuild line 524875 OASIS 6 230 781740 G24-159-TAP 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-311 | TO->FROM | 524875 OASIS 6 230 781740 G24-159-TAP 230 1 | B | 319 | 0.65354 | 125.4479 | Single 527799 EDDY_NORTH6 230 786270 G24-310-TAP 230 1 | TDF Impact | Rebuild line 524875 OASIS 6 230 781740 G24-159-TAP 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-317 | TO->FROM | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | B | 997 | 0.51281 | 100.166 | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | TDF Impact | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-317 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.059965 | 100.533 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-317 | TO->FROM | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | B | 997 | 0.51224 | 100.7286 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | TDF Impact | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-317 | TO->FROM | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | B | 997 | 0.51224 | 101.1047 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | TDF Impact | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-317 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.060959 | 102.9616 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-317 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.060959 | 102.9634 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-317 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.060959 | 103.0288 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-317 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.060959 | 103.4739 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-317 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.060959 | 104.1493 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 00NR | 1 | 29SP | T1 | GEN-2024-317 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | B | 211 | 0.037743 | 104.1932 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Rebuild line 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1
Thermal | 00NR | 1 | 29SP | T1 | GEN-2024-317 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | B | 211 | 0.038202 | 104.436 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | TDF Impact | Rebuild line 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1
Thermal | 00NR | 1 | 26SP | T1 | GEN-2024-317 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | B | 211 | 0.037854 | 105.7881 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Rebuild line 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1
Thermal | 00NR | 1 | 26SP | T1 | GEN-2024-317 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | B | 211 | 0.038315 | 106.2632 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | TDF Impact | Rebuild line 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-317 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.060959 | 107.2793 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-317 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.060959 | 107.2794 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-317 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.060959 | 107.3093 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-317 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.060959 | 107.7557 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-317 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.060959 | 108.1822 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-317 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.060959 | 108.2747 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-317 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.060959 | 111.3621 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-317 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | B | 171 | 0.033408 | 111.797 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Rebuild line 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-317 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | B | 171 | 0.033736 | 111.9445 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | TDF Impact | Rebuild line 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-317 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | B | 171 | 0.033502 | 113.6342 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Rebuild line 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-317 | TO->FROM | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | B | 171 | 0.033828 | 113.9786 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | TDF Impact | Rebuild line 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-317 | TO->FROM | 511467 L.E.S.-4 138 3WXFMR 520:LES 5 345 2 | B | 515 | 0.10855 | 114.4267 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-317 | TO->FROM | 511467 L.E.S.-4 138 3WXFMR 520:LES 5 345 2 | B | 515 | 0.10966 | 114.7092 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-317 | TO->FROM | 511467 L.E.S.-4 138 3WXFMR 520:LES 5 345 2 | B | 515 | 0.11496 | 115.4941 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | TDF Impact | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-317 | TO->FROM | 511467 L.E.S.-4 138 3WXFMR 520:LES 5 345 2 | B | 515 | 0.11615 | 117.1585 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | TDF Impact | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-318 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.064689 | 100.4398 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.070066 | 100.451 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-318 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1182 | 0.081356 | 100.7686 | Single 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-318 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1182 | 0.081453 | 100.7917 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | Cumulative Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.08096 | 101.1642 | Single 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | A | 901 | 0.049425 | 101.5467 | System Intact | TDF Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.081102 | 101.7923 | Single 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.052299 | 101.9139 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.070066 | 101.9296 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | A | 901 | 0.066682 | 102.5076 | System Intact | TDF Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.063038 | 102.6355 | Single 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Cumulative Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.08096 | 102.8031 | Single 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Cumulative Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.071013 | 102.8233 | P22:345:EES:CLARKSV7!:::EHV: | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.081102 | 103.1009 | Single 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.08096 | 103.3738 | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.082027 | 103.4829 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.081102 | 103.5409 | Single 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.062843 | 103.7549 | Single 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.053425 | 104.0394 | P22:345:EES:CLARKSV7!:::EHV: | Cumulative Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-318 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.064879 | 104.6561 | P22:345:EES:CLARKSV7!:::EHV: | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | TO->FROM | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | A | 1806 | 0.03544 | 104.7272 | System Intact | TDF Impact | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | TO->FROM | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | A | 1806 | 0.043085 | 104.7927 | System Intact | TDF Impact | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.071013 | 104.8397 | P22:345:EES:CLARKSV7!:::EHV: | Cumulative Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.081102 | 104.9783 | Single 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.063038 | 105.1591 | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | Cumulative Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.08096 | 105.2013 | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | Cumulative Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.062843 | 105.3089 | Single 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.082027 | 105.3978 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | Cumulative Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.066651 | 105.4314 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB:::: | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.066658 | 105.47 | P12:345:EES:CHAMSPR7!:CLARKSV7!:1:EHV: | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-318 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.061244 | 105.6463 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB:::: | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-318 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.061251 | 105.6708 | P12:345:EES:CHAMSPR7!:CLARKSV7!:1:EHV: | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.063741 | 105.6815 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | Cumulative Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.079803 | 106.3738 | P23:345:WERE:N345-345-20:EHV: | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1011 | 0.086619 | 106.9293 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-318 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.081356 | 107.6019 | Single 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1011 | 0.076524 | 107.7039 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.066651 | 107.8076 | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB:::: | Cumulative Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | TO->FROM | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | A | 827 | 0.048351 | 107.8643 | System Intact | TDF Impact | Rebuild line 532791 BENTON 7 345 532794 ROSEHIL7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.066658 | 107.867 | P12:345:EES:CHAMSPR7!:CLARKSV7!:1:EHV: | Cumulative Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.079803 | 108.4042 | P23:345:WERE:N345-345-20:EHV: | Cumulative Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | B | 1055 | 0.061581 | 108.8315 | P23:345:WERE:N345-345-20:EHV: | Cumulative Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-318 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.081356 | 109.031 | Single 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-318 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.081453 | 109.0559 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.052299 | 109.2662 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.063038 | 109.6648 | Single 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.062843 | 110.6179 | Single 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.053425 | 110.6357 | P22:345:EES:CLARKSV7!:::EHV: | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.063038 | 112.0601 | Single 532793 NEOSHO7 345 784170 G24-240-TAP 345 1 | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.062843 | 112.0812 | Single 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-318 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1187 | 0.11582 | 112.2151 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.063741 | 112.433 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-318 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.12952 | 112.5233 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | TO->FROM | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | A | 827 | 0.05108 | 113.506 | System Intact | TDF Impact | Rebuild line 532791 BENTON 7 345 532794 ROSEHIL7 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-318 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.12311 | 113.7225 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-318 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.12757 | 114.0272 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-318 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.12747 | 114.0895 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | TO->FROM | 512638 CATSAGR5 161 3WXFMR 523:CATAUTO1 138 1 | B | 188 | 0.10148 | 114.3095 | P13:138-161:GRDA:CATAUTO2:::HV: | Cumulative Impact | Add 3-winding transformer 512623 CATSAGD4 138 512638 CATSAGR5 161 512833 CATTER1 1 13 M2
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | TO->FROM | 512638 CATSAGR5 161 3WXFMR 523:CATAUTO1 138 1 | B | 188 | 0.10148 | 114.3095 | Single 509790 CATOOSA4 138 512636 CATSAGR4 138 Z1 | Cumulative Impact | Add 3-winding transformer 512623 CATSAGD4 138 512638 CATSAGR5 161 512833 CATTER1 1 13 M2
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | TO->FROM | 512638 CATSAGR5 161 3WXFMR 523:CATAUTO2 138 2 | B | 188 | 0.10178 | 114.6349 | P13:138-161:GRDA:CATAUTO1:::HV: | Cumulative Impact | Add 3-winding transformer 512636 CATSAGR4 138 512638 CATSAGR5 161 512834 CATTER2 1 13 M2
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | TO->FROM | 512638 CATSAGR5 161 3WXFMR 523:CATAUTO2 138 2 | B | 188 | 0.10178 | 114.6349 | Single 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | Cumulative Impact | Add 3-winding transformer 512636 CATSAGR4 138 512638 CATSAGR5 161 512834 CATTER2 1 13 M2
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-318 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.12245 | 115.4477 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-318 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.12747 | 115.647 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | TO->FROM | 512650 GRDA1 7 345 512865 GREC TAP7 345 1 | B | 1195 | 0.061581 | 115.6656 | P23:345:WERE:N345-345-20:EHV: | Cumulative Impact | Rebuild line 512650 GRDA1 7 345 512865 GREC TAP7 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-318 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.12245 | 117.1553 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-318 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.12245 | 117.1572 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-318 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.12245 | 119.7129 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-318 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.12245 | 124.3274 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | TO->FROM | 512638 CATSAGR5 161 3WXFMR 523:CATAUTO2 138 2 | B | 188 | 0.088363 | 127.7708 | Single 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | Cumulative Impact | Add 3-winding transformer 512636 CATSAGR4 138 512638 CATSAGR5 161 512834 CATTER2 1 13 M2
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.090293 | 137.9906 | System Intact | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.082972 | 138.1985 | System Intact | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-318 | TO->FROM | 512638 CATSAGR5 161 3WXFMR 523:CATAUTO2 138 2 | B | 188 | 0.086732 | 143.3437 | Single 509790 CATOOSA4 138 512623 CATSAGD4 138 Z1 | Cumulative Impact | Add 3-winding transformer 512636 CATSAGR4 138 512638 CATSAGR5 161 512834 CATTER2 1 13 M2
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.099529 | 155.4006 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.10262 | 155.7991 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.096213 | 155.8883 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.090148 | 158.3302 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.097183 | 159.2546 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.08885 | 159.5575 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.10489 | 160.5677 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.09665 | 161.638 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.10163 | 161.7992 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.097144 | 161.8408 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.088261 | 162.2698 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.093985 | 163.3422 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.09665 | 164.1736 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.09665 | 164.1763 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.088261 | 164.8475 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.088261 | 164.8482 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.09665 | 167.9939 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.088261 | 169.069 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-318 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.09665 | 175.0352 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-318 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.088261 | 177.0235 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-319 | TO->FROM | 541199 ST JOE 7 345 541400 EASTOWN7 345 1 | B | 1185 | 0.11845 | 100.396 | Single 541199 STJOE7 345 761383 G17-183-TAP 345 1 | Cumulative Impact | Rebuild line 541199 ST JOE 7 345 541400 EASTOWN7 345 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-319 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.079326 | 101.6955 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-319 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.079326 | 101.6955 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-319 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.079326 | 101.6955 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 26SP | T1 | GEN-2024-319 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.076831 | 105.0133 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 29WP | T1 | GEN-2024-319 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.073706 | 106.2154 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-319 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.07478 | 106.5956 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-319 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.07478 | 106.5956 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-319 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.07478 | 106.5956 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-319 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.052129 | 106.8199 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-319 | TO->FROM | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | B | 1195 | 0.13031 | 107.005 | Single 541199 STJOE7 345 761383 G17-183-TAP 345 1 | Cumulative Impact | Rebuild line 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-319 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | A | 311 | 0.046191 | 111.039 | System Intact | TDF Impact | Rebuild line 300071 5CLINTN 161 761278 G17-108-TAP 161 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-319 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.080962 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-319 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.080962 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-319 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.080962 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-319 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.07354 | 117.7598 | P55:345:OPPD:S3458 3::FN13:EHV: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-319 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | A | 311 | 0.046257 | 121.8886 | System Intact | TDF Impact | Rebuild line 300071 5CLINTN 161 761278 G17-108-TAP 161 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-319 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | A | 334 | 0.045178 | 145.0684 | System Intact | TDF Impact | Rebuild line 300071 5CLINTN 161 761278 G17-108-TAP 161 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-320 | TO->FROM | 541199 ST JOE 7 345 541400 EASTOWN7 345 1 | B | 1185 | 0.13886 | 100.396 | Single 541199 STJOE7 345 761383 G17-183-TAP 345 1 | Cumulative Impact | Rebuild line 541199 ST JOE 7 345 541400 EASTOWN7 345 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-320 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.079504 | 101.6955 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-320 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.079504 | 101.6955 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-320 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.079504 | 101.6955 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-320 | TO->FROM | 533238 EDWARVL3 115 533282 MUND 3 115 1 | B | 230 | 0.18011 | 102.2074 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild line 533238 EDWARVL3 115 533282 MUND 3 115 1
Thermal | 03ALL | 1 | 26SP | T1 | GEN-2024-320 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.075528 | 105.0133 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 29WP | T1 | GEN-2024-320 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.073686 | 106.2154 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-320 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.074636 | 106.5956 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-320 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.074636 | 106.5956 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-320 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.074636 | 106.5956 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-320 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.058736 | 106.8199 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-320 | TO->FROM | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | B | 1195 | 0.15269 | 107.005 | Single 541199 STJOE7 345 761383 G17-183-TAP 345 1 | Cumulative Impact | Rebuild line 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-320 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.052169 | 108.3331 | P42:345:NPPD:BKR-TOB-3304:::: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-320 | TO->FROM | 533238 EDWARVL3 115 533282 MUND 3 115 1 | B | 201 | 0.18144 | 109.2108 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild line 533238 EDWARVL3 115 533282 MUND 3 115 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-320 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | A | 311 | 0.043123 | 111.039 | System Intact | TDF Impact | Rebuild line 300071 5CLINTN 161 761278 G17-108-TAP 161 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-320 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.081121 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-320 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.081121 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-320 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.081121 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-320 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.07418 | 117.7598 | P55:345:OPPD:S3458 3::FN13:EHV: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-320 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | A | 311 | 0.043141 | 121.8886 | System Intact | TDF Impact | Rebuild line 300071 5CLINTN 161 761278 G17-108-TAP 161 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-320 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | A | 334 | 0.041959 | 145.0684 | System Intact | TDF Impact | Rebuild line 300071 5CLINTN 161 761278 G17-108-TAP 161 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-321 | TO->FROM | 514934 DRAPER 7 345 515045 SEMINOL7 345 2 | B | 717 | 0.23361 | 104.675 | P42:345:OKGE:SB_SEOL7385:::EHV: | TDF Impact | Rebuild line 514934 DRAPER 7 345 515045 SEMINOL7 345 2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-321 | TO->FROM | 514934 DRAPER 7 345 515045 SEMINOL7 345 2 | B | 717 | 0.23343 | 109.0105 | P42:345:OKGE:SB_SEOL7385:::EHV: | TDF Impact | Rebuild line 514934 DRAPER 7 345 515045 SEMINOL7 345 2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-323 | TO->FROM | 514808 JOHNCO 4 138 3WXFMR 524:524:JOHNCOT3 345 3 | B | 478 | 0.079452 | 100.3203 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-323 | TO->FROM | 507760 SW SHV 7 345 508809 LONGWD 7 345 1 | B | 1195 | 0.086142 | 100.4776 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | Cumulative Impact | Rebuild line 507760 SW SHV 7 345 508809 LONGWD 7 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-323 | TO->FROM | 514809 JOHNCO 7 345 787110 G24-338-TAP 345 1 | B | 1195 | 0.16201 | 101.4771 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-323 | TO->FROM | 507760 SW SHV 7 345 508809 LONGWD 7 345 1 | B | 1195 | 0.079474 | 102.0621 | P23:345:AEPW:DIANA CB 12000 NBTB:::: | Cumulative Impact | Rebuild line 507760 SW SHV 7 345 508809 LONGWD 7 345 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-323 | TO->FROM | 507760 SW SHV 7 345 508809 LONGWD 7 345 1 | B | 1195 | 0.078284 | 102.2481 | P12:345:AEPW:SWSHV7:DIANA7::: | Cumulative Impact | Rebuild line 507760 SW SHV 7 345 508809 LONGWD 7 345 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-323 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 | B | 191 | 0.050903 | 102.6582 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | Rebuild line 515117 ARBUCKL4 138 515121 MILLCKT4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-323 | TO->FROM | 514809 JOHNCO 7 345 787110 G24-338-TAP 345 1 | B | 1195 | 0.16101 | 103.3869 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-323 | TO->FROM | 507760 SW SHV 7 345 508809 LONGWD 7 345 1 | B | 1195 | 0.083184 | 104.4813 | Single 337376 7SAREPTA% 345 788340 G24-379-TAP 345 1 | Cumulative Impact | Rebuild line 507760 SW SHV 7 345 508809 LONGWD 7 345 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-323 | TO->FROM | 514934 DRAPER 7 345 515045 SEMINOL7 345 2 | B | 717 | 0.11119 | 104.675 | P42:345:OKGE:SB_SEOL7385:::EHV: | Cumulative Impact | Rebuild line 514934 DRAPER 7 345 515045 SEMINOL7 345 2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-323 | TO->FROM | 507760 SW SHV 7 345 508809 LONGWD 7 345 1 | B | 1195 | 0.080969 | 105.2021 | P23:345:AEPW:DIANA CB 12000 NBTB:::: | Cumulative Impact | Rebuild line 507760 SW SHV 7 345 508809 LONGWD 7 345 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-323 | TO->FROM | 507760 SW SHV 7 345 508809 LONGWD 7 345 1 | B | 1195 | 0.079755 | 105.4037 | P12:345:AEPW:SWSHV7:DIANA7::: | Cumulative Impact | Rebuild line 507760 SW SHV 7 345 508809 LONGWD 7 345 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-323 | TO->FROM | 514934 DRAPER 7 345 515045 SEMINOL7 345 2 | B | 717 | 0.11443 | 109.0105 | P42:345:OKGE:SB_SEOL7385:::EHV: | Cumulative Impact | Rebuild line 514934 DRAPER 7 345 515045 SEMINOL7 345 2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-323 | TO->FROM | 507760 SW SHV 7 345 508809 LONGWD 7 345 1 | B | 1195 | 0.084456 | 109.0412 | Single 337376 7SAREPTA% 345 788340 G24-379-TAP 345 1 | Cumulative Impact | Rebuild line 507760 SW SHV 7 345 508809 LONGWD 7 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-323 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 | B | 191 | 0.062131 | 112.3457 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-323 | TO->FROM | 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 | B | 222 | 0.060025 | 125.8151 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-323 | TO->FROM | 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 | B | 222 | 0.061086 | 129.9677 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-323 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 | B | 191 | 0.060025 | 141.9099 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-323 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 | B | 191 | 0.061086 | 146.7539 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 01ALL | 1 | 26SP | JTIQ - Expanded Scope Analysis | GEN-2024-327 | TO->FROM | 603022 SOURIS 7 115 603023 MALLARD7 115 1 | B | 112.6 | 0.13838 | 101.98 | P12:115:XEL-WAPA:MALLARD7:RUGBY7:1 | TDF Impact | Rebuild the SOURIS 7 to MALLARD7 115kV Line 1
Thermal | 01ALL | 1 | 26SP | JTIQ - Expanded Scope Analysis | GEN-2024-327 | TO->FROM | 603022 SOURIS 7 115 603023 MALLARD7 115 1 | B | 112.6 | 0.13838 | 101.98 | P12:115.0:UMZ:# N-1 #:: LINE MALLARD7-RUGBY 7-1 :HV: | TDF Impact | Rebuild the SOURIS 7 to MALLARD7 115kV Line 1
Thermal | 01ALL | 1 | 26SP | JTIQ - Expanded Scope Analysis | GEN-2024-327 | TO->FROM | 603022 SOURIS 7 115 603023 MALLARD7 115 1 | B | 112.6 | 0.11889 | 102.32 | P12:230.0:UMZ:# N-1 #:: LINE OWAN -MW4-JUDSON__-BE4-Z :HV: | TDF Impact | Rebuild the SOURIS 7 to MALLARD7 115kV Line 1
Thermal | 01ALL | 1 | 26SP | JTIQ - Expanded Scope Analysis | GEN-2024-327 | TO->FROM | 603022 SOURIS 7 115 603023 MALLARD7 115 1 | B | 112.6 | 0.10595 | 105.94 | P21:230:GRE:GRE-MCHENRY4:GRE-COALTP4:1:HV: | TDF Impact | Rebuild the SOURIS 7 to MALLARD7 115kV Line 1
Thermal | 01ALL | 1 | 26SP | JTIQ - Expanded Scope Analysis | GEN-2024-327 | TO->FROM | 603022 SOURIS 7 115 603023 MALLARD7 115 1 | B | 112.6 | 0.10583 | 107.01 | P12:230:GRE:CCK-STN-MCH | TDF Impact | Rebuild the SOURIS 7 to MALLARD7 115kV Line 1
Thermal | 01ALL | 1 | 26SP | JTIQ - Expanded Scope Analysis | GEN-2024-327 | TO->FROM | 603022 SOURIS 7 115 603023 MALLARD7 115 1 | B | 112.6 | 0.11889 | 110.32 | P11:22:GRE:GRE-COAL41G:1 | TDF Impact | Rebuild the SOURIS 7 to MALLARD7 115kV Line 1
Thermal | 01ALL | 1 | 26SP | JTIQ - Expanded Scope Analysis | GEN-2024-327 | TO->FROM | 603022 SOURIS 7 115 603023 MALLARD7 115 1 | B | 112.6 | 0.11889 | 110.78 | P11:22:GRE:GRE-COAL42G:2 | TDF Impact | Rebuild the SOURIS 7 to MALLARD7 115kV Line 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-330 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.063633 | 101.6955 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-330 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.063633 | 101.6955 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-330 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.063633 | 101.6955 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-330 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | B | 829 | 0.046138 | 103.7671 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | TDF Impact | Rebuild line 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-330 | TO->FROM | 532987 BUTLER 4 138 532990 MIDIAN 4 138 1 | B | 121 | 0.3999 | 105.8798 | P52:345:WERE:NRSS7:EHV: | TDF Impact | Rebuild line 532987 BUTLER 4 138 532990 MIDIAN 4 138 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-330 | TO->FROM | 532987 BUTLER 4 138 532990 MIDIAN 4 138 1 | B | 121 | 0.38671 | 105.98 | P12:115:WERE:EEUR-WEMP-115:HV: | TDF Impact | Rebuild line 532987 BUTLER 4 138 532990 MIDIAN 4 138 1
Thermal | 03ALL | 1 | 29WP | T1 | GEN-2024-330 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.056959 | 106.2154 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-330 | TO->FROM | 532987 BUTLER 4 138 532990 MIDIAN 4 138 1 | B | 121 | 0.39847 | 106.4515 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | TDF Impact | Rebuild line 532987 BUTLER 4 138 532990 MIDIAN 4 138 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-330 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.056208 | 106.5956 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-330 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.056208 | 106.5956 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-330 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.056208 | 106.5956 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-330 | TO->FROM | 532987 BUTLER 4 138 532990 MIDIAN 4 138 1 | B | 121 | 0.38671 | 106.9368 | Single 533308 VAUGHN3 115 533309 WEMPORI3 115 1 | TDF Impact | Rebuild line 532987 BUTLER 4 138 532990 MIDIAN 4 138 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-330 | TO->FROM | 532987 BUTLER 4 138 532990 MIDIAN 4 138 1 | B | 121 | 0.39857 | 107.1588 | Single 300739 7BLACKBERRY 345 785580 G24-287-TAP 345 1 | TDF Impact | Rebuild line 532987 BUTLER 4 138 532990 MIDIAN 4 138 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-330 | TO->FROM | 532987 BUTLER 4 138 532990 MIDIAN 4 138 1 | B | 121 | 0.40511 | 108.3626 | Single 533583 BUTLERN2 69 533597 MIDIAN2 69 1 | TDF Impact | Rebuild line 532987 BUTLER 4 138 532990 MIDIAN 4 138 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-330 | TO->FROM | 532987 BUTLER 4 138 532990 MIDIAN 4 138 1 | B | 121 | 0.39976 | 108.3647 | P12:345:WERE:NRSS-N345-345:EHV: | TDF Impact | Rebuild line 532987 BUTLER 4 138 532990 MIDIAN 4 138 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-330 | TO->FROM | 532987 BUTLER 4 138 532990 MIDIAN 4 138 1 | B | 121 | 0.38949 | 109.0424 | Single 533005 NEPARSN4 138 533022 NEOSHON4 138 1 | TDF Impact | Rebuild line 532987 BUTLER 4 138 532990 MIDIAN 4 138 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-330 | TO->FROM | 533583 BUTLERN2 69 533597 MIDIAN 2 69 1 | B | 57 | 0.12284 | 110.0631 | P13:69:WERE:BUTL-TX-1-138-69:HV: | Cumulative Impact | Rebuild line 533583 BUTLERN2 69 533597 MIDIAN 2 69 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-330 | TO->FROM | 532987 BUTLER 4 138 532990 MIDIAN 4 138 1 | B | 121 | 0.42173 | 111.1079 | Single 532990 MIDIAN4 138 533597 MIDIAN2 69 533117 'MIDIAN TX5 1' 13 5 | TDF Impact | Rebuild line 532987 BUTLER 4 138 532990 MIDIAN 4 138 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-330 | TO->FROM | 532987 BUTLER 4 138 532990 MIDIAN 4 138 1 | B | 121 | 0.4219 | 111.2267 | Single 532990 MIDIAN4 138 533597 MIDIAN2 69 533082 'MIDIAN TX3 1' 13 3 | TDF Impact | Rebuild line 532987 BUTLER 4 138 532990 MIDIAN 4 138 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-330 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.063595 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-330 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.063595 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-330 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.063595 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-330 | TO->FROM | 533583 BUTLERN2 69 533597 MIDIAN 2 69 1 | B | 57 | 0.17272 | 133.8619 | P12:138:WERE:BUTL-MIDI-138:HV: | Cumulative Impact | Rebuild line 533583 BUTLERN2 69 533597 MIDIAN 2 69 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-330 | TO->FROM | 533583 BUTLERN2 69 533597 MIDIAN 2 69 1 | B | 45 | 0.123 | 147.5692 | P13:69:WERE:BUTL-TX-1-138-69:HV: | Cumulative Impact | Rebuild line 533583 BUTLERN2 69 533597 MIDIAN 2 69 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-330 | TO->FROM | 533583 BUTLERN2 69 533597 MIDIAN 2 69 1 | B | 45 | 0.12192 | 154.7618 | P13:69:WERE:BUTL-TX-1-138-69:HV: | Cumulative Impact | Rebuild line 533583 BUTLERN2 69 533597 MIDIAN 2 69 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-330 | TO->FROM | 533583 BUTLERN2 69 533597 MIDIAN 2 69 1 | B | 45 | 0.17343 | 160.6574 | P12:138:WERE:BUTL-MIDI-138:HV: | Cumulative Impact | Rebuild line 533583 BUTLERN2 69 533597 MIDIAN 2 69 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-330 | TO->FROM | 533583 BUTLERN2 69 533597 MIDIAN 2 69 1 | B | 45 | 0.17299 | 177.1968 | P12:138:WERE:BUTL-MIDI-138:HV: | Cumulative Impact | Rebuild line 533583 BUTLERN2 69 533597 MIDIAN 2 69 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-333 | TO->FROM | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 | B | 1015 | 0.098503 | 102.04 | P42:345:OKGE:SB_DGSE7313:::EHV: | Cumulative Impact | Rebuild line 514715 WOODRNG7 345 515875 REDNGTN7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-333 | TO->FROM | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 | B | 1015 | 0.10618 | 102.2256 | P42:345:OKGE:SB_DGSE7313:::EHV: | Cumulative Impact | Rebuild line 514715 WOODRNG7 345 515875 REDNGTN7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-333 | TO->FROM | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | A | 1806 | 0.043169 | 104.7272 | System Intact | TDF Impact | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-333 | TO->FROM | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | A | 1806 | 0.04888 | 104.7927 | System Intact | TDF Impact | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-333 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1011 | 0.037608 | 106.9293 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-333 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1011 | 0.034662 | 107.7039 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-333 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1187 | 0.043478 | 112.2151 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-333 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.05256 | 113.7225 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-333 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.063841 | 114.4362 | System Intact | TDF Impact | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-333 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.057874 | 114.6025 | System Intact | TDF Impact | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-333 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.051902 | 115.4477 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-333 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.051902 | 117.1553 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-333 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.051902 | 117.1572 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-333 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.051902 | 119.7129 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-333 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.051902 | 124.3274 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-333 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.036696 | 137.9906 | System Intact | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-333 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.033791 | 138.1985 | System Intact | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-334 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | B | 829 | 0.031762 | 103.7671 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | TDF Impact | Rebuild line 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-336 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.0713 | 100.0488 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-336 | TO->FROM | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | B | 997 | 0.18085 | 100.166 | P12:345:OKGE-AEP:BKRBKR4291:::EHV: | Cumulative Impact | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-336 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.062504 | 100.533 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-336 | TO->FROM | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | B | 997 | 0.18453 | 100.7286 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-336 | TO->FROM | 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | B | 997 | 0.18453 | 101.1047 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Rebuild line 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-336 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063414 | 102.9616 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-336 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063414 | 102.9634 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-336 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063414 | 103.0288 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-336 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063414 | 103.4739 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-336 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.074829 | 103.9266 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-336 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063414 | 104.1493 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-336 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.074453 | 104.7552 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-336 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.074453 | 104.888 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-336 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.077923 | 107.2243 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-336 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063414 | 107.2793 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-336 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063414 | 107.2794 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 29WP | T0 | GEN-2024-336 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 373 | 0.077923 | 107.2951 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-336 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063414 | 107.3093 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-336 | TO->FROM | 523959 POTTER_CO 6 230 3WXFMR 526:WAUK 90343-A 230 1 | B | 559 | 0.096423 | 107.3794 | P42:345:SPS:HITCHLAND-1R15:::EHV: | Cumulative Impact | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-336 | TO->FROM | 523959 POTTER_CO 6 230 3WXFMR 526:WAUK 90343-A 230 1 | B | 559 | 0.096423 | 107.3953 | Single 523097 HITCHLAND7 345 523961 POTTER_CO7 345 1 | Cumulative Impact | 526_POTTERCO_transformer.idv : 2023 ITP, PID: 94067, NTC, ISD: 12/15/2028
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-336 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.072395 | 107.5866 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-336 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063414 | 107.7557 | P52:138:AEPW:NR5O.K.U:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-336 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.063414 | 108.1822 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-336 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063414 | 108.2747 | P52:345:AEPW:NR5O.K.U.-7:::: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-336 | TO->FROM | 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | B | 997 | 0.28126 | 109.7018 | Single 525832 TUCO_INT7 345 526000 CRAWFISH_DR 345 2 | TDF Impact | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1
Thermal | 05ALL | 1 | 29SP | T0 | GEN-2024-336 | TO->FROM | 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1 | B | 997 | 0.28339 | 111.09 | Single 525832 TUCO_INT7 345 526000 CRAWFISH_DR 345 2 | TDF Impact | Rebuild line 526000 CRAWFISH_DR 345 778200 G24-041-TAP 345 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-336 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.063414 | 111.3621 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-336 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.075565 | 111.723 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-336 | TO->FROM | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | B | 353 | 0.075565 | 111.8755 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Rebuild line 511490 ELKCITY6 230 511557 CHISHOLM6 230 1
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-336 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.072395 | 115.0541 | P42:345:OKGE:SB_GRNT7381:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-336 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.075565 | 118.9427 | P12:345:OKGE-AEPW:BKRBKR3715:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 05ALL | 1 | 26SP | T0 | GEN-2024-336 | TO->FROM | 511458 ELKCTY-4 138 3WXFMR 520:ELKCTY-6 230 1 | B | 330 | 0.075565 | 119.313 | P12:345:OKGE-AEPW:BKRBKR3710:::EHV: | Cumulative Impact | Add 3-winding transformer 511458 ELKCTY-4 138 511482 ELKC2-1 13 511490 ELKCITY6 230 M2
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-338 | TO->FROM | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | B | 1059 | 0.065743 | 100.2166 | P12:345:AEPW:R.S.S.-7:ONETA--7::: | Cumulative Impact | Rebuild line 509745 CLARKSV7 345 515224 MUSKOGE7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-338 | TO->FROM | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | B | 1059 | 0.07229 | 100.8866 | Single 515231 KEEFTON7 345 780360 G24-113-TAP 345 1 | Cumulative Impact | Rebuild line 509745 CLARKSV7 345 515224 MUSKOGE7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-338 | TO->FROM | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 | B | 1015 | 0.062495 | 102.04 | P42:345:OKGE:SB_DGSE7313:::EHV: | Cumulative Impact | Rebuild line 514715 WOODRNG7 345 515875 REDNGTN7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-338 | TO->FROM | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 | B | 1015 | 0.069187 | 102.2256 | P42:345:OKGE:SB_DGSE7313:::EHV: | Cumulative Impact | Rebuild line 514715 WOODRNG7 345 515875 REDNGTN7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-338 | TO->FROM | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | A | 1806 | 0.032243 | 104.7927 | System Intact | TDF Impact | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-338 | TO->FROM | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | B | 1059 | 0.072293 | 105.0001 | P42:345:OKGE:SB_FTTH7386:::EHV: | Cumulative Impact | Rebuild line 509745 CLARKSV7 345 515224 MUSKOGE7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-338 | TO->FROM | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | B | 1059 | 0.07229 | 105.0075 | Single 515012 RVRVALY7 345 515302 FTSMITH7 345 1 | Cumulative Impact | Rebuild line 509745 CLARKSV7 345 515224 MUSKOGE7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-338 | TO->FROM | 505600 TUPELO 4 138 505602 S BROWN4 138 1 | B | 147 | 0.0507 | 105.0878 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | Rebuild line 505600 TUPELO 4 138 505602 S BROWN4 138 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-338 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1011 | 0.037395 | 106.9293 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-338 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1011 | 0.033946 | 107.7039 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-338 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1187 | 0.043288 | 112.2151 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-338 | TO->FROM | 511467 L.E.S.-4 138 3WXFMR 520:LES 5 345 2 | B | 515 | 0.055836 | 114.4267 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-338 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.040998 | 114.4362 | System Intact | TDF Impact | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-338 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.034968 | 114.6025 | System Intact | TDF Impact | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-338 | TO->FROM | 511467 L.E.S.-4 138 3WXFMR 520:LES 5 345 2 | B | 515 | 0.056415 | 114.7092 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-338 | TO->FROM | 511467 L.E.S.-4 138 3WXFMR 520:LES 5 345 2 | B | 515 | 0.05404 | 115.4941 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | TDF Impact | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-338 | TO->FROM | 511467 L.E.S.-4 138 3WXFMR 520:LES 5 345 2 | B | 515 | 0.05474 | 117.1585 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | TDF Impact | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-338 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.035908 | 137.9906 | System Intact | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-338 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.032549 | 138.1985 | System Intact | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-339 | TO->FROM | 541199 ST JOE 7 345 541400 EASTOWN7 345 1 | B | 1185 | 0.16972 | 100.396 | Single 541199 STJOE7 345 761383 G17-183-TAP 345 1 | Cumulative Impact | Rebuild line 541199 ST JOE 7 345 541400 EASTOWN7 345 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-339 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.076257 | 101.6955 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-339 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.076257 | 101.6955 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-339 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.076257 | 101.6955 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-339 | TO->FROM | 533238 EDWARVL3 115 533282 MUND 3 115 1 | B | 230 | 0.055834 | 102.2074 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild line 533238 EDWARVL3 115 533282 MUND 3 115 1
Thermal | 03ALL | 1 | 26SP | T1 | GEN-2024-339 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.071584 | 105.0133 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 29WP | T1 | GEN-2024-339 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.069621 | 106.2154 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-339 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.070512 | 106.5956 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-339 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.070512 | 106.5956 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-339 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.070512 | 106.5956 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-339 | TO->FROM | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | B | 1195 | 0.2331 | 106.5998 | Single 542980 NASHUA7 345 542982 IATAN7 345 1 | TDF Impact | Rebuild line 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-339 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.06268 | 106.8199 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-339 | TO->FROM | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | B | 1195 | 0.18641 | 107.005 | Single 541199 STJOE7 345 761383 G17-183-TAP 345 1 | Cumulative Impact | Rebuild line 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-339 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.055654 | 108.3331 | P42:345:NPPD:BKR-TOB-3304:::: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-339 | TO->FROM | 533238 EDWARVL3 115 533282 MUND 3 115 1 | B | 201 | 0.056887 | 109.2108 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild line 533238 EDWARVL3 115 533282 MUND 3 115 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-339 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | A | 311 | 0.036599 | 111.039 | System Intact | TDF Impact | Rebuild line 300071 5CLINTN 161 761278 G17-108-TAP 161 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-339 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.077813 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-339 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.077813 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-339 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.077813 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-339 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.080346 | 117.7598 | P55:345:OPPD:S3458 3::FN13:EHV: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-339 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | A | 311 | 0.03667 | 121.8886 | System Intact | TDF Impact | Rebuild line 300071 5CLINTN 161 761278 G17-108-TAP 161 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-339 | TO->FROM | 300071 5CLINTN 161 761278 G17-108-TAP 161 1 | A | 334 | 0.035381 | 145.0684 | System Intact | TDF Impact | Rebuild line 300071 5CLINTN 161 761278 G17-108-TAP 161 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-339 | TO->FROM | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | B | 297 | 0.055077 | 175.5841 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-339 | TO->FROM | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | B | 261 | 0.053547 | 182.0098 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-339 | TO->FROM | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | B | 261 | 0.056084 | 196.2546 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-340 | TO->FROM | 514907 ARCADIA4 138 3WXFMR 524:524:ARCADIA4 345 4 | B | 448 | 0.077444 | 100.482 | P13:138:OKGE:BKRBKR_3W024:::HV: | Cumulative Impact | Add 3-winding transformer 514907 ARCADIA4 138 514908 ARCADIA7 345 515700 ARCADI41 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-340 | TO->FROM | 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1 | B | 1143 | 1 | 122.8144 | Single 787170 G24-340-TAP 345 787290 G24-344-TAP 345 1 | TDF Impact | Rebuild line 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-340 | TO->FROM | 514909 REDBUD 7 345 787290 G24-344-TAP 345 1 | B | 1143 | 1 | 122.9315 | P23:345:AEPW:RIVERSIDE CB 3405A NBTB:::: | TDF Impact | Rebuild line 514909 REDBUD 7 345 787290 G24-344-TAP 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-340 | TO->FROM | 514909 REDBUD 7 345 787290 G24-344-TAP 345 1 | B | 1143 | 1 | 122.9331 | Single 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1 | TDF Impact | Rebuild line 514909 REDBUD 7 345 787290 G24-344-TAP 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-340 | TO->FROM | 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1 | B | 1143 | 1 | 126.4143 | Single 514909 REDBUD7 345 787290 G24-344-TAP 345 1 | TDF Impact | Rebuild line 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-340 | TO->FROM | 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1 | B | 1143 | 1 | 126.4143 | P42:345:OKGE:SB_REUD7386:::EHV: | TDF Impact | Rebuild line 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-340 | TO->FROM | 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1 | B | 1143 | 1 | 126.4144 | P42:345:OKGE:SB_REUD7389:::EHV: | TDF Impact | Rebuild line 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-340 | TO->FROM | 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1 | B | 1055 | 1 | 133.1413 | Single 787170 G24-340-TAP 345 787290 G24-344-TAP 345 1 | TDF Impact | Rebuild line 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-340 | TO->FROM | 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1 | B | 1055 | 1 | 133.1907 | Single 787170 G24-340-TAP 345 787290 G24-344-TAP 345 1 | TDF Impact | Rebuild line 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-340 | TO->FROM | 514909 REDBUD 7 345 787290 G24-344-TAP 345 1 | B | 1055 | 1 | 133.2079 | P23:345:AEPW:RIVERSIDE CB 3405A NBTB:::: | TDF Impact | Rebuild line 514909 REDBUD 7 345 787290 G24-344-TAP 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-340 | TO->FROM | 514909 REDBUD 7 345 787290 G24-344-TAP 345 1 | B | 1055 | 1 | 133.208 | Single 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1 | TDF Impact | Rebuild line 514909 REDBUD 7 345 787290 G24-344-TAP 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-340 | TO->FROM | 514909 REDBUD 7 345 787290 G24-344-TAP 345 1 | B | 1055 | 1 | 133.2786 | P23:345:AEPW:RIVERSIDE CB 3405A NBTB:::: | TDF Impact | Rebuild line 514909 REDBUD 7 345 787290 G24-344-TAP 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-340 | TO->FROM | 514909 REDBUD 7 345 787290 G24-344-TAP 345 1 | B | 1055 | 1 | 133.2787 | Single 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1 | TDF Impact | Rebuild line 514909 REDBUD 7 345 787290 G24-344-TAP 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-340 | TO->FROM | 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1 | B | 1055 | 1 | 137.0482 | Single 514909 REDBUD7 345 787290 G24-344-TAP 345 1 | TDF Impact | Rebuild line 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-340 | TO->FROM | 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1 | B | 1055 | 1 | 137.0482 | P42:345:OKGE:SB_REUD7386:::EHV: | TDF Impact | Rebuild line 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-340 | TO->FROM | 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1 | B | 1055 | 1 | 137.0482 | P42:345:OKGE:SB_REUD7389:::EHV: | TDF Impact | Rebuild line 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-340 | TO->FROM | 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1 | B | 1055 | 1 | 137.0949 | P42:345:OKGE:SB_REUD7386:::EHV: | TDF Impact | Rebuild line 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-340 | TO->FROM | 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1 | B | 1055 | 1 | 137.0949 | Single 514909 REDBUD7 345 787290 G24-344-TAP 345 1 | TDF Impact | Rebuild line 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-340 | TO->FROM | 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1 | B | 1055 | 1 | 137.0949 | P42:345:OKGE:SB_REUD7389:::EHV: | TDF Impact | Rebuild line 509782 R.S.S.-7 345 787170 G24-340-TAP 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-341 | TO->FROM | 514808 JOHNCO 4 138 3WXFMR 524:524:JOHNCOT3 345 3 | B | 478 | 0.16504 | 100.3203 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-341 | TO->FROM | 514809 JOHNCO 7 345 787110 G24-338-TAP 345 1 | B | 1195 | 0.52085 | 101.4771 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-341 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 | B | 191 | 0.084227 | 102.6582 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | Rebuild line 515117 ARBUCKL4 138 515121 MILLCKT4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-341 | TO->FROM | 514809 JOHNCO 7 345 787110 G24-338-TAP 345 1 | B | 1195 | 0.52032 | 103.3869 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-341 | TO->FROM | 514934 DRAPER 7 345 515045 SEMINOL7 345 2 | B | 717 | 0.13824 | 104.675 | P42:345:OKGE:SB_SEOL7385:::EHV: | Cumulative Impact | Rebuild line 514934 DRAPER 7 345 515045 SEMINOL7 345 2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-341 | TO->FROM | 514934 DRAPER 7 345 515045 SEMINOL7 345 2 | B | 717 | 0.14062 | 109.0105 | P42:345:OKGE:SB_SEOL7385:::EHV: | Cumulative Impact | Rebuild line 514934 DRAPER 7 345 515045 SEMINOL7 345 2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-341 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 | B | 191 | 0.092545 | 112.3457 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-341 | TO->FROM | 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 | B | 222 | 0.090288 | 125.8151 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-341 | TO->FROM | 515121 MILLCKT4 138 515122 SXMLCKT4 138 1 | B | 222 | 0.09149 | 129.9677 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-341 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 | B | 191 | 0.090288 | 141.9099 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-341 | TO->FROM | 515117 ARBUCKL4 138 515121 MILLCKT4 138 1 | B | 191 | 0.09149 | 146.7539 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | TO->FROM | 508557 MARSHL-4 138 508562 PIRKEY 4 138 1 | B | 491 | 0.2117 | 100.1149 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | TDF Impact | Rebuild line 508557 MARSHL-4 138 508562 PIRKEY 4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | TO->FROM | 508557 MARSHL-4 138 508562 PIRKEY 4 138 1 | B | 491 | 0.21166 | 100.1434 | P12:345:AEPW:PIRKEY7:DIANA7::: | TDF Impact | Rebuild line 508557 MARSHL-4 138 508562 PIRKEY 4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | TO->FROM | 508072 NWTXARK7 345 508359 WELSH 7 345 1 | B | 927 | 0.27417 | 100.1454 | P23:345:AEPW:VALLIANT CB 3417A NBTB:::: | TDF Impact | Rebuild line 508072 NWTXARK7 345 508359 WELSH 7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | TO->FROM | 508557 MARSHL-4 138 508562 PIRKEY 4 138 1 | B | 491 | 0.21052 | 100.2536 | P23:345:AEPW:PIRKEY CB 13430 NBTB:::: | TDF Impact | Rebuild line 508557 MARSHL-4 138 508562 PIRKEY 4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | TO->FROM | 514808 JOHNCO 4 138 3WXFMR 524:524:JOHNCOT3 345 3 | B | 478 | 0.053518 | 100.3203 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-343 | TO->FROM | 507760 SW SHV 7 345 508809 LONGWD 7 345 1 | B | 1195 | 0.12397 | 100.4776 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | Cumulative Impact | Rebuild line 507760 SW SHV 7 345 508809 LONGWD 7 345 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-343 | TO->FROM | 507727 FLOURNY4 138 508816 OAKPH 4 138 1 | B | 395 | 0.054462 | 101.2557 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 507727 FLOURNY4 138 508816 OAKPH 4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | TO->FROM | 514809 JOHNCO 7 345 787110 G24-338-TAP 345 1 | B | 1195 | 0.13262 | 101.4771 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | TO->FROM | 508072 NWTXARK7 345 508359 WELSH 7 345 1 | B | 927 | 0.28233 | 101.9725 | P52:345:AEPW:NR3LYDIA 7:::: | TDF Impact | Rebuild line 508072 NWTXARK7 345 508359 WELSH 7 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | TO->FROM | 508072 NWTXARK7 345 508359 WELSH 7 345 1 | B | 927 | 0.28233 | 101.9725 | P23:345:AEPW:WELSH CB 11590 NBTB:::: | TDF Impact | Rebuild line 508072 NWTXARK7 345 508359 WELSH 7 345 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-343 | TO->FROM | 507760 SW SHV 7 345 508809 LONGWD 7 345 1 | B | 1195 | 0.15592 | 102.0621 | P23:345:AEPW:DIANA CB 12000 NBTB:::: | Cumulative Impact | Rebuild line 507760 SW SHV 7 345 508809 LONGWD 7 345 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-343 | TO->FROM | 509083 ROKHILL4 138 509087 TATUM 4 138 1 | A | 241 | 0.07447 | 102.1617 | System Intact | TDF Impact | Rebuild line 509083 ROKHILL4 138 509087 TATUM 4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | TO->FROM | 508072 NWTXARK7 345 508359 WELSH 7 345 1 | B | 927 | 0.27208 | 102.2152 | P23:345:AEPW:VALLIANT CB 3417A NBTB:::: | TDF Impact | Rebuild line 508072 NWTXARK7 345 508359 WELSH 7 345 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-343 | TO->FROM | 507760 SW SHV 7 345 508809 LONGWD 7 345 1 | B | 1195 | 0.16114 | 102.2481 | P12:345:AEPW:SWSHV7:DIANA7::: | Cumulative Impact | Rebuild line 507760 SW SHV 7 345 508809 LONGWD 7 345 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-343 | TO->FROM | 509083 ROKHILL4 138 509087 TATUM 4 138 1 | B | 350 | 0.090802 | 102.3453 | Single 334197 7ROCKYCRK% 345 783930 G24-232-TAP 345 1 | Cumulative Impact | Rebuild line 509083 ROKHILL4 138 509087 TATUM 4 138 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-343 | TO->FROM | 509083 ROKHILL4 138 509087 TATUM 4 138 1 | B | 350 | 0.090802 | 102.4052 | P23:345:EES::7ROCKYCRK%:1:EHV: | Cumulative Impact | Rebuild line 509083 ROKHILL4 138 509087 TATUM 4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | TO->FROM | 508072 NWTXARK7 345 508359 WELSH 7 345 1 | B | 927 | 0.30473 | 102.4055 | Single 508298 LYDIA7 345 779010 G24-068-TAP 345 1 | TDF Impact | Rebuild line 508072 NWTXARK7 345 508359 WELSH 7 345 1
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-343 | TO->FROM | 509083 ROKHILL4 138 509087 TATUM 4 138 1 | B | 379 | 0.10683 | 102.9027 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 509083 ROKHILL4 138 509087 TATUM 4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | TO->FROM | 508548 KNOXLEE4 138 509092 EASTON 4 138 1 | B | 547 | 0.099664 | 103.1422 | Single 508575 WHITNEY4 138 508595 HALLSVLS4 138 1 | Cumulative Impact | Rebuild line 508548 KNOXLEE4 138 509092 EASTON 4 138 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-343 | TO->FROM | 509083 ROKHILL4 138 509087 TATUM 4 138 1 | B | 350 | 0.13348 | 103.3121 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | Cumulative Impact | Rebuild line 509083 ROKHILL4 138 509087 TATUM 4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | TO->FROM | 508548 KNOXLEE4 138 509092 EASTON 4 138 1 | B | 547 | 0.099664 | 103.3611 | Single 508562 PIRKEY4 138 775840 G23-193-TAP 138 1 | Cumulative Impact | Rebuild line 508548 KNOXLEE4 138 509092 EASTON 4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | TO->FROM | 514809 JOHNCO 7 345 787110 G24-338-TAP 345 1 | B | 1195 | 0.13042 | 103.3869 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | TO->FROM | 508562 PIRKEY 4 138 3WXFMR 520:PIRKEY 1 345 1 | B | 600 | 0.35968 | 103.6673 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | TDF Impact | Add 3-winding transformer 508562 PIRKEY 4 138 508563 PIRKEY 7 345 508587 PIRKY1-1 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | TO->FROM | 508562 PIRKEY 4 138 3WXFMR 520:PIRKEY 1 345 1 | B | 600 | 0.35951 | 103.8062 | P12:345:AEPW:PIRKEY7:DIANA7::: | TDF Impact | Add 3-winding transformer 508562 PIRKEY 4 138 508563 PIRKEY 7 345 508587 PIRKY1-1 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | TO->FROM | 508562 PIRKEY 4 138 3WXFMR 520:PIRKEY 1 345 1 | B | 600 | 0.35729 | 103.9699 | P23:345:AEPW:PIRKEY CB 13430 NBTB:::: | TDF Impact | Add 3-winding transformer 508562 PIRKEY 4 138 508563 PIRKEY 7 345 508587 PIRKY1-1 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | TO->FROM | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.27398 | 104.0522 | Single 510907 PITTSB-7 345 787200 GEN-2024-341 345 1 | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | TO->FROM | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.27398 | 104.0523 | GEN-2024-341_POI_510907_Generator_outage | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | TO->FROM | 508548 KNOXLEE4 138 509092 EASTON 4 138 1 | B | 547 | 0.099664 | 104.0775 | Single 508595 HALLSVLS4 138 775840 G23-193-TAP 138 1 | Cumulative Impact | Rebuild line 508548 KNOXLEE4 138 509092 EASTON 4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | TO->FROM | 508072 NWTXARK7 345 508359 WELSH 7 345 1 | B | 927 | 0.28022 | 104.2605 | P23:345:AEPW:WELSH CB 11590 NBTB:::: | TDF Impact | Rebuild line 508072 NWTXARK7 345 508359 WELSH 7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | TO->FROM | 508072 NWTXARK7 345 508359 WELSH 7 345 1 | B | 927 | 0.28022 | 104.2605 | P52:345:AEPW:NR3LYDIA 7:::: | TDF Impact | Rebuild line 508072 NWTXARK7 345 508359 WELSH 7 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | TO->FROM | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.29677 | 104.4762 | P23:345:EES::7ROCKYCRK%:1:EHV: | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-343 | TO->FROM | 507760 SW SHV 7 345 508809 LONGWD 7 345 1 | B | 1195 | 0.14158 | 104.4813 | Single 337376 7SAREPTA% 345 788340 G24-379-TAP 345 1 | Cumulative Impact | Rebuild line 507760 SW SHV 7 345 508809 LONGWD 7 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | TO->FROM | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.29677 | 104.5302 | Single 334197 7ROCKYCRK% 345 783930 G24-232-TAP 345 1 | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-343 | TO->FROM | 514934 DRAPER 7 345 515045 SEMINOL7 345 2 | B | 717 | 0.13325 | 104.675 | P42:345:OKGE:SB_SEOL7385:::EHV: | Cumulative Impact | Rebuild line 514934 DRAPER 7 345 515045 SEMINOL7 345 2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | TO->FROM | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.2882 | 105.0097 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | TO->FROM | 508072 NWTXARK7 345 508359 WELSH 7 345 1 | B | 927 | 0.30267 | 105.1339 | Single 508298 LYDIA7 345 779010 G24-068-TAP 345 1 | TDF Impact | Rebuild line 508072 NWTXARK7 345 508359 WELSH 7 345 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-343 | TO->FROM | 507760 SW SHV 7 345 508809 LONGWD 7 345 1 | B | 1195 | 0.15688 | 105.2021 | P23:345:AEPW:DIANA CB 12000 NBTB:::: | Cumulative Impact | Rebuild line 507760 SW SHV 7 345 508809 LONGWD 7 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | TO->FROM | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.28798 | 105.2545 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-343 | TO->FROM | 508548 KNOXLEE4 138 509092 EASTON 4 138 1 | B | 618 | 0.20722 | 105.3303 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | TDF Impact | Rebuild line 508548 KNOXLEE4 138 509092 EASTON 4 138 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-343 | TO->FROM | 508562 PIRKEY 4 138 3WXFMR 520:PIRKEY 1 345 1 | B | 600 | 0.36108 | 105.3711 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | TDF Impact | Add 3-winding transformer 508562 PIRKEY 4 138 508563 PIRKEY 7 345 508587 PIRKY1-1 13 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-343 | TO->FROM | 507760 SW SHV 7 345 508809 LONGWD 7 345 1 | B | 1195 | 0.16209 | 105.4037 | P12:345:AEPW:SWSHV7:DIANA7::: | Cumulative Impact | Rebuild line 507760 SW SHV 7 345 508809 LONGWD 7 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-343 | TO->FROM | 508562 PIRKEY 4 138 3WXFMR 520:PIRKEY 1 345 1 | B | 600 | 0.3609 | 105.5396 | P12:345:AEPW:PIRKEY7:DIANA7::: | TDF Impact | Add 3-winding transformer 508562 PIRKEY 4 138 508563 PIRKEY 7 345 508587 PIRKY1-1 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-343 | TO->FROM | 508562 PIRKEY 4 138 3WXFMR 520:PIRKEY 1 345 1 | B | 600 | 0.35868 | 105.7103 | P23:345:AEPW:PIRKEY CB 13430 NBTB:::: | TDF Impact | Add 3-winding transformer 508562 PIRKEY 4 138 508563 PIRKEY 7 345 508587 PIRKY1-1 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-343 | TO->FROM | 508548 KNOXLEE4 138 509092 EASTON 4 138 1 | B | 618 | 0.20681 | 105.7356 | P12:345:AEPW:PIRKEY7:DIANA7::: | TDF Impact | Rebuild line 508548 KNOXLEE4 138 509092 EASTON 4 138 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-343 | TO->FROM | 509083 ROKHILL4 138 509087 TATUM 4 138 1 | A | 241 | 0.074465 | 105.8216 | System Intact | TDF Impact | Rebuild line 509083 ROKHILL4 138 509087 TATUM 4 138 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-343 | TO->FROM | 508548 KNOXLEE4 138 509092 EASTON 4 138 1 | B | 618 | 0.20527 | 105.8681 | P23:345:AEPW:PIRKEY CB 13430 NBTB:::: | TDF Impact | Rebuild line 508548 KNOXLEE4 138 509092 EASTON 4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | TO->FROM | 508562 PIRKEY 4 138 3WXFMR 520:PIRKEY 1 345 1 | B | 600 | 0.3616 | 106.2268 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | TDF Impact | Add 3-winding transformer 508562 PIRKEY 4 138 508563 PIRKEY 7 345 508587 PIRKY1-1 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | TO->FROM | 508562 PIRKEY 4 138 3WXFMR 520:PIRKEY 1 345 1 | B | 600 | 0.36141 | 106.3398 | P12:345:AEPW:PIRKEY7:DIANA7::: | TDF Impact | Add 3-winding transformer 508562 PIRKEY 4 138 508563 PIRKEY 7 345 508587 PIRKY1-1 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | TO->FROM | 508562 PIRKEY 4 138 3WXFMR 520:PIRKEY 1 345 1 | B | 600 | 0.35918 | 106.4715 | P23:345:AEPW:PIRKEY CB 13430 NBTB:::: | TDF Impact | Add 3-winding transformer 508562 PIRKEY 4 138 508563 PIRKEY 7 345 508587 PIRKY1-1 13 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-343 | TO->FROM | 509083 ROKHILL4 138 509087 TATUM 4 138 1 | B | 350 | 0.13326 | 107.2057 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | Cumulative Impact | Rebuild line 509083 ROKHILL4 138 509087 TATUM 4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | TO->FROM | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.29556 | 107.4655 | Single 509241 CROCKET7 345 783930 G24-232-TAP 345 1 | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | TO->FROM | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.31424 | 108.1752 | Single 337376 7SAREPTA% 345 788340 G24-379-TAP 345 1 | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | TO->FROM | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.29556 | 108.9129 | P23:345:EES::7ROCKYCRK%:1:EHV: | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | TO->FROM | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.29556 | 108.9659 | Single 334197 7ROCKYCRK% 345 783930 G24-232-TAP 345 1 | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-343 | TO->FROM | 514934 DRAPER 7 345 515045 SEMINOL7 345 2 | B | 717 | 0.13508 | 109.0105 | P42:345:OKGE:SB_SEOL7385:::EHV: | Cumulative Impact | Rebuild line 514934 DRAPER 7 345 515045 SEMINOL7 345 2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-343 | TO->FROM | 507760 SW SHV 7 345 508809 LONGWD 7 345 1 | B | 1195 | 0.14305 | 109.0412 | Single 337376 7SAREPTA% 345 788340 G24-379-TAP 345 1 | Cumulative Impact | Rebuild line 507760 SW SHV 7 345 508809 LONGWD 7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | TO->FROM | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.28858 | 109.2053 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | TO->FROM | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.28838 | 109.4344 | P42:500:OKGE:SB_FTTH8585:::EHV: | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | TO->FROM | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.28837 | 109.455 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | TO->FROM | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | A | 905 | 0.27398 | 109.5375 | System Intact | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | TO->FROM | 508567 SCOTTSV4 138 508569 SEMRSHL4 138 1 | B | 272 | 0.16715 | 109.7015 | P12:345:AEPW:PIRKEY7:DIANA7::: | Cumulative Impact | Rebuild line 508567 SCOTTSV4 138 508569 SEMRSHL4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | TO->FROM | 508567 SCOTTSV4 138 508569 SEMRSHL4 138 1 | B | 272 | 0.16624 | 109.8399 | P23:345:AEPW:PIRKEY CB 13430 NBTB:::: | Cumulative Impact | Rebuild line 508567 SCOTTSV4 138 508569 SEMRSHL4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | TO->FROM | 508567 SCOTTSV4 138 508569 SEMRSHL4 138 1 | B | 272 | 0.16602 | 111.3473 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | Cumulative Impact | Rebuild line 508567 SCOTTSV4 138 508569 SEMRSHL4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | TO->FROM | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | A | 905 | 0.2725 | 112.4635 | System Intact | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | TO->FROM | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.31375 | 112.9192 | Single 337376 7SAREPTA% 345 788340 G24-379-TAP 345 1 | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | TO->FROM | 508567 SCOTTSV4 138 508569 SEMRSHL4 138 1 | B | 272 | 0.16629 | 113.4583 | P12:345:AEPW:PIRKEY7:DIANA7::: | Cumulative Impact | Rebuild line 508567 SCOTTSV4 138 508569 SEMRSHL4 138 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-343 | TO->FROM | 509083 ROKHILL4 138 509087 TATUM 4 138 1 | B | 350 | 0.10676 | 113.4766 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 509083 ROKHILL4 138 509087 TATUM 4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | TO->FROM | 508567 SCOTTSV4 138 508569 SEMRSHL4 138 1 | B | 272 | 0.16538 | 113.6165 | P23:345:AEPW:PIRKEY CB 13430 NBTB:::: | Cumulative Impact | Rebuild line 508567 SCOTTSV4 138 508569 SEMRSHL4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | TO->FROM | 508567 SCOTTSV4 138 508569 SEMRSHL4 138 1 | B | 272 | 0.16525 | 115.6232 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | Cumulative Impact | Rebuild line 508567 SCOTTSV4 138 508569 SEMRSHL4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | TO->FROM | 508548 KNOXLEE4 138 509092 EASTON 4 138 1 | B | 547 | 0.2059 | 115.7374 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | TDF Impact | Rebuild line 508548 KNOXLEE4 138 509092 EASTON 4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | TO->FROM | 508548 KNOXLEE4 138 509092 EASTON 4 138 1 | B | 547 | 0.20552 | 116.1006 | P12:345:AEPW:PIRKEY7:DIANA7::: | TDF Impact | Rebuild line 508548 KNOXLEE4 138 509092 EASTON 4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | TO->FROM | 508548 KNOXLEE4 138 509092 EASTON 4 138 1 | B | 547 | 0.20398 | 116.2431 | P23:345:AEPW:PIRKEY CB 13430 NBTB:::: | TDF Impact | Rebuild line 508548 KNOXLEE4 138 509092 EASTON 4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | TO->FROM | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.36898 | 116.5992 | Single 508072 NWTXARK7 345 508359 WELSH7 345 1 | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | TO->FROM | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.36945 | 116.8814 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB:::: | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-343 | TO->FROM | 509083 ROKHILL4 138 509087 TATUM 4 138 1 | B | 350 | 0.10681 | 118.2437 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 509083 ROKHILL4 138 509087 TATUM 4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | TO->FROM | 508548 KNOXLEE4 138 509092 EASTON 4 138 1 | B | 547 | 0.20709 | 119.0778 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | TDF Impact | Rebuild line 508548 KNOXLEE4 138 509092 EASTON 4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | TO->FROM | 508548 KNOXLEE4 138 509092 EASTON 4 138 1 | B | 547 | 0.20667 | 119.3677 | P12:345:AEPW:PIRKEY7:DIANA7::: | TDF Impact | Rebuild line 508548 KNOXLEE4 138 509092 EASTON 4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | TO->FROM | 508548 KNOXLEE4 138 509092 EASTON 4 138 1 | B | 547 | 0.20512 | 119.4926 | P23:345:AEPW:PIRKEY CB 13430 NBTB:::: | TDF Impact | Rebuild line 508548 KNOXLEE4 138 509092 EASTON 4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | TO->FROM | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.3669 | 119.7688 | Single 508072 NWTXARK7 345 508359 WELSH7 345 1 | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | TO->FROM | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.36715 | 120.0073 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB:::: | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-343 | TO->FROM | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.37991 | 122.6891 | P23:345:AEPW:WELSH CB 10610 NBTB:::: | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-343 | TO->FROM | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.37797 | 126.1457 | P23:345:AEPW:WELSH CB 10610 NBTB:::: | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-344 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | A | 901 | 0.0302 | 101.5467 | System Intact | TDF Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-344 | TO->FROM | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 | B | 1015 | 0.051129 | 102.04 | P42:345:OKGE:SB_DGSE7313:::EHV: | Cumulative Impact | Rebuild line 514715 WOODRNG7 345 515875 REDNGTN7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-344 | TO->FROM | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 | B | 1015 | 0.073499 | 102.2256 | P42:345:OKGE:SB_DGSE7313:::EHV: | Cumulative Impact | Rebuild line 514715 WOODRNG7 345 515875 REDNGTN7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-344 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | A | 901 | 0.031064 | 102.5076 | System Intact | TDF Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-344 | TO->FROM | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | A | 1806 | 0.042218 | 104.7272 | System Intact | TDF Impact | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-344 | TO->FROM | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | A | 1806 | 0.047449 | 104.7927 | System Intact | TDF Impact | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-344 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1011 | 0.057188 | 106.9293 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-344 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1011 | 0.056699 | 107.7039 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-344 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1187 | 0.070083 | 112.2151 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-344 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.076508 | 112.5233 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-344 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.078681 | 113.7225 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-344 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.07567 | 114.0272 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-344 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.075281 | 114.0895 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-344 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.053252 | 114.4362 | System Intact | TDF Impact | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-344 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.045122 | 114.6025 | System Intact | TDF Impact | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-344 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.078023 | 115.4477 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-344 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.075281 | 115.647 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-344 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.078023 | 117.1553 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-344 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.078023 | 117.1572 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-344 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.078023 | 119.7129 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-344 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.078023 | 124.3274 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-344 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.054918 | 137.9906 | System Intact | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-344 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.054314 | 138.1985 | System Intact | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-344 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.059221 | 155.4006 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-344 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.059552 | 155.7991 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-344 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.058869 | 155.8883 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-344 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.058699 | 158.3302 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-344 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.062452 | 159.2546 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-344 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.061203 | 159.5575 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-344 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.061874 | 160.5677 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-344 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.061919 | 161.638 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-344 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.060556 | 161.7992 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-344 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.061043 | 161.8408 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-344 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.060614 | 162.2698 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-344 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.059745 | 163.3422 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-344 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.061919 | 164.1736 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-344 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.061919 | 164.1763 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-344 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.060614 | 164.8475 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-344 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.060614 | 164.8482 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-344 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.061919 | 167.9939 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-344 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.060614 | 169.069 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-344 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.061919 | 175.0352 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-344 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.060614 | 177.0235 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-352 | TO->FROM | 541199 ST JOE 7 345 541400 EASTOWN7 345 1 | B | 1185 | 0.077347 | 100.396 | Single 541199 STJOE7 345 761383 G17-183-TAP 345 1 | Cumulative Impact | Rebuild line 541199 ST JOE 7 345 541400 EASTOWN7 345 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-352 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.071611 | 101.6955 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-352 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.071611 | 101.6955 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-352 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.071611 | 101.6955 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 26SP | T1 | GEN-2024-352 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.070108 | 105.0133 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 29WP | T1 | GEN-2024-352 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.064909 | 106.2154 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-352 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.065665 | 106.5956 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-352 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.065665 | 106.5956 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-352 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.065665 | 106.5956 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-352 | TO->FROM | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | B | 1195 | 0.085468 | 107.005 | Single 541199 STJOE7 345 761383 G17-183-TAP 345 1 | Cumulative Impact | Rebuild line 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-352 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.073357 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-352 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.073357 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-352 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.073357 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-352 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.069736 | 117.7598 | P55:345:OPPD:S3458 3::FN13:EHV: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-360 | TO->FROM | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | B | 1059 | 0.050294 | 100.8866 | Single 515231 KEEFTON7 345 780360 G24-113-TAP 345 1 | Cumulative Impact | Rebuild line 509745 CLARKSV7 345 515224 MUSKOGE7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-360 | TO->FROM | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 | B | 1015 | 0.074588 | 102.04 | P42:345:OKGE:SB_DGSE7313:::EHV: | Cumulative Impact | Rebuild line 514715 WOODRNG7 345 515875 REDNGTN7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-360 | TO->FROM | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 | B | 1015 | 0.08353 | 102.2256 | P42:345:OKGE:SB_DGSE7313:::EHV: | Cumulative Impact | Rebuild line 514715 WOODRNG7 345 515875 REDNGTN7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-360 | TO->FROM | 515055 MAUD 4 138 787770 G24-360-TAP 138 1 | B | 287 | 0.42371 | 103.1 | P22:345:EES:MUSKOGE7!:::EHV: | TDF Impact | Rebuild line 515055 MAUD 4 138 787770 G24-360-TAP 138 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-360 | TO->FROM | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | A | 1806 | 0.035068 | 104.7272 | System Intact | TDF Impact | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-360 | TO->FROM | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | A | 1806 | 0.040872 | 104.7927 | System Intact | TDF Impact | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-360 | TO->FROM | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | B | 1059 | 0.050304 | 105.0001 | P42:345:OKGE:SB_FTTH7386:::EHV: | Cumulative Impact | Rebuild line 509745 CLARKSV7 345 515224 MUSKOGE7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-360 | TO->FROM | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | B | 1059 | 0.050294 | 105.0075 | Single 515012 RVRVALY7 345 515302 FTSMITH7 345 1 | Cumulative Impact | Rebuild line 509745 CLARKSV7 345 515224 MUSKOGE7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-360 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1011 | 0.041439 | 106.9293 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-360 | TO->FROM | 515055 MAUD 4 138 787770 G24-360-TAP 138 1 | B | 287 | 0.33788 | 107.4306 | P12:138:OKGE:BKRBKR2170:::HV: | TDF Impact | Rebuild line 515055 MAUD 4 138 787770 G24-360-TAP 138 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-360 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1011 | 0.038456 | 107.7039 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-360 | TO->FROM | 515055 MAUD 4 138 787770 G24-360-TAP 138 1 | B | 287 | 0.41108 | 107.8082 | P22:345:EES:MUSKOGE7!:::EHV: | TDF Impact | Rebuild line 515055 MAUD 4 138 787770 G24-360-TAP 138 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-360 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1187 | 0.048731 | 112.2151 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-360 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.053959 | 112.5233 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-360 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.05626 | 113.7225 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-360 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.053287 | 114.0272 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-360 | TO->FROM | 515055 MAUD 4 138 787770 G24-360-TAP 138 1 | B | 287 | 0.3552 | 114.0688 | P12:138:OKGE:BKRBKR2170:::HV: | TDF Impact | Rebuild line 515055 MAUD 4 138 787770 G24-360-TAP 138 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-360 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.051964 | 114.0895 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-360 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.051239 | 114.4362 | System Intact | TDF Impact | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-360 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.044936 | 114.6025 | System Intact | TDF Impact | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-360 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.055602 | 115.4477 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-360 | TO->FROM | 515055 MAUD 4 138 787770 G24-360-TAP 138 1 | B | 287 | 0.33811 | 115.6328 | P12:138:OKGE:BKRBKR2170:::HV: | TDF Impact | Rebuild line 515055 MAUD 4 138 787770 G24-360-TAP 138 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-360 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.051964 | 115.647 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-360 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.055602 | 117.1553 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-360 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.055602 | 117.1572 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-360 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.055602 | 119.7129 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-360 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.055602 | 124.3274 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-360 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.040063 | 137.9906 | System Intact | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-360 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.037146 | 138.1985 | System Intact | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-361 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | A | 901 | 0.031652 | 101.5467 | System Intact | TDF Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-361 | TO->FROM | 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1 | A | 901 | 0.033182 | 102.5076 | System Intact | TDF Impact | Rebuild line 513596 IGLOOV 7 345 765721 G21-047-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-361 | TO->FROM | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | A | 1806 | 0.050097 | 104.7272 | System Intact | TDF Impact | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-361 | TO->FROM | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | A | 1806 | 0.055761 | 104.7927 | System Intact | TDF Impact | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-361 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1011 | 0.052299 | 106.9293 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-361 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1011 | 0.049423 | 107.7039 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-361 | TO->FROM | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | A | 827 | 0.032316 | 107.8643 | System Intact | TDF Impact | Rebuild line 532791 BENTON 7 345 532794 ROSEHIL7 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-361 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1187 | 0.064716 | 112.2151 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-361 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.071255 | 112.5233 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-361 | TO->FROM | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | A | 827 | 0.034063 | 113.506 | System Intact | TDF Impact | Rebuild line 532791 BENTON 7 345 532794 ROSEHIL7 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-361 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.074833 | 113.7225 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-361 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.070467 | 114.0272 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-361 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.070322 | 114.0895 | Single 513596 IGLOOV7 345 765721 G21-047-TAP 345 1 | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-361 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.055684 | 114.4362 | System Intact | TDF Impact | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-361 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.049707 | 114.6025 | System Intact | TDF Impact | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-361 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.074175 | 115.4477 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-361 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.070322 | 115.647 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-361 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.074175 | 117.1553 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-361 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.074175 | 117.1572 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-361 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.074175 | 119.7129 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-361 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | B | 1324 | 0.074175 | 124.3274 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-361 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.051669 | 137.9906 | System Intact | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-361 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.048912 | 138.1985 | System Intact | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-361 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.056265 | 155.4006 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-361 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.05693 | 155.7991 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-361 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.053978 | 155.8883 | P12:138:AEPW-WERE:COFFEYT4:DEARING4::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-361 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.053508 | 158.3302 | P12:345:GRDA:GRDA1 7-GREC TAP7:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-361 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.060429 | 159.2546 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-361 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.056977 | 159.5575 | P42:345:OKGE:SB_RARD7311:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-361 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.058741 | 160.5677 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-361 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.059896 | 161.638 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-361 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.057503 | 161.7992 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-361 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.055485 | 161.8408 | Single 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-361 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.056388 | 162.2698 | P12:345:OKGE:BKRBKR3572:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-361 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.054377 | 163.3422 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-361 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.059896 | 164.1736 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-361 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.059896 | 164.1763 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-361 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.056388 | 164.8475 | P42:345:OKGE:SB_OPKY7388:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-361 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.056388 | 164.8482 | P42:345:OKGE:SB_OPKY7308:::EHV: | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-361 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.059896 | 167.9939 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-361 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.056388 | 169.069 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-361 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.059896 | 175.0352 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-361 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.056388 | 177.0235 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-362 | TO->FROM | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | B | 308 | 0.11328 | 100.6687 | P12:138:OKGE:BKRBKR1320:::HV: | TDF Impact | Rebuild line 514863 HAYMAKR4 138 514898 CIMARON4 138 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-362 | TO->FROM | 514893 XEROX 4 138 514894 CZECHAL4 138 1 | B | 382 | 0.10995 | 101.0677 | P12:138:OKGE:BKRBKR1260:::HV: | TDF Impact | Rebuild line 514893 XEROX 4 138 514894 CZECHAL4 138 1
Thermal | 00NR | 1 | 29SP | T1 | GEN-2024-362 | TO->FROM | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | A | 387 | 0.067673 | 101.3214 | System Intact | TDF Impact | Rebuild line 514894 CZECHAL4 138 514898 CIMARON4 138 1
Thermal | 00NR | 1 | 26SP | T1 | GEN-2024-362 | TO->FROM | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | B | 444 | 0.068344 | 101.4619 | 272052 | TDF Impact | Rebuild line 514894 CZECHAL4 138 514898 CIMARON4 138 1
Thermal | 00NR | 1 | 26SP | T1 | GEN-2024-362 | TO->FROM | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | B | 444 | 0.068344 | 101.4619 | Single 514887 WESTMOR4 138 514925 PENN4 138 1 | TDF Impact | Rebuild line 514894 CZECHAL4 138 514898 CIMARON4 138 1
Thermal | 00NR | 1 | 29SP | T1 | GEN-2024-362 | TO->FROM | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | B | 444 | 0.063317 | 101.5262 | Single 514853 DVISION4 138 514861 MUSTANG4 138 1 | TDF Impact | Rebuild line 514894 CZECHAL4 138 514898 CIMARON4 138 1
Thermal | 00NR | 1 | 26SP | T1 | GEN-2024-362 | TO->FROM | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | B | 444 | 0.068705 | 101.598 | 272053 | TDF Impact | Rebuild line 514894 CZECHAL4 138 514898 CIMARON4 138 1
Thermal | 00NR | 1 | 29SP | T1 | GEN-2024-362 | TO->FROM | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | B | 444 | 0.063317 | 101.7239 | P12:138:OKGE:BKRBKR1250:::HV: | TDF Impact | Rebuild line 514894 CZECHAL4 138 514898 CIMARON4 138 1
Thermal | 00NR | 1 | 29SP | T1 | GEN-2024-362 | TO->FROM | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | B | 444 | 0.08871 | 101.7426 | P12:138:OKGE:BKRBKR1260:::HV: | TDF Impact | Rebuild line 514894 CZECHAL4 138 514898 CIMARON4 138 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-362 | TO->FROM | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 | B | 1015 | 0.10966 | 102.04 | P42:345:OKGE:SB_DGSE7313:::EHV: | Cumulative Impact | Rebuild line 514715 WOODRNG7 345 515875 REDNGTN7 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-362 | TO->FROM | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | B | 308 | 0.11235 | 102.1233 | Single 514894 CZECHAL4 138 514898 CIMARON4 138 1 | TDF Impact | Rebuild line 514863 HAYMAKR4 138 514898 CIMARON4 138 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-362 | TO->FROM | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 | B | 1015 | 0.11271 | 102.2256 | P42:345:OKGE:SB_DGSE7313:::EHV: | Cumulative Impact | Rebuild line 514715 WOODRNG7 345 515875 REDNGTN7 345 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-362 | TO->FROM | 514893 XEROX 4 138 514894 CZECHAL4 138 1 | B | 382 | 0.10995 | 103.0036 | Single 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | TDF Impact | Rebuild line 514893 XEROX 4 138 514894 CZECHAL4 138 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-362 | TO->FROM | 514893 XEROX 4 138 514894 CZECHAL4 138 1 | B | 382 | 0.076562 | 103.2431 | Single 514853 DVISION4 138 514861 MUSTANG4 138 1 | TDF Impact | Rebuild line 514893 XEROX 4 138 514894 CZECHAL4 138 1
Thermal | 00NR | 1 | 26SP | T1 | GEN-2024-362 | TO->FROM | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | B | 444 | 0.089859 | 103.4096 | Single 514853 DVISION4 138 514863 HAYMAKR4 138 1 | TDF Impact | Rebuild line 514894 CZECHAL4 138 514898 CIMARON4 138 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-362 | TO->FROM | 514893 XEROX 4 138 514894 CZECHAL4 138 1 | B | 382 | 0.076562 | 103.4879 | P12:138:OKGE:BKRBKR1250:::HV: | TDF Impact | Rebuild line 514893 XEROX 4 138 514894 CZECHAL4 138 1
Thermal | 00NR | 1 | 29SP | T1 | GEN-2024-362 | TO->FROM | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | B | 444 | 0.08871 | 103.6301 | Single 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | TDF Impact | Rebuild line 514894 CZECHAL4 138 514898 CIMARON4 138 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-362 | TO->FROM | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | B | 308 | 0.11328 | 104.2764 | Single 514894 CZECHAL4 138 514898 CIMARON4 138 1 | TDF Impact | Rebuild line 514863 HAYMAKR4 138 514898 CIMARON4 138 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-362 | TO->FROM | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | A | 1806 | 0.035969 | 104.7272 | System Intact | TDF Impact | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-362 | TO->FROM | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | A | 1806 | 0.041815 | 104.7927 | System Intact | TDF Impact | Rebuild line 532794 ROSEHIL7 345 560053 G15052_T 345 1
Thermal | 00NR | 1 | 26SP | T1 | GEN-2024-362 | TO->FROM | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | A | 387 | 0.068445 | 104.9545 | System Intact | TDF Impact | Rebuild line 514894 CZECHAL4 138 514898 CIMARON4 138 1
Thermal | 00NR | 1 | 26SP | T1 | GEN-2024-362 | TO->FROM | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | B | 444 | 0.089859 | 105.2555 | P12:138:OKGE:BKRBKR1260:::HV: | TDF Impact | Rebuild line 514894 CZECHAL4 138 514898 CIMARON4 138 1
Thermal | 00NR | 1 | 26SP | T1 | GEN-2024-362 | TO->FROM | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | B | 444 | 0.064055 | 105.7058 | Single 514853 DVISION4 138 514861 MUSTANG4 138 1 | TDF Impact | Rebuild line 514894 CZECHAL4 138 514898 CIMARON4 138 1
Thermal | 00NR | 1 | 26SP | T1 | GEN-2024-362 | TO->FROM | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | B | 444 | 0.064055 | 105.9221 | P12:138:OKGE:BKRBKR1250:::HV: | TDF Impact | Rebuild line 514894 CZECHAL4 138 514898 CIMARON4 138 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-362 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1011 | 0.033829 | 106.9293 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 00NR | 1 | 26SP | T1 | GEN-2024-362 | TO->FROM | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | B | 444 | 0.089859 | 106.9994 | Single 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | TDF Impact | Rebuild line 514894 CZECHAL4 138 514898 CIMARON4 138 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-362 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1011 | 0.030145 | 107.7039 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-362 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1187 | 0.037951 | 112.2151 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-362 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.057995 | 114.4362 | System Intact | TDF Impact | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-362 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.05271 | 114.6025 | System Intact | TDF Impact | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-362 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.032941 | 137.9906 | System Intact | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-370 | TO->FROM | 541199 ST JOE 7 345 541400 EASTOWN7 345 1 | B | 1185 | 0.13308 | 100.396 | Single 541199 STJOE7 345 761383 G17-183-TAP 345 1 | Cumulative Impact | Rebuild line 541199 ST JOE 7 345 541400 EASTOWN7 345 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-370 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.073348 | 101.6955 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-370 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.073348 | 101.6955 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-370 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.073348 | 101.6955 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 26SP | T1 | GEN-2024-370 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.07115 | 105.0133 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 29WP | T1 | GEN-2024-370 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.066616 | 106.2154 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Rebuild line 510380 DELWARE7 345 784170 G24-240-TAP 345 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-370 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.067484 | 106.5956 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-370 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.067484 | 106.5956 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-370 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 956 | 0.067484 | 106.5956 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-370 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.052478 | 106.8199 | Single 640525 TOBIAS3 345 640600 DAYKIN3 345 1 | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-370 | TO->FROM | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | B | 1195 | 0.14622 | 107.005 | Single 541199 STJOE7 345 761383 G17-183-TAP 345 1 | Cumulative Impact | Rebuild line 541400 EASTOWN7 345 542982 IATAN 7 345 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-370 | TO->FROM | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | A | 274 | 0.81421 | 113.443 | System Intact | TDF Impact | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-370 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.075433 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | 536_WERE_NewLine_BuffaloFlats-Deleware_345kV.idv : 2024 ITP upgrade, PID : 94615, NTC, ISD : 12/31/2029
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-370 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.075433 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | AECI_330_Branch_Monett-NBRAN_345kV.idv : 2024 ITP upgrade, PID : 94721, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-370 | TO->FROM | 510380 DELWARE7 345 784170 G24-240-TAP 345 1 | B | 829 | 0.075433 | 114.8446 | P23:345:AECI:7BLACKBERRY:653::: | Cumulative Impact | Branch_Delaware-Monett_345.idv : 2024 ITP upgrade, PID : 94929, NTC, Need Date: 12/1/2025
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-370 | TO->FROM | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | B | 297 | 0.82605 | 116.2822 | Single 301552 5PLATCTY 161 541221 PLTCTY5 161 Z1 | TDF Impact | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-370 | TO->FROM | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | B | 297 | 0.85427 | 117.7121 | Single 541230 RNRIDGE5 161 541318 NCONGRS5 161 1 | TDF Impact | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-370 | TO->FROM | 640277 MOORE 3 345 640590 OLIVECREEK 3 345 1 | B | 956 | 0.084109 | 117.7598 | P55:345:OPPD:S3458 3::FN13:EHV: | Cumulative Impact | Add line and rebuild line 640277 MOORE 3 345 640590 OLIVECREEK 3 345 M2
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-370 | TO->FROM | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | B | 297 | 0.85427 | 117.8533 | P12:161:GMO:TWA-NCONGRESS-ROANRIDGE_1 | TDF Impact | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-370 | TO->FROM | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | B | 297 | 0.85427 | 117.8533 | P12:161:GMO:TWA-NCONGRESS-ROANRID:::HV: | TDF Impact | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-370 | TO->FROM | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | B | 297 | 0.85427 | 117.8665 | Single 541214 TWA5 161 541318 NCONGRS5 161 1 | TDF Impact | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-370 | TO->FROM | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | B | 297 | 0.85427 | 119.9331 | Single 541213 FRLVW5 161 541214 TWA5 161 1 | TDF Impact | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-370 | TO->FROM | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | A | 233 | 0.81451 | 123.2184 | System Intact | TDF Impact | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-370 | TO->FROM | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | B | 261 | 0.82636 | 124.2094 | Single 301552 5PLATCTY 161 541221 PLTCTY5 161 Z1 | TDF Impact | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-370 | TO->FROM | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | B | 261 | 0.82636 | 124.2094 | Single 300307 2PLATCTY 69 301552 5PLATCTY 161 1 | TDF Impact | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-370 | TO->FROM | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | B | 261 | 1 | 124.8942 | Single 541204 SMTHVL5 161 541221 PLTCTY5 161 1 | TDF Impact | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-370 | TO->FROM | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | B | 297 | 0.85427 | 124.9432 | Single 541212 KCI5 161 541213 FRLVW5 161 1 | TDF Impact | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-370 | TO->FROM | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | B | 261 | 0.72879 | 125.6142 | Single 542980 NASHUA7 345 543028 NASHUA-5 161 543640 'NASH T11 ' 13 11 | TDF Impact | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-370 | TO->FROM | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | B | 261 | 0.83317 | 125.903 | Single 541214 TWA5 161 541318 NCONGRS5 161 1 | TDF Impact | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-370 | TO->FROM | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | B | 261 | 0.79575 | 126.3641 | Single 541400 EASTOWN7 345 542982 IATAN7 345 1 | TDF Impact | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-370 | TO->FROM | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | B | 261 | 0.79575 | 126.3694 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1 | TDF Impact | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-370 | TO->FROM | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | B | 261 | 0.79575 | 126.3694 | P23:345:GMO:EASTOWNE-R7-14:::EHV: | TDF Impact | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-370 | TO->FROM | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | A | 233 | 0.79368 | 126.423 | System Intact | TDF Impact | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-370 | TO->FROM | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | B | 297 | 0.85427 | 127.7794 | Single 541212 KCI5 161 541221 PLTCTY5 161 1 | TDF Impact | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-370 | TO->FROM | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | B | 261 | 0.81656 | 128.0574 | Single 541400 EASTOWN7 345 542982 IATAN7 345 1 | TDF Impact | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-370 | TO->FROM | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | B | 261 | 0.81655 | 128.0739 | P23:345:GMO:EASTOWNE_R7-14::EASTOWNE-STJOE-IATAN_1 | TDF Impact | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-370 | TO->FROM | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | B | 261 | 0.81655 | 128.0739 | P23:345:GMO:EASTOWNE-R7-14:::EHV: | TDF Impact | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-370 | TO->FROM | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | B | 261 | 0.8548 | 128.1307 | Single 541212 KCI5 161 541213 FRLVW5 161 1 | TDF Impact | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-370 | TO->FROM | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | B | 261 | 0.83317 | 128.1691 | Single 541213 FRLVW5 161 541214 TWA5 161 1 | TDF Impact | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-370 | TO->FROM | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | B | 297 | 0.79901 | 129.7876 | Single 542980 NASHUA7 345 542982 IATAN7 345 1 | TDF Impact | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-370 | TO->FROM | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | B | 261 | 0.8548 | 131.3808 | Single 541212 KCI5 161 541221 PLTCTY5 161 1 | TDF Impact | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-370 | TO->FROM | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | B | 261 | 0.78284 | 132.6973 | Single 542980 NASHUA7 345 542982 IATAN7 345 1 | TDF Impact | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-370 | TO->FROM | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | B | 261 | 0.79958 | 133.9227 | Single 542980 NASHUA7 345 542982 IATAN7 345 1 | TDF Impact | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-370 | TO->FROM | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | B | 261 | 0.83317 | 134.9833 | Single 541212 KCI5 161 541213 FRLVW5 161 1 | TDF Impact | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-370 | TO->FROM | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | B | 261 | 0.83317 | 138.1474 | Single 541212 KCI5 161 541221 PLTCTY5 161 1 | TDF Impact | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
Thermal | 03ALL | 1 | 29WP | T0 | GEN-2024-370 | TO->FROM | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | B | 297 | 0.79579 | 175.5841 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
Thermal | 03ALL | 1 | 26SP | T0 | GEN-2024-370 | TO->FROM | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | B | 261 | 0.78191 | 182.0098 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
Thermal | 03ALL | 1 | 29SP | T0 | GEN-2024-370 | TO->FROM | 541203 NASHUA 5 161 541204 SMTHVL 5 161 1 | B | 261 | 0.79673 | 196.2546 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | Rebuild line 541203 NASHUA 5 161 541204 SMTHVL 5 161 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-372 | TO->FROM | 652552 SIOUXCY2 230 3WXFMR 652:652: SC2 KU1B 230 1 | B | 750 | 0.052001 | 100.7724 | P23:345:XEL:396 BKR SPK:::EHV: | TDF Impact | Add 3-winding transformer 652305 SIOUXC29 13 652552 SIOUXCY2 230 652564 SIOUXCY3 345 M2
Thermal | 02ALL | 1 | 29SP | T0 | GEN-2024-372 | TO->FROM | 646226 S1226 5 161 646247 S1247 5 161 1 | B | 217 | 1 | 107.6487 | P12:161:OPPD:S1247-S1252:::HV: | TDF Impact | Rebuild line 646226 S1226 5 161 646247 S1247 5 161 1
Thermal | 02ALL | 1 | 26SP | T0 | GEN-2024-372 | TO->FROM | 646226 S1226 5 161 646247 S1247 5 161 1 | B | 217 | 1 | 107.8107 | P12:161:OPPD:S1247-S1252:::HV: | TDF Impact | Rebuild line 646226 S1226 5 161 646247 S1247 5 161 1
Thermal | 02ALL | 1 | 29WP | T0 | GEN-2024-372 | TO->FROM | 646226 S1226 5 161 646247 S1247 5 161 1 | B | 217 | 1 | 109.762 | P12:161:OPPD:S1247-S1252:::HV: | TDF Impact | Rebuild line 646226 S1226 5 161 646247 S1247 5 161 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-373 | TO->FROM | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | B | 1059 | 0.056504 | 100.2166 | P12:345:AEPW:R.S.S.-7:ONETA--7::: | Cumulative Impact | Rebuild line 509745 CLARKSV7 345 515224 MUSKOGE7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-373 | TO->FROM | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | B | 1059 | 0.055375 | 100.8866 | Single 515231 KEEFTON7 345 780360 G24-113-TAP 345 1 | Cumulative Impact | Rebuild line 509745 CLARKSV7 345 515224 MUSKOGE7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-373 | TO->FROM | 505602 S BROWN4 138 769060 G22-104-TAP 138 1 | B | 287 | 1 | 101.9431 | Single 520918 FROGVIL4 138 520948 HUGOPP4 138 1 | TDF Impact | Rebuild line 505602 S BROWN4 138 769060 G22-104-TAP 138 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-373 | TO->FROM | 514715 WOODRNG7 345 515875 REDNGTN7 345 1 | B | 1015 | 0.055683 | 102.2256 | P42:345:OKGE:SB_DGSE7313:::EHV: | Cumulative Impact | Rebuild line 514715 WOODRNG7 345 515875 REDNGTN7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-373 | TO->FROM | 505602 S BROWN4 138 769060 G22-104-TAP 138 1 | B | 287 | 1 | 103.4164 | Single 520918 FROGVIL4 138 773820 G23-092-TAP 138 1 | TDF Impact | Rebuild line 505602 S BROWN4 138 769060 G22-104-TAP 138 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-373 | TO->FROM | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | B | 1059 | 0.055368 | 105.0001 | P42:345:OKGE:SB_FTTH7386:::EHV: | Cumulative Impact | Rebuild line 509745 CLARKSV7 345 515224 MUSKOGE7 345 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-373 | TO->FROM | 509745 CLARKSV7 345 515224 MUSKOGE7 345 1 | B | 1059 | 0.055375 | 105.0075 | Single 515012 RVRVALY7 345 515302 FTSMITH7 345 1 | Cumulative Impact | Rebuild line 509745 CLARKSV7 345 515224 MUSKOGE7 345 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-373 | TO->FROM | 505600 TUPELO 4 138 505602 S BROWN4 138 1 | B | 147 | 0.10566 | 105.0878 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | Rebuild line 505600 TUPELO 4 138 505602 S BROWN4 138 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-373 | TO->FROM | 505600 TUPELO 4 138 505602 S BROWN4 138 1 | B | 147 | 0.28407 | 105.5558 | Single 520918 FROGVIL4 138 520948 HUGOPP4 138 1 | TDF Impact | Rebuild line 505600 TUPELO 4 138 505602 S BROWN4 138 1
Thermal | 04ALL | 1 | 26SP | T0 | GEN-2024-373 | TO->FROM | 505600 TUPELO 4 138 505602 S BROWN4 138 1 | B | 147 | 0.28407 | 106.4089 | Single 520918 FROGVIL4 138 773820 G23-092-TAP 138 1 | TDF Impact | Rebuild line 505600 TUPELO 4 138 505602 S BROWN4 138 1
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-373 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1011 | 0.032905 | 106.9293 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 04ALL | 1 | 29WP | T0 | GEN-2024-373 | TO->FROM | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | A | 1187 | 0.037721 | 112.2151 | System Intact | TDF Impact | Rebuild line 510380 DELWARE7 345 770500 G22-176-TAP 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-373 | TO->FROM | 511467 L.E.S.-4 138 3WXFMR 520:LES 5 345 2 | B | 515 | 0.035707 | 114.4267 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-373 | TO->FROM | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | A | 1075 | 0.034779 | 114.4362 | System Intact | TDF Impact | Rebuild line 532798 VIOLA 7 345 763421 G18-128-TAP 345 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-373 | TO->FROM | 511467 L.E.S.-4 138 3WXFMR 520:LES 5 345 2 | B | 515 | 0.036292 | 114.7092 | P42:345:OKGE:SB_GRNT7313:::EHV: | TDF Impact | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-373 | TO->FROM | 511467 L.E.S.-4 138 3WXFMR 520:LES 5 345 2 | B | 515 | 0.033171 | 115.4941 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | TDF Impact | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-373 | TO->FROM | 511467 L.E.S.-4 138 3WXFMR 520:LES 5 345 2 | B | 515 | 0.033889 | 117.1585 | Single 515800 GRACMNT7 345 780810 G24-128-TAP 345 1 | TDF Impact | Add 3-winding transformer 511411 LES#5-1 13 511467 L.E.S.-4 138 511468 L.E.S.-7 345 M2
Thermal | 04ALL | 1 | 29SP | T0 | GEN-2024-373 | TO->FROM | 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1 | A | 829 | 0.031488 | 137.9906 | System Intact | TDF Impact | Rebuild line 532793 NEOSHO 7 345 784170 G24-240-TAP 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-374 | TO->FROM | 652425 BELFELD4 230 659124 DICKINSN-BE4 230 1 | B | 321 | 0.033897 | 100.0003 | P12:230.0:UMZ:# N-1 #:: LINE BOWMAN__-BE4-HETINGR4-1 :HV: | TDF Impact | Rebuild line 652425 BELFELD4 230 659124 DICKINSN-BE4 230 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-374 | TO->FROM | 653312 MORRILL 7 115 653313 GERING TAP 115 1 | B | 109 | 0.05533 | 103.4411 | Single 640109 CHADRON7 115 640147 CRAWFRD7 115 1 | TDF Impact | 640_NPPD_Rebuild_Morill_Gering_115.idv : 2024 ITP, PID: TBD, ISD: Unknown
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-374 | TO->FROM | 653312 MORRILL 7 115 653313 GERING TAP 115 1 | B | 109 | 0.05533 | 104.008 | P12:115:NPPD:690B:CHADRON7:VICTRYH7 BTB | TDF Impact | 640_NPPD_Rebuild_Morill_Gering_115.idv : 2024 ITP, PID: TBD, ISD: Unknown
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-374 | TO->FROM | 645454 S3454 3 345 650185 WAGENER 3 345 1 | B | 982 | 0.055784 | 104.6262 | P55:345:OPPD:S3740 3::FN13:EHV: | TDF Impact | Rebuild line 645454 S3454 3 345 650185 WAGENER 3 345 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-374 | TO->FROM | 653312 MORRILL 7 115 653313 GERING TAP 115 1 | B | 109 | 0.05533 | 104.7239 | Single 640147 CRAWFRD7 115 640397 VICTRYH7 115 1 | TDF Impact | 640_NPPD_Rebuild_Morill_Gering_115.idv : 2024 ITP, PID: TBD, ISD: Unknown
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-374 | TO->FROM | 640404 WAYSIDE 4 230 652873 STEGALL-LNX3 230 1 | B | 320 | 0.14972 | 106.7867 | Single 659131 LARAMIE_-MB3 345 800120 UNDERWOOD2 345 1 | TDF Impact | Rebuild line 640404 WAYSIDE 4 230 652873 STEGALL-LNX3 230 1
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-374 | TO->FROM | 653570 ALIANCE 7 115 659814 SNAKECK-TS7 115 1 | B | 109 | 0.043854 | 109.3918 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR_:HV: | TDF Impact | 640_NPPD_Rebuild_Morill_Gering_115.idv : 2024 ITP, PID: TBD, ISD: Unknown
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-374 | TO->FROM | 653570 ALIANCE 7 115 659814 SNAKECK-TS7 115 1 | B | 109 | 0.043854 | 109.4021 | P12:230.0:UMZ:# N-1 #:: LINE STEGALL 4-STEGALL-LNX3-Z :HV: | TDF Impact | 640_NPPD_Rebuild_Morill_Gering_115.idv : 2024 ITP, PID: TBD, ISD: Unknown
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-374 | TO->FROM | 653570 ALIANCE 7 115 659814 SNAKECK-TS7 115 1 | B | 109 | 0.043854 | 109.5519 | P12:230.0:UMZ:# N-1 #:: LINE WAYSIDE 4-STEGALL-LNX3-1 :HV: | TDF Impact | 640_NPPD_Rebuild_Morill_Gering_115.idv : 2024 ITP, PID: TBD, ISD: Unknown
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-374 | TO->FROM | 653312 MORRILL 7 115 653313 GERING TAP 115 1 | B | 109 | 0.069673 | 112.9527 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR_:HV: | TDF Impact | 640_NPPD_Rebuild_Morill_Gering_115.idv : 2024 ITP, PID: TBD, ISD: Unknown
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-374 | TO->FROM | 653312 MORRILL 7 115 653313 GERING TAP 115 1 | B | 109 | 0.069673 | 112.9615 | P12:230.0:UMZ:# N-1 #:: LINE STEGALL 4-STEGALL-LNX3-Z :HV: | TDF Impact | 640_NPPD_Rebuild_Morill_Gering_115.idv : 2024 ITP, PID: TBD, ISD: Unknown
Thermal | 00NR | 1 | 26SP | T0 | GEN-2024-374 | TO->FROM | 653312 MORRILL 7 115 653313 GERING TAP 115 1 | B | 109 | 0.069673 | 113.0139 | P12:230.0:UMZ:# N-1 #:: LINE WAYSIDE 4-STEGALL-LNX3-1 :HV: | TDF Impact | 640_NPPD_Rebuild_Morill_Gering_115.idv : 2024 ITP, PID: TBD, ISD: Unknown
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-374 | TO->FROM | 652497 MAURINE4 230 652884 NUNDRWD-LNX3 230 1 | B | 398 | 0.11683 | 114.6315 | Single 800120 UNDERWOOD2 345 800121 MAURINE2 345 1 | TDF Impact | Rebuild line 652497 MAURINE4 230 652884 NUNDRWD-LNX3 230 1
Thermal | 00NR | 1 | 26SP | T1 | GEN-2024-374 | TO->FROM | 653570 ALIANCE 7 115 659814 SNAKECK-TS7 115 1 | B | 109 | 0.048556 | 116.9725 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR_:HV: | TDF Impact | Rebuild line 653570 ALIANCE 7 115 659814 SNAKECK-TS7 115 1
Thermal | 00NR | 1 | 26SP | T1 | GEN-2024-374 | TO->FROM | 653570 ALIANCE 7 115 659814 SNAKECK-TS7 115 1 | B | 109 | 0.048556 | 116.9859 | P12:230.0:UMZ:# N-1 #:: LINE STEGALL 4-STEGALL-LNX3-Z :HV: | TDF Impact | Rebuild line 653570 ALIANCE 7 115 659814 SNAKECK-TS7 115 1
Thermal | 00NR | 1 | 26SP | T1 | GEN-2024-374 | TO->FROM | 653570 ALIANCE 7 115 659814 SNAKECK-TS7 115 1 | B | 109 | 0.048556 | 117.1431 | P12:230.0:UMZ:# N-1 #:: LINE WAYSIDE 4-STEGALL-LNX3-1 :HV: | TDF Impact | Rebuild line 653570 ALIANCE 7 115 659814 SNAKECK-TS7 115 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-374 | TO->FROM | 653312 MORRILL 7 115 653313 GERING TAP 115 1 | B | 109 | 0.068508 | 121.7825 | P14:345:UMZ:# 7216 #:: PROPER TAKE LINE WITH STEGALL LINE REACTOR_:HV: | TDF Impact | 640_NPPD_Rebuild_Morill_Gering_115.idv : 2024 ITP, PID: TBD, ISD: Unknown
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-374 | TO->FROM | 653312 MORRILL 7 115 653313 GERING TAP 115 1 | B | 109 | 0.068508 | 121.7901 | P12:230.0:UMZ:# N-1 #:: LINE STEGALL 4-STEGALL-LNX3-Z :HV: | TDF Impact | 640_NPPD_Rebuild_Morill_Gering_115.idv : 2024 ITP, PID: TBD, ISD: Unknown
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-374 | TO->FROM | 653312 MORRILL 7 115 653313 GERING TAP 115 1 | B | 109 | 0.068508 | 121.822 | P12:230.0:UMZ:# N-1 #:: LINE WAYSIDE 4-STEGALL-LNX3-1 :HV: | TDF Impact | 640_NPPD_Rebuild_Morill_Gering_115.idv : 2024 ITP, PID: TBD, ISD: Unknown
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-374 | TO->FROM | 659339 BOWMAN__-BE4 230 661047 HETINGR4 230 1 | B | 351 | 0.077067 | 124.0351 | Single 652424 BELFELD3 345 800121 MAURINE2 345 1 | TDF Impact | Rebuild line 659339 BOWMAN__-BE4 230 661047 HETINGR4 230 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-374 | TO->FROM | 645454 S3454 3 345 650185 WAGENER 3 345 1 | B | 982 | 0.095412 | 124.4523 | P55:345:OPPD:S3458 3::FN13:EHV: | TDF Impact | Rebuild line 645454 S3454 3 345 650185 WAGENER 3 345 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-376 | TO->FROM | 509691 4BROADUS 138 509692 4ETOIL 138 1 | B | 143 | 0.084302 | 100.4086 | P23:500:EES:HARTBURG:13670::EHV: | TDF Impact | Rebuild line 509691 4BROADUS 138 509692 4ETOIL 138 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-376 | TO->FROM | 509690 4PINELND 138 509691 4BROADUS 138 1 | B | 135 | 0.0854 | 100.6791 | Single 334197 7ROCKYCRK% 345 783930 G24-232-TAP 345 1 | TDF Impact | Rebuild line 509690 4PINELND 138 509691 4BROADUS 138 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-376 | TO->FROM | 509690 4PINELND 138 509691 4BROADUS 138 1 | B | 135 | 0.085391 | 101.13 | P23:345:EES::7ROCKYCRK%:1:EHV: | TDF Impact | Rebuild line 509690 4PINELND 138 509691 4BROADUS 138 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-376 | TO->FROM | 509691 4BROADUS 138 509692 4ETOIL 138 1 | B | 143 | 0.085021 | 103.5289 | Single 509241 CROCKET7 345 783930 G24-232-TAP 345 1 | TDF Impact | Rebuild line 509691 4BROADUS 138 509692 4ETOIL 138 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-376 | TO->FROM | 509691 4BROADUS 138 509692 4ETOIL 138 1 | B | 135 | 0.0854 | 105.5321 | Single 334197 7ROCKYCRK% 345 783930 G24-232-TAP 345 1 | TDF Impact | Rebuild line 509691 4BROADUS 138 509692 4ETOIL 138 1
Thermal | 00NR | 1 | 29SP | T0 | GEN-2024-376 | TO->FROM | 509691 4BROADUS 138 509692 4ETOIL 138 1 | B | 135 | 0.085391 | 105.9999 | P23:345:EES::7ROCKYCRK%:1:EHV: | TDF Impact | Rebuild line 509691 4BROADUS 138 509692 4ETOIL 138 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-376 | TO->FROM | 509690 4PINELND 138 509691 4BROADUS 138 1 | B | 143 | 0.085021 | 108.5463 | Single 334197 7ROCKYCRK% 345 783930 G24-232-TAP 345 1 | TDF Impact | Rebuild line 509690 4PINELND 138 509691 4BROADUS 138 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-376 | TO->FROM | 509690 4PINELND 138 509691 4BROADUS 138 1 | B | 143 | 0.085013 | 108.9938 | P23:345:EES::7ROCKYCRK%:1:EHV: | TDF Impact | Rebuild line 509690 4PINELND 138 509691 4BROADUS 138 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-376 | TO->FROM | 509691 4BROADUS 138 509692 4ETOIL 138 1 | B | 143 | 0.085021 | 115.3951 | Single 334197 7ROCKYCRK% 345 783930 G24-232-TAP 345 1 | TDF Impact | Rebuild line 509691 4BROADUS 138 509692 4ETOIL 138 1
Thermal | 00NR | 1 | 29WP | T0 | GEN-2024-376 | TO->FROM | 509691 4BROADUS 138 509692 4ETOIL 138 1 | B | 143 | 0.085013 | 115.8519 | P23:345:EES::7ROCKYCRK%:1:EHV: | TDF Impact | Rebuild line 509691 4BROADUS 138 509692 4ETOIL 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | TO->FROM | 508557 MARSHL-4 138 508562 PIRKEY 4 138 1 | B | 491 | 0.21397 | 100.1149 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | TDF Impact | Rebuild line 508557 MARSHL-4 138 508562 PIRKEY 4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | TO->FROM | 508557 MARSHL-4 138 508562 PIRKEY 4 138 1 | B | 491 | 0.21392 | 100.1434 | P12:345:AEPW:PIRKEY7:DIANA7::: | TDF Impact | Rebuild line 508557 MARSHL-4 138 508562 PIRKEY 4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | TO->FROM | 508072 NWTXARK7 345 508359 WELSH 7 345 1 | B | 927 | 0.27571 | 100.1454 | P23:345:AEPW:VALLIANT CB 3417A NBTB:::: | TDF Impact | Rebuild line 508072 NWTXARK7 345 508359 WELSH 7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | TO->FROM | 508557 MARSHL-4 138 508562 PIRKEY 4 138 1 | B | 491 | 0.21428 | 100.2536 | P23:345:AEPW:PIRKEY CB 13430 NBTB:::: | TDF Impact | Rebuild line 508557 MARSHL-4 138 508562 PIRKEY 4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | TO->FROM | 514808 JOHNCO 4 138 3WXFMR 524:524:JOHNCOT3 345 3 | B | 478 | 0.05376 | 100.3203 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-377 | TO->FROM | 507760 SW SHV 7 345 508809 LONGWD 7 345 1 | B | 1195 | 0.12497 | 100.4776 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | Cumulative Impact | Rebuild line 507760 SW SHV 7 345 508809 LONGWD 7 345 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-377 | TO->FROM | 507727 FLOURNY4 138 508816 OAKPH 4 138 1 | B | 395 | 0.055003 | 101.2557 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 507727 FLOURNY4 138 508816 OAKPH 4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | TO->FROM | 514809 JOHNCO 7 345 787110 G24-338-TAP 345 1 | B | 1195 | 0.13318 | 101.4771 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | TO->FROM | 508072 NWTXARK7 345 508359 WELSH 7 345 1 | B | 927 | 0.2839 | 101.9725 | P52:345:AEPW:NR3LYDIA 7:::: | TDF Impact | Rebuild line 508072 NWTXARK7 345 508359 WELSH 7 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | TO->FROM | 508072 NWTXARK7 345 508359 WELSH 7 345 1 | B | 927 | 0.2839 | 101.9725 | P23:345:AEPW:WELSH CB 11590 NBTB:::: | TDF Impact | Rebuild line 508072 NWTXARK7 345 508359 WELSH 7 345 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-377 | TO->FROM | 507760 SW SHV 7 345 508809 LONGWD 7 345 1 | B | 1195 | 0.15725 | 102.0621 | P23:345:AEPW:DIANA CB 12000 NBTB:::: | Cumulative Impact | Rebuild line 507760 SW SHV 7 345 508809 LONGWD 7 345 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-377 | TO->FROM | 509083 ROKHILL4 138 509087 TATUM 4 138 1 | A | 241 | 0.075261 | 102.1617 | System Intact | TDF Impact | Rebuild line 509083 ROKHILL4 138 509087 TATUM 4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | TO->FROM | 508072 NWTXARK7 345 508359 WELSH 7 345 1 | B | 927 | 0.27363 | 102.2152 | P23:345:AEPW:VALLIANT CB 3417A NBTB:::: | TDF Impact | Rebuild line 508072 NWTXARK7 345 508359 WELSH 7 345 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-377 | TO->FROM | 507760 SW SHV 7 345 508809 LONGWD 7 345 1 | B | 1195 | 0.16252 | 102.2481 | P12:345:AEPW:SWSHV7:DIANA7::: | Cumulative Impact | Rebuild line 507760 SW SHV 7 345 508809 LONGWD 7 345 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-377 | TO->FROM | 509083 ROKHILL4 138 509087 TATUM 4 138 1 | B | 350 | 0.090489 | 102.3453 | Single 334197 7ROCKYCRK% 345 783930 G24-232-TAP 345 1 | Cumulative Impact | Rebuild line 509083 ROKHILL4 138 509087 TATUM 4 138 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-377 | TO->FROM | 509083 ROKHILL4 138 509087 TATUM 4 138 1 | B | 350 | 0.090489 | 102.4052 | P23:345:EES::7ROCKYCRK%:1:EHV: | Cumulative Impact | Rebuild line 509083 ROKHILL4 138 509087 TATUM 4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | TO->FROM | 508072 NWTXARK7 345 508359 WELSH 7 345 1 | B | 927 | 0.3064 | 102.4055 | Single 508298 LYDIA7 345 779010 G24-068-TAP 345 1 | TDF Impact | Rebuild line 508072 NWTXARK7 345 508359 WELSH 7 345 1
Thermal | 00ALL | 1 | 29WP | T1 | GEN-2024-377 | TO->FROM | 509083 ROKHILL4 138 509087 TATUM 4 138 1 | B | 379 | 0.10795 | 102.9027 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 509083 ROKHILL4 138 509087 TATUM 4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | TO->FROM | 508548 KNOXLEE4 138 509092 EASTON 4 138 1 | B | 547 | 0.1018 | 103.1422 | Single 508575 WHITNEY4 138 508595 HALLSVLS4 138 1 | Cumulative Impact | Rebuild line 508548 KNOXLEE4 138 509092 EASTON 4 138 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-377 | TO->FROM | 509083 ROKHILL4 138 509087 TATUM 4 138 1 | B | 350 | 0.1349 | 103.3121 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | Cumulative Impact | Rebuild line 509083 ROKHILL4 138 509087 TATUM 4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | TO->FROM | 508548 KNOXLEE4 138 509092 EASTON 4 138 1 | B | 547 | 0.1018 | 103.3611 | Single 508562 PIRKEY4 138 775840 G23-193-TAP 138 1 | Cumulative Impact | Rebuild line 508548 KNOXLEE4 138 509092 EASTON 4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | TO->FROM | 514809 JOHNCO 7 345 787110 G24-338-TAP 345 1 | B | 1195 | 0.131 | 103.3869 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | TO->FROM | 508562 PIRKEY 4 138 3WXFMR 520:PIRKEY 1 345 1 | B | 600 | 0.36411 | 103.6673 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | TDF Impact | Add 3-winding transformer 508562 PIRKEY 4 138 508563 PIRKEY 7 345 508587 PIRKY1-1 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | TO->FROM | 508562 PIRKEY 4 138 3WXFMR 520:PIRKEY 1 345 1 | B | 600 | 0.36394 | 103.8062 | P12:345:AEPW:PIRKEY7:DIANA7::: | TDF Impact | Add 3-winding transformer 508562 PIRKEY 4 138 508563 PIRKEY 7 345 508587 PIRKY1-1 13 M2
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | TO->FROM | 508562 PIRKEY 4 138 3WXFMR 520:PIRKEY 1 345 1 | B | 600 | 0.36464 | 103.9699 | P23:345:AEPW:PIRKEY CB 13430 NBTB:::: | TDF Impact | Add 3-winding transformer 508562 PIRKEY 4 138 508563 PIRKEY 7 345 508587 PIRKY1-1 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | TO->FROM | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.2754 | 104.0522 | Single 510907 PITTSB-7 345 787200 GEN-2024-341 345 1 | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | TO->FROM | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.2754 | 104.0523 | GEN-2024-341_POI_510907_Generator_outage | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | TO->FROM | 508548 KNOXLEE4 138 509092 EASTON 4 138 1 | B | 547 | 0.1018 | 104.0775 | Single 508595 HALLSVLS4 138 775840 G23-193-TAP 138 1 | Cumulative Impact | Rebuild line 508548 KNOXLEE4 138 509092 EASTON 4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | TO->FROM | 508072 NWTXARK7 345 508359 WELSH 7 345 1 | B | 927 | 0.2818 | 104.2605 | P23:345:AEPW:WELSH CB 11590 NBTB:::: | TDF Impact | Rebuild line 508072 NWTXARK7 345 508359 WELSH 7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | TO->FROM | 508072 NWTXARK7 345 508359 WELSH 7 345 1 | B | 927 | 0.2818 | 104.2605 | P52:345:AEPW:NR3LYDIA 7:::: | TDF Impact | Rebuild line 508072 NWTXARK7 345 508359 WELSH 7 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | TO->FROM | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.29682 | 104.4762 | P23:345:EES::7ROCKYCRK%:1:EHV: | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-377 | TO->FROM | 507760 SW SHV 7 345 508809 LONGWD 7 345 1 | B | 1195 | 0.14317 | 104.4813 | Single 337376 7SAREPTA% 345 788340 G24-379-TAP 345 1 | Cumulative Impact | Rebuild line 507760 SW SHV 7 345 508809 LONGWD 7 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | TO->FROM | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.29682 | 104.5302 | Single 334197 7ROCKYCRK% 345 783930 G24-232-TAP 345 1 | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-377 | TO->FROM | 514934 DRAPER 7 345 515045 SEMINOL7 345 2 | B | 717 | 0.13361 | 104.675 | P42:345:OKGE:SB_SEOL7385:::EHV: | Cumulative Impact | Rebuild line 514934 DRAPER 7 345 515045 SEMINOL7 345 2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | TO->FROM | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.28954 | 105.0097 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | TO->FROM | 508072 NWTXARK7 345 508359 WELSH 7 345 1 | B | 927 | 0.30435 | 105.1339 | Single 508298 LYDIA7 345 779010 G24-068-TAP 345 1 | TDF Impact | Rebuild line 508072 NWTXARK7 345 508359 WELSH 7 345 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-377 | TO->FROM | 507760 SW SHV 7 345 508809 LONGWD 7 345 1 | B | 1195 | 0.15822 | 105.2021 | P23:345:AEPW:DIANA CB 12000 NBTB:::: | Cumulative Impact | Rebuild line 507760 SW SHV 7 345 508809 LONGWD 7 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | TO->FROM | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.28933 | 105.2545 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-377 | TO->FROM | 508548 KNOXLEE4 138 509092 EASTON 4 138 1 | B | 618 | 0.21028 | 105.3303 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | TDF Impact | Rebuild line 508548 KNOXLEE4 138 509092 EASTON 4 138 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-377 | TO->FROM | 508562 PIRKEY 4 138 3WXFMR 520:PIRKEY 1 345 1 | B | 600 | 0.36551 | 105.3711 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | TDF Impact | Add 3-winding transformer 508562 PIRKEY 4 138 508563 PIRKEY 7 345 508587 PIRKY1-1 13 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-377 | TO->FROM | 507760 SW SHV 7 345 508809 LONGWD 7 345 1 | B | 1195 | 0.16348 | 105.4037 | P12:345:AEPW:SWSHV7:DIANA7::: | Cumulative Impact | Rebuild line 507760 SW SHV 7 345 508809 LONGWD 7 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-377 | TO->FROM | 508562 PIRKEY 4 138 3WXFMR 520:PIRKEY 1 345 1 | B | 600 | 0.36534 | 105.5396 | P12:345:AEPW:PIRKEY7:DIANA7::: | TDF Impact | Add 3-winding transformer 508562 PIRKEY 4 138 508563 PIRKEY 7 345 508587 PIRKY1-1 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-377 | TO->FROM | 508562 PIRKEY 4 138 3WXFMR 520:PIRKEY 1 345 1 | B | 600 | 0.36603 | 105.7103 | P23:345:AEPW:PIRKEY CB 13430 NBTB:::: | TDF Impact | Add 3-winding transformer 508562 PIRKEY 4 138 508563 PIRKEY 7 345 508587 PIRKY1-1 13 M2
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-377 | TO->FROM | 508548 KNOXLEE4 138 509092 EASTON 4 138 1 | B | 618 | 0.20989 | 105.7356 | P12:345:AEPW:PIRKEY7:DIANA7::: | TDF Impact | Rebuild line 508548 KNOXLEE4 138 509092 EASTON 4 138 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-377 | TO->FROM | 509083 ROKHILL4 138 509087 TATUM 4 138 1 | A | 241 | 0.075257 | 105.8216 | System Intact | TDF Impact | Rebuild line 509083 ROKHILL4 138 509087 TATUM 4 138 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-377 | TO->FROM | 508548 KNOXLEE4 138 509092 EASTON 4 138 1 | B | 618 | 0.21037 | 105.8681 | P23:345:AEPW:PIRKEY CB 13430 NBTB:::: | TDF Impact | Rebuild line 508548 KNOXLEE4 138 509092 EASTON 4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | TO->FROM | 508562 PIRKEY 4 138 3WXFMR 520:PIRKEY 1 345 1 | B | 600 | 0.36603 | 106.2268 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | TDF Impact | Add 3-winding transformer 508562 PIRKEY 4 138 508563 PIRKEY 7 345 508587 PIRKY1-1 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | TO->FROM | 508562 PIRKEY 4 138 3WXFMR 520:PIRKEY 1 345 1 | B | 600 | 0.36584 | 106.3398 | P12:345:AEPW:PIRKEY7:DIANA7::: | TDF Impact | Add 3-winding transformer 508562 PIRKEY 4 138 508563 PIRKEY 7 345 508587 PIRKY1-1 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | TO->FROM | 508562 PIRKEY 4 138 3WXFMR 520:PIRKEY 1 345 1 | B | 600 | 0.36653 | 106.4715 | P23:345:AEPW:PIRKEY CB 13430 NBTB:::: | TDF Impact | Add 3-winding transformer 508562 PIRKEY 4 138 508563 PIRKEY 7 345 508587 PIRKY1-1 13 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-377 | TO->FROM | 509083 ROKHILL4 138 509087 TATUM 4 138 1 | B | 350 | 0.13468 | 107.2057 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | Cumulative Impact | Rebuild line 509083 ROKHILL4 138 509087 TATUM 4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | TO->FROM | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.29561 | 107.4655 | Single 509241 CROCKET7 345 783930 G24-232-TAP 345 1 | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | TO->FROM | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.31614 | 108.1752 | Single 337376 7SAREPTA% 345 788340 G24-379-TAP 345 1 | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | TO->FROM | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.29561 | 108.9129 | P23:345:EES::7ROCKYCRK%:1:EHV: | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | TO->FROM | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.29561 | 108.9659 | Single 334197 7ROCKYCRK% 345 783930 G24-232-TAP 345 1 | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-377 | TO->FROM | 514934 DRAPER 7 345 515045 SEMINOL7 345 2 | B | 717 | 0.13544 | 109.0105 | P42:345:OKGE:SB_SEOL7385:::EHV: | Cumulative Impact | Rebuild line 514934 DRAPER 7 345 515045 SEMINOL7 345 2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-377 | TO->FROM | 507760 SW SHV 7 345 508809 LONGWD 7 345 1 | B | 1195 | 0.14464 | 109.0412 | Single 337376 7SAREPTA% 345 788340 G24-379-TAP 345 1 | Cumulative Impact | Rebuild line 507760 SW SHV 7 345 508809 LONGWD 7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | TO->FROM | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.28993 | 109.2053 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | TO->FROM | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.28973 | 109.4344 | P42:500:OKGE:SB_FTTH8585:::EHV: | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | TO->FROM | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.28972 | 109.455 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | TO->FROM | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | A | 905 | 0.2754 | 109.5375 | System Intact | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | TO->FROM | 508567 SCOTTSV4 138 508569 SEMRSHL4 138 1 | B | 272 | 0.16898 | 109.7015 | P12:345:AEPW:PIRKEY7:DIANA7::: | Cumulative Impact | Rebuild line 508567 SCOTTSV4 138 508569 SEMRSHL4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | TO->FROM | 508567 SCOTTSV4 138 508569 SEMRSHL4 138 1 | B | 272 | 0.16926 | 109.8399 | P23:345:AEPW:PIRKEY CB 13430 NBTB:::: | Cumulative Impact | Rebuild line 508567 SCOTTSV4 138 508569 SEMRSHL4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | TO->FROM | 508567 SCOTTSV4 138 508569 SEMRSHL4 138 1 | B | 272 | 0.16789 | 111.3473 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | Cumulative Impact | Rebuild line 508567 SCOTTSV4 138 508569 SEMRSHL4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | TO->FROM | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | A | 905 | 0.27394 | 112.4635 | System Intact | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | TO->FROM | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.31567 | 112.9192 | Single 337376 7SAREPTA% 345 788340 G24-379-TAP 345 1 | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | TO->FROM | 508567 SCOTTSV4 138 508569 SEMRSHL4 138 1 | B | 272 | 0.16812 | 113.4583 | P12:345:AEPW:PIRKEY7:DIANA7::: | Cumulative Impact | Rebuild line 508567 SCOTTSV4 138 508569 SEMRSHL4 138 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-377 | TO->FROM | 509083 ROKHILL4 138 509087 TATUM 4 138 1 | B | 350 | 0.10789 | 113.4766 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 509083 ROKHILL4 138 509087 TATUM 4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | TO->FROM | 508567 SCOTTSV4 138 508569 SEMRSHL4 138 1 | B | 272 | 0.1684 | 113.6165 | P23:345:AEPW:PIRKEY CB 13430 NBTB:::: | Cumulative Impact | Rebuild line 508567 SCOTTSV4 138 508569 SEMRSHL4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | TO->FROM | 508567 SCOTTSV4 138 508569 SEMRSHL4 138 1 | B | 272 | 0.16711 | 115.6232 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | Cumulative Impact | Rebuild line 508567 SCOTTSV4 138 508569 SEMRSHL4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | TO->FROM | 508548 KNOXLEE4 138 509092 EASTON 4 138 1 | B | 547 | 0.20896 | 115.7374 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | TDF Impact | Rebuild line 508548 KNOXLEE4 138 509092 EASTON 4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | TO->FROM | 508548 KNOXLEE4 138 509092 EASTON 4 138 1 | B | 547 | 0.2086 | 116.1006 | P12:345:AEPW:PIRKEY7:DIANA7::: | TDF Impact | Rebuild line 508548 KNOXLEE4 138 509092 EASTON 4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | TO->FROM | 508548 KNOXLEE4 138 509092 EASTON 4 138 1 | B | 547 | 0.20908 | 116.2431 | P23:345:AEPW:PIRKEY CB 13430 NBTB:::: | TDF Impact | Rebuild line 508548 KNOXLEE4 138 509092 EASTON 4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | TO->FROM | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.37095 | 116.5992 | Single 508072 NWTXARK7 345 508359 WELSH7 345 1 | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | TO->FROM | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.37142 | 116.8814 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB:::: | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-377 | TO->FROM | 509083 ROKHILL4 138 509087 TATUM 4 138 1 | B | 350 | 0.10794 | 118.2437 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 509083 ROKHILL4 138 509087 TATUM 4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | TO->FROM | 508548 KNOXLEE4 138 509092 EASTON 4 138 1 | B | 547 | 0.21015 | 119.0778 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | TDF Impact | Rebuild line 508548 KNOXLEE4 138 509092 EASTON 4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | TO->FROM | 508548 KNOXLEE4 138 509092 EASTON 4 138 1 | B | 547 | 0.20975 | 119.3677 | P12:345:AEPW:PIRKEY7:DIANA7::: | TDF Impact | Rebuild line 508548 KNOXLEE4 138 509092 EASTON 4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | TO->FROM | 508548 KNOXLEE4 138 509092 EASTON 4 138 1 | B | 547 | 0.21022 | 119.4926 | P23:345:AEPW:PIRKEY CB 13430 NBTB:::: | TDF Impact | Rebuild line 508548 KNOXLEE4 138 509092 EASTON 4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | TO->FROM | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.36889 | 119.7688 | Single 508072 NWTXARK7 345 508359 WELSH7 345 1 | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | TO->FROM | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.36915 | 120.0073 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB:::: | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-377 | TO->FROM | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.38218 | 122.6891 | P23:345:AEPW:WELSH CB 10610 NBTB:::: | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-377 | TO->FROM | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.38027 | 126.1457 | P23:345:AEPW:WELSH CB 10610 NBTB:::: | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-379 | TO->FROM | 508072 NWTXARK7 345 508359 WELSH 7 345 1 | B | 927 | 0.20245 | 100.1454 | P23:345:AEPW:VALLIANT CB 3417A NBTB:::: | TDF Impact | Rebuild line 508072 NWTXARK7 345 508359 WELSH 7 345 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-379 | TO->FROM | 508808 LONGWD 4 138 3WXFMR 520:LONGWOOD 345 1 | B | 580 | 0.45335 | 100.4222 | P23:345:AEPW:LONGWOOD CB 1N60 NBTB:::: | TDF Impact | Add 3-winding transformer 508808 LONGWD 4 138 508809 LONGWD 7 345 508819 LONGW1-1 13 M2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-379 | TO->FROM | 507760 SW SHV 7 345 508809 LONGWD 7 345 1 | B | 1195 | 0.38004 | 100.4776 | P23:345:AEPW:DIANA CB 11910 NBTB:::: | TDF Impact | Rebuild line 507760 SW SHV 7 345 508809 LONGWD 7 345 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-379 | TO->FROM | 507727 FLOURNY4 138 508816 OAKPH 4 138 1 | B | 395 | 0.095591 | 101.2557 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 507727 FLOURNY4 138 508816 OAKPH 4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-379 | TO->FROM | 514809 JOHNCO 7 345 787110 G24-338-TAP 345 1 | B | 1195 | 0.11066 | 101.4771 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-379 | TO->FROM | 508072 NWTXARK7 345 508359 WELSH 7 345 1 | B | 927 | 0.2094 | 101.9725 | P52:345:AEPW:NR3LYDIA 7:::: | TDF Impact | Rebuild line 508072 NWTXARK7 345 508359 WELSH 7 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-379 | TO->FROM | 508072 NWTXARK7 345 508359 WELSH 7 345 1 | B | 927 | 0.2094 | 101.9725 | P23:345:AEPW:WELSH CB 11590 NBTB:::: | TDF Impact | Rebuild line 508072 NWTXARK7 345 508359 WELSH 7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-379 | TO->FROM | 507727 FLOURNY4 138 508816 OAKPH 4 138 1 | B | 287 | 0.05136 | 102.0609 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 507727 FLOURNY4 138 508816 OAKPH 4 138 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-379 | TO->FROM | 507760 SW SHV 7 345 508809 LONGWD 7 345 1 | B | 1195 | 0.38033 | 102.0621 | P23:345:AEPW:DIANA CB 12000 NBTB:::: | TDF Impact | Rebuild line 507760 SW SHV 7 345 508809 LONGWD 7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-379 | TO->FROM | 508072 NWTXARK7 345 508359 WELSH 7 345 1 | B | 927 | 0.19977 | 102.2152 | P23:345:AEPW:VALLIANT CB 3417A NBTB:::: | Cumulative Impact | Rebuild line 508072 NWTXARK7 345 508359 WELSH 7 345 1
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-379 | TO->FROM | 507760 SW SHV 7 345 508809 LONGWD 7 345 1 | B | 1195 | 0.38072 | 102.2481 | P12:345:AEPW:SWSHV7:DIANA7::: | TDF Impact | Rebuild line 507760 SW SHV 7 345 508809 LONGWD 7 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-379 | TO->FROM | 508072 NWTXARK7 345 508359 WELSH 7 345 1 | B | 927 | 0.22813 | 102.4055 | Single 508298 LYDIA7 345 779010 G24-068-TAP 345 1 | TDF Impact | Rebuild line 508072 NWTXARK7 345 508359 WELSH 7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-379 | TO->FROM | 514809 JOHNCO 7 345 787110 G24-338-TAP 345 1 | B | 1195 | 0.10813 | 103.3869 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-379 | TO->FROM | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.21085 | 104.0522 | Single 510907 PITTSB-7 345 787200 GEN-2024-341 345 1 | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-379 | TO->FROM | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.21085 | 104.0523 | GEN-2024-341_POI_510907_Generator_outage | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-379 | TO->FROM | 508072 NWTXARK7 345 508359 WELSH 7 345 1 | B | 927 | 0.20669 | 104.2605 | P23:345:AEPW:WELSH CB 11590 NBTB:::: | TDF Impact | Rebuild line 508072 NWTXARK7 345 508359 WELSH 7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-379 | TO->FROM | 508072 NWTXARK7 345 508359 WELSH 7 345 1 | B | 927 | 0.20669 | 104.2605 | P52:345:AEPW:NR3LYDIA 7:::: | TDF Impact | Rebuild line 508072 NWTXARK7 345 508359 WELSH 7 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-379 | TO->FROM | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.21579 | 104.4762 | P23:345:EES::7ROCKYCRK%:1:EHV: | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-379 | TO->FROM | 507760 SW SHV 7 345 508809 LONGWD 7 345 1 | B | 1195 | 0.60495 | 104.4813 | Single 337376 7SAREPTA% 345 788340 G24-379-TAP 345 1 | TDF Impact | Rebuild line 507760 SW SHV 7 345 508809 LONGWD 7 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-379 | TO->FROM | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.21579 | 104.5302 | Single 334197 7ROCKYCRK% 345 783930 G24-232-TAP 345 1 | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-379 | TO->FROM | 514934 DRAPER 7 345 515045 SEMINOL7 345 2 | B | 717 | 0.13129 | 104.675 | P42:345:OKGE:SB_SEOL7385:::EHV: | Cumulative Impact | Rebuild line 514934 DRAPER 7 345 515045 SEMINOL7 345 2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-379 | TO->FROM | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.22878 | 105.0097 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T2 | GEN-2024-379 | TO->FROM | 507711 ARSHILL4 138 507749 RAINES 4 138 1 | B | 289 | 0.074021 | 105.0342 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 507711 ARSHILL4 138 507749 RAINES 4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-379 | TO->FROM | 508072 NWTXARK7 345 508359 WELSH 7 345 1 | B | 927 | 0.22536 | 105.1339 | Single 508298 LYDIA7 345 779010 G24-068-TAP 345 1 | TDF Impact | Rebuild line 508072 NWTXARK7 345 508359 WELSH 7 345 1
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-379 | TO->FROM | 507760 SW SHV 7 345 508809 LONGWD 7 345 1 | B | 1195 | 0.38091 | 105.2021 | P23:345:AEPW:DIANA CB 12000 NBTB:::: | TDF Impact | Rebuild line 507760 SW SHV 7 345 508809 LONGWD 7 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-379 | TO->FROM | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.22852 | 105.2545 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-379 | TO->FROM | 507760 SW SHV 7 345 508809 LONGWD 7 345 1 | B | 1195 | 0.38127 | 105.4037 | P12:345:AEPW:SWSHV7:DIANA7::: | TDF Impact | Rebuild line 507760 SW SHV 7 345 508809 LONGWD 7 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-379 | TO->FROM | 507727 FLOURNY4 138 508816 OAKPH 4 138 1 | B | 188 | 0.056818 | 106.5719 | P12:345:AEPW:SWSHV7:LONGWD7::: | Cumulative Impact | Rebuild line 507727 FLOURNY4 138 508816 OAKPH 4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-379 | TO->FROM | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.21362 | 107.4655 | Single 509241 CROCKET7 345 783930 G24-232-TAP 345 1 | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-379 | TO->FROM | 337376 7SAREPTA% 345 788340 G24-379-TAP 345 1 | B | 1195 | 1 | 107.553 | Single 508809 LONGWD7 345 788340 G24-379-TAP 345 1 | TDF Impact | Rebuild line 337376 7SAREPTA% 345 788340 G24-379-TAP 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-379 | TO->FROM | 337376 7SAREPTA% 345 788340 G24-379-TAP 345 1 | B | 1195 | 1 | 107.5536 | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | TDF Impact | Rebuild line 337376 7SAREPTA% 345 788340 G24-379-TAP 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-379 | TO->FROM | 337376 7SAREPTA% 345 788340 G24-379-TAP 345 1 | B | 1195 | 1 | 107.6238 | Single 508809 LONGWD7 345 788340 G24-379-TAP 345 1 | TDF Impact | Rebuild line 337376 7SAREPTA% 345 788340 G24-379-TAP 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-379 | TO->FROM | 337376 7SAREPTA% 345 788340 G24-379-TAP 345 1 | B | 1195 | 1 | 107.6241 | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | TDF Impact | Rebuild line 337376 7SAREPTA% 345 788340 G24-379-TAP 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-379 | TO->FROM | 508809 LONGWD 7 345 788340 G24-379-TAP 345 1 | B | 1195 | 1 | 107.7877 | Single 337376 7SAREPTA% 345 788340 G24-379-TAP 345 1 | TDF Impact | Rebuild line 508809 LONGWD 7 345 788340 G24-379-TAP 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-379 | TO->FROM | 508809 LONGWD 7 345 788340 G24-379-TAP 345 1 | B | 1195 | 1 | 108.098 | Single 337376 7SAREPTA% 345 788340 G24-379-TAP 345 1 | TDF Impact | Rebuild line 508809 LONGWD 7 345 788340 G24-379-TAP 345 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-379 | TO->FROM | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.29912 | 108.1752 | Single 337376 7SAREPTA% 345 788340 G24-379-TAP 345 1 | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-379 | TO->FROM | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.21362 | 108.9129 | P23:345:EES::7ROCKYCRK%:1:EHV: | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-379 | TO->FROM | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.21362 | 108.9659 | Single 334197 7ROCKYCRK% 345 783930 G24-232-TAP 345 1 | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-379 | TO->FROM | 514934 DRAPER 7 345 515045 SEMINOL7 345 2 | B | 717 | 0.13292 | 109.0105 | P42:345:OKGE:SB_SEOL7385:::EHV: | Cumulative Impact | Rebuild line 514934 DRAPER 7 345 515045 SEMINOL7 345 2
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-379 | TO->FROM | 507760 SW SHV 7 345 508809 LONGWD 7 345 1 | B | 1195 | 0.60641 | 109.0412 | Single 337376 7SAREPTA% 345 788340 G24-379-TAP 345 1 | TDF Impact | Rebuild line 507760 SW SHV 7 345 508809 LONGWD 7 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-379 | TO->FROM | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.22889 | 109.2053 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-379 | TO->FROM | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.22864 | 109.4344 | P42:500:OKGE:SB_FTTH8585:::EHV: | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-379 | TO->FROM | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.22862 | 109.455 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-379 | TO->FROM | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | A | 905 | 0.21085 | 109.5375 | System Intact | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-379 | TO->FROM | 337376 7SAREPTA% 345 788340 G24-379-TAP 345 1 | B | 1195 | 1 | 111.4102 | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | TDF Impact | Rebuild line 337376 7SAREPTA% 345 788340 G24-379-TAP 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-379 | TO->FROM | 337376 7SAREPTA% 345 788340 G24-379-TAP 345 1 | B | 1195 | 1 | 111.4105 | Single 508809 LONGWD7 345 788340 G24-379-TAP 345 1 | TDF Impact | Rebuild line 337376 7SAREPTA% 345 788340 G24-379-TAP 345 1
Thermal | 00ALL | 1 | 29WP | T0 | GEN-2024-379 | TO->FROM | 508809 LONGWD 7 345 788340 G24-379-TAP 345 1 | B | 1195 | 1 | 111.4957 | Single 337376 7SAREPTA% 345 788340 G24-379-TAP 345 1 | TDF Impact | Rebuild line 508809 LONGWD 7 345 788340 G24-379-TAP 345 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-379 | TO->FROM | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | A | 905 | 0.20859 | 112.4635 | System Intact | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-379 | TO->FROM | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.29858 | 112.9192 | Single 337376 7SAREPTA% 345 788340 G24-379-TAP 345 1 | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-379 | TO->FROM | 508808 LONGWD 4 138 3WXFMR 520:LONGWOOD 345 1 | B | 580 | 0.269 | 113.9863 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | TDF Impact | Add 3-winding transformer 508808 LONGWD 4 138 508809 LONGWD 7 345 508819 LONGW1-1 13 M2
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-379 | TO->FROM | 508808 LONGWD 4 138 3WXFMR 520:LONGWOOD 345 1 | B | 580 | 0.26982 | 114.6946 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | TDF Impact | Add 3-winding transformer 508808 LONGWD 4 138 508809 LONGWD 7 345 508819 LONGW1-1 13 M2
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-379 | TO->FROM | 507727 FLOURNY4 138 508816 OAKPH 4 138 1 | B | 188 | 0.10377 | 114.866 | P23:345:AEPW:LONGWOOD CB 1N60 NBTB:::: | Cumulative Impact | Rebuild line 507727 FLOURNY4 138 508816 OAKPH 4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-379 | TO->FROM | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.27977 | 116.5992 | Single 508072 NWTXARK7 345 508359 WELSH7 345 1 | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-379 | TO->FROM | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.28018 | 116.8814 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB:::: | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T1 | GEN-2024-379 | TO->FROM | 507774 NORAM 4 138 508808 LONGWD 4 138 1 | B | 265 | 0.066676 | 117.6238 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 507774 NORAM 4 138 508808 LONGWD 4 138 1
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-379 | TO->FROM | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.2767 | 119.7688 | Single 508072 NWTXARK7 345 508359 WELSH7 345 1 | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-379 | TO->FROM | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.27693 | 120.0073 | P23:345:AEPW:NW TEXARKANA CB 16780 NBTB:::: | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | T1 | GEN-2024-379 | TO->FROM | 507774 NORAM 4 138 508808 LONGWD 4 138 1 | B | 265 | 0.066748 | 120.8439 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 507774 NORAM 4 138 508808 LONGWD 4 138 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-379 | TO->FROM | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.23811 | 122.6891 | P23:345:AEPW:WELSH CB 10610 NBTB:::: | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 29SP | T0 | GEN-2024-379 | TO->FROM | 508298 LYDIA 7 345 779010 G24-068-TAP 345 1 | B | 1059 | 0.23506 | 126.1457 | P23:345:AEPW:WELSH CB 10610 NBTB:::: | TDF Impact | 765_Seminole_SWShreveport.idv : 2025 ITP upgrade, PID : 900426, NTC, ISD : 11/18/2030
Thermal | 00ALL | 1 | 26SP | JTIQ - Expanded Scope Analysis | GEN-2024-379 | TO->FROM | 337361 3MINDEN_LA! 115 337363 3SAREPTA! 115 1 | B | 176 | 0.11158 | 126.86 | 508809 LONGWD 7 345 788340 G24-379-TAP 345 1 | TDF Impact | Rebuild the 3MINDEN_LA! to 3SAREPTA! 115kV Line 1
Thermal | 00ALL | 1 | 26SP | JTIQ - Expanded Scope Analysis | GEN-2024-379 | TO->FROM | 337361 3MINDEN_LA! 115 337363 3SAREPTA! 115 1 | B | 176 | 0.11158 | 127.59 | P42:345:AEPW:LONGWOOD CB 10280 NBTB+FAULT:::: | TDF Impact | Rebuild the 3MINDEN_LA! to 3SAREPTA! 115kV Line 1
Thermal | 00ALL | 1 | 26SP | JTIQ - Expanded Scope Analysis | GEN-2024-379 | TO->FROM | 337361 3MINDEN_LA! 115 337363 3SAREPTA! 115 1 | B | 176 | 0.11158 | 127.59 | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | TDF Impact | Rebuild the 3MINDEN_LA! to 3SAREPTA! 115kV Line 1
Thermal | 00ALL | 1 | 29SP | JTIQ - Expanded Scope Analysis | GEN-2024-379 | TO->FROM | 337361 3MINDEN_LA! 115 337363 3SAREPTA! 115 1 | B | 176 | 0.11133 | 127.85 | 508809 LONGWD 7 345 788340 G24-379-TAP 345 1 | TDF Impact | Rebuild the 3MINDEN_LA! to 3SAREPTA! 115kV Line 1
Thermal | 00ALL | 1 | 29WP | JTIQ - Expanded Scope Analysis | GEN-2024-379 | TO->FROM | 337361 3MINDEN_LA! 115 337363 3SAREPTA! 115 1 | B | 176 | 0.11125 | 128.5 | 508809 LONGWD 7 345 788340 G24-379-TAP 345 1 | TDF Impact | Rebuild the 3MINDEN_LA! to 3SAREPTA! 115kV Line 1
Thermal | 00ALL | 1 | 29SP | JTIQ - Expanded Scope Analysis | GEN-2024-379 | TO->FROM | 337361 3MINDEN_LA! 115 337363 3SAREPTA! 115 1 | B | 176 | 0.11132 | 128.66 | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | TDF Impact | Rebuild the 3MINDEN_LA! to 3SAREPTA! 115kV Line 1
Thermal | 00ALL | 1 | 29SP | JTIQ - Expanded Scope Analysis | GEN-2024-379 | TO->FROM | 337361 3MINDEN_LA! 115 337363 3SAREPTA! 115 1 | B | 176 | 0.11132 | 128.66 | P42:345:AEPW:LONGWOOD CB 10280 NBTB+FAULT:::: | TDF Impact | Rebuild the 3MINDEN_LA! to 3SAREPTA! 115kV Line 1
Thermal | 00ALL | 1 | 29WP | JTIQ - Expanded Scope Analysis | GEN-2024-379 | TO->FROM | 337361 3MINDEN_LA! 115 337363 3SAREPTA! 115 1 | B | 176 | 0.11125 | 129.19 | P42:345:AEPW:LONGWOOD CB 10280 NBTB+FAULT:::: | TDF Impact | Rebuild the 3MINDEN_LA! to 3SAREPTA! 115kV Line 1
Thermal | 00ALL | 1 | 29WP | JTIQ - Expanded Scope Analysis | GEN-2024-379 | TO->FROM | 337361 3MINDEN_LA! 115 337363 3SAREPTA! 115 1 | B | 176 | 0.11125 | 129.19 | P23:345:AEPW:LONGWOOD CB 10280 NBTB:::: | TDF Impact | Rebuild the 3MINDEN_LA! to 3SAREPTA! 115kV Line 1
Thermal | 00ALL | 1 | 26SP | T0 | GEN-2024-379 | TO->FROM | 507727 FLOURNY4 138 508816 OAKPH 4 138 1 | B | 188 | 0.050505 | 154.8742 | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | Cumulative Impact | Rebuild line 507727 FLOURNY4 138 508816 OAKPH 4 138 1
Non-Converged | 05ALL | 0 | 29WP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.07978 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Add line 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.20952 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.090972 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.090972 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.090972 |  | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.090972 |  | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.090972 |  | P52:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.090972 |  | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.090972 |  | P52:138:AEPW:NR5O.K.U:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.090294 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.090294 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.090294 |  | P52:138:AEPW:NR5O.K.U:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.090294 |  | P52:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.090972 |  | Single 525839 G17-151TAP 345 762467 G18-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.090294 |  | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.090294 |  | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.090294 |  | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | ASGI-2024-002 |  | Non-Converged |  |  | 0.07978 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.19071 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Add line 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.10666 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.20639 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.2288 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.20639 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.20639 |  | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.20639 |  | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.20639 |  | P52:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.20639 |  | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.2288 |  | Single 523097 HITCHLAND7 345 523961 POTTER_CO7 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.3184 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.20639 |  | P52:138:AEPW:NR5O.K.U:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.20517 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.20517 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.20517 |  | P52:138:AEPW:NR5O.K.U:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.20517 |  | P52:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.20639 |  | Single 525839 G17-151TAP 345 762467 G18-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.20517 |  | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.20517 |  | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.20517 |  | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-015 |  | Non-Converged |  |  | 0.19071 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.21978 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Add line 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.23535 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Add line 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.09101 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.24842 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.20272 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.24842 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.24842 |  | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.24842 |  | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.24842 |  | P52:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.24842 |  | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.20272 |  | Single 523097 HITCHLAND7 345 523961 POTTER_CO7 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.29511 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.24842 |  | P52:138:AEPW:NR5O.K.U:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.24724 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.24724 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.24724 |  | P52:138:AEPW:NR5O.K.U:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.24724 |  | P52:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.24842 |  | Single 525839 G17-151TAP 345 762467 G18-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.10164 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.21978 |  | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.21978 |  | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.21978 |  | Single 525839 G17-151TAP 345 762467 G18-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.10164 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.21978 |  | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.21978 |  | P52:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.10164 |  | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.21978 |  | P52:138:AEPW:NR5O.K.U:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.21978 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.24724 |  | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.24724 |  | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.24724 |  | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-041 |  | Non-Converged |  |  | 0.23535 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.21978 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Add line 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.23535 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Add line 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.09101 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.24842 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.20272 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.24842 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.24842 |  | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.24842 |  | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.24842 |  | P52:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.24842 |  | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.20272 |  | Single 523097 HITCHLAND7 345 523961 POTTER_CO7 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.29511 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.24842 |  | P52:138:AEPW:NR5O.K.U:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.24724 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.24724 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.24724 |  | P52:138:AEPW:NR5O.K.U:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.24724 |  | P52:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.24842 |  | Single 525839 G17-151TAP 345 762467 G18-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.10164 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.21978 |  | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.21978 |  | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.21978 |  | Single 525839 G17-151TAP 345 762467 G18-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.10164 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.21978 |  | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.21978 |  | P52:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.10164 |  | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.21978 |  | P52:138:AEPW:NR5O.K.U:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.21978 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.24724 |  | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.24724 |  | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.24724 |  | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-042 |  | Non-Converged |  |  | 0.23535 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.16063 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Add line 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.17224 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Add line 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.11292 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.18961 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.24967 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.18961 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.18961 |  | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.18961 |  | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.18961 |  | P52:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.18961 |  | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.24967 |  | Single 523097 HITCHLAND7 345 523961 POTTER_CO7 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.42571 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.18961 |  | P52:138:AEPW:NR5O.K.U:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.18809 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.18809 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.18809 |  | P52:138:AEPW:NR5O.K.U:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.18809 |  | P52:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.18961 |  | Single 525839 G17-151TAP 345 762467 G18-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.11471 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.16063 |  | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.16063 |  | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.16063 |  | Single 525839 G17-151TAP 345 762467 G18-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.11471 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.16063 |  | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.16063 |  | P52:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.11471 |  | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.16063 |  | P52:138:AEPW:NR5O.K.U:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.16063 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.18809 |  | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.18809 |  | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.18809 |  | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-043 |  | Non-Converged |  |  | 0.17224 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.032268 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.032268 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.032268 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.032268 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.036159 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.033527 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.036159 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.032268 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.032268 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.032268 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.032268 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.036159 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.033527 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.032345 |  | Single 539805 ELMCREEK7 345 640600 DAYKIN3 345 1 | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.036159 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.030351 |  | Single 515012 RVRVALY7 345 780360 G24-113-TAP 345 1 | TDF Impact | Add line 515012 RVRVALY7 345 780360 G24-113-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.033527 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | DIS2301-1_G03_ERIS_TurnOffReactors_Carpenter_Finney.idv : Switch out Carpenter 25 MVAR line reactor on the Carpenter to Hitchland 345 kV line
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.032268 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.032268 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.032268 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.032268 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.036159 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.033527 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.036159 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.072013 |  | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.030351 |  | Single 515012 RVRVALY7 345 515302 FTSMITH7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.076462 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.030213 |  | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.030351 |  | P42:345:OKGE:SB_FTTH7386:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.035016 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.035016 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-056 |  | Non-Converged |  |  | 0.031 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-067 |  | Non-Converged |  |  | 0.72951 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 00ALL | 0 | 26SP | N0 | GEN-2024-081 |  | Non-Converged |  |  | 0.64256 |  | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 21ITP_Multi - Tande - Finstad - Leland Olds 345 kV.idv : 2021 ITP, PID: 92168, NTC, ISD: 11/30/2026
Non-Converged | 00ALL | 0 | 26SP | N0 | GEN-2024-082 |  | Non-Converged |  |  | 0.64256 |  | Single 659330 SPRNGBRK-BE3 345 779400 G24-081-TAP 345 1 | TDF Impact | 21ITP_Multi - Tande - Finstad - Leland Olds 345 kV.idv : 2021 ITP, PID: 92168, NTC, ISD: 11/30/2026
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.16829 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Add line 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.11508 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.18397 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.2135 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.18397 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.18397 |  | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.18397 |  | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.18397 |  | P52:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.18397 |  | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.2135 |  | Single 523097 HITCHLAND7 345 523961 POTTER_CO7 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.12871 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.18397 |  | P52:138:AEPW:NR5O.K.U:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.1832 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.1832 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.1832 |  | P52:138:AEPW:NR5O.K.U:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.1832 |  | P52:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.18397 |  | Single 525839 G17-151TAP 345 762467 G18-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.1832 |  | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.1832 |  | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.1832 |  | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-099 |  | Non-Converged |  |  | 0.16829 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.15858 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Add line 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.17025 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Add line 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.11373 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.18746 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.2455 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.18746 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.18746 |  | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.18746 |  | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.18746 |  | P52:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.18746 |  | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.2455 |  | Single 523097 HITCHLAND7 345 523961 POTTER_CO7 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.2708 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.18746 |  | P52:138:AEPW:NR5O.K.U:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.18605 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.18605 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.18605 |  | P52:138:AEPW:NR5O.K.U:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.18605 |  | P52:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.18746 |  | Single 525839 G17-151TAP 345 762467 G18-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.11506 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.15858 |  | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.15858 |  | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.15858 |  | Single 525839 G17-151TAP 345 762467 G18-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.11506 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.15858 |  | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.15858 |  | P52:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.11506 |  | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.15858 |  | P52:138:AEPW:NR5O.K.U:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.15858 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.18605 |  | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.18605 |  | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.18605 |  | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-109 |  | Non-Converged |  |  | 0.17025 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.32182 |  | Single 515012 RVRVALY7 345 780360 G24-113-TAP 345 1 | TDF Impact | Add line 515012 RVRVALY7 345 780360 G24-113-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.32182 |  | Single 515012 RVRVALY7 345 515302 FTSMITH7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.32182 |  | P42:345:OKGE:SB_FTTH7386:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-113 |  | Non-Converged |  |  | 0.033874 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.048706 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.037637 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.048706 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.048706 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.048706 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.053129 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.053129 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.048706 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.037637 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.048706 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.048706 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.048706 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.053129 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.053129 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.037637 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | DIS2301-1_G03_ERIS_TurnOffReactors_Carpenter_Finney.idv : Switch out Carpenter 25 MVAR line reactor on the Carpenter to Hitchland 345 kV line
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.048706 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.037637 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.048706 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.048706 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.048706 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.053129 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.053129 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.037637 |  | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.033516 |  | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.031231 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.083258 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.037362 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-117 |  | Non-Converged |  |  | 0.037637 |  | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.035306 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.035306 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.035306 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.035306 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.039754 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.039754 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.035306 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.035306 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.035306 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.035306 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.039754 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.039754 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.036089 |  | Single 515012 RVRVALY7 345 780360 G24-113-TAP 345 1 | TDF Impact | Add line 515012 RVRVALY7 345 780360 G24-113-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.035306 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.035306 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.035306 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.035306 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.039754 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.039754 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.036089 |  | Single 515012 RVRVALY7 345 515302 FTSMITH7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.036089 |  | P42:345:OKGE:SB_FTTH7386:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.055442 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-118 |  | Non-Converged |  |  | 0.033871 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.031271 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.031271 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.031271 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.031271 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.034926 |  | Single 515012 RVRVALY7 345 780360 G24-113-TAP 345 1 | TDF Impact | Add line 515012 RVRVALY7 345 780360 G24-113-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.031271 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.031271 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.054041 |  | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.034926 |  | Single 515012 RVRVALY7 345 515302 FTSMITH7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.04303 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-120 |  | Non-Converged |  |  | 0.034926 |  | P42:345:OKGE:SB_FTTH7386:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.62692 |  | Single 523221 XIT_INTG6 230 523869 CHAN+TASCOS6 230 1 | TDF Impact | 526_SPS_New_Branch_MooreCo_XIT_230kv.idv : 2024 ITP upgrade, PID : 220945, NTC, ISD : 12/15/2028
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.62689 |  | Single 523869 CHAN+TASCOS6 230 523959 POTTER_CO6 230 1 | TDF Impact | 526_SPS_New_Branch_MooreCo_XIT_230kv.idv : 2024 ITP upgrade, PID : 220945, NTC, ISD : 12/15/2028
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.62689 |  | P12:230:SPS:K97:1:CHAN+TASCOS_POTTERCO___:HV: | TDF Impact | 526_SPS_New_Branch_MooreCo_XIT_230kv.idv : 2024 ITP upgrade, PID : 220945, NTC, ISD : 12/15/2028
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.10575 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Add line 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.11882 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Add line 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.14541 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.14016 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.1464 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.14016 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.14016 |  | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.14016 |  | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.14016 |  | P52:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.14016 |  | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.1464 |  | Single 523097 HITCHLAND7 345 523961 POTTER_CO7 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.14016 |  | P52:138:AEPW:NR5O.K.U:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.1332 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.1332 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.1332 |  | P52:138:AEPW:NR5O.K.U:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.1332 |  | P52:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.14016 |  | Single 525839 G17-151TAP 345 762467 G18-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.13568 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.10575 |  | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.10575 |  | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.10575 |  | Single 525839 G17-151TAP 345 762467 G18-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.13568 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.10575 |  | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.10575 |  | P52:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.13568 |  | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.10575 |  | P52:138:AEPW:NR5O.K.U:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.10575 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.1332 |  | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.1332 |  | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.1332 |  | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-143 |  | Non-Converged |  |  | 0.11882 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.62692 |  | Single 523221 XIT_INTG6 230 523869 CHAN+TASCOS6 230 1 | TDF Impact | 526_SPS_New_Branch_MooreCo_XIT_230kv.idv : 2024 ITP upgrade, PID : 220945, NTC, ISD : 12/15/2028
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.62689 |  | Single 523869 CHAN+TASCOS6 230 523959 POTTER_CO6 230 1 | TDF Impact | 526_SPS_New_Branch_MooreCo_XIT_230kv.idv : 2024 ITP upgrade, PID : 220945, NTC, ISD : 12/15/2028
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.62689 |  | P12:230:SPS:K97:1:CHAN+TASCOS_POTTERCO___:HV: | TDF Impact | 526_SPS_New_Branch_MooreCo_XIT_230kv.idv : 2024 ITP upgrade, PID : 220945, NTC, ISD : 12/15/2028
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.10575 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Add line 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.11882 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Add line 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.14541 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.14016 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.1464 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.14016 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.14016 |  | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.14016 |  | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.14016 |  | P52:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.14016 |  | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.1464 |  | Single 523097 HITCHLAND7 345 523961 POTTER_CO7 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.14016 |  | P52:138:AEPW:NR5O.K.U:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.1332 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.1332 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.1332 |  | P52:138:AEPW:NR5O.K.U:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.1332 |  | P52:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.14016 |  | Single 525839 G17-151TAP 345 762467 G18-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.13568 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.10575 |  | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.10575 |  | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.10575 |  | Single 525839 G17-151TAP 345 762467 G18-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.13568 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.10575 |  | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.10575 |  | P52:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.13568 |  | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.10575 |  | P52:138:AEPW:NR5O.K.U:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.10575 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.1332 |  | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.1332 |  | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.1332 |  | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-145 |  | Non-Converged |  |  | 0.11882 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.039733 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.039733 |  | P42:345:NPPD:BKR-MAC-3304:::: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.039733 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.039733 |  | Single 530583 POSTROCK7 345 640527 MACON3 345 1 | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.043922 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.043922 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.044603 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.037747 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.038898 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.044603 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.043922 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.043922 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.039733 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.039733 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.039733 |  | P42:345:NPPD:BKR-MAC-3304:::: | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.039733 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.039733 |  | Single 530583 POSTROCK7 345 640527 MACON3 345 1 | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.043922 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.043922 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.044603 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.037747 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.030094 |  | Single 539805 ELMCREEK7 345 640600 DAYKIN3 345 1 | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.038898 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.044603 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.037747 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | DIS2301-1_G03_ERIS_TurnOffReactors_Carpenter_Finney.idv : Switch out Carpenter 25 MVAR line reactor on the Carpenter to Hitchland 345 kV line
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.039733 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.039733 |  | P42:345:NPPD:BKR-MAC-3304:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.039733 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.039733 |  | Single 530583 POSTROCK7 345 640527 MACON3 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.043922 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.043922 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.044603 |  | Single 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.037747 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.038898 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.044603 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.042401 |  | P23:345:ITCGP:SV_BRK388:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.070387 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.039814 |  | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.039814 |  | Single 531451 MINGO7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.057171 |  | P23:345:SUNC:HLC_BRK282:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.057171 |  | P23:345:SUNC:HLC_BRK188:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.040983 |  | Single 531451 MINGO7 345 767280 G22-015-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.042401 |  | Single 530583 POSTROCK7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.070387 |  | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.039585 |  | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.039814 |  | P23:115-345:SUNC:MO_BRK188:::HV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.070387 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.080437 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.042401 |  | Single 531469 SPERVIL7 345 768480 G22-075-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.039814 |  | P23:345:SUNC:SB_BRK482:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-154 |  | Non-Converged |  |  | 0.039585 |  | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N1 | GEN-2024-154 |  | Non-Converged |  |  | 0.08393 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.17527 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Add line 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.11217 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.19167 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.23288 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.19167 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.19167 |  | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.19167 |  | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.19167 |  | P52:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.19167 |  | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.23288 |  | Single 523097 HITCHLAND7 345 523961 POTTER_CO7 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.24405 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.19167 |  | P52:138:AEPW:NR5O.K.U:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.19047 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.19047 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.19047 |  | P52:138:AEPW:NR5O.K.U:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.19047 |  | P52:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.19167 |  | Single 525839 G17-151TAP 345 762467 G18-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.19047 |  | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.19047 |  | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.19047 |  | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-159 |  | Non-Converged |  |  | 0.17527 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.037849 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.037849 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.037849 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.037849 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.042071 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.042071 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.037849 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.037849 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.037849 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.037849 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.042071 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.042071 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.033426 |  | Single 515012 RVRVALY7 345 780360 G24-113-TAP 345 1 | TDF Impact | Add line 515012 RVRVALY7 345 780360 G24-113-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.037849 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.037849 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.037849 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.037849 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.042071 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.042071 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.033426 |  | Single 515012 RVRVALY7 345 515302 FTSMITH7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.043822 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.033426 |  | P42:345:OKGE:SB_FTTH7386:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.057178 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-171 |  | Non-Converged |  |  | 0.034869 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-204 |  | Non-Converged |  |  | 0.03469 |  | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 03ALL | 0 | 26SP | N0 | GEN-2024-215 |  | Non-Converged |  |  | 0.70176 |  | Single 532773 SUMMIT7 345 539863 CIRRUS7 345 1 | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.030172 |  | Single 515012 RVRVALY7 345 780360 G24-113-TAP 345 1 | TDF Impact | Add line 515012 RVRVALY7 345 780360 G24-113-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.040575 |  | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.030172 |  | Single 515012 RVRVALY7 345 515302 FTSMITH7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.030685 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-219 |  | Non-Converged |  |  | 0.030172 |  | P42:345:OKGE:SB_FTTH7386:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.1634 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Add line 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 P2
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.1752 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Add line 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.1119 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.19236 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.24781 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.19236 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.19236 |  | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.19236 |  | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.19236 |  | P52:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.19236 |  | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.24781 |  | Single 523097 HITCHLAND7 345 523961 POTTER_CO7 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.43686 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.19236 |  | P52:138:AEPW:NR5O.K.U:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.19086 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.19086 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.19086 |  | P52:138:AEPW:NR5O.K.U:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.19086 |  | P52:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.19236 |  | Single 525839 G17-151TAP 345 762467 G18-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.1141 |  | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.1634 |  | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.1634 |  | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.1634 |  | Single 525839 G17-151TAP 345 762467 G18-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.1141 |  | P42:345:SPS:CARPENTER-OR335:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.1634 |  | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.1634 |  | P52:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.1141 |  | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.1634 |  | P52:138:AEPW:NR5O.K.U:::: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29L | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.1634 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.19086 |  | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.19086 |  | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.19086 |  | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-221 |  | Non-Converged |  |  | 0.1752 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.034758 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.034758 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.034758 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.034758 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.038725 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.038725 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.034758 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.034758 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.034758 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.034758 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.038725 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.03078 |  | Single 539805 ELMCREEK7 345 640600 DAYKIN3 345 1 | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.038725 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.033638 |  | Single 515012 RVRVALY7 345 780360 G24-113-TAP 345 1 | TDF Impact | Add line 515012 RVRVALY7 345 780360 G24-113-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.034758 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.034758 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.034758 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.034758 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.038725 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.038725 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.049121 |  | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.033638 |  | Single 515012 RVRVALY7 345 515302 FTSMITH7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.11204 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.030295 |  | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.033638 |  | P42:345:OKGE:SB_FTTH7386:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.044493 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.031202 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.038399 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-235 |  | Non-Converged |  |  | 0.032058 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.068941 |  | Single 515012 RVRVALY7 345 780360 G24-113-TAP 345 1 | TDF Impact | Add line 515012 RVRVALY7 345 780360 G24-113-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.037205 |  | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.068941 |  | Single 515012 RVRVALY7 345 515302 FTSMITH7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.031511 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.068941 |  | P42:345:OKGE:SB_FTTH7386:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-236 |  | Non-Converged |  |  | 0.032009 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.030134 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.030134 |  | P42:345:NPPD:BKR-MAC-3304:::: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.030134 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.030134 |  | Single 530583 POSTROCK7 345 640527 MACON3 345 1 | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.030534 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.030534 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.030134 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.030134 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.030134 |  | P42:345:NPPD:BKR-MAC-3304:::: | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.030134 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.030134 |  | Single 530583 POSTROCK7 345 640527 MACON3 345 1 | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.030534 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.030534 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.031869 |  | Single 515012 RVRVALY7 345 780360 G24-113-TAP 345 1 | TDF Impact | Add line 515012 RVRVALY7 345 780360 G24-113-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.030134 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.030134 |  | P42:345:NPPD:BKR-MAC-3304:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.030134 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.030134 |  | Single 530583 POSTROCK7 345 640527 MACON3 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.030534 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.030534 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.061289 |  | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.031869 |  | Single 515012 RVRVALY7 345 515302 FTSMITH7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.041156 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.031869 |  | P42:345:OKGE:SB_FTTH7386:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.031341 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.031341 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-239 |  | Non-Converged |  |  | 0.038523 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N1 | GEN-2024-239 |  | Non-Converged |  |  | 0.037751 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.063308 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.050057 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.063308 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.063308 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.063308 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.068005 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.068005 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.063308 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.050057 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.063308 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.063308 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.063308 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.068005 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.068005 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.050057 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | DIS2301-1_G03_ERIS_TurnOffReactors_Carpenter_Finney.idv : Switch out Carpenter 25 MVAR line reactor on the Carpenter to Hitchland 345 kV line
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.063308 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.050057 |  | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.063308 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.063308 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.063308 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.068005 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.068005 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.050057 |  | Single 542965 W.GRDNR7 345 542981 LACYGNE7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.034694 |  | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.036286 |  | Single 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.12076 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.043715 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-240 |  | Non-Converged |  |  | 0.050057 |  | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.030134 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.030134 |  | P42:345:NPPD:BKR-MAC-3304:::: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.030134 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.030134 |  | Single 530583 POSTROCK7 345 640527 MACON3 345 1 | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.030534 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.030534 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.030134 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.030134 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.030134 |  | P42:345:NPPD:BKR-MAC-3304:::: | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.030134 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.030134 |  | Single 530583 POSTROCK7 345 640527 MACON3 345 1 | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.030534 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.030534 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.031869 |  | Single 515012 RVRVALY7 345 780360 G24-113-TAP 345 1 | TDF Impact | Add line 515012 RVRVALY7 345 780360 G24-113-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.030134 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.030134 |  | P42:345:NPPD:BKR-MAC-3304:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.030134 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.030134 |  | Single 530583 POSTROCK7 345 640527 MACON3 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.030534 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.030534 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.061289 |  | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.031869 |  | Single 515012 RVRVALY7 345 515302 FTSMITH7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.041156 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.031869 |  | P42:345:OKGE:SB_FTTH7386:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.031341 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.031341 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-252 |  | Non-Converged |  |  | 0.038523 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N1 | GEN-2024-252 |  | Non-Converged |  |  | 0.037751 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.031138 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.031138 |  | P42:345:NPPD:BKR-MAC-3304:::: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.031138 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.031138 |  | Single 530583 POSTROCK7 345 640527 MACON3 345 1 | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.030835 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.032037 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.030835 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.031138 |  | Single 640065 AXTELL3 345 640527 MACON3 345 1 | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.031138 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.031138 |  | P42:345:NPPD:BKR-MAC-3304:::: | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.031138 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.031138 |  | Single 530583 POSTROCK7 345 640527 MACON3 345 1 | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.030835 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.032037 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.030516 |  | Single 539805 ELMCREEK7 345 640600 DAYKIN3 345 1 | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.030835 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.030736 |  | Single 515012 RVRVALY7 345 780360 G24-113-TAP 345 1 | TDF Impact | Add line 515012 RVRVALY7 345 780360 G24-113-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.032037 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | DIS2301-1_G03_ERIS_TurnOffReactors_Carpenter_Finney.idv : Switch out Carpenter 25 MVAR line reactor on the Carpenter to Hitchland 345 kV line
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.031138 |  | P42:345:NPPD:BKR-AXT-3306:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.031138 |  | P42:345:NPPD:BKR-MAC-3304:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.031138 |  | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.031138 |  | Single 530583 POSTROCK7 345 640527 MACON3 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.030835 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.032037 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.030835 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.066919 |  | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.030736 |  | Single 515012 RVRVALY7 345 515302 FTSMITH7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.041222 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.030736 |  | P42:345:OKGE:SB_FTTH7386:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.032621 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.032621 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-254 |  | Non-Converged |  |  | 0.040946 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N1 | GEN-2024-254 |  | Non-Converged |  |  | 0.039725 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.032089 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.030373 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.032089 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.032089 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.030373 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.03043 |  | Single 539805 ELMCREEK7 345 640600 DAYKIN3 345 1 | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.032089 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.031953 |  | Single 515012 RVRVALY7 345 780360 G24-113-TAP 345 1 | TDF Impact | Add line 515012 RVRVALY7 345 780360 G24-113-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.030373 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | DIS2301-1_G03_ERIS_TurnOffReactors_Carpenter_Finney.idv : Switch out Carpenter 25 MVAR line reactor on the Carpenter to Hitchland 345 kV line
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.032089 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.030373 |  | P51:13:WERE:EMPEC 7:EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.032089 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.061669 |  | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.031953 |  | Single 515012 RVRVALY7 345 515302 FTSMITH7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.05868 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.031953 |  | P42:345:OKGE:SB_FTTH7386:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.032041 |  | P23:345:WERE:WICH-345-50:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.032041 |  | P12:345:WERE:RENO-WICH-345:EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-255 |  | Non-Converged |  |  | 0.030703 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.18663 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Add line 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.10805 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.20268 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.23631 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.20268 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.20268 |  | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.20268 |  | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.20268 |  | P52:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.20268 |  | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.23631 |  | Single 523097 HITCHLAND7 345 523961 POTTER_CO7 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.38089 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.20268 |  | P52:138:AEPW:NR5O.K.U:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.20149 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.20149 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.20149 |  | P52:138:AEPW:NR5O.K.U:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.20149 |  | P52:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.20268 |  | Single 525839 G17-151TAP 345 762467 G18-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.20149 |  | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.20149 |  | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.20149 |  | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-261 |  | Non-Converged |  |  | 0.18663 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.18696 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Add line 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.10794 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.20298 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.23581 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.20298 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.20298 |  | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.20298 |  | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.20298 |  | P52:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.20298 |  | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.23581 |  | Single 523097 HITCHLAND7 345 523961 POTTER_CO7 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.37715 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.20298 |  | P52:138:AEPW:NR5O.K.U:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.2018 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.2018 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.2018 |  | P52:138:AEPW:NR5O.K.U:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.2018 |  | P52:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.20298 |  | Single 525839 G17-151TAP 345 762467 G18-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.2018 |  | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.2018 |  | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.2018 |  | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-265 |  | Non-Converged |  |  | 0.18696 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.14178 |  | Single 515012 RVRVALY7 345 780360 G24-113-TAP 345 1 | TDF Impact | Add line 515012 RVRVALY7 345 780360 G24-113-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.14178 |  | Single 515012 RVRVALY7 345 515302 FTSMITH7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.14178 |  | P42:345:OKGE:SB_FTTH7386:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-268 |  | Non-Converged |  |  | 0.039828 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.18397 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Add line 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.10882 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.20062 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.24012 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.20062 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.20062 |  | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.20062 |  | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.20062 |  | P52:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.20062 |  | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.24012 |  | Single 523097 HITCHLAND7 345 523961 POTTER_CO7 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.41239 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.20062 |  | P52:138:AEPW:NR5O.K.U:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.19904 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.19904 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.19904 |  | P52:138:AEPW:NR5O.K.U:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.19904 |  | P52:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.20062 |  | Single 525839 G17-151TAP 345 762467 G18-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.19904 |  | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.19904 |  | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.19904 |  | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-280 |  | Non-Converged |  |  | 0.18397 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.18459 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Add line 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.10865 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.20108 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.23971 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.20108 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.20108 |  | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.20108 |  | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.20108 |  | P52:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.20108 |  | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.23971 |  | Single 523097 HITCHLAND7 345 523961 POTTER_CO7 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.41168 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.20108 |  | P52:138:AEPW:NR5O.K.U:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.19968 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.19968 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.19968 |  | P52:138:AEPW:NR5O.K.U:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.19968 |  | P52:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.20108 |  | Single 525839 G17-151TAP 345 762467 G18-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.19968 |  | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.19968 |  | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.19968 |  | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-281 |  | Non-Converged |  |  | 0.18459 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.036631 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.036631 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.036631 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.036631 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.041192 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.041192 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.036631 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.036631 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.036631 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.036631 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.041192 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.041192 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.036631 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.036631 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.036631 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.036631 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.041192 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.041192 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.057828 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-294 |  | Non-Converged |  |  | 0.037913 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.18583 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Add line 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.10821 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.20226 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.24046 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.20226 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.20226 |  | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.20226 |  | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.20226 |  | P52:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.20226 |  | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.24046 |  | Single 523097 HITCHLAND7 345 523961 POTTER_CO7 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.43477 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.20226 |  | P52:138:AEPW:NR5O.K.U:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.20086 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.20086 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.20086 |  | P52:138:AEPW:NR5O.K.U:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.20086 |  | P52:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.20226 |  | Single 525839 G17-151TAP 345 762467 G18-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.20086 |  | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.20086 |  | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.20086 |  | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-295 |  | Non-Converged |  |  | 0.18583 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.077732 |  | Single 515012 RVRVALY7 345 780360 G24-113-TAP 345 1 | TDF Impact | Add line 515012 RVRVALY7 345 780360 G24-113-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.077732 |  | Single 515012 RVRVALY7 345 515302 FTSMITH7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.077732 |  | P42:345:OKGE:SB_FTTH7386:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-296 |  | Non-Converged |  |  | 0.03389 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.077732 |  | Single 515012 RVRVALY7 345 780360 G24-113-TAP 345 1 | TDF Impact | Add line 515012 RVRVALY7 345 780360 G24-113-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.077732 |  | Single 515012 RVRVALY7 345 515302 FTSMITH7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.077732 |  | P42:345:OKGE:SB_FTTH7386:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-297 |  | Non-Converged |  |  | 0.03389 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.17249 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Add line 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.11282 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.18988 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.25018 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.18988 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.18988 |  | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.18988 |  | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.18988 |  | P52:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.18988 |  | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.25018 |  | Single 523097 HITCHLAND7 345 523961 POTTER_CO7 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.44454 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.18988 |  | P52:138:AEPW:NR5O.K.U:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.18834 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.18834 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.18834 |  | P52:138:AEPW:NR5O.K.U:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.18834 |  | P52:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.18988 |  | Single 525839 G17-151TAP 345 762467 G18-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.18834 |  | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.18834 |  | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.18834 |  | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-303 |  | Non-Converged |  |  | 0.17249 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.17249 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Add line 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.11282 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.18988 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.25018 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.18988 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.18988 |  | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.18988 |  | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.18988 |  | P52:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.18988 |  | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.25018 |  | Single 523097 HITCHLAND7 345 523961 POTTER_CO7 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.44454 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.18988 |  | P52:138:AEPW:NR5O.K.U:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.18834 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.18834 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.18834 |  | P52:138:AEPW:NR5O.K.U:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.18834 |  | P52:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.18988 |  | Single 525839 G17-151TAP 345 762467 G18-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.18834 |  | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.18834 |  | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.18834 |  | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-304 |  | Non-Converged |  |  | 0.17249 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.18114 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Add line 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.10994 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.19762 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.23929 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.19762 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.19762 |  | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.19762 |  | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.19762 |  | P52:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.19762 |  | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.23929 |  | Single 523097 HITCHLAND7 345 523961 POTTER_CO7 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.3765 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.19762 |  | P52:138:AEPW:NR5O.K.U:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.19631 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.19631 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.19631 |  | P52:138:AEPW:NR5O.K.U:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.19631 |  | P52:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.19762 |  | Single 525839 G17-151TAP 345 762467 G18-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.19631 |  | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.19631 |  | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.19631 |  | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-310 |  | Non-Converged |  |  | 0.18114 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.18114 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Add line 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.10994 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.19762 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.23929 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.19762 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.19762 |  | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.19762 |  | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.19762 |  | P52:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.19762 |  | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.23929 |  | Single 523097 HITCHLAND7 345 523961 POTTER_CO7 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.3765 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.19762 |  | P52:138:AEPW:NR5O.K.U:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.19631 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.19631 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.19631 |  | P52:138:AEPW:NR5O.K.U:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.19631 |  | P52:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.19762 |  | Single 525839 G17-151TAP 345 762467 G18-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.19631 |  | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.19631 |  | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.19631 |  | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-311 |  | Non-Converged |  |  | 0.18114 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.49303 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Add line 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.058647 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.50211 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.14378 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.50211 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.50211 |  | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.50211 |  | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.50211 |  | P52:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.50211 |  | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.14378 |  | Single 523097 HITCHLAND7 345 523961 POTTER_CO7 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.19825 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.50211 |  | P52:138:AEPW:NR5O.K.U:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.50123 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.50123 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.50123 |  | P52:138:AEPW:NR5O.K.U:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.50123 |  | P52:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.50123 |  | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.50123 |  | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.50123 |  | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-317 |  | Non-Converged |  |  | 0.49303 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.03653 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.03653 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.03653 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.03653 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.041106 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.041106 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.03653 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.03653 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.03653 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.03653 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.041106 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.041106 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.033939 |  | Single 515012 RVRVALY7 345 780360 G24-113-TAP 345 1 | TDF Impact | Add line 515012 RVRVALY7 345 780360 G24-113-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.03653 |  | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.03653 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.03653 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.03653 |  | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.041106 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.041106 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.033939 |  | Single 515012 RVRVALY7 345 515302 FTSMITH7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.034697 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.033939 |  | P42:345:OKGE:SB_FTTH7386:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.056369 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-318 |  | Non-Converged |  |  | 0.034183 |  | Single 532768 EMPEC7 345 766141 G21-096-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.030797 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.030797 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.030797 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.030797 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.033774 |  | Single 515012 RVRVALY7 345 780360 G24-113-TAP 345 1 | TDF Impact | Add line 515012 RVRVALY7 345 780360 G24-113-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.030797 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.030797 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.056766 |  | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.033774 |  | Single 515012 RVRVALY7 345 515302 FTSMITH7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.042499 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.033774 |  | P42:345:OKGE:SB_FTTH7386:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-333 |  | Non-Converged |  |  | 0.032121 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N1 | GEN-2024-333 |  | Non-Converged |  |  | 0.031468 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.18878 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Add line 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 P2
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.10732 |  | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.20464 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.23324 |  | P42:345:SPS:HITCHLAND-1R15:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.20464 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.20464 |  | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.20464 |  | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.20464 |  | P52:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.20464 |  | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.23324 |  | Single 523097 HITCHLAND7 345 523961 POTTER_CO7 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.35732 |  | Single 523966 POTTER_CO9 765 527669 CROSSROADS9 765 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.20464 |  | P52:138:AEPW:NR5O.K.U:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.20345 |  | Single 511468 L.E.S.-7 345 511607 O.K.U.3-7 345 1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.20345 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.20345 |  | P52:138:AEPW:NR5O.K.U:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.20345 |  | P52:345:AEPW:NR5O.K.U.-7:::: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 05ALL | 0 | 26SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.20464 |  | Single 525839 G17-151TAP 345 762467 G18-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.20345 |  | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.20345 |  | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | TDF Impact | None
Non-Converged | 05ALL | 0 | 29SP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.20345 |  | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | TDF Impact | None
Non-Converged | 05ALL | 0 | 29WP | N0 | GEN-2024-336 |  | Non-Converged |  |  | 0.18878 |  | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-338 |  | Non-Converged |  |  | 0.034486 |  | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.03301 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.03301 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.03301 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.03301 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.044292 |  | Single 515012 RVRVALY7 345 780360 G24-113-TAP 345 1 | TDF Impact | Add line 515012 RVRVALY7 345 780360 G24-113-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.03301 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.03301 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.044059 |  | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.044292 |  | Single 515012 RVRVALY7 345 515302 FTSMITH7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.04157 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.044292 |  | P42:345:OKGE:SB_FTTH7386:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-344 |  | Non-Converged |  |  | 0.035728 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.036034 |  | Single 515012 RVRVALY7 345 780360 G24-113-TAP 345 1 | TDF Impact | Add line 515012 RVRVALY7 345 780360 G24-113-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.044086 |  | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.036034 |  | Single 515012 RVRVALY7 345 515302 FTSMITH7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.034604 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-360 |  | Non-Converged |  |  | 0.036034 |  | P42:345:OKGE:SB_FTTH7386:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.033685 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.033685 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | 640_NPPD_NewBranch_Sidney-Holcom_345.idv : 2024 ITP upgrade, PID : 94811, NTC, ISD: 10/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.033685 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.033685 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | 640_NPPD_TO_0000_Tobias_elmcreek_345_78_updated_rachelcass.idv : 2024ITP, PID: 94911, NTC, ISD: 12/1/2030
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.038259 |  | Single 515012 RVRVALY7 345 780360 G24-113-TAP 345 1 | TDF Impact | Add line 515012 RVRVALY7 345 780360 G24-113-TAP 345 P2
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.033685 |  | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 29SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.033685 |  | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | Line - Woodward - Crawfish Draw 765 kV New Line.idv : 2025 ITP upgrade, PID : 900427, NTC, ISD : 1/1/2032
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.048593 |  | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.038259 |  | Single 515012 RVRVALY7 345 515302 FTSMITH7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.049405 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.038259 |  | P42:345:OKGE:SB_FTTH7386:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-361 |  | Non-Converged |  |  | 0.034788 |  | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.03103 |  | Single 515012 RVRVALY7 345 780360 G24-113-TAP 345 1 | TDF Impact | Add line 515012 RVRVALY7 345 780360 G24-113-TAP 345 P2
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.051862 |  | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.03103 |  | Single 515012 RVRVALY7 345 515302 FTSMITH7 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.035545 |  | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.03103 |  | P42:345:OKGE:SB_FTTH7386:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N0 | GEN-2024-362 |  | Non-Converged |  |  | 0.03904 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None
Non-Converged | 04ALL | 0 | 26SP | N1 | GEN-2024-362 |  | Non-Converged |  |  | 0.039356 |  | P42:345:OKGE:SB_DGSE7313:::EHV: | TDF Impact | None

## All Voltage
SOLUTIONTYPE | Group | Scenario | Season | Mitigation Iteration | Source | MONTCOMMONNAME | BC Voltage | TC Voltage | Voltage Diff | VINIT | VMIN | VMAX | TDF | CONTNAME | Upgrade Name
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-013 | FINNEY 7 | 1.0388 | 1.0633 | 0.024538 |  | 0.9 | 1.05 | 0.033665 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-128 | FINNEY 7 | 1.0388 | 1.0633 | 0.024538 |  | 0.9 | 1.05 | 0.041332 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-252 | FINNEY 7 | 1.0388 | 1.0633 | 0.024538 |  | 0.9 | 1.05 | 0.035152 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-254 | FINNEY 7 | 1.0388 | 1.0633 | 0.024538 |  | 0.9 | 1.05 | 0.035772 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-255 | FINNEY 7 | 1.0388 | 1.0633 | 0.024538 |  | 0.9 | 1.05 | 0.033435 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-321 | FINNEY 7 | 1.0388 | 1.0633 | 0.024538 |  | 0.9 | 1.05 | 0.030541 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-128 | FINNEY 7 | 1.0388 | 1.0632 | 0.024328 |  | 0.9 | 1.05 | 0.041332 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-252 | FINNEY 7 | 1.0388 | 1.0632 | 0.024328 |  | 0.9 | 1.05 | 0.030444 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-254 | FINNEY 7 | 1.0388 | 1.0632 | 0.024328 |  | 0.9 | 1.05 | 0.030464 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-128 | FINNEY 7 | 1.0388 | 1.0632 | 0.024328 |  | 0.9 | 1.05 | 0.041332 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-252 | FINNEY 7 | 1.0388 | 1.0632 | 0.024328 |  | 0.9 | 1.05 | 0.030444 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-254 | FINNEY 7 | 1.0388 | 1.0632 | 0.024328 |  | 0.9 | 1.05 | 0.030464 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-128 | FINNEY 7 | 1.0388 | 1.0632 | 0.024328 |  | 0.9 | 1.05 | 0.041332 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-252 | FINNEY 7 | 1.0388 | 1.0632 | 0.024328 |  | 0.9 | 1.05 | 0.030444 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-254 | FINNEY 7 | 1.0388 | 1.0632 | 0.024328 |  | 0.9 | 1.05 | 0.030464 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 26SP | V | ASGI-2024-020 | FINNEY 7 | 1.0388 | 1.0619 | 0.023081 |  | 0.9 | 1.05 | 0.054809 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-128 | FINNEY 7 | 1.0388 | 1.0619 | 0.023081 |  | 0.9 | 1.05 | 0.041332 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-249 | FINNEY 7 | 1.0388 | 1.0619 | 0.023081 |  | 0.9 | 1.05 | 0.034357 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-252 | FINNEY 7 | 1.0388 | 1.0619 | 0.023081 |  | 0.9 | 1.05 | 0.030444 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-254 | FINNEY 7 | 1.0388 | 1.0619 | 0.023081 |  | 0.9 | 1.05 | 0.030464 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-003 | G17-140-BUS | 1.1368 | 1.2288 | 0.091991 |  | 0.92 | 1.05 | 0.097544 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-013 | G17-140-BUS | 1.1368 | 1.2288 | 0.091991 |  | 0.92 | 1.05 | 0.05832 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-128 | G17-140-BUS | 1.1368 | 1.2288 | 0.091991 |  | 0.92 | 1.05 | 0.052354 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-252 | G17-140-BUS | 1.1368 | 1.2288 | 0.091991 |  | 0.92 | 1.05 | 0.041623 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-254 | G17-140-BUS | 1.1368 | 1.2288 | 0.091991 |  | 0.92 | 1.05 | 0.03629 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-255 | G17-140-BUS | 1.1368 | 1.2288 | 0.091991 |  | 0.92 | 1.05 | 0.031156 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-286 | G17-140-BUS | 1.1368 | 1.2288 | 0.091991 |  | 0.92 | 1.05 | 0.1117 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-293 | G17-140-BUS | 1.1368 | 1.2288 | 0.091991 |  | 0.92 | 1.05 | 0.29297 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-299 | G17-140-BUS | 1.1368 | 1.2288 | 0.091991 |  | 0.92 | 1.05 | 0.17252 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-321 | G17-140-BUS | 1.1368 | 1.2288 | 0.091991 |  | 0.92 | 1.05 | 0.087138 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-323 | G17-140-BUS | 1.1368 | 1.2288 | 0.091991 |  | 0.92 | 1.05 | 0.092447 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-341 | G17-140-BUS | 1.1368 | 1.2288 | 0.091991 |  | 0.92 | 1.05 | 0.11906 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-343 | G17-140-BUS | 1.1368 | 1.2288 | 0.091991 |  | 0.92 | 1.05 | 0.078893 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-377 | G17-140-BUS | 1.1368 | 1.2288 | 0.091991 |  | 0.92 | 1.05 | 0.079045 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-379 | G17-140-BUS | 1.1368 | 1.2288 | 0.091991 |  | 0.92 | 1.05 | 0.074875 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-003 | G17-140-BUS | 1.1367 | 1.227 | 0.090214 |  | 0.92 | 1.05 | 0.097544 | P22:345:EES:MUSKOGE7!:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-013 | G17-140-BUS | 1.1367 | 1.227 | 0.090214 |  | 0.92 | 1.05 | 0.05832 | P22:345:EES:MUSKOGE7!:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-128 | G17-140-BUS | 1.1367 | 1.227 | 0.090214 |  | 0.92 | 1.05 | 0.052354 | P22:345:EES:MUSKOGE7!:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-252 | G17-140-BUS | 1.1367 | 1.227 | 0.090214 |  | 0.92 | 1.05 | 0.041623 | P22:345:EES:MUSKOGE7!:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-254 | G17-140-BUS | 1.1367 | 1.227 | 0.090214 |  | 0.92 | 1.05 | 0.03629 | P22:345:EES:MUSKOGE7!:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-255 | G17-140-BUS | 1.1367 | 1.227 | 0.090214 |  | 0.92 | 1.05 | 0.031156 | P22:345:EES:MUSKOGE7!:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-286 | G17-140-BUS | 1.1367 | 1.227 | 0.090214 |  | 0.92 | 1.05 | 0.1117 | P22:345:EES:MUSKOGE7!:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-293 | G17-140-BUS | 1.1367 | 1.227 | 0.090214 |  | 0.92 | 1.05 | 1 | P22:345:EES:MUSKOGE7!:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-299 | G17-140-BUS | 1.1367 | 1.227 | 0.090214 |  | 0.92 | 1.05 | 0.19239 | P22:345:EES:MUSKOGE7!:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-321 | G17-140-BUS | 1.1367 | 1.227 | 0.090214 |  | 0.92 | 1.05 | 0.090904 | P22:345:EES:MUSKOGE7!:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-323 | G17-140-BUS | 1.1367 | 1.227 | 0.090214 |  | 0.92 | 1.05 | 0.092447 | P22:345:EES:MUSKOGE7!:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-341 | G17-140-BUS | 1.1367 | 1.227 | 0.090214 |  | 0.92 | 1.05 | 0.12421 | P22:345:EES:MUSKOGE7!:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-343 | G17-140-BUS | 1.1367 | 1.227 | 0.090214 |  | 0.92 | 1.05 | 0.078893 | P22:345:EES:MUSKOGE7!:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-377 | G17-140-BUS | 1.1367 | 1.227 | 0.090214 |  | 0.92 | 1.05 | 0.079045 | P22:345:EES:MUSKOGE7!:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-379 | G17-140-BUS | 1.1367 | 1.227 | 0.090214 |  | 0.92 | 1.05 | 0.074875 | P22:345:EES:MUSKOGE7!:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | ASGI-2024-001 | G17-140-BUS | 1.1314 | 1.2165 | 0.085106 |  | 0.92 | 1.05 | 0.043598 | Single 515231 KEEFTON7 345 780360 G24-113-TAP 345 1 | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | ASGI-2024-007 | G17-140-BUS | 1.1314 | 1.2165 | 0.085106 |  | 0.92 | 1.05 | 0.032944 | Single 515231 KEEFTON7 345 780360 G24-113-TAP 345 1 | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | ASGI-2024-008 | G17-140-BUS | 1.1314 | 1.2165 | 0.085106 |  | 0.92 | 1.05 | 0.032944 | Single 515231 KEEFTON7 345 780360 G24-113-TAP 345 1 | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-003 | G17-140-BUS | 1.1314 | 1.2165 | 0.085106 |  | 0.92 | 1.05 | 0.22885 | Single 515231 KEEFTON7 345 780360 G24-113-TAP 345 1 | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-081 | G17-140-BUS | 1.1314 | 1.2165 | 0.085106 |  | 0.92 | 1.05 | 0.039559 | Single 515231 KEEFTON7 345 780360 G24-113-TAP 345 1 | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-082 | G17-140-BUS | 1.1314 | 1.2165 | 0.085106 |  | 0.92 | 1.05 | 0.039559 | Single 515231 KEEFTON7 345 780360 G24-113-TAP 345 1 | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-286 | G17-140-BUS | 1.1314 | 1.2165 | 0.085106 |  | 0.92 | 1.05 | 0.25936 | Single 515231 KEEFTON7 345 780360 G24-113-TAP 345 1 | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-299 | G17-140-BUS | 1.1314 | 1.2165 | 0.085106 |  | 0.92 | 1.05 | 0.50031 | Single 515231 KEEFTON7 345 780360 G24-113-TAP 345 1 | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-343 | G17-140-BUS | 1.1314 | 1.2165 | 0.085106 |  | 0.92 | 1.05 | 0.065399 | Single 515231 KEEFTON7 345 780360 G24-113-TAP 345 1 | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-377 | G17-140-BUS | 1.1314 | 1.2165 | 0.085106 |  | 0.92 | 1.05 | 0.064935 | Single 515231 KEEFTON7 345 780360 G24-113-TAP 345 1 | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-379 | G17-140-BUS | 1.1314 | 1.2165 | 0.085106 |  | 0.92 | 1.05 | 0.087838 | Single 515231 KEEFTON7 345 780360 G24-113-TAP 345 1 | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | ASGI-2024-001 | G17-140-BUS | 1.1311 | 1.2161 | 0.084954 |  | 0.92 | 1.05 | 0.060871 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | ASGI-2024-007 | G17-140-BUS | 1.1311 | 1.2161 | 0.084954 |  | 0.92 | 1.05 | 0.044179 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | ASGI-2024-008 | G17-140-BUS | 1.1311 | 1.2161 | 0.084954 |  | 0.92 | 1.05 | 0.044179 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-017 | G17-140-BUS | 1.1311 | 1.2161 | 0.084954 |  | 0.92 | 1.05 | 0.033327 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-018 | G17-140-BUS | 1.1311 | 1.2161 | 0.084954 |  | 0.92 | 1.05 | 0.032976 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-019 | G17-140-BUS | 1.1311 | 1.2161 | 0.084954 |  | 0.92 | 1.05 | 0.032976 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-020 | G17-140-BUS | 1.1311 | 1.2161 | 0.084954 |  | 0.92 | 1.05 | 0.033327 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-021 | G17-140-BUS | 1.1311 | 1.2161 | 0.084954 |  | 0.92 | 1.05 | 0.033327 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-022 | G17-140-BUS | 1.1311 | 1.2161 | 0.084954 |  | 0.92 | 1.05 | 0.032976 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-023 | G17-140-BUS | 1.1311 | 1.2161 | 0.084954 |  | 0.92 | 1.05 | 0.032976 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-081 | G17-140-BUS | 1.1311 | 1.2161 | 0.084954 |  | 0.92 | 1.05 | 0.055534 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-082 | G17-140-BUS | 1.1311 | 1.2161 | 0.084954 |  | 0.92 | 1.05 | 0.055534 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-211 | G17-140-BUS | 1.1311 | 1.2161 | 0.084954 |  | 0.92 | 1.05 | 0.038004 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-212 | G17-140-BUS | 1.1311 | 1.2161 | 0.084954 |  | 0.92 | 1.05 | 0.038004 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-213 | G17-140-BUS | 1.1311 | 1.2161 | 0.084954 |  | 0.92 | 1.05 | 0.038004 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-343 | G17-140-BUS | 1.1311 | 1.2161 | 0.084954 |  | 0.92 | 1.05 | 0.10045 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-377 | G17-140-BUS | 1.1311 | 1.2161 | 0.084954 |  | 0.92 | 1.05 | 0.099837 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-379 | G17-140-BUS | 1.1311 | 1.2161 | 0.084954 |  | 0.92 | 1.05 | 0.13066 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | ASGI-2024-001 | G17-140-BUS | 1.1312 | 1.2161 | 0.084913 |  | 0.92 | 1.05 | 0.060871 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | ASGI-2024-007 | G17-140-BUS | 1.1312 | 1.2161 | 0.084913 |  | 0.92 | 1.05 | 0.044179 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | ASGI-2024-008 | G17-140-BUS | 1.1312 | 1.2161 | 0.084913 |  | 0.92 | 1.05 | 0.044179 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-003 | G17-140-BUS | 1.1312 | 1.2161 | 0.084913 |  | 0.92 | 1.05 | 0.12886 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-017 | G17-140-BUS | 1.1312 | 1.2161 | 0.084913 |  | 0.92 | 1.05 | 0.033327 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-018 | G17-140-BUS | 1.1312 | 1.2161 | 0.084913 |  | 0.92 | 1.05 | 0.032976 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-019 | G17-140-BUS | 1.1312 | 1.2161 | 0.084913 |  | 0.92 | 1.05 | 0.032976 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-020 | G17-140-BUS | 1.1312 | 1.2161 | 0.084913 |  | 0.92 | 1.05 | 0.033327 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-021 | G17-140-BUS | 1.1312 | 1.2161 | 0.084913 |  | 0.92 | 1.05 | 0.033327 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-022 | G17-140-BUS | 1.1312 | 1.2161 | 0.084913 |  | 0.92 | 1.05 | 0.032976 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-023 | G17-140-BUS | 1.1312 | 1.2161 | 0.084913 |  | 0.92 | 1.05 | 0.032976 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-081 | G17-140-BUS | 1.1312 | 1.2161 | 0.084913 |  | 0.92 | 1.05 | 0.055534 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-082 | G17-140-BUS | 1.1312 | 1.2161 | 0.084913 |  | 0.92 | 1.05 | 0.055534 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-211 | G17-140-BUS | 1.1312 | 1.2161 | 0.084913 |  | 0.92 | 1.05 | 0.038004 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-212 | G17-140-BUS | 1.1312 | 1.2161 | 0.084913 |  | 0.92 | 1.05 | 0.038004 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-213 | G17-140-BUS | 1.1312 | 1.2161 | 0.084913 |  | 0.92 | 1.05 | 0.038004 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-286 | G17-140-BUS | 1.1312 | 1.2161 | 0.084913 |  | 0.92 | 1.05 | 0.14302 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-293 | G17-140-BUS | 1.1312 | 1.2161 | 0.084913 |  | 0.92 | 1.05 | 0.052638 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-299 | G17-140-BUS | 1.1312 | 1.2161 | 0.084913 |  | 0.92 | 1.05 | 0.13907 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-340 | G17-140-BUS | 1.1312 | 1.2161 | 0.084913 |  | 0.92 | 1.05 | 0.031044 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-343 | G17-140-BUS | 1.1312 | 1.2161 | 0.084913 |  | 0.92 | 1.05 | 0.10045 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-377 | G17-140-BUS | 1.1312 | 1.2161 | 0.084913 |  | 0.92 | 1.05 | 0.099837 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-379 | G17-140-BUS | 1.1312 | 1.2161 | 0.084913 |  | 0.92 | 1.05 | 0.13066 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-013 | G23-015-TAP | 1.0374 | 1.0619 | 0.024454 |  | 0.9 | 1.05 | 0.033665 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-128 | G23-015-TAP | 1.0374 | 1.0619 | 0.024454 |  | 0.9 | 1.05 | 0.041332 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-252 | G23-015-TAP | 1.0374 | 1.0619 | 0.024454 |  | 0.9 | 1.05 | 0.035152 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-254 | G23-015-TAP | 1.0374 | 1.0619 | 0.024454 |  | 0.9 | 1.05 | 0.035772 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-255 | G23-015-TAP | 1.0374 | 1.0619 | 0.024454 |  | 0.9 | 1.05 | 0.033435 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-321 | G23-015-TAP | 1.0374 | 1.0619 | 0.024454 |  | 0.9 | 1.05 | 0.030541 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-128 | G23-015-TAP | 1.0375 | 1.0617 | 0.024245 |  | 0.9 | 1.05 | 0.041332 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-252 | G23-015-TAP | 1.0375 | 1.0617 | 0.024245 |  | 0.9 | 1.05 | 0.030444 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-254 | G23-015-TAP | 1.0375 | 1.0617 | 0.024245 |  | 0.9 | 1.05 | 0.030464 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-128 | G23-015-TAP | 1.0375 | 1.0617 | 0.024245 |  | 0.9 | 1.05 | 0.041332 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-252 | G23-015-TAP | 1.0375 | 1.0617 | 0.024245 |  | 0.9 | 1.05 | 0.030444 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-254 | G23-015-TAP | 1.0375 | 1.0617 | 0.024245 |  | 0.9 | 1.05 | 0.030464 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-128 | G23-015-TAP | 1.0375 | 1.0617 | 0.024245 |  | 0.9 | 1.05 | 0.041332 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-252 | G23-015-TAP | 1.0375 | 1.0617 | 0.024245 |  | 0.9 | 1.05 | 0.030444 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-254 | G23-015-TAP | 1.0375 | 1.0617 | 0.024245 |  | 0.9 | 1.05 | 0.030464 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 26SP | V | ASGI-2024-020 | G23-015-TAP | 1.0375 | 1.0605 | 0.023004 |  | 0.9 | 1.05 | 0.054809 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-128 | G23-015-TAP | 1.0375 | 1.0605 | 0.023004 |  | 0.9 | 1.05 | 0.041332 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-249 | G23-015-TAP | 1.0375 | 1.0605 | 0.023004 |  | 0.9 | 1.05 | 0.034357 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-252 | G23-015-TAP | 1.0375 | 1.0605 | 0.023004 |  | 0.9 | 1.05 | 0.030444 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-254 | G23-015-TAP | 1.0375 | 1.0605 | 0.023004 |  | 0.9 | 1.05 | 0.030464 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-003 | GEN-2017-140 | 1.1369 | 1.2288 | 0.091867 |  | 0.92 | 1.05 | 0.097544 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-013 | GEN-2017-140 | 1.1369 | 1.2288 | 0.091867 |  | 0.92 | 1.05 | 0.05832 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-128 | GEN-2017-140 | 1.1369 | 1.2288 | 0.091867 |  | 0.92 | 1.05 | 0.052354 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2017-140 | 1.1369 | 1.2288 | 0.091867 |  | 0.92 | 1.05 | 0.041623 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2017-140 | 1.1369 | 1.2288 | 0.091867 |  | 0.92 | 1.05 | 0.03629 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2017-140 | 1.1369 | 1.2288 | 0.091867 |  | 0.92 | 1.05 | 0.031156 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-286 | GEN-2017-140 | 1.1369 | 1.2288 | 0.091867 |  | 0.92 | 1.05 | 0.1117 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-293 | GEN-2017-140 | 1.1369 | 1.2288 | 0.091867 |  | 0.92 | 1.05 | 0.29297 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-299 | GEN-2017-140 | 1.1369 | 1.2288 | 0.091867 |  | 0.92 | 1.05 | 0.17252 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-321 | GEN-2017-140 | 1.1369 | 1.2288 | 0.091867 |  | 0.92 | 1.05 | 0.087138 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-323 | GEN-2017-140 | 1.1369 | 1.2288 | 0.091867 |  | 0.92 | 1.05 | 0.092447 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-341 | GEN-2017-140 | 1.1369 | 1.2288 | 0.091867 |  | 0.92 | 1.05 | 0.11906 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-343 | GEN-2017-140 | 1.1369 | 1.2288 | 0.091867 |  | 0.92 | 1.05 | 0.078893 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-377 | GEN-2017-140 | 1.1369 | 1.2288 | 0.091867 |  | 0.92 | 1.05 | 0.079045 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-379 | GEN-2017-140 | 1.1369 | 1.2288 | 0.091867 |  | 0.92 | 1.05 | 0.074875 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-003 | GEN-2017-140 | 1.1369 | 1.227 | 0.09009 |  | 0.92 | 1.05 | 0.097544 | P22:345:EES:MUSKOGE7!:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-013 | GEN-2017-140 | 1.1369 | 1.227 | 0.09009 |  | 0.92 | 1.05 | 0.05832 | P22:345:EES:MUSKOGE7!:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-128 | GEN-2017-140 | 1.1369 | 1.227 | 0.09009 |  | 0.92 | 1.05 | 0.052354 | P22:345:EES:MUSKOGE7!:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2017-140 | 1.1369 | 1.227 | 0.09009 |  | 0.92 | 1.05 | 0.041623 | P22:345:EES:MUSKOGE7!:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2017-140 | 1.1369 | 1.227 | 0.09009 |  | 0.92 | 1.05 | 0.03629 | P22:345:EES:MUSKOGE7!:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2017-140 | 1.1369 | 1.227 | 0.09009 |  | 0.92 | 1.05 | 0.031156 | P22:345:EES:MUSKOGE7!:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-286 | GEN-2017-140 | 1.1369 | 1.227 | 0.09009 |  | 0.92 | 1.05 | 0.1117 | P22:345:EES:MUSKOGE7!:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-293 | GEN-2017-140 | 1.1369 | 1.227 | 0.09009 |  | 0.92 | 1.05 | 1 | P22:345:EES:MUSKOGE7!:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-299 | GEN-2017-140 | 1.1369 | 1.227 | 0.09009 |  | 0.92 | 1.05 | 0.19239 | P22:345:EES:MUSKOGE7!:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-321 | GEN-2017-140 | 1.1369 | 1.227 | 0.09009 |  | 0.92 | 1.05 | 0.090904 | P22:345:EES:MUSKOGE7!:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-323 | GEN-2017-140 | 1.1369 | 1.227 | 0.09009 |  | 0.92 | 1.05 | 0.092447 | P22:345:EES:MUSKOGE7!:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-341 | GEN-2017-140 | 1.1369 | 1.227 | 0.09009 |  | 0.92 | 1.05 | 0.12421 | P22:345:EES:MUSKOGE7!:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-343 | GEN-2017-140 | 1.1369 | 1.227 | 0.09009 |  | 0.92 | 1.05 | 0.078893 | P22:345:EES:MUSKOGE7!:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-377 | GEN-2017-140 | 1.1369 | 1.227 | 0.09009 |  | 0.92 | 1.05 | 0.079045 | P22:345:EES:MUSKOGE7!:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-379 | GEN-2017-140 | 1.1369 | 1.227 | 0.09009 |  | 0.92 | 1.05 | 0.074875 | P22:345:EES:MUSKOGE7!:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | ASGI-2024-001 | GEN-2017-140 | 1.1315 | 1.2165 | 0.084981 |  | 0.92 | 1.05 | 0.043598 | Single 515231 KEEFTON7 345 780360 G24-113-TAP 345 1 | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | ASGI-2024-007 | GEN-2017-140 | 1.1315 | 1.2165 | 0.084981 |  | 0.92 | 1.05 | 0.032944 | Single 515231 KEEFTON7 345 780360 G24-113-TAP 345 1 | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | ASGI-2024-008 | GEN-2017-140 | 1.1315 | 1.2165 | 0.084981 |  | 0.92 | 1.05 | 0.032944 | Single 515231 KEEFTON7 345 780360 G24-113-TAP 345 1 | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-003 | GEN-2017-140 | 1.1315 | 1.2165 | 0.084981 |  | 0.92 | 1.05 | 0.22885 | Single 515231 KEEFTON7 345 780360 G24-113-TAP 345 1 | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-081 | GEN-2017-140 | 1.1315 | 1.2165 | 0.084981 |  | 0.92 | 1.05 | 0.039559 | Single 515231 KEEFTON7 345 780360 G24-113-TAP 345 1 | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-082 | GEN-2017-140 | 1.1315 | 1.2165 | 0.084981 |  | 0.92 | 1.05 | 0.039559 | Single 515231 KEEFTON7 345 780360 G24-113-TAP 345 1 | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-286 | GEN-2017-140 | 1.1315 | 1.2165 | 0.084981 |  | 0.92 | 1.05 | 0.25936 | Single 515231 KEEFTON7 345 780360 G24-113-TAP 345 1 | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-299 | GEN-2017-140 | 1.1315 | 1.2165 | 0.084981 |  | 0.92 | 1.05 | 0.50031 | Single 515231 KEEFTON7 345 780360 G24-113-TAP 345 1 | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-343 | GEN-2017-140 | 1.1315 | 1.2165 | 0.084981 |  | 0.92 | 1.05 | 0.065399 | Single 515231 KEEFTON7 345 780360 G24-113-TAP 345 1 | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-377 | GEN-2017-140 | 1.1315 | 1.2165 | 0.084981 |  | 0.92 | 1.05 | 0.064935 | Single 515231 KEEFTON7 345 780360 G24-113-TAP 345 1 | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-379 | GEN-2017-140 | 1.1315 | 1.2165 | 0.084981 |  | 0.92 | 1.05 | 0.087838 | Single 515231 KEEFTON7 345 780360 G24-113-TAP 345 1 | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | ASGI-2024-001 | GEN-2017-140 | 1.1312 | 1.2161 | 0.08483 |  | 0.92 | 1.05 | 0.060871 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | ASGI-2024-007 | GEN-2017-140 | 1.1312 | 1.2161 | 0.08483 |  | 0.92 | 1.05 | 0.044179 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | ASGI-2024-008 | GEN-2017-140 | 1.1312 | 1.2161 | 0.08483 |  | 0.92 | 1.05 | 0.044179 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-017 | GEN-2017-140 | 1.1312 | 1.2161 | 0.08483 |  | 0.92 | 1.05 | 0.033327 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-018 | GEN-2017-140 | 1.1312 | 1.2161 | 0.08483 |  | 0.92 | 1.05 | 0.032976 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-019 | GEN-2017-140 | 1.1312 | 1.2161 | 0.08483 |  | 0.92 | 1.05 | 0.032976 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-020 | GEN-2017-140 | 1.1312 | 1.2161 | 0.08483 |  | 0.92 | 1.05 | 0.033327 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-021 | GEN-2017-140 | 1.1312 | 1.2161 | 0.08483 |  | 0.92 | 1.05 | 0.033327 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-022 | GEN-2017-140 | 1.1312 | 1.2161 | 0.08483 |  | 0.92 | 1.05 | 0.032976 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-023 | GEN-2017-140 | 1.1312 | 1.2161 | 0.08483 |  | 0.92 | 1.05 | 0.032976 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-081 | GEN-2017-140 | 1.1312 | 1.2161 | 0.08483 |  | 0.92 | 1.05 | 0.055534 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-082 | GEN-2017-140 | 1.1312 | 1.2161 | 0.08483 |  | 0.92 | 1.05 | 0.055534 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-211 | GEN-2017-140 | 1.1312 | 1.2161 | 0.08483 |  | 0.92 | 1.05 | 0.038004 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-212 | GEN-2017-140 | 1.1312 | 1.2161 | 0.08483 |  | 0.92 | 1.05 | 0.038004 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-213 | GEN-2017-140 | 1.1312 | 1.2161 | 0.08483 |  | 0.92 | 1.05 | 0.038004 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-343 | GEN-2017-140 | 1.1312 | 1.2161 | 0.08483 |  | 0.92 | 1.05 | 0.10045 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-377 | GEN-2017-140 | 1.1312 | 1.2161 | 0.08483 |  | 0.92 | 1.05 | 0.099837 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-379 | GEN-2017-140 | 1.1312 | 1.2161 | 0.08483 |  | 0.92 | 1.05 | 0.13066 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | ASGI-2024-001 | GEN-2017-140 | 1.1313 | 1.2161 | 0.084788 |  | 0.92 | 1.05 | 0.060871 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | ASGI-2024-007 | GEN-2017-140 | 1.1313 | 1.2161 | 0.084788 |  | 0.92 | 1.05 | 0.044179 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | ASGI-2024-008 | GEN-2017-140 | 1.1313 | 1.2161 | 0.084788 |  | 0.92 | 1.05 | 0.044179 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-003 | GEN-2017-140 | 1.1313 | 1.2161 | 0.084788 |  | 0.92 | 1.05 | 0.12886 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-017 | GEN-2017-140 | 1.1313 | 1.2161 | 0.084788 |  | 0.92 | 1.05 | 0.033327 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-018 | GEN-2017-140 | 1.1313 | 1.2161 | 0.084788 |  | 0.92 | 1.05 | 0.032976 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-019 | GEN-2017-140 | 1.1313 | 1.2161 | 0.084788 |  | 0.92 | 1.05 | 0.032976 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-020 | GEN-2017-140 | 1.1313 | 1.2161 | 0.084788 |  | 0.92 | 1.05 | 0.033327 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-021 | GEN-2017-140 | 1.1313 | 1.2161 | 0.084788 |  | 0.92 | 1.05 | 0.033327 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-022 | GEN-2017-140 | 1.1313 | 1.2161 | 0.084788 |  | 0.92 | 1.05 | 0.032976 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-023 | GEN-2017-140 | 1.1313 | 1.2161 | 0.084788 |  | 0.92 | 1.05 | 0.032976 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-081 | GEN-2017-140 | 1.1313 | 1.2161 | 0.084788 |  | 0.92 | 1.05 | 0.055534 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-082 | GEN-2017-140 | 1.1313 | 1.2161 | 0.084788 |  | 0.92 | 1.05 | 0.055534 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-211 | GEN-2017-140 | 1.1313 | 1.2161 | 0.084788 |  | 0.92 | 1.05 | 0.038004 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-212 | GEN-2017-140 | 1.1313 | 1.2161 | 0.084788 |  | 0.92 | 1.05 | 0.038004 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-213 | GEN-2017-140 | 1.1313 | 1.2161 | 0.084788 |  | 0.92 | 1.05 | 0.038004 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-286 | GEN-2017-140 | 1.1313 | 1.2161 | 0.084788 |  | 0.92 | 1.05 | 0.14302 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-293 | GEN-2017-140 | 1.1313 | 1.2161 | 0.084788 |  | 0.92 | 1.05 | 0.052638 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-299 | GEN-2017-140 | 1.1313 | 1.2161 | 0.084788 |  | 0.92 | 1.05 | 0.13907 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-340 | GEN-2017-140 | 1.1313 | 1.2161 | 0.084788 |  | 0.92 | 1.05 | 0.031044 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-343 | GEN-2017-140 | 1.1313 | 1.2161 | 0.084788 |  | 0.92 | 1.05 | 0.10045 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-377 | GEN-2017-140 | 1.1313 | 1.2161 | 0.084788 |  | 0.92 | 1.05 | 0.099837 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-379 | GEN-2017-140 | 1.1313 | 1.2161 | 0.084788 |  | 0.92 | 1.05 | 0.13066 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-013 | GEN-2023-015 | 1.0374 | 1.0619 | 0.024454 |  | 0.9 | 1.05 | 0.033665 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-128 | GEN-2023-015 | 1.0374 | 1.0619 | 0.024454 |  | 0.9 | 1.05 | 0.041332 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2023-015 | 1.0374 | 1.0619 | 0.024454 |  | 0.9 | 1.05 | 0.035152 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2023-015 | 1.0374 | 1.0619 | 0.024454 |  | 0.9 | 1.05 | 0.035772 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2023-015 | 1.0374 | 1.0619 | 0.024454 |  | 0.9 | 1.05 | 0.033435 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-321 | GEN-2023-015 | 1.0374 | 1.0619 | 0.024454 |  | 0.9 | 1.05 | 0.030541 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-128 | GEN-2023-015 | 1.0375 | 1.0617 | 0.024245 |  | 0.9 | 1.05 | 0.041332 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2023-015 | 1.0375 | 1.0617 | 0.024245 |  | 0.9 | 1.05 | 0.030444 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2023-015 | 1.0375 | 1.0617 | 0.024245 |  | 0.9 | 1.05 | 0.030464 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-128 | GEN-2023-015 | 1.0375 | 1.0617 | 0.024245 |  | 0.9 | 1.05 | 0.041332 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2023-015 | 1.0375 | 1.0617 | 0.024245 |  | 0.9 | 1.05 | 0.030444 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2023-015 | 1.0375 | 1.0617 | 0.024245 |  | 0.9 | 1.05 | 0.030464 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-128 | GEN-2023-015 | 1.0375 | 1.0617 | 0.024245 |  | 0.9 | 1.05 | 0.041332 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2023-015 | 1.0375 | 1.0617 | 0.024245 |  | 0.9 | 1.05 | 0.030444 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2023-015 | 1.0375 | 1.0617 | 0.024245 |  | 0.9 | 1.05 | 0.030464 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 26SP | V | ASGI-2024-020 | GEN-2023-015 | 1.0375 | 1.0605 | 0.023004 |  | 0.9 | 1.05 | 0.054809 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-128 | GEN-2023-015 | 1.0375 | 1.0605 | 0.023004 |  | 0.9 | 1.05 | 0.041332 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-249 | GEN-2023-015 | 1.0375 | 1.0605 | 0.023004 |  | 0.9 | 1.05 | 0.034357 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2023-015 | 1.0375 | 1.0605 | 0.023004 |  | 0.9 | 1.05 | 0.030444 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2023-015 | 1.0375 | 1.0605 | 0.023004 |  | 0.9 | 1.05 | 0.030464 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 00ALL | 2 | 26SP | V | ASGI-2024-007 | MALTABN5 | 0.98001 | 0.89774 | -0.082268 |  | 0.93 | 1.05 | 0.058759 | Single 543059 MALTABN5 161 543064 NORTON5 161 1 | Add 7 MVAR switched shunt at SWAVRLY5 161 kV
Voltage | 00ALL | 2 | 26SP | V | ASGI-2024-008 | MALTABN5 | 0.98001 | 0.89774 | -0.082268 |  | 0.93 | 1.05 | 0.058759 | Single 543059 MALTABN5 161 543064 NORTON5 161 1 | Add 7 MVAR switched shunt at SWAVRLY5 161 kV
Voltage | 00ALL | 2 | 26SP | V | ASGI-2024-007 | SWAVCAP5 | 0.9806 | 0.89836 | -0.082232 |  | 0.93 | 1.05 | 0.058759 | Single 543059 MALTABN5 161 543064 NORTON5 161 1 | Add 7 MVAR switched shunt at SWAVRLY5 161 kV
Voltage | 00ALL | 2 | 26SP | V | ASGI-2024-008 | SWAVCAP5 | 0.9806 | 0.89836 | -0.082232 |  | 0.93 | 1.05 | 0.058759 | Single 543059 MALTABN5 161 543064 NORTON5 161 1 | Add 7 MVAR switched shunt at SWAVRLY5 161 kV
Voltage | 00ALL | 2 | 26SP | V | ASGI-2024-007 | SWAVCAP5 | 0.98878 | 0.91468 | -0.074093 |  | 0.93 | 1.05 | 0.59576 | P12:161:KCPL:NORTREAC-NORT-MALTAB-SWAV:::HV: | None
Voltage | 00ALL | 2 | 26SP | V | ASGI-2024-008 | SWAVCAP5 | 0.98878 | 0.91468 | -0.074093 |  | 0.93 | 1.05 | 0.59576 | P12:161:KCPL:NORTREAC-NORT-MALTAB-SWAV:::HV: | None
Voltage | 00ALL | 2 | 26SP | V | ASGI-2024-007 | SWAVCAP5 | 0.98841 | 0.91446 | -0.073943 |  | 0.93 | 1.05 | 0.058759 | Single 543059 MALTABN5 161 543063 SWAVRLY5 161 1 | None
Voltage | 00ALL | 2 | 26SP | V | ASGI-2024-008 | SWAVCAP5 | 0.98841 | 0.91446 | -0.073943 |  | 0.93 | 1.05 | 0.058759 | Single 543059 MALTABN5 161 543063 SWAVRLY5 161 1 | None
Voltage | 00ALL | 2 | 26SP | V | ASGI-2024-007 | SWAVRLY5 | 0.98038 | 0.89817 | -0.082214 |  | 0.93 | 1.05 | 0.058759 | Single 543059 MALTABN5 161 543064 NORTON5 161 1 | Add 7 MVAR switched shunt at SWAVRLY5 161 kV
Voltage | 00ALL | 2 | 26SP | V | ASGI-2024-008 | SWAVRLY5 | 0.98038 | 0.89817 | -0.082214 |  | 0.93 | 1.05 | 0.058759 | Single 543059 MALTABN5 161 543064 NORTON5 161 1 | Add 7 MVAR switched shunt at SWAVRLY5 161 kV
Voltage | 00ALL | 2 | 26SP | V | ASGI-2024-007 | SWAVRLY5 | 0.98856 | 0.91448 | -0.074077 |  | 0.93 | 1.05 | 0.59576 | P12:161:KCPL:NORTREAC-NORT-MALTAB-SWAV:::HV: | None
Voltage | 00ALL | 2 | 26SP | V | ASGI-2024-008 | SWAVRLY5 | 0.98856 | 0.91448 | -0.074077 |  | 0.93 | 1.05 | 0.59576 | P12:161:KCPL:NORTREAC-NORT-MALTAB-SWAV:::HV: | None
Voltage | 00ALL | 2 | 26SP | V | ASGI-2024-007 | SWAVRLY5 | 0.98819 | 0.91427 | -0.073927 |  | 0.93 | 1.05 | 0.058759 | Single 543059 MALTABN5 161 543063 SWAVRLY5 161 1 | None
Voltage | 00ALL | 2 | 26SP | V | ASGI-2024-008 | SWAVRLY5 | 0.98819 | 0.91427 | -0.073927 |  | 0.93 | 1.05 | 0.058759 | Single 543059 MALTABN5 161 543063 SWAVRLY5 161 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-374 | DH_CS_EA-TS4 | 0.95159 | 0.89411 | -0.057476 |  | 0.9 | 1.05 | 0.16876 | P13:345-230.0:UMZ:# N-1 #:: 3WND STEGALL_-MB3-STEGALL_-MB4-STEGALL_-MB9-1 SGQ KV3A:EHV: | Add 78 MVAR switched shunt at DH_CS_EA-TS4 230 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-374 | DH_CS_EA-TS4 | 0.94785 | 0.89722 | -0.050627 |  | 0.9 | 1.05 | 0.16876 | P12:230.0:UMZ:# N-1 #:: LINE STEGALL 4-STEGALL_-MB4-1 :HV: | Add 78 MVAR switched shunt at DH_CS_EA-TS4 230 kV
Voltage | 00NR | 2 | 26SP | V | ASGI-2024-006 | G17-140-BUS | 1.1373 | 1.2088 | 0.071448 |  | 0.92 | 1.05 | 0.035629 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 26SP | V | ASGI-2024-023 | G17-140-BUS | 1.1373 | 1.2088 | 0.071448 |  | 0.92 | 1.05 | 0.082049 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-013 | G17-140-BUS | 1.1373 | 1.2088 | 0.071448 |  | 0.92 | 1.05 | 0.051307 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-025 | G17-140-BUS | 1.1373 | 1.2088 | 0.071448 |  | 0.92 | 1.05 | 0.085392 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-068 | G17-140-BUS | 1.1373 | 1.2088 | 0.071448 |  | 0.92 | 1.05 | 0.084538 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-071 | G17-140-BUS | 1.1373 | 1.2088 | 0.071448 |  | 0.92 | 1.05 | 0.081836 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-113 | G17-140-BUS | 1.1373 | 1.2088 | 0.071448 |  | 0.92 | 1.05 | 0.2026 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-120 | G17-140-BUS | 1.1373 | 1.2088 | 0.071448 |  | 0.92 | 1.05 | 0.033602 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-122 | G17-140-BUS | 1.1373 | 1.2088 | 0.071448 |  | 0.92 | 1.05 | 0.078463 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-128 | G17-140-BUS | 1.1373 | 1.2088 | 0.071448 |  | 0.92 | 1.05 | 0.044814 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-154 | G17-140-BUS | 1.1373 | 1.2088 | 0.071448 |  | 0.92 | 1.05 | 0.030049 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-177 | G17-140-BUS | 1.1373 | 1.2088 | 0.071448 |  | 0.92 | 1.05 | 0.077734 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-178 | G17-140-BUS | 1.1373 | 1.2088 | 0.071448 |  | 0.92 | 1.05 | 0.079113 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-204 | G17-140-BUS | 1.1373 | 1.2088 | 0.071448 |  | 0.92 | 1.05 | 0.07925 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-219 | G17-140-BUS | 1.1373 | 1.2088 | 0.071448 |  | 0.92 | 1.05 | 0.073562 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-220 | G17-140-BUS | 1.1373 | 1.2088 | 0.071448 |  | 0.92 | 1.05 | 0.081605 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-232 | G17-140-BUS | 1.1373 | 1.2088 | 0.071448 |  | 0.92 | 1.05 | 0.074754 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-236 | G17-140-BUS | 1.1373 | 1.2088 | 0.071448 |  | 0.92 | 1.05 | 0.13963 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-239 | G17-140-BUS | 1.1373 | 1.2088 | 0.071448 |  | 0.92 | 1.05 | 0.03471 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-241 | G17-140-BUS | 1.1373 | 1.2088 | 0.071448 |  | 0.92 | 1.05 | 0.085392 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-252 | G17-140-BUS | 1.1373 | 1.2088 | 0.071448 |  | 0.92 | 1.05 | 0.03471 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-268 | G17-140-BUS | 1.1373 | 1.2088 | 0.071448 |  | 0.92 | 1.05 | 0.26113 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-296 | G17-140-BUS | 1.1373 | 1.2088 | 0.071448 |  | 0.92 | 1.05 | 0.17974 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-297 | G17-140-BUS | 1.1373 | 1.2088 | 0.071448 |  | 0.92 | 1.05 | 0.17974 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-317 | G17-140-BUS | 1.1373 | 1.2088 | 0.071448 |  | 0.92 | 1.05 | 0.038574 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-321 | G17-140-BUS | 1.1373 | 1.2088 | 0.071448 |  | 0.92 | 1.05 | 0.079996 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-333 | G17-140-BUS | 1.1373 | 1.2088 | 0.071448 |  | 0.92 | 1.05 | 0.03652 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-338 | G17-140-BUS | 1.1373 | 1.2088 | 0.071448 |  | 0.92 | 1.05 | 0.092156 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-341 | G17-140-BUS | 1.1373 | 1.2088 | 0.071448 |  | 0.92 | 1.05 | 0.11286 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-343 | G17-140-BUS | 1.1373 | 1.2088 | 0.071448 |  | 0.92 | 1.05 | 0.079049 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-360 | G17-140-BUS | 1.1373 | 1.2088 | 0.071448 |  | 0.92 | 1.05 | 0.067458 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-362 | G17-140-BUS | 1.1373 | 1.2088 | 0.071448 |  | 0.92 | 1.05 | 0.042322 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-373 | G17-140-BUS | 1.1373 | 1.2088 | 0.071448 |  | 0.92 | 1.05 | 0.084702 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-376 | G17-140-BUS | 1.1373 | 1.2088 | 0.071448 |  | 0.92 | 1.05 | 0.072428 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-377 | G17-140-BUS | 1.1373 | 1.2088 | 0.071448 |  | 0.92 | 1.05 | 0.079185 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-379 | G17-140-BUS | 1.1373 | 1.2088 | 0.071448 |  | 0.92 | 1.05 | 0.076189 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 26SP | V | ASGI-2024-006 | G17-140-BUS | 1.1354 | 1.2067 | 0.07134 |  | 0.92 | 1.05 | 0.035629 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 26SP | V | ASGI-2024-023 | G17-140-BUS | 1.1354 | 1.2067 | 0.07134 |  | 0.92 | 1.05 | 0.082049 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-013 | G17-140-BUS | 1.1354 | 1.2067 | 0.07134 |  | 0.92 | 1.05 | 0.051307 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-025 | G17-140-BUS | 1.1354 | 1.2067 | 0.07134 |  | 0.92 | 1.05 | 0.085392 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-068 | G17-140-BUS | 1.1354 | 1.2067 | 0.07134 |  | 0.92 | 1.05 | 0.084538 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-071 | G17-140-BUS | 1.1354 | 1.2067 | 0.07134 |  | 0.92 | 1.05 | 0.081836 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-113 | G17-140-BUS | 1.1354 | 1.2067 | 0.07134 |  | 0.92 | 1.05 | 0.2416 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-120 | G17-140-BUS | 1.1354 | 1.2067 | 0.07134 |  | 0.92 | 1.05 | 0.033602 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-122 | G17-140-BUS | 1.1354 | 1.2067 | 0.07134 |  | 0.92 | 1.05 | 0.078463 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-128 | G17-140-BUS | 1.1354 | 1.2067 | 0.07134 |  | 0.92 | 1.05 | 0.044814 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-154 | G17-140-BUS | 1.1354 | 1.2067 | 0.07134 |  | 0.92 | 1.05 | 0.030049 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-177 | G17-140-BUS | 1.1354 | 1.2067 | 0.07134 |  | 0.92 | 1.05 | 0.077734 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-178 | G17-140-BUS | 1.1354 | 1.2067 | 0.07134 |  | 0.92 | 1.05 | 0.079113 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-204 | G17-140-BUS | 1.1354 | 1.2067 | 0.07134 |  | 0.92 | 1.05 | 0.07925 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-219 | G17-140-BUS | 1.1354 | 1.2067 | 0.07134 |  | 0.92 | 1.05 | 0.073562 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-220 | G17-140-BUS | 1.1354 | 1.2067 | 0.07134 |  | 0.92 | 1.05 | 0.081605 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-232 | G17-140-BUS | 1.1354 | 1.2067 | 0.07134 |  | 0.92 | 1.05 | 0.074754 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-236 | G17-140-BUS | 1.1354 | 1.2067 | 0.07134 |  | 0.92 | 1.05 | 0.1534 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-239 | G17-140-BUS | 1.1354 | 1.2067 | 0.07134 |  | 0.92 | 1.05 | 0.03471 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-241 | G17-140-BUS | 1.1354 | 1.2067 | 0.07134 |  | 0.92 | 1.05 | 0.085392 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-252 | G17-140-BUS | 1.1354 | 1.2067 | 0.07134 |  | 0.92 | 1.05 | 0.03471 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-268 | G17-140-BUS | 1.1354 | 1.2067 | 0.07134 |  | 0.92 | 1.05 | 0.32293 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-296 | G17-140-BUS | 1.1354 | 1.2067 | 0.07134 |  | 0.92 | 1.05 | 0.20337 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-297 | G17-140-BUS | 1.1354 | 1.2067 | 0.07134 |  | 0.92 | 1.05 | 0.20337 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-317 | G17-140-BUS | 1.1354 | 1.2067 | 0.07134 |  | 0.92 | 1.05 | 0.038574 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-321 | G17-140-BUS | 1.1354 | 1.2067 | 0.07134 |  | 0.92 | 1.05 | 0.079996 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-333 | G17-140-BUS | 1.1354 | 1.2067 | 0.07134 |  | 0.92 | 1.05 | 0.03652 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-338 | G17-140-BUS | 1.1354 | 1.2067 | 0.07134 |  | 0.92 | 1.05 | 0.092156 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-341 | G17-140-BUS | 1.1354 | 1.2067 | 0.07134 |  | 0.92 | 1.05 | 0.11501 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-343 | G17-140-BUS | 1.1354 | 1.2067 | 0.07134 |  | 0.92 | 1.05 | 0.079049 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-360 | G17-140-BUS | 1.1354 | 1.2067 | 0.07134 |  | 0.92 | 1.05 | 0.067458 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-362 | G17-140-BUS | 1.1354 | 1.2067 | 0.07134 |  | 0.92 | 1.05 | 0.042322 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-373 | G17-140-BUS | 1.1354 | 1.2067 | 0.07134 |  | 0.92 | 1.05 | 0.084702 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-376 | G17-140-BUS | 1.1354 | 1.2067 | 0.07134 |  | 0.92 | 1.05 | 0.072428 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-377 | G17-140-BUS | 1.1354 | 1.2067 | 0.07134 |  | 0.92 | 1.05 | 0.079185 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-379 | G17-140-BUS | 1.1354 | 1.2067 | 0.07134 |  | 0.92 | 1.05 | 0.076189 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 26SP | V | ASGI-2024-006 | G17-140-BUS | 1.1338 | 1.2006 | 0.066813 |  | 0.92 | 1.05 | 0.035825 | P52:345:AEPW:NR4PITTSB-7:::: | None
Voltage | 00NR | 2 | 26SP | V | ASGI-2024-023 | G17-140-BUS | 1.1338 | 1.2006 | 0.066813 |  | 0.92 | 1.05 | 0.17931 | P52:345:AEPW:NR4PITTSB-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-013 | G17-140-BUS | 1.1338 | 1.2006 | 0.066813 |  | 0.92 | 1.05 | 0.031448 | P52:345:AEPW:NR4PITTSB-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-015 | G17-140-BUS | 1.1338 | 1.2006 | 0.066813 |  | 0.92 | 1.05 | 0.030351 | P52:345:AEPW:NR4PITTSB-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-025 | G17-140-BUS | 1.1338 | 1.2006 | 0.066813 |  | 0.92 | 1.05 | 0.22895 | P52:345:AEPW:NR4PITTSB-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-041 | G17-140-BUS | 1.1338 | 1.2006 | 0.066813 |  | 0.92 | 1.05 | 0.03316 | P52:345:AEPW:NR4PITTSB-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-042 | G17-140-BUS | 1.1338 | 1.2006 | 0.066813 |  | 0.92 | 1.05 | 0.03316 | P52:345:AEPW:NR4PITTSB-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-068 | G17-140-BUS | 1.1338 | 1.2006 | 0.066813 |  | 0.92 | 1.05 | 0.21371 | P52:345:AEPW:NR4PITTSB-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-071 | G17-140-BUS | 1.1338 | 1.2006 | 0.066813 |  | 0.92 | 1.05 | 0.16373 | P52:345:AEPW:NR4PITTSB-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-113 | G17-140-BUS | 1.1338 | 1.2006 | 0.066813 |  | 0.92 | 1.05 | 0.030566 | P52:345:AEPW:NR4PITTSB-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-122 | G17-140-BUS | 1.1338 | 1.2006 | 0.066813 |  | 0.92 | 1.05 | 0.10218 | P52:345:AEPW:NR4PITTSB-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-128 | G17-140-BUS | 1.1338 | 1.2006 | 0.066813 |  | 0.92 | 1.05 | 0.053523 | P52:345:AEPW:NR4PITTSB-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-177 | G17-140-BUS | 1.1338 | 1.2006 | 0.066813 |  | 0.92 | 1.05 | 0.086868 | P52:345:AEPW:NR4PITTSB-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-178 | G17-140-BUS | 1.1338 | 1.2006 | 0.066813 |  | 0.92 | 1.05 | 0.12536 | P52:345:AEPW:NR4PITTSB-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-204 | G17-140-BUS | 1.1338 | 1.2006 | 0.066813 |  | 0.92 | 1.05 | 0.17907 | P52:345:AEPW:NR4PITTSB-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-219 | G17-140-BUS | 1.1338 | 1.2006 | 0.066813 |  | 0.92 | 1.05 | 0.13234 | P52:345:AEPW:NR4PITTSB-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-220 | G17-140-BUS | 1.1338 | 1.2006 | 0.066813 |  | 0.92 | 1.05 | 0.15868 | P52:345:AEPW:NR4PITTSB-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-232 | G17-140-BUS | 1.1338 | 1.2006 | 0.066813 |  | 0.92 | 1.05 | 0.1009 | P52:345:AEPW:NR4PITTSB-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-241 | G17-140-BUS | 1.1338 | 1.2006 | 0.066813 |  | 0.92 | 1.05 | 0.22895 | P52:345:AEPW:NR4PITTSB-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-261 | G17-140-BUS | 1.1338 | 1.2006 | 0.066813 |  | 0.92 | 1.05 | 0.030012 | P52:345:AEPW:NR4PITTSB-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-265 | G17-140-BUS | 1.1338 | 1.2006 | 0.066813 |  | 0.92 | 1.05 | 0.030037 | P52:345:AEPW:NR4PITTSB-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-268 | G17-140-BUS | 1.1338 | 1.2006 | 0.066813 |  | 0.92 | 1.05 | 0.036837 | P52:345:AEPW:NR4PITTSB-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-296 | G17-140-BUS | 1.1338 | 1.2006 | 0.066813 |  | 0.92 | 1.05 | 0.16175 | P52:345:AEPW:NR4PITTSB-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-297 | G17-140-BUS | 1.1338 | 1.2006 | 0.066813 |  | 0.92 | 1.05 | 0.16175 | P52:345:AEPW:NR4PITTSB-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-317 | G17-140-BUS | 1.1338 | 1.2006 | 0.066813 |  | 0.92 | 1.05 | 0.062484 | P52:345:AEPW:NR4PITTSB-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-321 | G17-140-BUS | 1.1338 | 1.2006 | 0.066813 |  | 0.92 | 1.05 | 0.051892 | P52:345:AEPW:NR4PITTSB-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-336 | G17-140-BUS | 1.1338 | 1.2006 | 0.066813 |  | 0.92 | 1.05 | 0.030178 | P52:345:AEPW:NR4PITTSB-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-338 | G17-140-BUS | 1.1338 | 1.2006 | 0.066813 |  | 0.92 | 1.05 | 0.47577 | P52:345:AEPW:NR4PITTSB-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-341 | G17-140-BUS | 1.1338 | 1.2006 | 0.066813 |  | 0.92 | 1.05 | 1 | P52:345:AEPW:NR4PITTSB-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-343 | G17-140-BUS | 1.1338 | 1.2006 | 0.066813 |  | 0.92 | 1.05 | 0.12723 | P52:345:AEPW:NR4PITTSB-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-360 | G17-140-BUS | 1.1338 | 1.2006 | 0.066813 |  | 0.92 | 1.05 | 0.038693 | P52:345:AEPW:NR4PITTSB-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-373 | G17-140-BUS | 1.1338 | 1.2006 | 0.066813 |  | 0.92 | 1.05 | 0.16735 | P52:345:AEPW:NR4PITTSB-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-376 | G17-140-BUS | 1.1338 | 1.2006 | 0.066813 |  | 0.92 | 1.05 | 0.072489 | P52:345:AEPW:NR4PITTSB-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-377 | G17-140-BUS | 1.1338 | 1.2006 | 0.066813 |  | 0.92 | 1.05 | 0.12806 | P52:345:AEPW:NR4PITTSB-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-379 | G17-140-BUS | 1.1338 | 1.2006 | 0.066813 |  | 0.92 | 1.05 | 0.078757 | P52:345:AEPW:NR4PITTSB-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-341 | G17-140-BUS | 1.1335 | 1.1997 | 0.066233 |  | 0.92 | 1.05 | 1 | Single 510907 PITTSB-7 345 787200 GEN-2024-341 345 1 | None
Voltage | 00NR | 2 | 26SP | V | ASGI-2024-006 | G17-140-BUS | 1.133 | 1.1996 | 0.066589 |  | 0.92 | 1.05 | 0.035554 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | ASGI-2024-023 | G17-140-BUS | 1.133 | 1.1996 | 0.066589 |  | 0.92 | 1.05 | 0.080033 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-013 | G17-140-BUS | 1.133 | 1.1996 | 0.066589 |  | 0.92 | 1.05 | 0.030062 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-025 | G17-140-BUS | 1.133 | 1.1996 | 0.066589 |  | 0.92 | 1.05 | 0.10345 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-068 | G17-140-BUS | 1.133 | 1.1996 | 0.066589 |  | 0.92 | 1.05 | 0.097832 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-071 | G17-140-BUS | 1.133 | 1.1996 | 0.066589 |  | 0.92 | 1.05 | 0.079911 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-122 | G17-140-BUS | 1.133 | 1.1996 | 0.066589 |  | 0.92 | 1.05 | 0.056906 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-128 | G17-140-BUS | 1.133 | 1.1996 | 0.066589 |  | 0.92 | 1.05 | 0.04004 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-177 | G17-140-BUS | 1.133 | 1.1996 | 0.066589 |  | 0.92 | 1.05 | 0.051878 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-178 | G17-140-BUS | 1.133 | 1.1996 | 0.066589 |  | 0.92 | 1.05 | 0.063986 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-204 | G17-140-BUS | 1.133 | 1.1996 | 0.066589 |  | 0.92 | 1.05 | 0.11622 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-219 | G17-140-BUS | 1.133 | 1.1996 | 0.066589 |  | 0.92 | 1.05 | 0.085225 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-220 | G17-140-BUS | 1.133 | 1.1996 | 0.066589 |  | 0.92 | 1.05 | 0.078211 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-232 | G17-140-BUS | 1.133 | 1.1996 | 0.066589 |  | 0.92 | 1.05 | 0.046505 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-241 | G17-140-BUS | 1.133 | 1.1996 | 0.066589 |  | 0.92 | 1.05 | 0.10345 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-296 | G17-140-BUS | 1.133 | 1.1996 | 0.066589 |  | 0.92 | 1.05 | 0.55682 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-297 | G17-140-BUS | 1.133 | 1.1996 | 0.066589 |  | 0.92 | 1.05 | 0.55682 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-317 | G17-140-BUS | 1.133 | 1.1996 | 0.066589 |  | 0.92 | 1.05 | 0.037729 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-321 | G17-140-BUS | 1.133 | 1.1996 | 0.066589 |  | 0.92 | 1.05 | 0.044768 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-338 | G17-140-BUS | 1.133 | 1.1996 | 0.066589 |  | 0.92 | 1.05 | 0.16684 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-341 | G17-140-BUS | 1.133 | 1.1996 | 0.066589 |  | 0.92 | 1.05 | 0.23795 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-343 | G17-140-BUS | 1.133 | 1.1996 | 0.066589 |  | 0.92 | 1.05 | 0.064223 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-360 | G17-140-BUS | 1.133 | 1.1996 | 0.066589 |  | 0.92 | 1.05 | 0.047575 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-362 | G17-140-BUS | 1.133 | 1.1996 | 0.066589 |  | 0.92 | 1.05 | 0.03045 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-373 | G17-140-BUS | 1.133 | 1.1996 | 0.066589 |  | 0.92 | 1.05 | 0.1258 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-376 | G17-140-BUS | 1.133 | 1.1996 | 0.066589 |  | 0.92 | 1.05 | 0.033661 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-377 | G17-140-BUS | 1.133 | 1.1996 | 0.066589 |  | 0.92 | 1.05 | 0.064787 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-379 | G17-140-BUS | 1.133 | 1.1996 | 0.066589 |  | 0.92 | 1.05 | 0.041183 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-239 | NP-GLAZIR_G2 | 0.7043 | 0.68414 | -0.020159 |  | 0.9 | 1.05 | 0.030446 | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-252 | NP-GLAZIR_G2 | 0.7043 | 0.68414 | -0.020159 |  | 0.9 | 1.05 | 0.030446 | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-254 | NP-GLAZIR_G2 | 0.7043 | 0.68414 | -0.020159 |  | 0.9 | 1.05 | 0.032849 | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-255 | NP-GLAZIR_G2 | 0.7043 | 0.68414 | -0.020159 |  | 0.9 | 1.05 | 0.030095 | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | ASGI-2024-003 | NP-GLAZIR_G2 | 0.71222 | 0.69708 | -0.01514 |  | 0.9 | 1.05 | 0.046521 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | ASGI-2024-006 | NP-GLAZIR_G2 | 0.71222 | 0.69708 | -0.01514 |  | 0.9 | 1.05 | 0.074703 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-015 | NP-GLAZIR_G2 | 0.71222 | 0.69708 | -0.01514 |  | 0.9 | 1.05 | 0.12365 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-041 | NP-GLAZIR_G2 | 0.71222 | 0.69708 | -0.01514 |  | 0.9 | 1.05 | 0.1562 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-042 | NP-GLAZIR_G2 | 0.71222 | 0.69708 | -0.01514 |  | 0.9 | 1.05 | 0.1562 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-043 | NP-GLAZIR_G2 | 0.71222 | 0.69708 | -0.01514 |  | 0.9 | 1.05 | 0.11064 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-099 | NP-GLAZIR_G2 | 0.71222 | 0.69708 | -0.01514 |  | 0.9 | 1.05 | 0.10819 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-109 | NP-GLAZIR_G2 | 0.71222 | 0.69708 | -0.01514 |  | 0.9 | 1.05 | 0.10967 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-143 | NP-GLAZIR_G2 | 0.71222 | 0.69708 | -0.01514 |  | 0.9 | 1.05 | 0.073716 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-145 | NP-GLAZIR_G2 | 0.71222 | 0.69708 | -0.01514 |  | 0.9 | 1.05 | 0.073716 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-159 | NP-GLAZIR_G2 | 0.71222 | 0.69708 | -0.01514 |  | 0.9 | 1.05 | 0.11297 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-221 | NP-GLAZIR_G2 | 0.71222 | 0.69708 | -0.01514 |  | 0.9 | 1.05 | 0.11247 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-261 | NP-GLAZIR_G2 | 0.71222 | 0.69708 | -0.01514 |  | 0.9 | 1.05 | 0.12021 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-265 | NP-GLAZIR_G2 | 0.71222 | 0.69708 | -0.01514 |  | 0.9 | 1.05 | 0.12047 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-280 | NP-GLAZIR_G2 | 0.71222 | 0.69708 | -0.01514 |  | 0.9 | 1.05 | 0.1183 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-281 | NP-GLAZIR_G2 | 0.71222 | 0.69708 | -0.01514 |  | 0.9 | 1.05 | 0.11865 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-295 | NP-GLAZIR_G2 | 0.71222 | 0.69708 | -0.01514 |  | 0.9 | 1.05 | 0.11877 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-303 | NP-GLAZIR_G2 | 0.71222 | 0.69708 | -0.01514 |  | 0.9 | 1.05 | 0.11076 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-304 | NP-GLAZIR_G2 | 0.71222 | 0.69708 | -0.01514 |  | 0.9 | 1.05 | 0.11076 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-311 | NP-GLAZIR_G2 | 0.71222 | 0.69708 | -0.01514 |  | 0.9 | 1.05 | 0.11634 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-317 | NP-GLAZIR_G2 | 0.71222 | 0.69708 | -0.01514 |  | 0.9 | 1.05 | 0.47052 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-336 | NP-GLAZIR_G2 | 0.71222 | 0.69708 | -0.01514 |  | 0.9 | 1.05 | 0.12194 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | ASGI-2024-003 | NP-GLAZIR_G2 | 0.71275 | 0.69764 | -0.015109 |  | 0.9 | 1.05 | 0.035702 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | ASGI-2024-006 | NP-GLAZIR_G2 | 0.71275 | 0.69764 | -0.015109 |  | 0.9 | 1.05 | 0.053043 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-013 | NP-GLAZIR_G2 | 0.71275 | 0.69764 | -0.015109 |  | 0.9 | 1.05 | 0.037495 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-015 | NP-GLAZIR_G2 | 0.71275 | 0.69764 | -0.015109 |  | 0.9 | 1.05 | 0.057538 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-041 | NP-GLAZIR_G2 | 0.71275 | 0.69764 | -0.015109 |  | 0.9 | 1.05 | 0.059056 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-042 | NP-GLAZIR_G2 | 0.71275 | 0.69764 | -0.015109 |  | 0.9 | 1.05 | 0.059056 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-043 | NP-GLAZIR_G2 | 0.71275 | 0.69764 | -0.015109 |  | 0.9 | 1.05 | 0.056962 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-099 | NP-GLAZIR_G2 | 0.71275 | 0.69764 | -0.015109 |  | 0.9 | 1.05 | 0.056989 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-109 | NP-GLAZIR_G2 | 0.71275 | 0.69764 | -0.015109 |  | 0.9 | 1.05 | 0.056997 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-128 | NP-GLAZIR_G2 | 0.71275 | 0.69764 | -0.015109 |  | 0.9 | 1.05 | 0.25306 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-143 | NP-GLAZIR_G2 | 0.71275 | 0.69764 | -0.015109 |  | 0.9 | 1.05 | 0.051595 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-145 | NP-GLAZIR_G2 | 0.71275 | 0.69764 | -0.015109 |  | 0.9 | 1.05 | 0.051595 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-154 | NP-GLAZIR_G2 | 0.71275 | 0.69764 | -0.015109 |  | 0.9 | 1.05 | 0.084292 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-159 | NP-GLAZIR_G2 | 0.71275 | 0.69764 | -0.015109 |  | 0.9 | 1.05 | 0.057127 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-204 | NP-GLAZIR_G2 | 0.71275 | 0.69764 | -0.015109 |  | 0.9 | 1.05 | 0.041671 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-219 | NP-GLAZIR_G2 | 0.71275 | 0.69764 | -0.015109 |  | 0.9 | 1.05 | 0.03293 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-221 | NP-GLAZIR_G2 | 0.71275 | 0.69764 | -0.015109 |  | 0.9 | 1.05 | 0.057003 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-261 | NP-GLAZIR_G2 | 0.71275 | 0.69764 | -0.015109 |  | 0.9 | 1.05 | 0.057308 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-265 | NP-GLAZIR_G2 | 0.71275 | 0.69764 | -0.015109 |  | 0.9 | 1.05 | 0.057324 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-280 | NP-GLAZIR_G2 | 0.71275 | 0.69764 | -0.015109 |  | 0.9 | 1.05 | 0.057182 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-281 | NP-GLAZIR_G2 | 0.71275 | 0.69764 | -0.015109 |  | 0.9 | 1.05 | 0.057175 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-295 | NP-GLAZIR_G2 | 0.71275 | 0.69764 | -0.015109 |  | 0.9 | 1.05 | 0.057109 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-303 | NP-GLAZIR_G2 | 0.71275 | 0.69764 | -0.015109 |  | 0.9 | 1.05 | 0.056958 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-304 | NP-GLAZIR_G2 | 0.71275 | 0.69764 | -0.015109 |  | 0.9 | 1.05 | 0.056958 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-311 | NP-GLAZIR_G2 | 0.71275 | 0.69764 | -0.015109 |  | 0.9 | 1.05 | 0.057138 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-317 | NP-GLAZIR_G2 | 0.71275 | 0.69764 | -0.015109 |  | 0.9 | 1.05 | 0.10561 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-336 | NP-GLAZIR_G2 | 0.71275 | 0.69764 | -0.015109 |  | 0.9 | 1.05 | 0.057417 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-338 | NP-GLAZIR_G2 | 0.71275 | 0.69764 | -0.015109 |  | 0.9 | 1.05 | 0.047162 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-373 | NP-GLAZIR_G2 | 0.71275 | 0.69764 | -0.015109 |  | 0.9 | 1.05 | 0.030913 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | ASGI-2024-003 | NP-GLAZIR_G2 | 0.71145 | 0.69695 | -0.014502 |  | 0.9 | 1.05 | 0.046521 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | ASGI-2024-006 | NP-GLAZIR_G2 | 0.71145 | 0.69695 | -0.014502 |  | 0.9 | 1.05 | 0.074703 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-015 | NP-GLAZIR_G2 | 0.71145 | 0.69695 | -0.014502 |  | 0.9 | 1.05 | 0.12365 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-041 | NP-GLAZIR_G2 | 0.71145 | 0.69695 | -0.014502 |  | 0.9 | 1.05 | 0.1562 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-042 | NP-GLAZIR_G2 | 0.71145 | 0.69695 | -0.014502 |  | 0.9 | 1.05 | 0.1562 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-043 | NP-GLAZIR_G2 | 0.71145 | 0.69695 | -0.014502 |  | 0.9 | 1.05 | 0.11064 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-099 | NP-GLAZIR_G2 | 0.71145 | 0.69695 | -0.014502 |  | 0.9 | 1.05 | 0.10819 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-109 | NP-GLAZIR_G2 | 0.71145 | 0.69695 | -0.014502 |  | 0.9 | 1.05 | 0.10967 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-143 | NP-GLAZIR_G2 | 0.71145 | 0.69695 | -0.014502 |  | 0.9 | 1.05 | 0.073716 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-145 | NP-GLAZIR_G2 | 0.71145 | 0.69695 | -0.014502 |  | 0.9 | 1.05 | 0.073716 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-159 | NP-GLAZIR_G2 | 0.71145 | 0.69695 | -0.014502 |  | 0.9 | 1.05 | 0.11297 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-221 | NP-GLAZIR_G2 | 0.71145 | 0.69695 | -0.014502 |  | 0.9 | 1.05 | 0.11247 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-261 | NP-GLAZIR_G2 | 0.71145 | 0.69695 | -0.014502 |  | 0.9 | 1.05 | 0.12021 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-265 | NP-GLAZIR_G2 | 0.71145 | 0.69695 | -0.014502 |  | 0.9 | 1.05 | 0.12047 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-280 | NP-GLAZIR_G2 | 0.71145 | 0.69695 | -0.014502 |  | 0.9 | 1.05 | 0.1183 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-281 | NP-GLAZIR_G2 | 0.71145 | 0.69695 | -0.014502 |  | 0.9 | 1.05 | 0.11865 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-295 | NP-GLAZIR_G2 | 0.71145 | 0.69695 | -0.014502 |  | 0.9 | 1.05 | 0.11877 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-303 | NP-GLAZIR_G2 | 0.71145 | 0.69695 | -0.014502 |  | 0.9 | 1.05 | 0.11076 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-304 | NP-GLAZIR_G2 | 0.71145 | 0.69695 | -0.014502 |  | 0.9 | 1.05 | 0.11076 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-311 | NP-GLAZIR_G2 | 0.71145 | 0.69695 | -0.014502 |  | 0.9 | 1.05 | 0.11634 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-317 | NP-GLAZIR_G2 | 0.71145 | 0.69695 | -0.014502 |  | 0.9 | 1.05 | 0.47052 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-336 | NP-GLAZIR_G2 | 0.71145 | 0.69695 | -0.014502 |  | 0.9 | 1.05 | 0.12194 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | ASGI-2024-003 | NP-GLAZIR_G2 | 0.71214 | 0.69706 | -0.015078 |  | 0.9 | 1.05 | 0.046521 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | ASGI-2024-006 | NP-GLAZIR_G2 | 0.71214 | 0.69706 | -0.015078 |  | 0.9 | 1.05 | 0.074703 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-015 | NP-GLAZIR_G2 | 0.71214 | 0.69706 | -0.015078 |  | 0.9 | 1.05 | 0.12365 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-041 | NP-GLAZIR_G2 | 0.71214 | 0.69706 | -0.015078 |  | 0.9 | 1.05 | 0.1562 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-042 | NP-GLAZIR_G2 | 0.71214 | 0.69706 | -0.015078 |  | 0.9 | 1.05 | 0.1562 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-043 | NP-GLAZIR_G2 | 0.71214 | 0.69706 | -0.015078 |  | 0.9 | 1.05 | 0.11064 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-099 | NP-GLAZIR_G2 | 0.71214 | 0.69706 | -0.015078 |  | 0.9 | 1.05 | 0.10819 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-109 | NP-GLAZIR_G2 | 0.71214 | 0.69706 | -0.015078 |  | 0.9 | 1.05 | 0.10967 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-143 | NP-GLAZIR_G2 | 0.71214 | 0.69706 | -0.015078 |  | 0.9 | 1.05 | 0.073716 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-145 | NP-GLAZIR_G2 | 0.71214 | 0.69706 | -0.015078 |  | 0.9 | 1.05 | 0.073716 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-159 | NP-GLAZIR_G2 | 0.71214 | 0.69706 | -0.015078 |  | 0.9 | 1.05 | 0.11297 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-221 | NP-GLAZIR_G2 | 0.71214 | 0.69706 | -0.015078 |  | 0.9 | 1.05 | 0.11247 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-261 | NP-GLAZIR_G2 | 0.71214 | 0.69706 | -0.015078 |  | 0.9 | 1.05 | 0.12021 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-265 | NP-GLAZIR_G2 | 0.71214 | 0.69706 | -0.015078 |  | 0.9 | 1.05 | 0.12047 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-280 | NP-GLAZIR_G2 | 0.71214 | 0.69706 | -0.015078 |  | 0.9 | 1.05 | 0.1183 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-281 | NP-GLAZIR_G2 | 0.71214 | 0.69706 | -0.015078 |  | 0.9 | 1.05 | 0.11865 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-295 | NP-GLAZIR_G2 | 0.71214 | 0.69706 | -0.015078 |  | 0.9 | 1.05 | 0.11877 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-303 | NP-GLAZIR_G2 | 0.71214 | 0.69706 | -0.015078 |  | 0.9 | 1.05 | 0.11076 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-304 | NP-GLAZIR_G2 | 0.71214 | 0.69706 | -0.015078 |  | 0.9 | 1.05 | 0.11076 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-311 | NP-GLAZIR_G2 | 0.71214 | 0.69706 | -0.015078 |  | 0.9 | 1.05 | 0.11634 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-317 | NP-GLAZIR_G2 | 0.71214 | 0.69706 | -0.015078 |  | 0.9 | 1.05 | 0.47052 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-336 | NP-GLAZIR_G2 | 0.71214 | 0.69706 | -0.015078 |  | 0.9 | 1.05 | 0.12194 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-239 | NP-LIPSCOMB2 | 0.66748 | 0.64646 | -0.02102 |  | 0.9 | 1.05 | 0.030446 | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-252 | NP-LIPSCOMB2 | 0.66748 | 0.64646 | -0.02102 |  | 0.9 | 1.05 | 0.030446 | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-254 | NP-LIPSCOMB2 | 0.66748 | 0.64646 | -0.02102 |  | 0.9 | 1.05 | 0.032849 | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-255 | NP-LIPSCOMB2 | 0.66748 | 0.64646 | -0.02102 |  | 0.9 | 1.05 | 0.030095 | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | ASGI-2024-003 | NP-LIPSCOMB2 | 0.67578 | 0.65994 | -0.015836 |  | 0.9 | 1.05 | 0.046521 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | ASGI-2024-006 | NP-LIPSCOMB2 | 0.67578 | 0.65994 | -0.015836 |  | 0.9 | 1.05 | 0.074703 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-015 | NP-LIPSCOMB2 | 0.67578 | 0.65994 | -0.015836 |  | 0.9 | 1.05 | 0.12365 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-041 | NP-LIPSCOMB2 | 0.67578 | 0.65994 | -0.015836 |  | 0.9 | 1.05 | 0.1562 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-042 | NP-LIPSCOMB2 | 0.67578 | 0.65994 | -0.015836 |  | 0.9 | 1.05 | 0.1562 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-043 | NP-LIPSCOMB2 | 0.67578 | 0.65994 | -0.015836 |  | 0.9 | 1.05 | 0.11064 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-099 | NP-LIPSCOMB2 | 0.67578 | 0.65994 | -0.015836 |  | 0.9 | 1.05 | 0.10819 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-109 | NP-LIPSCOMB2 | 0.67578 | 0.65994 | -0.015836 |  | 0.9 | 1.05 | 0.10967 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-143 | NP-LIPSCOMB2 | 0.67578 | 0.65994 | -0.015836 |  | 0.9 | 1.05 | 0.073716 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-145 | NP-LIPSCOMB2 | 0.67578 | 0.65994 | -0.015836 |  | 0.9 | 1.05 | 0.073716 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-159 | NP-LIPSCOMB2 | 0.67578 | 0.65994 | -0.015836 |  | 0.9 | 1.05 | 0.11297 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-221 | NP-LIPSCOMB2 | 0.67578 | 0.65994 | -0.015836 |  | 0.9 | 1.05 | 0.11247 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-261 | NP-LIPSCOMB2 | 0.67578 | 0.65994 | -0.015836 |  | 0.9 | 1.05 | 0.12021 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-265 | NP-LIPSCOMB2 | 0.67578 | 0.65994 | -0.015836 |  | 0.9 | 1.05 | 0.12047 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-280 | NP-LIPSCOMB2 | 0.67578 | 0.65994 | -0.015836 |  | 0.9 | 1.05 | 0.1183 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-281 | NP-LIPSCOMB2 | 0.67578 | 0.65994 | -0.015836 |  | 0.9 | 1.05 | 0.11865 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-295 | NP-LIPSCOMB2 | 0.67578 | 0.65994 | -0.015836 |  | 0.9 | 1.05 | 0.11877 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-303 | NP-LIPSCOMB2 | 0.67578 | 0.65994 | -0.015836 |  | 0.9 | 1.05 | 0.11076 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-304 | NP-LIPSCOMB2 | 0.67578 | 0.65994 | -0.015836 |  | 0.9 | 1.05 | 0.11076 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-311 | NP-LIPSCOMB2 | 0.67578 | 0.65994 | -0.015836 |  | 0.9 | 1.05 | 0.11634 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-317 | NP-LIPSCOMB2 | 0.67578 | 0.65994 | -0.015836 |  | 0.9 | 1.05 | 0.47052 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-336 | NP-LIPSCOMB2 | 0.67578 | 0.65994 | -0.015836 |  | 0.9 | 1.05 | 0.12194 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | ASGI-2024-003 | NP-LIPSCOMB2 | 0.67633 | 0.66052 | -0.015805 |  | 0.9 | 1.05 | 0.035702 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | ASGI-2024-006 | NP-LIPSCOMB2 | 0.67633 | 0.66052 | -0.015805 |  | 0.9 | 1.05 | 0.053043 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-013 | NP-LIPSCOMB2 | 0.67633 | 0.66052 | -0.015805 |  | 0.9 | 1.05 | 0.037495 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-015 | NP-LIPSCOMB2 | 0.67633 | 0.66052 | -0.015805 |  | 0.9 | 1.05 | 0.057538 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-041 | NP-LIPSCOMB2 | 0.67633 | 0.66052 | -0.015805 |  | 0.9 | 1.05 | 0.059056 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-042 | NP-LIPSCOMB2 | 0.67633 | 0.66052 | -0.015805 |  | 0.9 | 1.05 | 0.059056 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-043 | NP-LIPSCOMB2 | 0.67633 | 0.66052 | -0.015805 |  | 0.9 | 1.05 | 0.056962 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-099 | NP-LIPSCOMB2 | 0.67633 | 0.66052 | -0.015805 |  | 0.9 | 1.05 | 0.056989 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-109 | NP-LIPSCOMB2 | 0.67633 | 0.66052 | -0.015805 |  | 0.9 | 1.05 | 0.056997 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-128 | NP-LIPSCOMB2 | 0.67633 | 0.66052 | -0.015805 |  | 0.9 | 1.05 | 0.25306 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-143 | NP-LIPSCOMB2 | 0.67633 | 0.66052 | -0.015805 |  | 0.9 | 1.05 | 0.051595 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-145 | NP-LIPSCOMB2 | 0.67633 | 0.66052 | -0.015805 |  | 0.9 | 1.05 | 0.051595 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-154 | NP-LIPSCOMB2 | 0.67633 | 0.66052 | -0.015805 |  | 0.9 | 1.05 | 0.084292 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-159 | NP-LIPSCOMB2 | 0.67633 | 0.66052 | -0.015805 |  | 0.9 | 1.05 | 0.057127 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-204 | NP-LIPSCOMB2 | 0.67633 | 0.66052 | -0.015805 |  | 0.9 | 1.05 | 0.041671 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-219 | NP-LIPSCOMB2 | 0.67633 | 0.66052 | -0.015805 |  | 0.9 | 1.05 | 0.03293 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-221 | NP-LIPSCOMB2 | 0.67633 | 0.66052 | -0.015805 |  | 0.9 | 1.05 | 0.057003 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-261 | NP-LIPSCOMB2 | 0.67633 | 0.66052 | -0.015805 |  | 0.9 | 1.05 | 0.057308 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-265 | NP-LIPSCOMB2 | 0.67633 | 0.66052 | -0.015805 |  | 0.9 | 1.05 | 0.057324 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-280 | NP-LIPSCOMB2 | 0.67633 | 0.66052 | -0.015805 |  | 0.9 | 1.05 | 0.057182 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-281 | NP-LIPSCOMB2 | 0.67633 | 0.66052 | -0.015805 |  | 0.9 | 1.05 | 0.057175 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-295 | NP-LIPSCOMB2 | 0.67633 | 0.66052 | -0.015805 |  | 0.9 | 1.05 | 0.057109 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-303 | NP-LIPSCOMB2 | 0.67633 | 0.66052 | -0.015805 |  | 0.9 | 1.05 | 0.056958 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-304 | NP-LIPSCOMB2 | 0.67633 | 0.66052 | -0.015805 |  | 0.9 | 1.05 | 0.056958 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-311 | NP-LIPSCOMB2 | 0.67633 | 0.66052 | -0.015805 |  | 0.9 | 1.05 | 0.057138 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-317 | NP-LIPSCOMB2 | 0.67633 | 0.66052 | -0.015805 |  | 0.9 | 1.05 | 0.10561 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-336 | NP-LIPSCOMB2 | 0.67633 | 0.66052 | -0.015805 |  | 0.9 | 1.05 | 0.057417 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-338 | NP-LIPSCOMB2 | 0.67633 | 0.66052 | -0.015805 |  | 0.9 | 1.05 | 0.047162 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-373 | NP-LIPSCOMB2 | 0.67633 | 0.66052 | -0.015805 |  | 0.9 | 1.05 | 0.030913 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | ASGI-2024-003 | NP-LIPSCOMB2 | 0.67497 | 0.65981 | -0.015166 |  | 0.9 | 1.05 | 0.046521 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | ASGI-2024-006 | NP-LIPSCOMB2 | 0.67497 | 0.65981 | -0.015166 |  | 0.9 | 1.05 | 0.074703 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-015 | NP-LIPSCOMB2 | 0.67497 | 0.65981 | -0.015166 |  | 0.9 | 1.05 | 0.12365 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-041 | NP-LIPSCOMB2 | 0.67497 | 0.65981 | -0.015166 |  | 0.9 | 1.05 | 0.1562 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-042 | NP-LIPSCOMB2 | 0.67497 | 0.65981 | -0.015166 |  | 0.9 | 1.05 | 0.1562 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-043 | NP-LIPSCOMB2 | 0.67497 | 0.65981 | -0.015166 |  | 0.9 | 1.05 | 0.11064 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-099 | NP-LIPSCOMB2 | 0.67497 | 0.65981 | -0.015166 |  | 0.9 | 1.05 | 0.10819 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-109 | NP-LIPSCOMB2 | 0.67497 | 0.65981 | -0.015166 |  | 0.9 | 1.05 | 0.10967 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-143 | NP-LIPSCOMB2 | 0.67497 | 0.65981 | -0.015166 |  | 0.9 | 1.05 | 0.073716 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-145 | NP-LIPSCOMB2 | 0.67497 | 0.65981 | -0.015166 |  | 0.9 | 1.05 | 0.073716 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-159 | NP-LIPSCOMB2 | 0.67497 | 0.65981 | -0.015166 |  | 0.9 | 1.05 | 0.11297 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-221 | NP-LIPSCOMB2 | 0.67497 | 0.65981 | -0.015166 |  | 0.9 | 1.05 | 0.11247 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-261 | NP-LIPSCOMB2 | 0.67497 | 0.65981 | -0.015166 |  | 0.9 | 1.05 | 0.12021 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-265 | NP-LIPSCOMB2 | 0.67497 | 0.65981 | -0.015166 |  | 0.9 | 1.05 | 0.12047 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-280 | NP-LIPSCOMB2 | 0.67497 | 0.65981 | -0.015166 |  | 0.9 | 1.05 | 0.1183 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-281 | NP-LIPSCOMB2 | 0.67497 | 0.65981 | -0.015166 |  | 0.9 | 1.05 | 0.11865 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-295 | NP-LIPSCOMB2 | 0.67497 | 0.65981 | -0.015166 |  | 0.9 | 1.05 | 0.11877 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-303 | NP-LIPSCOMB2 | 0.67497 | 0.65981 | -0.015166 |  | 0.9 | 1.05 | 0.11076 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-304 | NP-LIPSCOMB2 | 0.67497 | 0.65981 | -0.015166 |  | 0.9 | 1.05 | 0.11076 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-311 | NP-LIPSCOMB2 | 0.67497 | 0.65981 | -0.015166 |  | 0.9 | 1.05 | 0.11634 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-317 | NP-LIPSCOMB2 | 0.67497 | 0.65981 | -0.015166 |  | 0.9 | 1.05 | 0.47052 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-336 | NP-LIPSCOMB2 | 0.67497 | 0.65981 | -0.015166 |  | 0.9 | 1.05 | 0.12194 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | ASGI-2024-003 | NP-LIPSCOMB2 | 0.67569 | 0.65992 | -0.01577 |  | 0.9 | 1.05 | 0.046521 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | ASGI-2024-006 | NP-LIPSCOMB2 | 0.67569 | 0.65992 | -0.01577 |  | 0.9 | 1.05 | 0.074703 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-015 | NP-LIPSCOMB2 | 0.67569 | 0.65992 | -0.01577 |  | 0.9 | 1.05 | 0.12365 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-041 | NP-LIPSCOMB2 | 0.67569 | 0.65992 | -0.01577 |  | 0.9 | 1.05 | 0.1562 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-042 | NP-LIPSCOMB2 | 0.67569 | 0.65992 | -0.01577 |  | 0.9 | 1.05 | 0.1562 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-043 | NP-LIPSCOMB2 | 0.67569 | 0.65992 | -0.01577 |  | 0.9 | 1.05 | 0.11064 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-099 | NP-LIPSCOMB2 | 0.67569 | 0.65992 | -0.01577 |  | 0.9 | 1.05 | 0.10819 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-109 | NP-LIPSCOMB2 | 0.67569 | 0.65992 | -0.01577 |  | 0.9 | 1.05 | 0.10967 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-143 | NP-LIPSCOMB2 | 0.67569 | 0.65992 | -0.01577 |  | 0.9 | 1.05 | 0.073716 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-145 | NP-LIPSCOMB2 | 0.67569 | 0.65992 | -0.01577 |  | 0.9 | 1.05 | 0.073716 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-159 | NP-LIPSCOMB2 | 0.67569 | 0.65992 | -0.01577 |  | 0.9 | 1.05 | 0.11297 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-221 | NP-LIPSCOMB2 | 0.67569 | 0.65992 | -0.01577 |  | 0.9 | 1.05 | 0.11247 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-261 | NP-LIPSCOMB2 | 0.67569 | 0.65992 | -0.01577 |  | 0.9 | 1.05 | 0.12021 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-265 | NP-LIPSCOMB2 | 0.67569 | 0.65992 | -0.01577 |  | 0.9 | 1.05 | 0.12047 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-280 | NP-LIPSCOMB2 | 0.67569 | 0.65992 | -0.01577 |  | 0.9 | 1.05 | 0.1183 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-281 | NP-LIPSCOMB2 | 0.67569 | 0.65992 | -0.01577 |  | 0.9 | 1.05 | 0.11865 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-295 | NP-LIPSCOMB2 | 0.67569 | 0.65992 | -0.01577 |  | 0.9 | 1.05 | 0.11877 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-303 | NP-LIPSCOMB2 | 0.67569 | 0.65992 | -0.01577 |  | 0.9 | 1.05 | 0.11076 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-304 | NP-LIPSCOMB2 | 0.67569 | 0.65992 | -0.01577 |  | 0.9 | 1.05 | 0.11076 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-311 | NP-LIPSCOMB2 | 0.67569 | 0.65992 | -0.01577 |  | 0.9 | 1.05 | 0.11634 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-317 | NP-LIPSCOMB2 | 0.67569 | 0.65992 | -0.01577 |  | 0.9 | 1.05 | 0.47052 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-336 | NP-LIPSCOMB2 | 0.67569 | 0.65992 | -0.01577 |  | 0.9 | 1.05 | 0.12194 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-239 | NP-LIPS_SHA2 | 0.66748 | 0.64646 | -0.02102 |  | 0.9 | 1.05 | 0.030446 | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-252 | NP-LIPS_SHA2 | 0.66748 | 0.64646 | -0.02102 |  | 0.9 | 1.05 | 0.030446 | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-254 | NP-LIPS_SHA2 | 0.66748 | 0.64646 | -0.02102 |  | 0.9 | 1.05 | 0.032849 | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-255 | NP-LIPS_SHA2 | 0.66748 | 0.64646 | -0.02102 |  | 0.9 | 1.05 | 0.030095 | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | ASGI-2024-003 | NP-LIPS_SHA2 | 0.67578 | 0.65994 | -0.015836 |  | 0.9 | 1.05 | 0.046521 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | ASGI-2024-006 | NP-LIPS_SHA2 | 0.67578 | 0.65994 | -0.015836 |  | 0.9 | 1.05 | 0.074703 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-015 | NP-LIPS_SHA2 | 0.67578 | 0.65994 | -0.015836 |  | 0.9 | 1.05 | 0.12365 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-041 | NP-LIPS_SHA2 | 0.67578 | 0.65994 | -0.015836 |  | 0.9 | 1.05 | 0.1562 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-042 | NP-LIPS_SHA2 | 0.67578 | 0.65994 | -0.015836 |  | 0.9 | 1.05 | 0.1562 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-043 | NP-LIPS_SHA2 | 0.67578 | 0.65994 | -0.015836 |  | 0.9 | 1.05 | 0.11064 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-099 | NP-LIPS_SHA2 | 0.67578 | 0.65994 | -0.015836 |  | 0.9 | 1.05 | 0.10819 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-109 | NP-LIPS_SHA2 | 0.67578 | 0.65994 | -0.015836 |  | 0.9 | 1.05 | 0.10967 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-143 | NP-LIPS_SHA2 | 0.67578 | 0.65994 | -0.015836 |  | 0.9 | 1.05 | 0.073716 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-145 | NP-LIPS_SHA2 | 0.67578 | 0.65994 | -0.015836 |  | 0.9 | 1.05 | 0.073716 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-159 | NP-LIPS_SHA2 | 0.67578 | 0.65994 | -0.015836 |  | 0.9 | 1.05 | 0.11297 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-221 | NP-LIPS_SHA2 | 0.67578 | 0.65994 | -0.015836 |  | 0.9 | 1.05 | 0.11247 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-261 | NP-LIPS_SHA2 | 0.67578 | 0.65994 | -0.015836 |  | 0.9 | 1.05 | 0.12021 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-265 | NP-LIPS_SHA2 | 0.67578 | 0.65994 | -0.015836 |  | 0.9 | 1.05 | 0.12047 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-280 | NP-LIPS_SHA2 | 0.67578 | 0.65994 | -0.015836 |  | 0.9 | 1.05 | 0.1183 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-281 | NP-LIPS_SHA2 | 0.67578 | 0.65994 | -0.015836 |  | 0.9 | 1.05 | 0.11865 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-295 | NP-LIPS_SHA2 | 0.67578 | 0.65994 | -0.015836 |  | 0.9 | 1.05 | 0.11877 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-303 | NP-LIPS_SHA2 | 0.67578 | 0.65994 | -0.015836 |  | 0.9 | 1.05 | 0.11076 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-304 | NP-LIPS_SHA2 | 0.67578 | 0.65994 | -0.015836 |  | 0.9 | 1.05 | 0.11076 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-311 | NP-LIPS_SHA2 | 0.67578 | 0.65994 | -0.015836 |  | 0.9 | 1.05 | 0.11634 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-317 | NP-LIPS_SHA2 | 0.67578 | 0.65994 | -0.015836 |  | 0.9 | 1.05 | 0.47052 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-336 | NP-LIPS_SHA2 | 0.67578 | 0.65994 | -0.015836 |  | 0.9 | 1.05 | 0.12194 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | ASGI-2024-003 | NP-LIPS_SHA2 | 0.67633 | 0.66052 | -0.015805 |  | 0.9 | 1.05 | 0.035702 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | ASGI-2024-006 | NP-LIPS_SHA2 | 0.67633 | 0.66052 | -0.015805 |  | 0.9 | 1.05 | 0.053043 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-013 | NP-LIPS_SHA2 | 0.67633 | 0.66052 | -0.015805 |  | 0.9 | 1.05 | 0.037495 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-015 | NP-LIPS_SHA2 | 0.67633 | 0.66052 | -0.015805 |  | 0.9 | 1.05 | 0.057538 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-041 | NP-LIPS_SHA2 | 0.67633 | 0.66052 | -0.015805 |  | 0.9 | 1.05 | 0.059056 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-042 | NP-LIPS_SHA2 | 0.67633 | 0.66052 | -0.015805 |  | 0.9 | 1.05 | 0.059056 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-043 | NP-LIPS_SHA2 | 0.67633 | 0.66052 | -0.015805 |  | 0.9 | 1.05 | 0.056962 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-099 | NP-LIPS_SHA2 | 0.67633 | 0.66052 | -0.015805 |  | 0.9 | 1.05 | 0.056989 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-109 | NP-LIPS_SHA2 | 0.67633 | 0.66052 | -0.015805 |  | 0.9 | 1.05 | 0.056997 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-128 | NP-LIPS_SHA2 | 0.67633 | 0.66052 | -0.015805 |  | 0.9 | 1.05 | 0.25306 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-143 | NP-LIPS_SHA2 | 0.67633 | 0.66052 | -0.015805 |  | 0.9 | 1.05 | 0.051595 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-145 | NP-LIPS_SHA2 | 0.67633 | 0.66052 | -0.015805 |  | 0.9 | 1.05 | 0.051595 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-154 | NP-LIPS_SHA2 | 0.67633 | 0.66052 | -0.015805 |  | 0.9 | 1.05 | 0.084292 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-159 | NP-LIPS_SHA2 | 0.67633 | 0.66052 | -0.015805 |  | 0.9 | 1.05 | 0.057127 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-204 | NP-LIPS_SHA2 | 0.67633 | 0.66052 | -0.015805 |  | 0.9 | 1.05 | 0.041671 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-219 | NP-LIPS_SHA2 | 0.67633 | 0.66052 | -0.015805 |  | 0.9 | 1.05 | 0.03293 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-221 | NP-LIPS_SHA2 | 0.67633 | 0.66052 | -0.015805 |  | 0.9 | 1.05 | 0.057003 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-261 | NP-LIPS_SHA2 | 0.67633 | 0.66052 | -0.015805 |  | 0.9 | 1.05 | 0.057308 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-265 | NP-LIPS_SHA2 | 0.67633 | 0.66052 | -0.015805 |  | 0.9 | 1.05 | 0.057324 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-280 | NP-LIPS_SHA2 | 0.67633 | 0.66052 | -0.015805 |  | 0.9 | 1.05 | 0.057182 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-281 | NP-LIPS_SHA2 | 0.67633 | 0.66052 | -0.015805 |  | 0.9 | 1.05 | 0.057175 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-295 | NP-LIPS_SHA2 | 0.67633 | 0.66052 | -0.015805 |  | 0.9 | 1.05 | 0.057109 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-303 | NP-LIPS_SHA2 | 0.67633 | 0.66052 | -0.015805 |  | 0.9 | 1.05 | 0.056958 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-304 | NP-LIPS_SHA2 | 0.67633 | 0.66052 | -0.015805 |  | 0.9 | 1.05 | 0.056958 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-311 | NP-LIPS_SHA2 | 0.67633 | 0.66052 | -0.015805 |  | 0.9 | 1.05 | 0.057138 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-317 | NP-LIPS_SHA2 | 0.67633 | 0.66052 | -0.015805 |  | 0.9 | 1.05 | 0.10561 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-336 | NP-LIPS_SHA2 | 0.67633 | 0.66052 | -0.015805 |  | 0.9 | 1.05 | 0.057417 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-338 | NP-LIPS_SHA2 | 0.67633 | 0.66052 | -0.015805 |  | 0.9 | 1.05 | 0.047162 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-373 | NP-LIPS_SHA2 | 0.67633 | 0.66052 | -0.015805 |  | 0.9 | 1.05 | 0.030913 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | ASGI-2024-003 | NP-LIPS_SHA2 | 0.67497 | 0.65981 | -0.015166 |  | 0.9 | 1.05 | 0.046521 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | ASGI-2024-006 | NP-LIPS_SHA2 | 0.67497 | 0.65981 | -0.015166 |  | 0.9 | 1.05 | 0.074703 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-015 | NP-LIPS_SHA2 | 0.67497 | 0.65981 | -0.015166 |  | 0.9 | 1.05 | 0.12365 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-041 | NP-LIPS_SHA2 | 0.67497 | 0.65981 | -0.015166 |  | 0.9 | 1.05 | 0.1562 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-042 | NP-LIPS_SHA2 | 0.67497 | 0.65981 | -0.015166 |  | 0.9 | 1.05 | 0.1562 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-043 | NP-LIPS_SHA2 | 0.67497 | 0.65981 | -0.015166 |  | 0.9 | 1.05 | 0.11064 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-099 | NP-LIPS_SHA2 | 0.67497 | 0.65981 | -0.015166 |  | 0.9 | 1.05 | 0.10819 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-109 | NP-LIPS_SHA2 | 0.67497 | 0.65981 | -0.015166 |  | 0.9 | 1.05 | 0.10967 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-143 | NP-LIPS_SHA2 | 0.67497 | 0.65981 | -0.015166 |  | 0.9 | 1.05 | 0.073716 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-145 | NP-LIPS_SHA2 | 0.67497 | 0.65981 | -0.015166 |  | 0.9 | 1.05 | 0.073716 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-159 | NP-LIPS_SHA2 | 0.67497 | 0.65981 | -0.015166 |  | 0.9 | 1.05 | 0.11297 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-221 | NP-LIPS_SHA2 | 0.67497 | 0.65981 | -0.015166 |  | 0.9 | 1.05 | 0.11247 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-261 | NP-LIPS_SHA2 | 0.67497 | 0.65981 | -0.015166 |  | 0.9 | 1.05 | 0.12021 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-265 | NP-LIPS_SHA2 | 0.67497 | 0.65981 | -0.015166 |  | 0.9 | 1.05 | 0.12047 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-280 | NP-LIPS_SHA2 | 0.67497 | 0.65981 | -0.015166 |  | 0.9 | 1.05 | 0.1183 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-281 | NP-LIPS_SHA2 | 0.67497 | 0.65981 | -0.015166 |  | 0.9 | 1.05 | 0.11865 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-295 | NP-LIPS_SHA2 | 0.67497 | 0.65981 | -0.015166 |  | 0.9 | 1.05 | 0.11877 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-303 | NP-LIPS_SHA2 | 0.67497 | 0.65981 | -0.015166 |  | 0.9 | 1.05 | 0.11076 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-304 | NP-LIPS_SHA2 | 0.67497 | 0.65981 | -0.015166 |  | 0.9 | 1.05 | 0.11076 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-311 | NP-LIPS_SHA2 | 0.67497 | 0.65981 | -0.015166 |  | 0.9 | 1.05 | 0.11634 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-317 | NP-LIPS_SHA2 | 0.67497 | 0.65981 | -0.015166 |  | 0.9 | 1.05 | 0.47052 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-336 | NP-LIPS_SHA2 | 0.67497 | 0.65981 | -0.015166 |  | 0.9 | 1.05 | 0.12194 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | ASGI-2024-003 | NP-LIPS_SHA2 | 0.67569 | 0.65992 | -0.01577 |  | 0.9 | 1.05 | 0.046521 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | ASGI-2024-006 | NP-LIPS_SHA2 | 0.67569 | 0.65992 | -0.01577 |  | 0.9 | 1.05 | 0.074703 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-015 | NP-LIPS_SHA2 | 0.67569 | 0.65992 | -0.01577 |  | 0.9 | 1.05 | 0.12365 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-041 | NP-LIPS_SHA2 | 0.67569 | 0.65992 | -0.01577 |  | 0.9 | 1.05 | 0.1562 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-042 | NP-LIPS_SHA2 | 0.67569 | 0.65992 | -0.01577 |  | 0.9 | 1.05 | 0.1562 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-043 | NP-LIPS_SHA2 | 0.67569 | 0.65992 | -0.01577 |  | 0.9 | 1.05 | 0.11064 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-099 | NP-LIPS_SHA2 | 0.67569 | 0.65992 | -0.01577 |  | 0.9 | 1.05 | 0.10819 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-109 | NP-LIPS_SHA2 | 0.67569 | 0.65992 | -0.01577 |  | 0.9 | 1.05 | 0.10967 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-143 | NP-LIPS_SHA2 | 0.67569 | 0.65992 | -0.01577 |  | 0.9 | 1.05 | 0.073716 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-145 | NP-LIPS_SHA2 | 0.67569 | 0.65992 | -0.01577 |  | 0.9 | 1.05 | 0.073716 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-159 | NP-LIPS_SHA2 | 0.67569 | 0.65992 | -0.01577 |  | 0.9 | 1.05 | 0.11297 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-221 | NP-LIPS_SHA2 | 0.67569 | 0.65992 | -0.01577 |  | 0.9 | 1.05 | 0.11247 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-261 | NP-LIPS_SHA2 | 0.67569 | 0.65992 | -0.01577 |  | 0.9 | 1.05 | 0.12021 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-265 | NP-LIPS_SHA2 | 0.67569 | 0.65992 | -0.01577 |  | 0.9 | 1.05 | 0.12047 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-280 | NP-LIPS_SHA2 | 0.67569 | 0.65992 | -0.01577 |  | 0.9 | 1.05 | 0.1183 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-281 | NP-LIPS_SHA2 | 0.67569 | 0.65992 | -0.01577 |  | 0.9 | 1.05 | 0.11865 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-295 | NP-LIPS_SHA2 | 0.67569 | 0.65992 | -0.01577 |  | 0.9 | 1.05 | 0.11877 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-303 | NP-LIPS_SHA2 | 0.67569 | 0.65992 | -0.01577 |  | 0.9 | 1.05 | 0.11076 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-304 | NP-LIPS_SHA2 | 0.67569 | 0.65992 | -0.01577 |  | 0.9 | 1.05 | 0.11076 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-311 | NP-LIPS_SHA2 | 0.67569 | 0.65992 | -0.01577 |  | 0.9 | 1.05 | 0.11634 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-317 | NP-LIPS_SHA2 | 0.67569 | 0.65992 | -0.01577 |  | 0.9 | 1.05 | 0.47052 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-336 | NP-LIPS_SHA2 | 0.67569 | 0.65992 | -0.01577 |  | 0.9 | 1.05 | 0.12194 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-239 | NP-LUCKY_CR2 | 0.7898 | 0.77192 | -0.017874 |  | 0.9 | 1.05 | 0.030446 | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-252 | NP-LUCKY_CR2 | 0.7898 | 0.77192 | -0.017874 |  | 0.9 | 1.05 | 0.030446 | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-254 | NP-LUCKY_CR2 | 0.7898 | 0.77192 | -0.017874 |  | 0.9 | 1.05 | 0.032849 | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-255 | NP-LUCKY_CR2 | 0.7898 | 0.77192 | -0.017874 |  | 0.9 | 1.05 | 0.030095 | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-239 | NP-VALERO_P2 | 0.67523 | 0.65438 | -0.020847 |  | 0.9 | 1.05 | 0.030446 | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-252 | NP-VALERO_P2 | 0.67523 | 0.65438 | -0.020847 |  | 0.9 | 1.05 | 0.030446 | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-254 | NP-VALERO_P2 | 0.67523 | 0.65438 | -0.020847 |  | 0.9 | 1.05 | 0.032849 | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-255 | NP-VALERO_P2 | 0.67523 | 0.65438 | -0.020847 |  | 0.9 | 1.05 | 0.030095 | P12:345:SPS:J12_J13-1::HITCH_BVR:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | ASGI-2024-003 | NP-VALERO_P2 | 0.68345 | 0.66775 | -0.015696 |  | 0.9 | 1.05 | 0.046521 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | ASGI-2024-006 | NP-VALERO_P2 | 0.68345 | 0.66775 | -0.015696 |  | 0.9 | 1.05 | 0.074703 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-015 | NP-VALERO_P2 | 0.68345 | 0.66775 | -0.015696 |  | 0.9 | 1.05 | 0.12365 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-041 | NP-VALERO_P2 | 0.68345 | 0.66775 | -0.015696 |  | 0.9 | 1.05 | 0.1562 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-042 | NP-VALERO_P2 | 0.68345 | 0.66775 | -0.015696 |  | 0.9 | 1.05 | 0.1562 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-043 | NP-VALERO_P2 | 0.68345 | 0.66775 | -0.015696 |  | 0.9 | 1.05 | 0.11064 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-099 | NP-VALERO_P2 | 0.68345 | 0.66775 | -0.015696 |  | 0.9 | 1.05 | 0.10819 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-109 | NP-VALERO_P2 | 0.68345 | 0.66775 | -0.015696 |  | 0.9 | 1.05 | 0.10967 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-143 | NP-VALERO_P2 | 0.68345 | 0.66775 | -0.015696 |  | 0.9 | 1.05 | 0.073716 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-145 | NP-VALERO_P2 | 0.68345 | 0.66775 | -0.015696 |  | 0.9 | 1.05 | 0.073716 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-159 | NP-VALERO_P2 | 0.68345 | 0.66775 | -0.015696 |  | 0.9 | 1.05 | 0.11297 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-221 | NP-VALERO_P2 | 0.68345 | 0.66775 | -0.015696 |  | 0.9 | 1.05 | 0.11247 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-261 | NP-VALERO_P2 | 0.68345 | 0.66775 | -0.015696 |  | 0.9 | 1.05 | 0.12021 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-265 | NP-VALERO_P2 | 0.68345 | 0.66775 | -0.015696 |  | 0.9 | 1.05 | 0.12047 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-280 | NP-VALERO_P2 | 0.68345 | 0.66775 | -0.015696 |  | 0.9 | 1.05 | 0.1183 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-281 | NP-VALERO_P2 | 0.68345 | 0.66775 | -0.015696 |  | 0.9 | 1.05 | 0.11865 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-295 | NP-VALERO_P2 | 0.68345 | 0.66775 | -0.015696 |  | 0.9 | 1.05 | 0.11877 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-303 | NP-VALERO_P2 | 0.68345 | 0.66775 | -0.015696 |  | 0.9 | 1.05 | 0.11076 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-304 | NP-VALERO_P2 | 0.68345 | 0.66775 | -0.015696 |  | 0.9 | 1.05 | 0.11076 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-311 | NP-VALERO_P2 | 0.68345 | 0.66775 | -0.015696 |  | 0.9 | 1.05 | 0.11634 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-317 | NP-VALERO_P2 | 0.68345 | 0.66775 | -0.015696 |  | 0.9 | 1.05 | 0.47052 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-336 | NP-VALERO_P2 | 0.68345 | 0.66775 | -0.015696 |  | 0.9 | 1.05 | 0.12194 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | ASGI-2024-003 | NP-VALERO_P2 | 0.68399 | 0.66833 | -0.015665 |  | 0.9 | 1.05 | 0.035702 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | ASGI-2024-006 | NP-VALERO_P2 | 0.68399 | 0.66833 | -0.015665 |  | 0.9 | 1.05 | 0.053043 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-013 | NP-VALERO_P2 | 0.68399 | 0.66833 | -0.015665 |  | 0.9 | 1.05 | 0.037495 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-015 | NP-VALERO_P2 | 0.68399 | 0.66833 | -0.015665 |  | 0.9 | 1.05 | 0.057538 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-041 | NP-VALERO_P2 | 0.68399 | 0.66833 | -0.015665 |  | 0.9 | 1.05 | 0.059056 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-042 | NP-VALERO_P2 | 0.68399 | 0.66833 | -0.015665 |  | 0.9 | 1.05 | 0.059056 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-043 | NP-VALERO_P2 | 0.68399 | 0.66833 | -0.015665 |  | 0.9 | 1.05 | 0.056962 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-099 | NP-VALERO_P2 | 0.68399 | 0.66833 | -0.015665 |  | 0.9 | 1.05 | 0.056989 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-109 | NP-VALERO_P2 | 0.68399 | 0.66833 | -0.015665 |  | 0.9 | 1.05 | 0.056997 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-128 | NP-VALERO_P2 | 0.68399 | 0.66833 | -0.015665 |  | 0.9 | 1.05 | 0.25306 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-143 | NP-VALERO_P2 | 0.68399 | 0.66833 | -0.015665 |  | 0.9 | 1.05 | 0.051595 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-145 | NP-VALERO_P2 | 0.68399 | 0.66833 | -0.015665 |  | 0.9 | 1.05 | 0.051595 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-154 | NP-VALERO_P2 | 0.68399 | 0.66833 | -0.015665 |  | 0.9 | 1.05 | 0.084292 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-159 | NP-VALERO_P2 | 0.68399 | 0.66833 | -0.015665 |  | 0.9 | 1.05 | 0.057127 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-204 | NP-VALERO_P2 | 0.68399 | 0.66833 | -0.015665 |  | 0.9 | 1.05 | 0.041671 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-219 | NP-VALERO_P2 | 0.68399 | 0.66833 | -0.015665 |  | 0.9 | 1.05 | 0.03293 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-221 | NP-VALERO_P2 | 0.68399 | 0.66833 | -0.015665 |  | 0.9 | 1.05 | 0.057003 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-261 | NP-VALERO_P2 | 0.68399 | 0.66833 | -0.015665 |  | 0.9 | 1.05 | 0.057308 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-265 | NP-VALERO_P2 | 0.68399 | 0.66833 | -0.015665 |  | 0.9 | 1.05 | 0.057324 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-280 | NP-VALERO_P2 | 0.68399 | 0.66833 | -0.015665 |  | 0.9 | 1.05 | 0.057182 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-281 | NP-VALERO_P2 | 0.68399 | 0.66833 | -0.015665 |  | 0.9 | 1.05 | 0.057175 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-295 | NP-VALERO_P2 | 0.68399 | 0.66833 | -0.015665 |  | 0.9 | 1.05 | 0.057109 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-303 | NP-VALERO_P2 | 0.68399 | 0.66833 | -0.015665 |  | 0.9 | 1.05 | 0.056958 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-304 | NP-VALERO_P2 | 0.68399 | 0.66833 | -0.015665 |  | 0.9 | 1.05 | 0.056958 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-311 | NP-VALERO_P2 | 0.68399 | 0.66833 | -0.015665 |  | 0.9 | 1.05 | 0.057138 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-317 | NP-VALERO_P2 | 0.68399 | 0.66833 | -0.015665 |  | 0.9 | 1.05 | 0.10561 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-336 | NP-VALERO_P2 | 0.68399 | 0.66833 | -0.015665 |  | 0.9 | 1.05 | 0.057417 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-338 | NP-VALERO_P2 | 0.68399 | 0.66833 | -0.015665 |  | 0.9 | 1.05 | 0.047162 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-373 | NP-VALERO_P2 | 0.68399 | 0.66833 | -0.015665 |  | 0.9 | 1.05 | 0.030913 | P23:345:OKGE:IF_MICO7302:::EHV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 26SP | V | ASGI-2024-003 | NP-VALERO_P2 | 0.68265 | 0.66762 | -0.015033 |  | 0.9 | 1.05 | 0.046521 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | ASGI-2024-006 | NP-VALERO_P2 | 0.68265 | 0.66762 | -0.015033 |  | 0.9 | 1.05 | 0.074703 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-015 | NP-VALERO_P2 | 0.68265 | 0.66762 | -0.015033 |  | 0.9 | 1.05 | 0.12365 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-041 | NP-VALERO_P2 | 0.68265 | 0.66762 | -0.015033 |  | 0.9 | 1.05 | 0.1562 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-042 | NP-VALERO_P2 | 0.68265 | 0.66762 | -0.015033 |  | 0.9 | 1.05 | 0.1562 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-043 | NP-VALERO_P2 | 0.68265 | 0.66762 | -0.015033 |  | 0.9 | 1.05 | 0.11064 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-099 | NP-VALERO_P2 | 0.68265 | 0.66762 | -0.015033 |  | 0.9 | 1.05 | 0.10819 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-109 | NP-VALERO_P2 | 0.68265 | 0.66762 | -0.015033 |  | 0.9 | 1.05 | 0.10967 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-143 | NP-VALERO_P2 | 0.68265 | 0.66762 | -0.015033 |  | 0.9 | 1.05 | 0.073716 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-145 | NP-VALERO_P2 | 0.68265 | 0.66762 | -0.015033 |  | 0.9 | 1.05 | 0.073716 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-159 | NP-VALERO_P2 | 0.68265 | 0.66762 | -0.015033 |  | 0.9 | 1.05 | 0.11297 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-221 | NP-VALERO_P2 | 0.68265 | 0.66762 | -0.015033 |  | 0.9 | 1.05 | 0.11247 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-261 | NP-VALERO_P2 | 0.68265 | 0.66762 | -0.015033 |  | 0.9 | 1.05 | 0.12021 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-265 | NP-VALERO_P2 | 0.68265 | 0.66762 | -0.015033 |  | 0.9 | 1.05 | 0.12047 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-280 | NP-VALERO_P2 | 0.68265 | 0.66762 | -0.015033 |  | 0.9 | 1.05 | 0.1183 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-281 | NP-VALERO_P2 | 0.68265 | 0.66762 | -0.015033 |  | 0.9 | 1.05 | 0.11865 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-295 | NP-VALERO_P2 | 0.68265 | 0.66762 | -0.015033 |  | 0.9 | 1.05 | 0.11877 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-303 | NP-VALERO_P2 | 0.68265 | 0.66762 | -0.015033 |  | 0.9 | 1.05 | 0.11076 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-304 | NP-VALERO_P2 | 0.68265 | 0.66762 | -0.015033 |  | 0.9 | 1.05 | 0.11076 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-311 | NP-VALERO_P2 | 0.68265 | 0.66762 | -0.015033 |  | 0.9 | 1.05 | 0.11634 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-317 | NP-VALERO_P2 | 0.68265 | 0.66762 | -0.015033 |  | 0.9 | 1.05 | 0.47052 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-336 | NP-VALERO_P2 | 0.68265 | 0.66762 | -0.015033 |  | 0.9 | 1.05 | 0.12194 | P52:345:AEPW:NR5O.K.U.-7:::: | None
Voltage | 00NR | 2 | 26SP | V | ASGI-2024-003 | NP-VALERO_P2 | 0.68337 | 0.66773 | -0.015631 |  | 0.9 | 1.05 | 0.046521 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | ASGI-2024-006 | NP-VALERO_P2 | 0.68337 | 0.66773 | -0.015631 |  | 0.9 | 1.05 | 0.074703 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-015 | NP-VALERO_P2 | 0.68337 | 0.66773 | -0.015631 |  | 0.9 | 1.05 | 0.12365 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-041 | NP-VALERO_P2 | 0.68337 | 0.66773 | -0.015631 |  | 0.9 | 1.05 | 0.1562 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-042 | NP-VALERO_P2 | 0.68337 | 0.66773 | -0.015631 |  | 0.9 | 1.05 | 0.1562 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-043 | NP-VALERO_P2 | 0.68337 | 0.66773 | -0.015631 |  | 0.9 | 1.05 | 0.11064 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-099 | NP-VALERO_P2 | 0.68337 | 0.66773 | -0.015631 |  | 0.9 | 1.05 | 0.10819 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-109 | NP-VALERO_P2 | 0.68337 | 0.66773 | -0.015631 |  | 0.9 | 1.05 | 0.10967 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-143 | NP-VALERO_P2 | 0.68337 | 0.66773 | -0.015631 |  | 0.9 | 1.05 | 0.073716 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-145 | NP-VALERO_P2 | 0.68337 | 0.66773 | -0.015631 |  | 0.9 | 1.05 | 0.073716 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-159 | NP-VALERO_P2 | 0.68337 | 0.66773 | -0.015631 |  | 0.9 | 1.05 | 0.11297 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-221 | NP-VALERO_P2 | 0.68337 | 0.66773 | -0.015631 |  | 0.9 | 1.05 | 0.11247 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-261 | NP-VALERO_P2 | 0.68337 | 0.66773 | -0.015631 |  | 0.9 | 1.05 | 0.12021 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-265 | NP-VALERO_P2 | 0.68337 | 0.66773 | -0.015631 |  | 0.9 | 1.05 | 0.12047 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-280 | NP-VALERO_P2 | 0.68337 | 0.66773 | -0.015631 |  | 0.9 | 1.05 | 0.1183 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-281 | NP-VALERO_P2 | 0.68337 | 0.66773 | -0.015631 |  | 0.9 | 1.05 | 0.11865 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-295 | NP-VALERO_P2 | 0.68337 | 0.66773 | -0.015631 |  | 0.9 | 1.05 | 0.11877 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-303 | NP-VALERO_P2 | 0.68337 | 0.66773 | -0.015631 |  | 0.9 | 1.05 | 0.11076 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-304 | NP-VALERO_P2 | 0.68337 | 0.66773 | -0.015631 |  | 0.9 | 1.05 | 0.11076 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-311 | NP-VALERO_P2 | 0.68337 | 0.66773 | -0.015631 |  | 0.9 | 1.05 | 0.11634 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-317 | NP-VALERO_P2 | 0.68337 | 0.66773 | -0.015631 |  | 0.9 | 1.05 | 0.47052 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-336 | NP-VALERO_P2 | 0.68337 | 0.66773 | -0.015631 |  | 0.9 | 1.05 | 0.12194 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | None
Voltage | 00NR | 2 | 26SP | V | GEN-2024-374 | STEGALL 4 | 0.95159 | 0.89411 | -0.057476 |  | 0.9 | 1.05 | 0.16876 | P13:345-230.0:UMZ:# N-1 #:: 3WND STEGALL_-MB3-STEGALL_-MB4-STEGALL_-MB9-1 SGQ KV3A:EHV: | Add 78 MVAR switched shunt at DH_CS_EA-TS4 230 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-374 | STEGALL 4 | 0.94785 | 0.89722 | -0.050627 |  | 0.9 | 1.05 | 0.16876 | P12:230.0:UMZ:# N-1 #:: LINE STEGALL 4-STEGALL_-MB4-1 :HV: | Add 78 MVAR switched shunt at DH_CS_EA-TS4 230 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-374 | STEGALL-LNX3 | 0.95159 | 0.89411 | -0.057476 |  | 0.9 | 1.05 | 0.16876 | P13:345-230.0:UMZ:# N-1 #:: 3WND STEGALL_-MB3-STEGALL_-MB4-STEGALL_-MB9-1 SGQ KV3A:EHV: | Add 78 MVAR switched shunt at DH_CS_EA-TS4 230 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-374 | STEGALL-LNX3 | 0.94785 | 0.89722 | -0.050627 |  | 0.9 | 1.05 | 0.16876 | P12:230.0:UMZ:# N-1 #:: LINE STEGALL 4-STEGALL_-MB4-1 :HV: | Add 78 MVAR switched shunt at DH_CS_EA-TS4 230 kV
Voltage | 00NR | 2 | 26SP | V | GEN-2024-374 | STEGALL_-MB4 | 0.9516 | 0.89412 | -0.057477 |  | 0.9 | 1.05 | 0.16876 | P13:345-230.0:UMZ:# N-1 #:: 3WND STEGALL_-MB3-STEGALL_-MB4-STEGALL_-MB9-1 SGQ KV3A:EHV: | Add 78 MVAR switched shunt at DH_CS_EA-TS4 230 kV
Voltage | 03ALL | 2 | 26SP | V | ASGI-2024-003 | DVRSION-WIND | 1.0407 | 1.0725 | 0.031761 |  | 0.92 | 1.05 | 0.033782 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | None
Voltage | 03ALL | 2 | 26SP | V | ASGI-2024-006 | DVRSION-WIND | 1.0407 | 1.0725 | 0.031761 |  | 0.92 | 1.05 | 0.070205 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | 12MILE 4 | 0.98265 | 0.54382 | -0.43883 |  | 0.92 | 1.05 | 0.053331 | P12:138:WFEC:LOCO_MARIETTA:::: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | 12MILE 4 | 0.98265 | 0.54382 | -0.43883 |  | 0.92 | 1.05 | 0.030151 | P12:138:WFEC:LOCO_MARIETTA:::: | None
Voltage | 04ALL | 2 | 26SP | V | ASGI-2024-023 | 12MILE 4 | 0.98228 | 0.54358 | -0.4387 |  | 0.92 | 1.05 | 0.039761 | P52:138:AEPW:NR5O.K.U:::: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | 12MILE 4 | 0.98228 | 0.54358 | -0.4387 |  | 0.92 | 1.05 | 0.042719 | P52:138:AEPW:NR5O.K.U:::: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-068 | 12MILE 4 | 0.98228 | 0.54358 | -0.4387 |  | 0.92 | 1.05 | 0.04207 | P52:138:AEPW:NR5O.K.U:::: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-071 | 12MILE 4 | 0.98228 | 0.54358 | -0.4387 |  | 0.92 | 1.05 | 0.039983 | P52:138:AEPW:NR5O.K.U:::: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | 12MILE 4 | 0.98228 | 0.54358 | -0.4387 |  | 0.92 | 1.05 | 0.030965 | P52:138:AEPW:NR5O.K.U:::: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | 12MILE 4 | 0.98228 | 0.54358 | -0.4387 |  | 0.92 | 1.05 | 0.031268 | P52:138:AEPW:NR5O.K.U:::: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-122 | 12MILE 4 | 0.98228 | 0.54358 | -0.4387 |  | 0.92 | 1.05 | 0.037431 | P52:138:AEPW:NR5O.K.U:::: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-177 | 12MILE 4 | 0.98228 | 0.54358 | -0.4387 |  | 0.92 | 1.05 | 0.036839 | P52:138:AEPW:NR5O.K.U:::: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-178 | 12MILE 4 | 0.98228 | 0.54358 | -0.4387 |  | 0.92 | 1.05 | 0.038118 | P52:138:AEPW:NR5O.K.U:::: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | 12MILE 4 | 0.98228 | 0.54358 | -0.4387 |  | 0.92 | 1.05 | 0.054212 | P52:138:AEPW:NR5O.K.U:::: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | 12MILE 4 | 0.98228 | 0.54358 | -0.4387 |  | 0.92 | 1.05 | 0.050188 | P52:138:AEPW:NR5O.K.U:::: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-220 | 12MILE 4 | 0.98228 | 0.54358 | -0.4387 |  | 0.92 | 1.05 | 0.039815 | P52:138:AEPW:NR5O.K.U:::: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-232 | 12MILE 4 | 0.98228 | 0.54358 | -0.4387 |  | 0.92 | 1.05 | 0.035865 | P52:138:AEPW:NR5O.K.U:::: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | 12MILE 4 | 0.98228 | 0.54358 | -0.4387 |  | 0.92 | 1.05 | 0.035923 | P52:138:AEPW:NR5O.K.U:::: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | 12MILE 4 | 0.98228 | 0.54358 | -0.4387 |  | 0.92 | 1.05 | 0.042719 | P52:138:AEPW:NR5O.K.U:::: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | 12MILE 4 | 0.98228 | 0.54358 | -0.4387 |  | 0.92 | 1.05 | 0.031618 | P52:138:AEPW:NR5O.K.U:::: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | 12MILE 4 | 0.98228 | 0.54358 | -0.4387 |  | 0.92 | 1.05 | 0.03789 | P52:138:AEPW:NR5O.K.U:::: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | 12MILE 4 | 0.98228 | 0.54358 | -0.4387 |  | 0.92 | 1.05 | 0.03789 | P52:138:AEPW:NR5O.K.U:::: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | 12MILE 4 | 0.98228 | 0.54358 | -0.4387 |  | 0.92 | 1.05 | 0.031295 | P52:138:AEPW:NR5O.K.U:::: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | 12MILE 4 | 0.98228 | 0.54358 | -0.4387 |  | 0.92 | 1.05 | 0.05841 | P52:138:AEPW:NR5O.K.U:::: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | 12MILE 4 | 0.98228 | 0.54358 | -0.4387 |  | 0.92 | 1.05 | 0.03942 | P52:138:AEPW:NR5O.K.U:::: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | 12MILE 4 | 0.98228 | 0.54358 | -0.4387 |  | 0.92 | 1.05 | 0.04269 | P52:138:AEPW:NR5O.K.U:::: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | 12MILE 4 | 0.98228 | 0.54358 | -0.4387 |  | 0.92 | 1.05 | 0.050356 | P52:138:AEPW:NR5O.K.U:::: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-376 | 12MILE 4 | 0.98228 | 0.54358 | -0.4387 |  | 0.92 | 1.05 | 0.034317 | P52:138:AEPW:NR5O.K.U:::: | None
Voltage | 04ALL | 2 | 26SP | V | ASGI-2024-023 | 12MILE 4 | 0.98242 | 0.54335 | -0.43907 |  | 0.92 | 1.05 | 0.031024 | P42:345:OKGE:SB_GRIN7312:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | 12MILE 4 | 0.98242 | 0.54335 | -0.43907 |  | 0.92 | 1.05 | 0.033117 | P42:345:OKGE:SB_GRIN7312:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-068 | 12MILE 4 | 0.98242 | 0.54335 | -0.43907 |  | 0.92 | 1.05 | 0.032634 | P42:345:OKGE:SB_GRIN7312:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-071 | 12MILE 4 | 0.98242 | 0.54335 | -0.43907 |  | 0.92 | 1.05 | 0.031036 | P42:345:OKGE:SB_GRIN7312:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | 12MILE 4 | 0.98242 | 0.54335 | -0.43907 |  | 0.92 | 1.05 | 0.12176 | P42:345:OKGE:SB_GRIN7312:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-220 | 12MILE 4 | 0.98242 | 0.54335 | -0.43907 |  | 0.92 | 1.05 | 0.030909 | P42:345:OKGE:SB_GRIN7312:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | 12MILE 4 | 0.98242 | 0.54335 | -0.43907 |  | 0.92 | 1.05 | 0.071258 | P42:345:OKGE:SB_GRIN7312:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | 12MILE 4 | 0.98242 | 0.54335 | -0.43907 |  | 0.92 | 1.05 | 0.033117 | P42:345:OKGE:SB_GRIN7312:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | 12MILE 4 | 0.98242 | 0.54335 | -0.43907 |  | 0.92 | 1.05 | 0.1624 | P42:345:OKGE:SB_GRIN7312:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | 12MILE 4 | 0.98242 | 0.54335 | -0.43907 |  | 0.92 | 1.05 | 0.099752 | P42:345:OKGE:SB_GRIN7312:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | 12MILE 4 | 0.98242 | 0.54335 | -0.43907 |  | 0.92 | 1.05 | 0.099752 | P42:345:OKGE:SB_GRIN7312:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | 12MILE 4 | 0.98242 | 0.54335 | -0.43907 |  | 0.92 | 1.05 | 0.037142 | P42:345:OKGE:SB_GRIN7312:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | 12MILE 4 | 0.98242 | 0.54335 | -0.43907 |  | 0.92 | 1.05 | 0.030865 | P42:345:OKGE:SB_GRIN7312:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | ASGI-2024-023 | 12MILE 4 | 0.98242 | 0.54335 | -0.43907 |  | 0.92 | 1.05 | 0.031024 | P42:345:OKGE:SB_GRIN7382:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | 12MILE 4 | 0.98242 | 0.54335 | -0.43907 |  | 0.92 | 1.05 | 0.033117 | P42:345:OKGE:SB_GRIN7382:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-068 | 12MILE 4 | 0.98242 | 0.54335 | -0.43907 |  | 0.92 | 1.05 | 0.032634 | P42:345:OKGE:SB_GRIN7382:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-071 | 12MILE 4 | 0.98242 | 0.54335 | -0.43907 |  | 0.92 | 1.05 | 0.031036 | P42:345:OKGE:SB_GRIN7382:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | 12MILE 4 | 0.98242 | 0.54335 | -0.43907 |  | 0.92 | 1.05 | 0.12176 | P42:345:OKGE:SB_GRIN7382:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-220 | 12MILE 4 | 0.98242 | 0.54335 | -0.43907 |  | 0.92 | 1.05 | 0.030909 | P42:345:OKGE:SB_GRIN7382:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | 12MILE 4 | 0.98242 | 0.54335 | -0.43907 |  | 0.92 | 1.05 | 0.071258 | P42:345:OKGE:SB_GRIN7382:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | 12MILE 4 | 0.98242 | 0.54335 | -0.43907 |  | 0.92 | 1.05 | 0.033117 | P42:345:OKGE:SB_GRIN7382:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | 12MILE 4 | 0.98242 | 0.54335 | -0.43907 |  | 0.92 | 1.05 | 0.1624 | P42:345:OKGE:SB_GRIN7382:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | 12MILE 4 | 0.98242 | 0.54335 | -0.43907 |  | 0.92 | 1.05 | 0.099752 | P42:345:OKGE:SB_GRIN7382:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | 12MILE 4 | 0.98242 | 0.54335 | -0.43907 |  | 0.92 | 1.05 | 0.099752 | P42:345:OKGE:SB_GRIN7382:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | 12MILE 4 | 0.98242 | 0.54335 | -0.43907 |  | 0.92 | 1.05 | 0.037142 | P42:345:OKGE:SB_GRIN7382:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | 12MILE 4 | 0.98242 | 0.54335 | -0.43907 |  | 0.92 | 1.05 | 0.030865 | P42:345:OKGE:SB_GRIN7382:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | 12MILE 4 | 0.98264 | 0.54388 | -0.43876 |  | 0.92 | 1.05 | 0.053331 | Single 520988 MARIETA4 138 521061 SWILSON4 138 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | 12MILE 4 | 0.98264 | 0.54388 | -0.43876 |  | 0.92 | 1.05 | 0.030151 | Single 520988 MARIETA4 138 521061 SWILSON4 138 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | 15THSTRT | 0.99147 | 0.92083 | -0.070644 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | 15THSTRT | 0.99147 | 0.92083 | -0.070644 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | 15THSTRT | 0.99147 | 0.92083 | -0.070644 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | 15THSTRT | 0.99147 | 0.92083 | -0.070644 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | 15THSTRT | 0.99147 | 0.92083 | -0.070644 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | 15THSTRT | 0.99147 | 0.92083 | -0.070644 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | 15THSTRT | 0.99147 | 0.92083 | -0.070644 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | 15THSTRT | 0.99147 | 0.92083 | -0.070644 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | 15THSTRT | 0.99147 | 0.92083 | -0.070644 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | 15THSTRT | 0.99147 | 0.92083 | -0.070644 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | 15THSTRT | 0.99147 | 0.92083 | -0.070644 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | 15THSTRT | 0.99147 | 0.92083 | -0.070644 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | 15THSTRT | 0.99147 | 0.92083 | -0.070644 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | 15THSTRT | 0.99147 | 0.92083 | -0.070644 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | 15THSTRT | 0.99147 | 0.92083 | -0.070644 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | 15THSTRT | 0.99147 | 0.92083 | -0.070644 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | 15THSTRT | 0.99147 | 0.92083 | -0.070644 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | 15THSTRT | 0.99147 | 0.92083 | -0.070644 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | 15THSTRT | 0.99147 | 0.92083 | -0.070644 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | 15THSTRT | 0.99147 | 0.92083 | -0.070644 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | 15THSTRT | 0.99147 | 0.92083 | -0.070644 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | 15THSTRT | 0.99147 | 0.92083 | -0.070644 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | 15THSTRT | 0.99147 | 0.92083 | -0.070644 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | 15THSTRT | 0.99147 | 0.92083 | -0.070644 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | 15THSTRT | 0.99147 | 0.92083 | -0.070644 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | 4CORNER3 | 0.98191 | 0.91849 | -0.063424 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | 4CORNER3 | 0.98191 | 0.91849 | -0.063424 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | 4CORNER3 | 0.98191 | 0.91849 | -0.063424 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | 4CORNER3 | 0.98191 | 0.91849 | -0.063424 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | 4CORNER3 | 0.98191 | 0.91849 | -0.063424 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | 4CORNER3 | 0.98191 | 0.91849 | -0.063424 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | 4CORNER3 | 0.98191 | 0.91849 | -0.063424 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | 4CORNER3 | 0.98191 | 0.91849 | -0.063424 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | 4CORNER3 | 0.98191 | 0.91849 | -0.063424 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | 4CORNER3 | 0.98191 | 0.91849 | -0.063424 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | 4CORNER3 | 0.98191 | 0.91849 | -0.063424 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | 4CORNER3 | 0.98191 | 0.91849 | -0.063424 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | 4CORNER3 | 0.98191 | 0.91849 | -0.063424 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | 4CORNER3 | 0.98191 | 0.91849 | -0.063424 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | 4CORNER3 | 0.98191 | 0.91849 | -0.063424 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | 4CORNER3 | 0.98191 | 0.91849 | -0.063424 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | 4CORNER3 | 0.98191 | 0.91849 | -0.063424 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | 4CORNER3 | 0.98191 | 0.91849 | -0.063424 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | 4CORNER3 | 0.98191 | 0.91849 | -0.063424 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | 4CORNER3 | 0.98191 | 0.91849 | -0.063424 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | 4CORNER3 | 0.98191 | 0.91849 | -0.063424 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | 4CORNER3 | 0.98191 | 0.91849 | -0.063424 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | 4CORNER3 | 0.98191 | 0.91849 | -0.063424 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | 4CORNER3 | 0.98191 | 0.91849 | -0.063424 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | 4CORNER3 | 0.98191 | 0.91849 | -0.063424 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | 87TH 7 | 0.9789 | 0.94981 | -0.029082 |  | 0.95 | 1.05 | 0.036307 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | 87TH 7 | 0.9789 | 0.94981 | -0.029082 |  | 0.95 | 1.05 | 0.052743 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | 87TH 7 | 0.9789 | 0.94981 | -0.029082 |  | 0.95 | 1.05 | 0.039345 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | 87TH 7 | 0.9789 | 0.94981 | -0.029082 |  | 0.95 | 1.05 | 0.031366 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | 87TH 7 | 0.9789 | 0.94981 | -0.029082 |  | 0.95 | 1.05 | 0.041888 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | 87TH 7 | 0.9789 | 0.94981 | -0.029082 |  | 0.95 | 1.05 | 0.038797 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | 87TH 7 | 0.9789 | 0.94981 | -0.029082 |  | 0.95 | 1.05 | 0.030557 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | 87TH 7 | 0.9789 | 0.94981 | -0.029082 |  | 0.95 | 1.05 | 0.067346 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | 87TH 7 | 0.9789 | 0.94981 | -0.029082 |  | 0.95 | 1.05 | 0.030557 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | 87TH 7 | 0.9789 | 0.94981 | -0.029082 |  | 0.95 | 1.05 | 0.030851 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | 87TH 7 | 0.9789 | 0.94981 | -0.029082 |  | 0.95 | 1.05 | 0.032161 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | 87TH 7 | 0.9789 | 0.94981 | -0.029082 |  | 0.95 | 1.05 | 0.04067 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | 87TH 7 | 0.9789 | 0.94981 | -0.029082 |  | 0.95 | 1.05 | 0.040569 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | 87TH 7 | 0.9789 | 0.94981 | -0.029082 |  | 0.95 | 1.05 | 0.03086 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | 87TH 7 | 0.9789 | 0.94981 | -0.029082 |  | 0.95 | 1.05 | 0.033223 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | 87TH 7 | 0.9789 | 0.94981 | -0.029082 |  | 0.95 | 1.05 | 0.033733 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | 87TH 7 | 0.97455 | 0.94053 | -0.03402 |  | 0.95 | 1.05 | 0.036307 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | 87TH 7 | 0.97455 | 0.94053 | -0.03402 |  | 0.95 | 1.05 | 0.052743 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | 87TH 7 | 0.97455 | 0.94053 | -0.03402 |  | 0.95 | 1.05 | 0.039345 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | 87TH 7 | 0.97455 | 0.94053 | -0.03402 |  | 0.95 | 1.05 | 0.031366 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | 87TH 7 | 0.97455 | 0.94053 | -0.03402 |  | 0.95 | 1.05 | 0.041888 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | 87TH 7 | 0.97455 | 0.94053 | -0.03402 |  | 0.95 | 1.05 | 0.038797 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | 87TH 7 | 0.97455 | 0.94053 | -0.03402 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | 87TH 7 | 0.97455 | 0.94053 | -0.03402 |  | 0.95 | 1.05 | 0.067346 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | 87TH 7 | 0.97455 | 0.94053 | -0.03402 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | 87TH 7 | 0.97455 | 0.94053 | -0.03402 |  | 0.95 | 1.05 | 0.030851 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | 87TH 7 | 0.97455 | 0.94053 | -0.03402 |  | 0.95 | 1.05 | 0.032161 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | 87TH 7 | 0.97455 | 0.94053 | -0.03402 |  | 0.95 | 1.05 | 0.04067 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | 87TH 7 | 0.97455 | 0.94053 | -0.03402 |  | 0.95 | 1.05 | 0.040569 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | 87TH 7 | 0.97455 | 0.94053 | -0.03402 |  | 0.95 | 1.05 | 0.03086 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | 87TH 7 | 0.97455 | 0.94053 | -0.03402 |  | 0.95 | 1.05 | 0.033223 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | 87TH 7 | 0.97455 | 0.94053 | -0.03402 |  | 0.95 | 1.05 | 0.033733 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | 87TH 7 | 0.98216 | 0.94313 | -0.039031 |  | 0.95 | 1.05 | 0.036307 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | 87TH 7 | 0.98216 | 0.94313 | -0.039031 |  | 0.95 | 1.05 | 0.052743 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | 87TH 7 | 0.98216 | 0.94313 | -0.039031 |  | 0.95 | 1.05 | 0.039345 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | 87TH 7 | 0.98216 | 0.94313 | -0.039031 |  | 0.95 | 1.05 | 0.031366 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | 87TH 7 | 0.98216 | 0.94313 | -0.039031 |  | 0.95 | 1.05 | 0.041888 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | 87TH 7 | 0.98216 | 0.94313 | -0.039031 |  | 0.95 | 1.05 | 0.038797 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | 87TH 7 | 0.98216 | 0.94313 | -0.039031 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | 87TH 7 | 0.98216 | 0.94313 | -0.039031 |  | 0.95 | 1.05 | 0.067346 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | 87TH 7 | 0.98216 | 0.94313 | -0.039031 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | 87TH 7 | 0.98216 | 0.94313 | -0.039031 |  | 0.95 | 1.05 | 0.030851 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | 87TH 7 | 0.98216 | 0.94313 | -0.039031 |  | 0.95 | 1.05 | 0.032161 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | 87TH 7 | 0.98216 | 0.94313 | -0.039031 |  | 0.95 | 1.05 | 0.04067 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | 87TH 7 | 0.98216 | 0.94313 | -0.039031 |  | 0.95 | 1.05 | 0.040569 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | 87TH 7 | 0.98216 | 0.94313 | -0.039031 |  | 0.95 | 1.05 | 0.03086 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | 87TH 7 | 0.98216 | 0.94313 | -0.039031 |  | 0.95 | 1.05 | 0.033223 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | 87TH 7 | 0.98216 | 0.94313 | -0.039031 |  | 0.95 | 1.05 | 0.033733 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | 87TH 7 | 0.98746 | 0.93521 | -0.052243 |  | 0.95 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | 87TH 7 | 0.98746 | 0.93521 | -0.052243 |  | 0.95 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | 87TH 7 | 0.98746 | 0.93521 | -0.052243 |  | 0.95 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | 87TH 7 | 0.98746 | 0.93521 | -0.052243 |  | 0.95 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | 87TH 7 | 0.98746 | 0.93521 | -0.052243 |  | 0.95 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | 87TH 7 | 0.98746 | 0.93521 | -0.052243 |  | 0.95 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | 87TH 7 | 0.98746 | 0.93521 | -0.052243 |  | 0.95 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | 87TH 7 | 0.98746 | 0.93521 | -0.052243 |  | 0.95 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | 87TH 7 | 0.98746 | 0.93521 | -0.052243 |  | 0.95 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | 87TH 7 | 0.98746 | 0.93521 | -0.052243 |  | 0.95 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | 87TH 7 | 0.98746 | 0.93521 | -0.052243 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | 87TH 7 | 0.98746 | 0.93521 | -0.052243 |  | 0.95 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | 87TH 7 | 0.98746 | 0.93521 | -0.052243 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | 87TH 7 | 0.98746 | 0.93521 | -0.052243 |  | 0.95 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | 87TH 7 | 0.98746 | 0.93521 | -0.052243 |  | 0.95 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | 87TH 7 | 0.98746 | 0.93521 | -0.052243 |  | 0.95 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | 87TH 7 | 0.98746 | 0.93521 | -0.052243 |  | 0.95 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | 87TH 7 | 0.98746 | 0.93521 | -0.052243 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | 87TH 7 | 0.98746 | 0.93521 | -0.052243 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | 87TH 7 | 0.98746 | 0.93521 | -0.052243 |  | 0.95 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | 87TH 7 | 0.98746 | 0.93521 | -0.052243 |  | 0.95 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | 87TH 7 | 0.98746 | 0.93521 | -0.052243 |  | 0.95 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | 87TH 7 | 0.98746 | 0.93521 | -0.052243 |  | 0.95 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | 87TH 7 | 0.98746 | 0.93521 | -0.052243 |  | 0.95 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | 87TH 7 | 0.98746 | 0.93521 | -0.052243 |  | 0.95 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | 87TH 7 | 0.97834 | 0.94865 | -0.029686 |  | 0.95 | 1.05 | 0.036307 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | 87TH 7 | 0.97834 | 0.94865 | -0.029686 |  | 0.95 | 1.05 | 0.052743 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | 87TH 7 | 0.97834 | 0.94865 | -0.029686 |  | 0.95 | 1.05 | 0.039345 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | 87TH 7 | 0.97834 | 0.94865 | -0.029686 |  | 0.95 | 1.05 | 0.031366 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | 87TH 7 | 0.97834 | 0.94865 | -0.029686 |  | 0.95 | 1.05 | 0.041888 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | 87TH 7 | 0.97834 | 0.94865 | -0.029686 |  | 0.95 | 1.05 | 0.038797 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | 87TH 7 | 0.97834 | 0.94865 | -0.029686 |  | 0.95 | 1.05 | 0.030557 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | 87TH 7 | 0.97834 | 0.94865 | -0.029686 |  | 0.95 | 1.05 | 0.067346 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | 87TH 7 | 0.97834 | 0.94865 | -0.029686 |  | 0.95 | 1.05 | 0.030557 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | 87TH 7 | 0.97834 | 0.94865 | -0.029686 |  | 0.95 | 1.05 | 0.030851 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | 87TH 7 | 0.97834 | 0.94865 | -0.029686 |  | 0.95 | 1.05 | 0.032161 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | 87TH 7 | 0.97834 | 0.94865 | -0.029686 |  | 0.95 | 1.05 | 0.04067 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | 87TH 7 | 0.97834 | 0.94865 | -0.029686 |  | 0.95 | 1.05 | 0.040569 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | 87TH 7 | 0.97834 | 0.94865 | -0.029686 |  | 0.95 | 1.05 | 0.03086 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | 87TH 7 | 0.97834 | 0.94865 | -0.029686 |  | 0.95 | 1.05 | 0.033223 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | 87TH 7 | 0.97834 | 0.94865 | -0.029686 |  | 0.95 | 1.05 | 0.033733 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | ADRIAN 5 | 0.98687 | 0.92823 | -0.058645 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | ADRIAN 5 | 0.98687 | 0.92823 | -0.058645 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | ADRIAN 5 | 0.98687 | 0.92823 | -0.058645 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | ADRIAN 5 | 0.98687 | 0.92823 | -0.058645 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | ADRIAN 5 | 0.98687 | 0.92823 | -0.058645 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | ADRIAN 5 | 0.98687 | 0.92823 | -0.058645 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | ADRIAN 5 | 0.98687 | 0.92823 | -0.058645 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | ADRIAN 5 | 0.98687 | 0.92823 | -0.058645 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | ADRIAN 5 | 0.98687 | 0.92823 | -0.058645 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | ADRIAN 5 | 0.98687 | 0.92823 | -0.058645 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | ADRIAN 5 | 0.98687 | 0.92823 | -0.058645 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | ADRIAN 5 | 0.98687 | 0.92823 | -0.058645 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | ADRIAN 5 | 0.98687 | 0.92823 | -0.058645 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | ADRIAN 5 | 0.98687 | 0.92823 | -0.058645 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | ADRIAN 5 | 0.98687 | 0.92823 | -0.058645 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | ADRIAN 5 | 0.98687 | 0.92823 | -0.058645 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | ADRIAN 5 | 0.98687 | 0.92823 | -0.058645 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | ADRIAN 5 | 0.98687 | 0.92823 | -0.058645 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | ADRIAN 5 | 0.98687 | 0.92823 | -0.058645 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | ADRIAN 5 | 0.98687 | 0.92823 | -0.058645 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | ADRIAN 5 | 0.98687 | 0.92823 | -0.058645 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | ADRIAN 5 | 0.98687 | 0.92823 | -0.058645 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | ADRIAN 5 | 0.98687 | 0.92823 | -0.058645 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | ADRIAN 5 | 0.98687 | 0.92823 | -0.058645 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | ADRIAN 5 | 0.98687 | 0.92823 | -0.058645 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | ASGI-2024-023 | ALTAMNS2 | 0.9466 | 0.8962 | -0.050403 |  | 0.93 | 1.05 | 0.079962 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | ALTAMNS2 | 0.9466 | 0.8962 | -0.050403 |  | 0.93 | 1.05 | 0.065323 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-068 | ALTAMNS2 | 0.9466 | 0.8962 | -0.050403 |  | 0.93 | 1.05 | 0.067422 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-071 | ALTAMNS2 | 0.9466 | 0.8962 | -0.050403 |  | 0.93 | 1.05 | 0.074668 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | ALTAMNS2 | 0.9466 | 0.8962 | -0.050403 |  | 0.93 | 1.05 | 0.053027 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-122 | ALTAMNS2 | 0.9466 | 0.8962 | -0.050403 |  | 0.93 | 1.05 | 0.082926 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-177 | ALTAMNS2 | 0.9466 | 0.8962 | -0.050403 |  | 0.93 | 1.05 | 0.084694 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-178 | ALTAMNS2 | 0.9466 | 0.8962 | -0.050403 |  | 0.93 | 1.05 | 0.078867 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | ALTAMNS2 | 0.9466 | 0.8962 | -0.050403 |  | 0.93 | 1.05 | 0.031571 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-220 | ALTAMNS2 | 0.9466 | 0.8962 | -0.050403 |  | 0.93 | 1.05 | 0.075331 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-232 | ALTAMNS2 | 0.9466 | 0.8962 | -0.050403 |  | 0.93 | 1.05 | 0.078906 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | ALTAMNS2 | 0.9466 | 0.8962 | -0.050403 |  | 0.93 | 1.05 | 0.065323 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | ALTAMNS2 | 0.9466 | 0.8962 | -0.050403 |  | 0.93 | 1.05 | 0.03431 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | ALTAMNS2 | 0.9466 | 0.8962 | -0.050403 |  | 0.93 | 1.05 | 0.031504 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | ALTAMNS2 | 0.9466 | 0.8962 | -0.050403 |  | 0.93 | 1.05 | 0.031504 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | ALTAMNS2 | 0.9466 | 0.8962 | -0.050403 |  | 0.93 | 1.05 | 0.030663 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | ALTAMNS2 | 0.9466 | 0.8962 | -0.050403 |  | 0.93 | 1.05 | 0.04269 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-376 | ALTAMNS2 | 0.9466 | 0.8962 | -0.050403 |  | 0.93 | 1.05 | 0.082476 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | ASGI-2024-023 | ALTAMNS2 | 0.94745 | 0.89952 | -0.047926 |  | 0.93 | 1.05 | 0.10682 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | ALTAMNS2 | 0.94745 | 0.89952 | -0.047926 |  | 0.93 | 1.05 | 0.084049 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-068 | ALTAMNS2 | 0.94745 | 0.89952 | -0.047926 |  | 0.93 | 1.05 | 0.087538 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-071 | ALTAMNS2 | 0.94745 | 0.89952 | -0.047926 |  | 0.93 | 1.05 | 0.099263 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | ALTAMNS2 | 0.94745 | 0.89952 | -0.047926 |  | 0.93 | 1.05 | 0.088785 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-122 | ALTAMNS2 | 0.94745 | 0.89952 | -0.047926 |  | 0.93 | 1.05 | 0.11321 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-177 | ALTAMNS2 | 0.94745 | 0.89952 | -0.047926 |  | 0.93 | 1.05 | 0.11622 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-178 | ALTAMNS2 | 0.94745 | 0.89952 | -0.047926 |  | 0.93 | 1.05 | 0.10702 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | ALTAMNS2 | 0.94745 | 0.89952 | -0.047926 |  | 0.93 | 1.05 | 0.031044 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-220 | ALTAMNS2 | 0.94745 | 0.89952 | -0.047926 |  | 0.93 | 1.05 | 0.10032 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-232 | ALTAMNS2 | 0.94745 | 0.89952 | -0.047926 |  | 0.93 | 1.05 | 0.10939 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | ALTAMNS2 | 0.94745 | 0.89952 | -0.047926 |  | 0.93 | 1.05 | 0.036829 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | ALTAMNS2 | 0.94745 | 0.89952 | -0.047926 |  | 0.93 | 1.05 | 0.084049 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | ALTAMNS2 | 0.94745 | 0.89952 | -0.047926 |  | 0.93 | 1.05 | 0.053387 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | ALTAMNS2 | 0.94745 | 0.89952 | -0.047926 |  | 0.93 | 1.05 | 0.042012 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | ALTAMNS2 | 0.94745 | 0.89952 | -0.047926 |  | 0.93 | 1.05 | 0.042012 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | ALTAMNS2 | 0.94745 | 0.89952 | -0.047926 |  | 0.93 | 1.05 | 0.031418 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | ALTAMNS2 | 0.94745 | 0.89952 | -0.047926 |  | 0.93 | 1.05 | 0.030073 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | ALTAMNS2 | 0.94745 | 0.89952 | -0.047926 |  | 0.93 | 1.05 | 0.047594 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-376 | ALTAMNS2 | 0.94745 | 0.89952 | -0.047926 |  | 0.93 | 1.05 | 0.11583 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | ALTAMNS2 | 0.94805 | 0.89859 | -0.049464 |  | 0.93 | 1.05 | 0.035768 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | ALTAMNS2 | 0.94805 | 0.89859 | -0.049464 |  | 0.93 | 1.05 | 0.088718 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | ALTAMNS2 | 0.94805 | 0.89859 | -0.049464 |  | 0.93 | 1.05 | 0.031473 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | ALTAMNS2 | 0.94805 | 0.89859 | -0.049464 |  | 0.93 | 1.05 | 0.034941 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | ALTAMNS2 | 0.94805 | 0.89859 | -0.049464 |  | 0.93 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | ALTAMNS2 | 0.94805 | 0.89859 | -0.049464 |  | 0.93 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | ALTAMNS2 | 0.94805 | 0.89859 | -0.049464 |  | 0.93 | 1.05 | 0.049224 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | ALTAMNS2 | 0.94805 | 0.89859 | -0.049464 |  | 0.93 | 1.05 | 0.038981 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | ALTAMNS2 | 0.94805 | 0.89859 | -0.049464 |  | 0.93 | 1.05 | 0.040399 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | ALTAMNS2 | 0.94805 | 0.89859 | -0.049464 |  | 0.93 | 1.05 | 0.031912 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | ALTAMNS2 | 0.94805 | 0.89859 | -0.049464 |  | 0.93 | 1.05 | 0.034127 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | ALTAMNS2 | 0.94805 | 0.89859 | -0.049464 |  | 0.93 | 1.05 | 0.047318 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | ALTAMNS2 | 0.94497 | 0.89222 | -0.052752 |  | 0.93 | 1.05 | 0.040439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | ALTAMNS2 | 0.94497 | 0.89222 | -0.052752 |  | 0.93 | 1.05 | 0.034853 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | ALTAMNS2 | 0.94497 | 0.89222 | -0.052752 |  | 0.93 | 1.05 | 0.046783 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | ALTAMNS2 | 0.94497 | 0.89222 | -0.052752 |  | 0.93 | 1.05 | 0.047615 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | ALTAMNS2 | 0.94497 | 0.89222 | -0.052752 |  | 0.93 | 1.05 | 0.034938 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | ALTAMNS2 | 0.94497 | 0.89222 | -0.052752 |  | 0.93 | 1.05 | 0.037875 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | ALTAMNS2 | 0.94497 | 0.89222 | -0.052752 |  | 0.93 | 1.05 | 0.044022 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | ALTAMNS2 | 0.94497 | 0.89222 | -0.052752 |  | 0.93 | 1.05 | 0.030552 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | ALTAMNS2 | 0.94497 | 0.89222 | -0.052752 |  | 0.93 | 1.05 | 0.038531 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | ALTAMNS2 | 0.94497 | 0.89222 | -0.052752 |  | 0.93 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | ALTAMNS2 | 0.94497 | 0.89222 | -0.052752 |  | 0.93 | 1.05 | 0.062491 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | ALTAMNS2 | 0.94497 | 0.89222 | -0.052752 |  | 0.93 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | ALTAMNS2 | 0.94497 | 0.89222 | -0.052752 |  | 0.93 | 1.05 | 0.038129 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | ALTAMNS2 | 0.94497 | 0.89222 | -0.052752 |  | 0.93 | 1.05 | 0.038066 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | ALTAMNS2 | 0.94497 | 0.89222 | -0.052752 |  | 0.93 | 1.05 | 0.034955 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | ALTAMNS2 | 0.94497 | 0.89222 | -0.052752 |  | 0.93 | 1.05 | 0.06281 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | ALTAMNS2 | 0.94497 | 0.89222 | -0.052752 |  | 0.93 | 1.05 | 0.045309 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | ALTAMNS2 | 0.94497 | 0.89222 | -0.052752 |  | 0.93 | 1.05 | 0.035805 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | ALTAMNS2 | 0.94497 | 0.89222 | -0.052752 |  | 0.93 | 1.05 | 0.032364 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | ALTAMNS2 | 0.94497 | 0.89222 | -0.052752 |  | 0.93 | 1.05 | 0.031815 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | ALTAMNS2 | 0.94497 | 0.89222 | -0.052752 |  | 0.93 | 1.05 | 0.033886 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | ALTAMNS2 | 0.94497 | 0.89222 | -0.052752 |  | 0.93 | 1.05 | 0.035554 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | ALTAMNS2 | 0.94639 | 0.87826 | -0.068134 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | ALTAMNS2 | 0.94639 | 0.87826 | -0.068134 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | ALTAMNS2 | 0.94639 | 0.87826 | -0.068134 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | ALTAMNS2 | 0.94639 | 0.87826 | -0.068134 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | ALTAMNS2 | 0.94639 | 0.87826 | -0.068134 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | ALTAMNS2 | 0.94639 | 0.87826 | -0.068134 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | ALTAMNS2 | 0.94639 | 0.87826 | -0.068134 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | ALTAMNS2 | 0.94639 | 0.87826 | -0.068134 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | ALTAMNS2 | 0.94639 | 0.87826 | -0.068134 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | ALTAMNS2 | 0.94639 | 0.87826 | -0.068134 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | ALTAMNS2 | 0.94639 | 0.87826 | -0.068134 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | ALTAMNS2 | 0.94639 | 0.87826 | -0.068134 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | ALTAMNS2 | 0.94639 | 0.87826 | -0.068134 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | ALTAMNS2 | 0.94639 | 0.87826 | -0.068134 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | ALTAMNS2 | 0.94639 | 0.87826 | -0.068134 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | ALTAMNS2 | 0.94639 | 0.87826 | -0.068134 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | ALTAMNS2 | 0.94639 | 0.87826 | -0.068134 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | ALTAMNS2 | 0.94639 | 0.87826 | -0.068134 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | ALTAMNS2 | 0.94639 | 0.87826 | -0.068134 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | ALTAMNS2 | 0.94639 | 0.87826 | -0.068134 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | ALTAMNS2 | 0.94639 | 0.87826 | -0.068134 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | ALTAMNS2 | 0.94639 | 0.87826 | -0.068134 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None