Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | ALTAMNS2 | 0.94639 | 0.87826 | -0.068134 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | ALTAMNS2 | 0.94639 | 0.87826 | -0.068134 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | ALTAMNS2 | 0.94639 | 0.87826 | -0.068134 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | ASGI-2024-023 | ALTAMNT2 | 0.94002 | 0.88923 | -0.050789 |  | 0.93 | 1.05 | 0.079962 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | ALTAMNT2 | 0.94002 | 0.88923 | -0.050789 |  | 0.93 | 1.05 | 0.065323 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-068 | ALTAMNT2 | 0.94002 | 0.88923 | -0.050789 |  | 0.93 | 1.05 | 0.067422 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-071 | ALTAMNT2 | 0.94002 | 0.88923 | -0.050789 |  | 0.93 | 1.05 | 0.074668 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | ALTAMNT2 | 0.94002 | 0.88923 | -0.050789 |  | 0.93 | 1.05 | 0.053027 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-122 | ALTAMNT2 | 0.94002 | 0.88923 | -0.050789 |  | 0.93 | 1.05 | 0.082926 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-177 | ALTAMNT2 | 0.94002 | 0.88923 | -0.050789 |  | 0.93 | 1.05 | 0.084694 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-178 | ALTAMNT2 | 0.94002 | 0.88923 | -0.050789 |  | 0.93 | 1.05 | 0.078867 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | ALTAMNT2 | 0.94002 | 0.88923 | -0.050789 |  | 0.93 | 1.05 | 0.031571 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-220 | ALTAMNT2 | 0.94002 | 0.88923 | -0.050789 |  | 0.93 | 1.05 | 0.075331 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-232 | ALTAMNT2 | 0.94002 | 0.88923 | -0.050789 |  | 0.93 | 1.05 | 0.078906 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | ALTAMNT2 | 0.94002 | 0.88923 | -0.050789 |  | 0.93 | 1.05 | 0.065323 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | ALTAMNT2 | 0.94002 | 0.88923 | -0.050789 |  | 0.93 | 1.05 | 0.03431 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | ALTAMNT2 | 0.94002 | 0.88923 | -0.050789 |  | 0.93 | 1.05 | 0.031504 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | ALTAMNT2 | 0.94002 | 0.88923 | -0.050789 |  | 0.93 | 1.05 | 0.031504 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | ALTAMNT2 | 0.94002 | 0.88923 | -0.050789 |  | 0.93 | 1.05 | 0.030663 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | ALTAMNT2 | 0.94002 | 0.88923 | -0.050789 |  | 0.93 | 1.05 | 0.04269 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-376 | ALTAMNT2 | 0.94002 | 0.88923 | -0.050789 |  | 0.93 | 1.05 | 0.082476 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | ASGI-2024-023 | ALTAMNT2 | 0.94087 | 0.89258 | -0.048292 |  | 0.93 | 1.05 | 0.10682 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | ALTAMNT2 | 0.94087 | 0.89258 | -0.048292 |  | 0.93 | 1.05 | 0.084049 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-068 | ALTAMNT2 | 0.94087 | 0.89258 | -0.048292 |  | 0.93 | 1.05 | 0.087538 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-071 | ALTAMNT2 | 0.94087 | 0.89258 | -0.048292 |  | 0.93 | 1.05 | 0.099263 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | ALTAMNT2 | 0.94087 | 0.89258 | -0.048292 |  | 0.93 | 1.05 | 0.088785 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-122 | ALTAMNT2 | 0.94087 | 0.89258 | -0.048292 |  | 0.93 | 1.05 | 0.11321 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-177 | ALTAMNT2 | 0.94087 | 0.89258 | -0.048292 |  | 0.93 | 1.05 | 0.11622 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-178 | ALTAMNT2 | 0.94087 | 0.89258 | -0.048292 |  | 0.93 | 1.05 | 0.10702 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | ALTAMNT2 | 0.94087 | 0.89258 | -0.048292 |  | 0.93 | 1.05 | 0.031044 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-220 | ALTAMNT2 | 0.94087 | 0.89258 | -0.048292 |  | 0.93 | 1.05 | 0.10032 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-232 | ALTAMNT2 | 0.94087 | 0.89258 | -0.048292 |  | 0.93 | 1.05 | 0.10939 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | ALTAMNT2 | 0.94087 | 0.89258 | -0.048292 |  | 0.93 | 1.05 | 0.036829 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | ALTAMNT2 | 0.94087 | 0.89258 | -0.048292 |  | 0.93 | 1.05 | 0.084049 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | ALTAMNT2 | 0.94087 | 0.89258 | -0.048292 |  | 0.93 | 1.05 | 0.053387 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | ALTAMNT2 | 0.94087 | 0.89258 | -0.048292 |  | 0.93 | 1.05 | 0.042012 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | ALTAMNT2 | 0.94087 | 0.89258 | -0.048292 |  | 0.93 | 1.05 | 0.042012 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | ALTAMNT2 | 0.94087 | 0.89258 | -0.048292 |  | 0.93 | 1.05 | 0.031418 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | ALTAMNT2 | 0.94087 | 0.89258 | -0.048292 |  | 0.93 | 1.05 | 0.030073 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | ALTAMNT2 | 0.94087 | 0.89258 | -0.048292 |  | 0.93 | 1.05 | 0.047594 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-376 | ALTAMNT2 | 0.94087 | 0.89258 | -0.048292 |  | 0.93 | 1.05 | 0.11583 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | ALTAMNT2 | 0.94148 | 0.89164 | -0.049842 |  | 0.93 | 1.05 | 0.035768 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | ALTAMNT2 | 0.94148 | 0.89164 | -0.049842 |  | 0.93 | 1.05 | 0.088718 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | ALTAMNT2 | 0.94148 | 0.89164 | -0.049842 |  | 0.93 | 1.05 | 0.031473 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | ALTAMNT2 | 0.94148 | 0.89164 | -0.049842 |  | 0.93 | 1.05 | 0.034941 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | ALTAMNT2 | 0.94148 | 0.89164 | -0.049842 |  | 0.93 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | ALTAMNT2 | 0.94148 | 0.89164 | -0.049842 |  | 0.93 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | ALTAMNT2 | 0.94148 | 0.89164 | -0.049842 |  | 0.93 | 1.05 | 0.049224 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | ALTAMNT2 | 0.94148 | 0.89164 | -0.049842 |  | 0.93 | 1.05 | 0.038981 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | ALTAMNT2 | 0.94148 | 0.89164 | -0.049842 |  | 0.93 | 1.05 | 0.040399 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | ALTAMNT2 | 0.94148 | 0.89164 | -0.049842 |  | 0.93 | 1.05 | 0.031912 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | ALTAMNT2 | 0.94148 | 0.89164 | -0.049842 |  | 0.93 | 1.05 | 0.034127 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | ALTAMNT2 | 0.94148 | 0.89164 | -0.049842 |  | 0.93 | 1.05 | 0.047318 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | ALTAMNT2 | 0.93838 | 0.88522 | -0.053159 |  | 0.93 | 1.05 | 0.040439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | ALTAMNT2 | 0.93838 | 0.88522 | -0.053159 |  | 0.93 | 1.05 | 0.034853 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | ALTAMNT2 | 0.93838 | 0.88522 | -0.053159 |  | 0.93 | 1.05 | 0.046783 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | ALTAMNT2 | 0.93838 | 0.88522 | -0.053159 |  | 0.93 | 1.05 | 0.047615 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | ALTAMNT2 | 0.93838 | 0.88522 | -0.053159 |  | 0.93 | 1.05 | 0.034938 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | ALTAMNT2 | 0.93838 | 0.88522 | -0.053159 |  | 0.93 | 1.05 | 0.037875 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | ALTAMNT2 | 0.93838 | 0.88522 | -0.053159 |  | 0.93 | 1.05 | 0.044022 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | ALTAMNT2 | 0.93838 | 0.88522 | -0.053159 |  | 0.93 | 1.05 | 0.030552 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | ALTAMNT2 | 0.93838 | 0.88522 | -0.053159 |  | 0.93 | 1.05 | 0.038531 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | ALTAMNT2 | 0.93838 | 0.88522 | -0.053159 |  | 0.93 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | ALTAMNT2 | 0.93838 | 0.88522 | -0.053159 |  | 0.93 | 1.05 | 0.062491 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | ALTAMNT2 | 0.93838 | 0.88522 | -0.053159 |  | 0.93 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | ALTAMNT2 | 0.93838 | 0.88522 | -0.053159 |  | 0.93 | 1.05 | 0.038129 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | ALTAMNT2 | 0.93838 | 0.88522 | -0.053159 |  | 0.93 | 1.05 | 0.038066 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | ALTAMNT2 | 0.93838 | 0.88522 | -0.053159 |  | 0.93 | 1.05 | 0.034955 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | ALTAMNT2 | 0.93838 | 0.88522 | -0.053159 |  | 0.93 | 1.05 | 0.06281 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | ALTAMNT2 | 0.93838 | 0.88522 | -0.053159 |  | 0.93 | 1.05 | 0.045309 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | ALTAMNT2 | 0.93838 | 0.88522 | -0.053159 |  | 0.93 | 1.05 | 0.035805 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | ALTAMNT2 | 0.93838 | 0.88522 | -0.053159 |  | 0.93 | 1.05 | 0.032364 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | ALTAMNT2 | 0.93838 | 0.88522 | -0.053159 |  | 0.93 | 1.05 | 0.031815 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | ALTAMNT2 | 0.93838 | 0.88522 | -0.053159 |  | 0.93 | 1.05 | 0.033886 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | ALTAMNT2 | 0.93838 | 0.88522 | -0.053159 |  | 0.93 | 1.05 | 0.035554 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | ALTAMNT2 | 0.93981 | 0.87114 | -0.068668 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | ALTAMNT2 | 0.93981 | 0.87114 | -0.068668 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | ALTAMNT2 | 0.93981 | 0.87114 | -0.068668 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | ALTAMNT2 | 0.93981 | 0.87114 | -0.068668 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | ALTAMNT2 | 0.93981 | 0.87114 | -0.068668 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | ALTAMNT2 | 0.93981 | 0.87114 | -0.068668 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | ALTAMNT2 | 0.93981 | 0.87114 | -0.068668 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | ALTAMNT2 | 0.93981 | 0.87114 | -0.068668 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | ALTAMNT2 | 0.93981 | 0.87114 | -0.068668 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | ALTAMNT2 | 0.93981 | 0.87114 | -0.068668 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | ALTAMNT2 | 0.93981 | 0.87114 | -0.068668 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | ALTAMNT2 | 0.93981 | 0.87114 | -0.068668 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | ALTAMNT2 | 0.93981 | 0.87114 | -0.068668 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | ALTAMNT2 | 0.93981 | 0.87114 | -0.068668 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | ALTAMNT2 | 0.93981 | 0.87114 | -0.068668 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | ALTAMNT2 | 0.93981 | 0.87114 | -0.068668 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | ALTAMNT2 | 0.93981 | 0.87114 | -0.068668 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | ALTAMNT2 | 0.93981 | 0.87114 | -0.068668 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | ALTAMNT2 | 0.93981 | 0.87114 | -0.068668 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | ALTAMNT2 | 0.93981 | 0.87114 | -0.068668 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | ALTAMNT2 | 0.93981 | 0.87114 | -0.068668 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | ALTAMNT2 | 0.93981 | 0.87114 | -0.068668 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | ALTAMNT2 | 0.93981 | 0.87114 | -0.068668 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | ALTAMNT2 | 0.93981 | 0.87114 | -0.068668 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | ALTAMNT2 | 0.93981 | 0.87114 | -0.068668 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | ALTOONA4 | 0.96575 | 0.92862 | -0.037133 |  | 0.93 | 1.05 | 0.091967 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | ALTOONA4 | 0.96575 | 0.92862 | -0.037133 |  | 0.93 | 1.05 | 0.033356 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | ALTOONA4 | 0.96575 | 0.92862 | -0.037133 |  | 0.93 | 1.05 | 0.044346 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | ALTOONA4 | 0.96575 | 0.92862 | -0.037133 |  | 0.93 | 1.05 | 0.058536 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | ALTOONA4 | 0.96575 | 0.92862 | -0.037133 |  | 0.93 | 1.05 | 0.059327 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | ALTOONA4 | 0.96575 | 0.92862 | -0.037133 |  | 0.93 | 1.05 | 0.041874 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | ALTOONA4 | 0.96575 | 0.92862 | -0.037133 |  | 0.93 | 1.05 | 0.046192 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | ALTOONA4 | 0.96575 | 0.92862 | -0.037133 |  | 0.93 | 1.05 | 0.12754 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | ALTOONA4 | 0.96575 | 0.92862 | -0.037133 |  | 0.93 | 1.05 | 0.047018 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | ALTOONA4 | 0.96575 | 0.92862 | -0.037133 |  | 0.93 | 1.05 | 0.056662 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | ALTOONA4 | 0.96575 | 0.92862 | -0.037133 |  | 0.93 | 1.05 | 0.056662 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | ALTOONA4 | 0.96575 | 0.92862 | -0.037133 |  | 0.93 | 1.05 | 0.056727 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | ALTOONA4 | 0.96575 | 0.92862 | -0.037133 |  | 0.93 | 1.05 | 0.074186 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | ALTOONA4 | 0.96575 | 0.92862 | -0.037133 |  | 0.93 | 1.05 | 0.040839 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | ALTOONA4 | 0.96575 | 0.92862 | -0.037133 |  | 0.93 | 1.05 | 0.03863 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | ALTOONA4 | 0.96575 | 0.92862 | -0.037133 |  | 0.93 | 1.05 | 0.042285 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | ALTOONA4 | 0.96575 | 0.92862 | -0.037133 |  | 0.93 | 1.05 | 0.042285 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | ALTOONA4 | 0.96575 | 0.92862 | -0.037133 |  | 0.93 | 1.05 | 0.050204 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | ALTOONA4 | 0.96575 | 0.92862 | -0.037133 |  | 0.93 | 1.05 | 0.058005 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | ALTOONA4 | 0.96575 | 0.92862 | -0.037133 |  | 0.93 | 1.05 | 0.041735 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | ALTOONA4 | 0.96575 | 0.92862 | -0.037133 |  | 0.93 | 1.05 | 0.057076 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | ALTOONA4 | 0.96575 | 0.92862 | -0.037133 |  | 0.93 | 1.05 | 0.050111 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | ALTOONA4 | 0.96575 | 0.92862 | -0.037133 |  | 0.93 | 1.05 | 0.06491 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | ALTOONA4 | 0.96575 | 0.92862 | -0.037133 |  | 0.93 | 1.05 | 0.051051 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | ALTOONA4 | 0.96575 | 0.92862 | -0.037133 |  | 0.93 | 1.05 | 0.036279 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | ALTOONA4 | 0.97153 | 0.92911 | -0.042424 |  | 0.93 | 1.05 | 0.035768 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | ALTOONA4 | 0.97153 | 0.92911 | -0.042424 |  | 0.93 | 1.05 | 0.088718 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | ALTOONA4 | 0.97153 | 0.92911 | -0.042424 |  | 0.93 | 1.05 | 0.031473 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | ALTOONA4 | 0.97153 | 0.92911 | -0.042424 |  | 0.93 | 1.05 | 0.034941 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | ALTOONA4 | 0.97153 | 0.92911 | -0.042424 |  | 0.93 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | ALTOONA4 | 0.97153 | 0.92911 | -0.042424 |  | 0.93 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | ALTOONA4 | 0.97153 | 0.92911 | -0.042424 |  | 0.93 | 1.05 | 0.049224 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | ALTOONA4 | 0.97153 | 0.92911 | -0.042424 |  | 0.93 | 1.05 | 0.038981 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | ALTOONA4 | 0.97153 | 0.92911 | -0.042424 |  | 0.93 | 1.05 | 0.040399 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | ALTOONA4 | 0.97153 | 0.92911 | -0.042424 |  | 0.93 | 1.05 | 0.031912 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | ALTOONA4 | 0.97153 | 0.92911 | -0.042424 |  | 0.93 | 1.05 | 0.034127 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | ALTOONA4 | 0.97153 | 0.92911 | -0.042424 |  | 0.93 | 1.05 | 0.047318 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | ALTOONA4 | 0.96198 | 0.91743 | -0.044556 |  | 0.93 | 1.05 | 0.040439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | ALTOONA4 | 0.96198 | 0.91743 | -0.044556 |  | 0.93 | 1.05 | 0.034853 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | ALTOONA4 | 0.96198 | 0.91743 | -0.044556 |  | 0.93 | 1.05 | 0.046783 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | ALTOONA4 | 0.96198 | 0.91743 | -0.044556 |  | 0.93 | 1.05 | 0.047615 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | ALTOONA4 | 0.96198 | 0.91743 | -0.044556 |  | 0.93 | 1.05 | 0.034938 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | ALTOONA4 | 0.96198 | 0.91743 | -0.044556 |  | 0.93 | 1.05 | 0.037875 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | ALTOONA4 | 0.96198 | 0.91743 | -0.044556 |  | 0.93 | 1.05 | 0.044022 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | ALTOONA4 | 0.96198 | 0.91743 | -0.044556 |  | 0.93 | 1.05 | 0.030552 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | ALTOONA4 | 0.96198 | 0.91743 | -0.044556 |  | 0.93 | 1.05 | 0.038531 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | ALTOONA4 | 0.96198 | 0.91743 | -0.044556 |  | 0.93 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | ALTOONA4 | 0.96198 | 0.91743 | -0.044556 |  | 0.93 | 1.05 | 0.062491 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | ALTOONA4 | 0.96198 | 0.91743 | -0.044556 |  | 0.93 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | ALTOONA4 | 0.96198 | 0.91743 | -0.044556 |  | 0.93 | 1.05 | 0.038129 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | ALTOONA4 | 0.96198 | 0.91743 | -0.044556 |  | 0.93 | 1.05 | 0.038066 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | ALTOONA4 | 0.96198 | 0.91743 | -0.044556 |  | 0.93 | 1.05 | 0.034955 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | ALTOONA4 | 0.96198 | 0.91743 | -0.044556 |  | 0.93 | 1.05 | 0.06281 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | ALTOONA4 | 0.96198 | 0.91743 | -0.044556 |  | 0.93 | 1.05 | 0.045309 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | ALTOONA4 | 0.96198 | 0.91743 | -0.044556 |  | 0.93 | 1.05 | 0.035805 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | ALTOONA4 | 0.96198 | 0.91743 | -0.044556 |  | 0.93 | 1.05 | 0.032364 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | ALTOONA4 | 0.96198 | 0.91743 | -0.044556 |  | 0.93 | 1.05 | 0.031815 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | ALTOONA4 | 0.96198 | 0.91743 | -0.044556 |  | 0.93 | 1.05 | 0.033886 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | ALTOONA4 | 0.96198 | 0.91743 | -0.044556 |  | 0.93 | 1.05 | 0.035554 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | ALTOONA4 | 0.96705 | 0.9052 | -0.061849 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | ALTOONA4 | 0.96705 | 0.9052 | -0.061849 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | ALTOONA4 | 0.96705 | 0.9052 | -0.061849 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | ALTOONA4 | 0.96705 | 0.9052 | -0.061849 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | ALTOONA4 | 0.96705 | 0.9052 | -0.061849 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | ALTOONA4 | 0.96705 | 0.9052 | -0.061849 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | ALTOONA4 | 0.96705 | 0.9052 | -0.061849 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | ALTOONA4 | 0.96705 | 0.9052 | -0.061849 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | ALTOONA4 | 0.96705 | 0.9052 | -0.061849 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | ALTOONA4 | 0.96705 | 0.9052 | -0.061849 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | ALTOONA4 | 0.96705 | 0.9052 | -0.061849 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | ALTOONA4 | 0.96705 | 0.9052 | -0.061849 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | ALTOONA4 | 0.96705 | 0.9052 | -0.061849 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | ALTOONA4 | 0.96705 | 0.9052 | -0.061849 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | ALTOONA4 | 0.96705 | 0.9052 | -0.061849 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | ALTOONA4 | 0.96705 | 0.9052 | -0.061849 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | ALTOONA4 | 0.96705 | 0.9052 | -0.061849 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | ALTOONA4 | 0.96705 | 0.9052 | -0.061849 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | ALTOONA4 | 0.96705 | 0.9052 | -0.061849 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | ALTOONA4 | 0.96705 | 0.9052 | -0.061849 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | ALTOONA4 | 0.96705 | 0.9052 | -0.061849 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | ALTOONA4 | 0.96705 | 0.9052 | -0.061849 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | ALTOONA4 | 0.96705 | 0.9052 | -0.061849 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | ALTOONA4 | 0.96705 | 0.9052 | -0.061849 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | ALTOONA4 | 0.96705 | 0.9052 | -0.061849 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | ANTIOCH5 | 0.97266 | 0.92817 | -0.044493 |  | 0.93 | 1.05 | 0.036307 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | ANTIOCH5 | 0.97266 | 0.92817 | -0.044493 |  | 0.93 | 1.05 | 0.052743 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | ANTIOCH5 | 0.97266 | 0.92817 | -0.044493 |  | 0.93 | 1.05 | 0.039345 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | ANTIOCH5 | 0.97266 | 0.92817 | -0.044493 |  | 0.93 | 1.05 | 0.031366 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | ANTIOCH5 | 0.97266 | 0.92817 | -0.044493 |  | 0.93 | 1.05 | 0.041888 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | ANTIOCH5 | 0.97266 | 0.92817 | -0.044493 |  | 0.93 | 1.05 | 0.038797 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | ANTIOCH5 | 0.97266 | 0.92817 | -0.044493 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | ANTIOCH5 | 0.97266 | 0.92817 | -0.044493 |  | 0.93 | 1.05 | 0.067346 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | ANTIOCH5 | 0.97266 | 0.92817 | -0.044493 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | ANTIOCH5 | 0.97266 | 0.92817 | -0.044493 |  | 0.93 | 1.05 | 0.030851 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | ANTIOCH5 | 0.97266 | 0.92817 | -0.044493 |  | 0.93 | 1.05 | 0.032161 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | ANTIOCH5 | 0.97266 | 0.92817 | -0.044493 |  | 0.93 | 1.05 | 0.04067 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | ANTIOCH5 | 0.97266 | 0.92817 | -0.044493 |  | 0.93 | 1.05 | 0.040569 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | ANTIOCH5 | 0.97266 | 0.92817 | -0.044493 |  | 0.93 | 1.05 | 0.03086 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | ANTIOCH5 | 0.97266 | 0.92817 | -0.044493 |  | 0.93 | 1.05 | 0.033223 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | ANTIOCH5 | 0.97266 | 0.92817 | -0.044493 |  | 0.93 | 1.05 | 0.033733 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | ANTIOCH5 | 0.98591 | 0.90546 | -0.080443 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | ANTIOCH5 | 0.98591 | 0.90546 | -0.080443 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | ANTIOCH5 | 0.98591 | 0.90546 | -0.080443 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | ANTIOCH5 | 0.98591 | 0.90546 | -0.080443 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | ANTIOCH5 | 0.98591 | 0.90546 | -0.080443 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | ANTIOCH5 | 0.98591 | 0.90546 | -0.080443 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | ANTIOCH5 | 0.98591 | 0.90546 | -0.080443 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | ANTIOCH5 | 0.98591 | 0.90546 | -0.080443 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | ANTIOCH5 | 0.98591 | 0.90546 | -0.080443 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | ANTIOCH5 | 0.98591 | 0.90546 | -0.080443 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | ANTIOCH5 | 0.98591 | 0.90546 | -0.080443 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | ANTIOCH5 | 0.98591 | 0.90546 | -0.080443 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | ANTIOCH5 | 0.98591 | 0.90546 | -0.080443 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | ANTIOCH5 | 0.98591 | 0.90546 | -0.080443 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | ANTIOCH5 | 0.98591 | 0.90546 | -0.080443 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | ANTIOCH5 | 0.98591 | 0.90546 | -0.080443 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | ANTIOCH5 | 0.98591 | 0.90546 | -0.080443 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | ANTIOCH5 | 0.98591 | 0.90546 | -0.080443 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | ANTIOCH5 | 0.98591 | 0.90546 | -0.080443 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | ANTIOCH5 | 0.98591 | 0.90546 | -0.080443 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | ANTIOCH5 | 0.98591 | 0.90546 | -0.080443 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | ANTIOCH5 | 0.98591 | 0.90546 | -0.080443 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | ANTIOCH5 | 0.98591 | 0.90546 | -0.080443 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | ANTIOCH5 | 0.98591 | 0.90546 | -0.080443 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | ANTIOCH5 | 0.98591 | 0.90546 | -0.080443 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | ASG-2018-011 | 1.0107 | 0.91815 | -0.092535 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | ASG-2018-011 | 1.0107 | 0.91815 | -0.092535 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | ASG-2018-011 | 1.0107 | 0.91815 | -0.092535 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | ASG-2018-011 | 1.0107 | 0.91815 | -0.092535 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | ASG-2018-011 | 1.0107 | 0.91815 | -0.092535 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | ASG-2018-011 | 1.0107 | 0.91815 | -0.092535 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | ASG-2018-011 | 1.0107 | 0.91815 | -0.092535 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | ASG-2018-011 | 1.0107 | 0.91815 | -0.092535 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | ASG-2018-011 | 1.0107 | 0.91815 | -0.092535 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | ASG-2018-011 | 1.0107 | 0.91815 | -0.092535 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | ASG-2018-011 | 1.0107 | 0.91815 | -0.092535 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | ASG-2018-011 | 1.0107 | 0.91815 | -0.092535 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | ASG-2018-011 | 1.0107 | 0.91815 | -0.092535 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | ASG-2018-011 | 1.0107 | 0.91815 | -0.092535 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | ASG-2018-011 | 1.0107 | 0.91815 | -0.092535 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | ASG-2018-011 | 1.0107 | 0.91815 | -0.092535 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | ASG-2018-011 | 1.0107 | 0.91815 | -0.092535 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | ASG-2018-011 | 1.0107 | 0.91815 | -0.092535 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | ASG-2018-011 | 1.0107 | 0.91815 | -0.092535 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | ASG-2018-011 | 1.0107 | 0.91815 | -0.092535 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | ASG-2018-011 | 1.0107 | 0.91815 | -0.092535 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | ASG-2018-011 | 1.0107 | 0.91815 | -0.092535 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | ASG-2018-011 | 1.0107 | 0.91815 | -0.092535 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | ASG-2018-011 | 1.0107 | 0.91815 | -0.092535 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | ASG-2018-011 | 1.0107 | 0.91815 | -0.092535 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | ATLNTIC3 | 0.96792 | 0.92353 | -0.044392 |  | 0.93 | 1.05 | 0.036307 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | ATLNTIC3 | 0.96792 | 0.92353 | -0.044392 |  | 0.93 | 1.05 | 0.052743 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | ATLNTIC3 | 0.96792 | 0.92353 | -0.044392 |  | 0.93 | 1.05 | 0.039345 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | ATLNTIC3 | 0.96792 | 0.92353 | -0.044392 |  | 0.93 | 1.05 | 0.031366 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | ATLNTIC3 | 0.96792 | 0.92353 | -0.044392 |  | 0.93 | 1.05 | 0.041888 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | ATLNTIC3 | 0.96792 | 0.92353 | -0.044392 |  | 0.93 | 1.05 | 0.038797 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | ATLNTIC3 | 0.96792 | 0.92353 | -0.044392 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | ATLNTIC3 | 0.96792 | 0.92353 | -0.044392 |  | 0.93 | 1.05 | 0.067346 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | ATLNTIC3 | 0.96792 | 0.92353 | -0.044392 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | ATLNTIC3 | 0.96792 | 0.92353 | -0.044392 |  | 0.93 | 1.05 | 0.030851 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | ATLNTIC3 | 0.96792 | 0.92353 | -0.044392 |  | 0.93 | 1.05 | 0.032161 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | ATLNTIC3 | 0.96792 | 0.92353 | -0.044392 |  | 0.93 | 1.05 | 0.04067 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | ATLNTIC3 | 0.96792 | 0.92353 | -0.044392 |  | 0.93 | 1.05 | 0.040569 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | ATLNTIC3 | 0.96792 | 0.92353 | -0.044392 |  | 0.93 | 1.05 | 0.03086 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | ATLNTIC3 | 0.96792 | 0.92353 | -0.044392 |  | 0.93 | 1.05 | 0.033223 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | ATLNTIC3 | 0.96792 | 0.92353 | -0.044392 |  | 0.93 | 1.05 | 0.033733 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | ATLNTIC3 | 0.97806 | 0.92688 | -0.051176 |  | 0.93 | 1.05 | 0.036307 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | ATLNTIC3 | 0.97806 | 0.92688 | -0.051176 |  | 0.93 | 1.05 | 0.052743 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | ATLNTIC3 | 0.97806 | 0.92688 | -0.051176 |  | 0.93 | 1.05 | 0.039345 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | ATLNTIC3 | 0.97806 | 0.92688 | -0.051176 |  | 0.93 | 1.05 | 0.031366 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | ATLNTIC3 | 0.97806 | 0.92688 | -0.051176 |  | 0.93 | 1.05 | 0.041888 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | ATLNTIC3 | 0.97806 | 0.92688 | -0.051176 |  | 0.93 | 1.05 | 0.038797 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | ATLNTIC3 | 0.97806 | 0.92688 | -0.051176 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | ATLNTIC3 | 0.97806 | 0.92688 | -0.051176 |  | 0.93 | 1.05 | 0.067346 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | ATLNTIC3 | 0.97806 | 0.92688 | -0.051176 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | ATLNTIC3 | 0.97806 | 0.92688 | -0.051176 |  | 0.93 | 1.05 | 0.030851 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | ATLNTIC3 | 0.97806 | 0.92688 | -0.051176 |  | 0.93 | 1.05 | 0.032161 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | ATLNTIC3 | 0.97806 | 0.92688 | -0.051176 |  | 0.93 | 1.05 | 0.04067 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | ATLNTIC3 | 0.97806 | 0.92688 | -0.051176 |  | 0.93 | 1.05 | 0.040569 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | ATLNTIC3 | 0.97806 | 0.92688 | -0.051176 |  | 0.93 | 1.05 | 0.03086 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | ATLNTIC3 | 0.97806 | 0.92688 | -0.051176 |  | 0.93 | 1.05 | 0.033223 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | ATLNTIC3 | 0.97806 | 0.92688 | -0.051176 |  | 0.93 | 1.05 | 0.033733 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | ATLNTIC3 | 0.98485 | 0.91679 | -0.06806 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | ATLNTIC3 | 0.98485 | 0.91679 | -0.06806 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | ATLNTIC3 | 0.98485 | 0.91679 | -0.06806 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | ATLNTIC3 | 0.98485 | 0.91679 | -0.06806 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | ATLNTIC3 | 0.98485 | 0.91679 | -0.06806 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | ATLNTIC3 | 0.98485 | 0.91679 | -0.06806 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | ATLNTIC3 | 0.98485 | 0.91679 | -0.06806 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | ATLNTIC3 | 0.98485 | 0.91679 | -0.06806 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | ATLNTIC3 | 0.98485 | 0.91679 | -0.06806 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | ATLNTIC3 | 0.98485 | 0.91679 | -0.06806 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | ATLNTIC3 | 0.98485 | 0.91679 | -0.06806 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | ATLNTIC3 | 0.98485 | 0.91679 | -0.06806 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | ATLNTIC3 | 0.98485 | 0.91679 | -0.06806 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | ATLNTIC3 | 0.98485 | 0.91679 | -0.06806 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | ATLNTIC3 | 0.98485 | 0.91679 | -0.06806 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | ATLNTIC3 | 0.98485 | 0.91679 | -0.06806 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | ATLNTIC3 | 0.98485 | 0.91679 | -0.06806 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | ATLNTIC3 | 0.98485 | 0.91679 | -0.06806 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | ATLNTIC3 | 0.98485 | 0.91679 | -0.06806 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | ATLNTIC3 | 0.98485 | 0.91679 | -0.06806 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | ATLNTIC3 | 0.98485 | 0.91679 | -0.06806 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | ATLNTIC3 | 0.98485 | 0.91679 | -0.06806 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | ATLNTIC3 | 0.98485 | 0.91679 | -0.06806 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | ATLNTIC3 | 0.98485 | 0.91679 | -0.06806 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | ATLNTIC3 | 0.98485 | 0.91679 | -0.06806 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | ATLNTIC7 | 0.96854 | 0.92771 | -0.040829 |  | 0.95 | 1.05 | 0.036307 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | ATLNTIC7 | 0.96854 | 0.92771 | -0.040829 |  | 0.95 | 1.05 | 0.052743 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | ATLNTIC7 | 0.96854 | 0.92771 | -0.040829 |  | 0.95 | 1.05 | 0.039345 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | ATLNTIC7 | 0.96854 | 0.92771 | -0.040829 |  | 0.95 | 1.05 | 0.031366 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | ATLNTIC7 | 0.96854 | 0.92771 | -0.040829 |  | 0.95 | 1.05 | 0.041888 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | ATLNTIC7 | 0.96854 | 0.92771 | -0.040829 |  | 0.95 | 1.05 | 0.038797 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | ATLNTIC7 | 0.96854 | 0.92771 | -0.040829 |  | 0.95 | 1.05 | 0.030557 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | ATLNTIC7 | 0.96854 | 0.92771 | -0.040829 |  | 0.95 | 1.05 | 0.067346 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | ATLNTIC7 | 0.96854 | 0.92771 | -0.040829 |  | 0.95 | 1.05 | 0.030557 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | ATLNTIC7 | 0.96854 | 0.92771 | -0.040829 |  | 0.95 | 1.05 | 0.030851 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | ATLNTIC7 | 0.96854 | 0.92771 | -0.040829 |  | 0.95 | 1.05 | 0.032161 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | ATLNTIC7 | 0.96854 | 0.92771 | -0.040829 |  | 0.95 | 1.05 | 0.04067 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | ATLNTIC7 | 0.96854 | 0.92771 | -0.040829 |  | 0.95 | 1.05 | 0.040569 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | ATLNTIC7 | 0.96854 | 0.92771 | -0.040829 |  | 0.95 | 1.05 | 0.03086 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | ATLNTIC7 | 0.96854 | 0.92771 | -0.040829 |  | 0.95 | 1.05 | 0.033223 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | ATLNTIC7 | 0.96854 | 0.92771 | -0.040829 |  | 0.95 | 1.05 | 0.033733 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | ATLNTIC7 | 0.96195 | 0.9139 | -0.048048 |  | 0.95 | 1.05 | 0.036307 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | ATLNTIC7 | 0.96195 | 0.9139 | -0.048048 |  | 0.95 | 1.05 | 0.052743 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | ATLNTIC7 | 0.96195 | 0.9139 | -0.048048 |  | 0.95 | 1.05 | 0.039345 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | ATLNTIC7 | 0.96195 | 0.9139 | -0.048048 |  | 0.95 | 1.05 | 0.031366 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | ATLNTIC7 | 0.96195 | 0.9139 | -0.048048 |  | 0.95 | 1.05 | 0.041888 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | ATLNTIC7 | 0.96195 | 0.9139 | -0.048048 |  | 0.95 | 1.05 | 0.038797 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | ATLNTIC7 | 0.96195 | 0.9139 | -0.048048 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | ATLNTIC7 | 0.96195 | 0.9139 | -0.048048 |  | 0.95 | 1.05 | 0.067346 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | ATLNTIC7 | 0.96195 | 0.9139 | -0.048048 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | ATLNTIC7 | 0.96195 | 0.9139 | -0.048048 |  | 0.95 | 1.05 | 0.030851 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | ATLNTIC7 | 0.96195 | 0.9139 | -0.048048 |  | 0.95 | 1.05 | 0.032161 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | ATLNTIC7 | 0.96195 | 0.9139 | -0.048048 |  | 0.95 | 1.05 | 0.04067 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | ATLNTIC7 | 0.96195 | 0.9139 | -0.048048 |  | 0.95 | 1.05 | 0.040569 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | ATLNTIC7 | 0.96195 | 0.9139 | -0.048048 |  | 0.95 | 1.05 | 0.03086 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | ATLNTIC7 | 0.96195 | 0.9139 | -0.048048 |  | 0.95 | 1.05 | 0.033223 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | ATLNTIC7 | 0.96195 | 0.9139 | -0.048048 |  | 0.95 | 1.05 | 0.033733 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | ATLNTIC7 | 0.97394 | 0.9177 | -0.056236 |  | 0.95 | 1.05 | 0.036307 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | ATLNTIC7 | 0.97394 | 0.9177 | -0.056236 |  | 0.95 | 1.05 | 0.052743 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | ATLNTIC7 | 0.97394 | 0.9177 | -0.056236 |  | 0.95 | 1.05 | 0.039345 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | ATLNTIC7 | 0.97394 | 0.9177 | -0.056236 |  | 0.95 | 1.05 | 0.031366 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | ATLNTIC7 | 0.97394 | 0.9177 | -0.056236 |  | 0.95 | 1.05 | 0.041888 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | ATLNTIC7 | 0.97394 | 0.9177 | -0.056236 |  | 0.95 | 1.05 | 0.038797 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | ATLNTIC7 | 0.97394 | 0.9177 | -0.056236 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | ATLNTIC7 | 0.97394 | 0.9177 | -0.056236 |  | 0.95 | 1.05 | 0.067346 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | ATLNTIC7 | 0.97394 | 0.9177 | -0.056236 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | ATLNTIC7 | 0.97394 | 0.9177 | -0.056236 |  | 0.95 | 1.05 | 0.030851 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | ATLNTIC7 | 0.97394 | 0.9177 | -0.056236 |  | 0.95 | 1.05 | 0.032161 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | ATLNTIC7 | 0.97394 | 0.9177 | -0.056236 |  | 0.95 | 1.05 | 0.04067 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | ATLNTIC7 | 0.97394 | 0.9177 | -0.056236 |  | 0.95 | 1.05 | 0.040569 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | ATLNTIC7 | 0.97394 | 0.9177 | -0.056236 |  | 0.95 | 1.05 | 0.03086 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | ATLNTIC7 | 0.97394 | 0.9177 | -0.056236 |  | 0.95 | 1.05 | 0.033223 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | ATLNTIC7 | 0.97394 | 0.9177 | -0.056236 |  | 0.95 | 1.05 | 0.033733 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | ATLNTIC7 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | ATLNTIC7 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | ATLNTIC7 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | ATLNTIC7 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | ATLNTIC7 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | ATLNTIC7 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | ATLNTIC7 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | ATLNTIC7 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | ATLNTIC7 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | ATLNTIC7 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | ATLNTIC7 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | ATLNTIC7 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | ATLNTIC7 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | ATLNTIC7 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | ATLNTIC7 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | ATLNTIC7 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | ATLNTIC7 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | ATLNTIC7 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | ATLNTIC7 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | ATLNTIC7 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | ATLNTIC7 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | ATLNTIC7 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | ATLNTIC7 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | ATLNTIC7 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | ATLNTIC7 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | ATLNTIC7 | 0.96773 | 0.92612 | -0.041612 |  | 0.95 | 1.05 | 0.036307 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | ATLNTIC7 | 0.96773 | 0.92612 | -0.041612 |  | 0.95 | 1.05 | 0.052743 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | ATLNTIC7 | 0.96773 | 0.92612 | -0.041612 |  | 0.95 | 1.05 | 0.039345 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | ATLNTIC7 | 0.96773 | 0.92612 | -0.041612 |  | 0.95 | 1.05 | 0.031366 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | ATLNTIC7 | 0.96773 | 0.92612 | -0.041612 |  | 0.95 | 1.05 | 0.041888 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | ATLNTIC7 | 0.96773 | 0.92612 | -0.041612 |  | 0.95 | 1.05 | 0.038797 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | ATLNTIC7 | 0.96773 | 0.92612 | -0.041612 |  | 0.95 | 1.05 | 0.030557 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | ATLNTIC7 | 0.96773 | 0.92612 | -0.041612 |  | 0.95 | 1.05 | 0.067346 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | ATLNTIC7 | 0.96773 | 0.92612 | -0.041612 |  | 0.95 | 1.05 | 0.030557 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | ATLNTIC7 | 0.96773 | 0.92612 | -0.041612 |  | 0.95 | 1.05 | 0.030851 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | ATLNTIC7 | 0.96773 | 0.92612 | -0.041612 |  | 0.95 | 1.05 | 0.032161 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | ATLNTIC7 | 0.96773 | 0.92612 | -0.041612 |  | 0.95 | 1.05 | 0.04067 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | ATLNTIC7 | 0.96773 | 0.92612 | -0.041612 |  | 0.95 | 1.05 | 0.040569 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | ATLNTIC7 | 0.96773 | 0.92612 | -0.041612 |  | 0.95 | 1.05 | 0.03086 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | ATLNTIC7 | 0.96773 | 0.92612 | -0.041612 |  | 0.95 | 1.05 | 0.033223 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | ATLNTIC7 | 0.96773 | 0.92612 | -0.041612 |  | 0.95 | 1.05 | 0.033733 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | AUBURN 6 | 0.9723 | 0.93442 | -0.03788 |  | 0.95 | 1.05 | 0.039728 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | AUBURN 6 | 0.9723 | 0.93442 | -0.03788 |  | 0.95 | 1.05 | 0.040762 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | AUBURN 6 | 0.9723 | 0.93442 | -0.03788 |  | 0.95 | 1.05 | 0.030778 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | AUBURN 6 | 0.9723 | 0.93442 | -0.03788 |  | 0.95 | 1.05 | 0.034227 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | AUBURN 6 | 0.9723 | 0.93442 | -0.03788 |  | 0.95 | 1.05 | 0.037164 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | AUBURN 6 | 0.9723 | 0.93442 | -0.03788 |  | 0.95 | 1.05 | 0.031937 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | AUBURN 6 | 0.9723 | 0.93442 | -0.03788 |  | 0.95 | 1.05 | 0.03782 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | AUBURN 6 | 0.9723 | 0.93442 | -0.03788 |  | 0.95 | 1.05 | 0.036407 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | AUBURN 6 | 0.9723 | 0.93442 | -0.03788 |  | 0.95 | 1.05 | 0.053181 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | AUBURN 6 | 0.9723 | 0.93442 | -0.03788 |  | 0.95 | 1.05 | 0.036407 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | AUBURN 6 | 0.9723 | 0.93442 | -0.03788 |  | 0.95 | 1.05 | 0.037418 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | AUBURN 6 | 0.9723 | 0.93442 | -0.03788 |  | 0.95 | 1.05 | 0.037355 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | AUBURN 6 | 0.9723 | 0.93442 | -0.03788 |  | 0.95 | 1.05 | 0.032533 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | AUBURN 6 | 0.9723 | 0.93442 | -0.03788 |  | 0.95 | 1.05 | 0.031326 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | AUBURN 6 | 0.9723 | 0.93442 | -0.03788 |  | 0.95 | 1.05 | 0.035094 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | AUBURN 6 | 0.9723 | 0.93442 | -0.03788 |  | 0.95 | 1.05 | 0.031652 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | AUBURN 6 | 0.9723 | 0.93442 | -0.03788 |  | 0.95 | 1.05 | 0.031104 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | AUBURN 6 | 0.9723 | 0.93442 | -0.03788 |  | 0.95 | 1.05 | 0.033175 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | AUBURN 6 | 0.9723 | 0.93442 | -0.03788 |  | 0.95 | 1.05 | 0.034843 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | AUBURN 6 | 0.97765 | 0.93863 | -0.039022 |  | 0.95 | 1.05 | 0.03053 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | AUBURN 6 | 0.97765 | 0.93863 | -0.039022 |  | 0.95 | 1.05 | 0.044933 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | AUBURN 6 | 0.97765 | 0.93863 | -0.039022 |  | 0.95 | 1.05 | 0.047811 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | AUBURN 6 | 0.97765 | 0.93863 | -0.039022 |  | 0.95 | 1.05 | 0.09719 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | AUBURN 6 | 0.97765 | 0.93863 | -0.039022 |  | 0.95 | 1.05 | 0.069376 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | AUBURN 6 | 0.97765 | 0.93863 | -0.039022 |  | 0.95 | 1.05 | 0.04277 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | AUBURN 6 | 0.97765 | 0.93863 | -0.039022 |  | 0.95 | 1.05 | 0.071112 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | AUBURN 6 | 0.97765 | 0.93863 | -0.039022 |  | 0.95 | 1.05 | 0.039357 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | AUBURN 6 | 0.97765 | 0.93863 | -0.039022 |  | 0.95 | 1.05 | 0.04035 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | AUBURN 6 | 0.97765 | 0.93863 | -0.039022 |  | 0.95 | 1.05 | 0.052332 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | AUBURN 6 | 0.97765 | 0.93863 | -0.039022 |  | 0.95 | 1.05 | 0.045944 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | AUBURN 6 | 0.97765 | 0.93863 | -0.039022 |  | 0.95 | 1.05 | 0.038178 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | AUBURN 6 | 0.97765 | 0.93863 | -0.039022 |  | 0.95 | 1.05 | 0.13469 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | AUBURN 6 | 0.97765 | 0.93863 | -0.039022 |  | 0.95 | 1.05 | 0.03053 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | AUBURN 6 | 0.97765 | 0.93863 | -0.039022 |  | 0.95 | 1.05 | 0.038178 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | AUBURN 6 | 0.97765 | 0.93863 | -0.039022 |  | 0.95 | 1.05 | 0.037309 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | AUBURN 6 | 0.97765 | 0.93863 | -0.039022 |  | 0.95 | 1.05 | 0.040075 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | AUBURN 6 | 0.97765 | 0.93863 | -0.039022 |  | 0.95 | 1.05 | 0.053764 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | AUBURN 6 | 0.97765 | 0.93863 | -0.039022 |  | 0.95 | 1.05 | 0.071762 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | AUBURN 6 | 0.97765 | 0.93863 | -0.039022 |  | 0.95 | 1.05 | 0.047827 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | AUBURN 6 | 0.97765 | 0.93863 | -0.039022 |  | 0.95 | 1.05 | 0.047827 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | AUBURN 6 | 0.97765 | 0.93863 | -0.039022 |  | 0.95 | 1.05 | 0.070303 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | AUBURN 6 | 0.97765 | 0.93863 | -0.039022 |  | 0.95 | 1.05 | 0.040614 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | AUBURN 6 | 0.97765 | 0.93863 | -0.039022 |  | 0.95 | 1.05 | 0.039729 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | AUBURN 6 | 0.97765 | 0.93863 | -0.039022 |  | 0.95 | 1.05 | 0.049662 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | AUBURN 6 | 0.97765 | 0.93863 | -0.039022 |  | 0.95 | 1.05 | 0.042332 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | AUBURN 6 | 0.97765 | 0.93863 | -0.039022 |  | 0.95 | 1.05 | 0.048722 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | AUBURN 6 | 0.97765 | 0.93863 | -0.039022 |  | 0.95 | 1.05 | 0.038156 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | AUBURN 6 | 0.97765 | 0.93863 | -0.039022 |  | 0.95 | 1.05 | 0.036794 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | AUBURN 6 | 0.9699 | 0.93181 | -0.038084 |  | 0.95 | 1.05 | 0.036307 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | AUBURN 6 | 0.9699 | 0.93181 | -0.038084 |  | 0.95 | 1.05 | 0.052743 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | AUBURN 6 | 0.9699 | 0.93181 | -0.038084 |  | 0.95 | 1.05 | 0.039345 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | AUBURN 6 | 0.9699 | 0.93181 | -0.038084 |  | 0.95 | 1.05 | 0.031366 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | AUBURN 6 | 0.9699 | 0.93181 | -0.038084 |  | 0.95 | 1.05 | 0.041888 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | AUBURN 6 | 0.9699 | 0.93181 | -0.038084 |  | 0.95 | 1.05 | 0.038797 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | AUBURN 6 | 0.9699 | 0.93181 | -0.038084 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | AUBURN 6 | 0.9699 | 0.93181 | -0.038084 |  | 0.95 | 1.05 | 0.067346 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | AUBURN 6 | 0.9699 | 0.93181 | -0.038084 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | AUBURN 6 | 0.9699 | 0.93181 | -0.038084 |  | 0.95 | 1.05 | 0.030851 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | AUBURN 6 | 0.9699 | 0.93181 | -0.038084 |  | 0.95 | 1.05 | 0.032161 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | AUBURN 6 | 0.9699 | 0.93181 | -0.038084 |  | 0.95 | 1.05 | 0.04067 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | AUBURN 6 | 0.9699 | 0.93181 | -0.038084 |  | 0.95 | 1.05 | 0.040569 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | AUBURN 6 | 0.9699 | 0.93181 | -0.038084 |  | 0.95 | 1.05 | 0.03086 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | AUBURN 6 | 0.9699 | 0.93181 | -0.038084 |  | 0.95 | 1.05 | 0.033223 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | AUBURN 6 | 0.9699 | 0.93181 | -0.038084 |  | 0.95 | 1.05 | 0.033733 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | AUBURN 6 | 0.97411 | 0.92997 | -0.044141 |  | 0.95 | 1.05 | 0.036307 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | AUBURN 6 | 0.97411 | 0.92997 | -0.044141 |  | 0.95 | 1.05 | 0.052743 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | AUBURN 6 | 0.97411 | 0.92997 | -0.044141 |  | 0.95 | 1.05 | 0.039345 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | AUBURN 6 | 0.97411 | 0.92997 | -0.044141 |  | 0.95 | 1.05 | 0.031366 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | AUBURN 6 | 0.97411 | 0.92997 | -0.044141 |  | 0.95 | 1.05 | 0.041888 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | AUBURN 6 | 0.97411 | 0.92997 | -0.044141 |  | 0.95 | 1.05 | 0.038797 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | AUBURN 6 | 0.97411 | 0.92997 | -0.044141 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | AUBURN 6 | 0.97411 | 0.92997 | -0.044141 |  | 0.95 | 1.05 | 0.067346 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | AUBURN 6 | 0.97411 | 0.92997 | -0.044141 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | AUBURN 6 | 0.97411 | 0.92997 | -0.044141 |  | 0.95 | 1.05 | 0.030851 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | AUBURN 6 | 0.97411 | 0.92997 | -0.044141 |  | 0.95 | 1.05 | 0.032161 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | AUBURN 6 | 0.97411 | 0.92997 | -0.044141 |  | 0.95 | 1.05 | 0.04067 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | AUBURN 6 | 0.97411 | 0.92997 | -0.044141 |  | 0.95 | 1.05 | 0.040569 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | AUBURN 6 | 0.97411 | 0.92997 | -0.044141 |  | 0.95 | 1.05 | 0.03086 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | AUBURN 6 | 0.97411 | 0.92997 | -0.044141 |  | 0.95 | 1.05 | 0.033223 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | AUBURN 6 | 0.97411 | 0.92997 | -0.044141 |  | 0.95 | 1.05 | 0.033733 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | AUBURN 6 | 0.97681 | 0.93152 | -0.045291 |  | 0.95 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | AUBURN 6 | 0.97681 | 0.93152 | -0.045291 |  | 0.95 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | AUBURN 6 | 0.97681 | 0.93152 | -0.045291 |  | 0.95 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | AUBURN 6 | 0.97681 | 0.93152 | -0.045291 |  | 0.95 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | AUBURN 6 | 0.97681 | 0.93152 | -0.045291 |  | 0.95 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | AUBURN 6 | 0.97681 | 0.93152 | -0.045291 |  | 0.95 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | AUBURN 6 | 0.97681 | 0.93152 | -0.045291 |  | 0.95 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | AUBURN 6 | 0.97681 | 0.93152 | -0.045291 |  | 0.95 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | AUBURN 6 | 0.97681 | 0.93152 | -0.045291 |  | 0.95 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | AUBURN 6 | 0.97681 | 0.93152 | -0.045291 |  | 0.95 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | AUBURN 6 | 0.97681 | 0.93152 | -0.045291 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | AUBURN 6 | 0.97681 | 0.93152 | -0.045291 |  | 0.95 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | AUBURN 6 | 0.97681 | 0.93152 | -0.045291 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | AUBURN 6 | 0.97681 | 0.93152 | -0.045291 |  | 0.95 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | AUBURN 6 | 0.97681 | 0.93152 | -0.045291 |  | 0.95 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | AUBURN 6 | 0.97681 | 0.93152 | -0.045291 |  | 0.95 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | AUBURN 6 | 0.97681 | 0.93152 | -0.045291 |  | 0.95 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | AUBURN 6 | 0.97681 | 0.93152 | -0.045291 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | AUBURN 6 | 0.97681 | 0.93152 | -0.045291 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | AUBURN 6 | 0.97681 | 0.93152 | -0.045291 |  | 0.95 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | AUBURN 6 | 0.97681 | 0.93152 | -0.045291 |  | 0.95 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | AUBURN 6 | 0.97681 | 0.93152 | -0.045291 |  | 0.95 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | AUBURN 6 | 0.97681 | 0.93152 | -0.045291 |  | 0.95 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | AUBURN 6 | 0.97681 | 0.93152 | -0.045291 |  | 0.95 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | AUBURN 6 | 0.97681 | 0.93152 | -0.045291 |  | 0.95 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | AUR124 5 | 0.96806 | 0.91814 | -0.049917 |  | 0.925 | 1.05 | 0.033596 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | AUR124 5 | 0.96806 | 0.91814 | -0.049917 |  | 0.925 | 1.05 | 0.040193 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | AUR124 5 | 0.96806 | 0.91814 | -0.049917 |  | 0.925 | 1.05 | 0.088122 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | AUR124 5 | 0.96806 | 0.91814 | -0.049917 |  | 0.925 | 1.05 | 0.074664 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | AUR124 5 | 0.96806 | 0.91814 | -0.049917 |  | 0.925 | 1.05 | 0.068051 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | AUR124 5 | 0.96806 | 0.91814 | -0.049917 |  | 0.925 | 1.05 | 0.035565 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | AUR124 5 | 0.96806 | 0.91814 | -0.049917 |  | 0.925 | 1.05 | 0.033904 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | AUR124 5 | 0.96806 | 0.91814 | -0.049917 |  | 0.925 | 1.05 | 0.16366 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | AUR124 5 | 0.96806 | 0.91814 | -0.049917 |  | 0.925 | 1.05 | 0.045569 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | AUR124 5 | 0.96806 | 0.91814 | -0.049917 |  | 0.925 | 1.05 | 0.13458 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | AUR124 5 | 0.96806 | 0.91814 | -0.049917 |  | 0.925 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | AUR124 5 | 0.96806 | 0.91814 | -0.049917 |  | 0.925 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | AUR124 5 | 0.96806 | 0.91814 | -0.049917 |  | 0.925 | 1.05 | 0.068426 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | AUR124 5 | 0.96806 | 0.91814 | -0.049917 |  | 0.925 | 1.05 | 0.035223 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | AUR124 5 | 0.96806 | 0.91814 | -0.049917 |  | 0.925 | 1.05 | 0.034504 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | AUR124 5 | 0.9685 | 0.92007 | -0.048439 |  | 0.925 | 1.05 | 0.040193 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | AUR124 5 | 0.9685 | 0.92007 | -0.048439 |  | 0.925 | 1.05 | 0.088122 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | AUR124 5 | 0.9685 | 0.92007 | -0.048439 |  | 0.925 | 1.05 | 0.074664 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | AUR124 5 | 0.9685 | 0.92007 | -0.048439 |  | 0.925 | 1.05 | 0.068051 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | AUR124 5 | 0.9685 | 0.92007 | -0.048439 |  | 0.925 | 1.05 | 0.034774 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | AUR124 5 | 0.9685 | 0.92007 | -0.048439 |  | 0.925 | 1.05 | 0.033904 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | AUR124 5 | 0.9685 | 0.92007 | -0.048439 |  | 0.925 | 1.05 | 0.16366 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | AUR124 5 | 0.9685 | 0.92007 | -0.048439 |  | 0.925 | 1.05 | 0.045569 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | AUR124 5 | 0.9685 | 0.92007 | -0.048439 |  | 0.925 | 1.05 | 0.13458 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | AUR124 5 | 0.9685 | 0.92007 | -0.048439 |  | 0.925 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | AUR124 5 | 0.9685 | 0.92007 | -0.048439 |  | 0.925 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | AUR124 5 | 0.9685 | 0.92007 | -0.048439 |  | 0.925 | 1.05 | 0.068426 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | AUR124 5 | 0.9685 | 0.92007 | -0.048439 |  | 0.925 | 1.05 | 0.035223 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | AUR124 5 | 0.9685 | 0.92007 | -0.048439 |  | 0.925 | 1.05 | 0.034504 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | AUR124 5 | 0.96873 | 0.91762 | -0.051113 |  | 0.925 | 1.05 | 0.033596 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.2 MVAR switched shunt at GROVE 5 161 kV; Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | AUR124 5 | 0.96873 | 0.91762 | -0.051113 |  | 0.925 | 1.05 | 0.088122 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.2 MVAR switched shunt at GROVE 5 161 kV; Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | AUR124 5 | 0.96873 | 0.91762 | -0.051113 |  | 0.925 | 1.05 | 0.030897 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.2 MVAR switched shunt at GROVE 5 161 kV; Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | AUR124 5 | 0.96873 | 0.91762 | -0.051113 |  | 0.925 | 1.05 | 0.038719 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.2 MVAR switched shunt at GROVE 5 161 kV; Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | AUR124 5 | 0.96873 | 0.91762 | -0.051113 |  | 0.925 | 1.05 | 0.035565 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.2 MVAR switched shunt at GROVE 5 161 kV; Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | AUR124 5 | 0.96873 | 0.91762 | -0.051113 |  | 0.925 | 1.05 | 0.16366 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.2 MVAR switched shunt at GROVE 5 161 kV; Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | AUR124 5 | 0.96873 | 0.91762 | -0.051113 |  | 0.925 | 1.05 | 0.038589 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.2 MVAR switched shunt at GROVE 5 161 kV; Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | AUR124 5 | 0.96873 | 0.91762 | -0.051113 |  | 0.925 | 1.05 | 0.034208 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.2 MVAR switched shunt at GROVE 5 161 kV; Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | AUR124 5 | 0.96761 | 0.91697 | -0.050643 |  | 0.925 | 1.05 | 0.033596 | P23:345:AECI:7JASPER:1182::: | Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | AUR124 5 | 0.96761 | 0.91697 | -0.050643 |  | 0.925 | 1.05 | 0.056051 | P23:345:AECI:7JASPER:1182::: | Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | AUR124 5 | 0.96761 | 0.91697 | -0.050643 |  | 0.925 | 1.05 | 0.030897 | P23:345:AECI:7JASPER:1182::: | Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | AUR124 5 | 0.96761 | 0.91697 | -0.050643 |  | 0.925 | 1.05 | 0.038719 | P23:345:AECI:7JASPER:1182::: | Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | AUR124 5 | 0.96761 | 0.91697 | -0.050643 |  | 0.925 | 1.05 | 0.035565 | P23:345:AECI:7JASPER:1182::: | Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | AUR124 5 | 0.96761 | 0.91697 | -0.050643 |  | 0.925 | 1.05 | 0.082596 | P23:345:AECI:7JASPER:1182::: | Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | AUR124 5 | 0.96761 | 0.91697 | -0.050643 |  | 0.925 | 1.05 | 0.038589 | P23:345:AECI:7JASPER:1182::: | Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | AUR124 5 | 0.96761 | 0.91697 | -0.050643 |  | 0.925 | 1.05 | 0.034208 | P23:345:AECI:7JASPER:1182::: | Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | AUR124 5 | 0.96894 | 0.92207 | -0.04687 |  | 0.925 | 1.05 | 0.033596 | P12:345:AECI:BLCKBRRY:JSPR345:1:: | Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | AUR124 5 | 0.96894 | 0.92207 | -0.04687 |  | 0.925 | 1.05 | 0.056051 | P12:345:AECI:BLCKBRRY:JSPR345:1:: | Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | AUR124 5 | 0.96894 | 0.92207 | -0.04687 |  | 0.925 | 1.05 | 0.030897 | P12:345:AECI:BLCKBRRY:JSPR345:1:: | Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | AUR124 5 | 0.96894 | 0.92207 | -0.04687 |  | 0.925 | 1.05 | 0.038719 | P12:345:AECI:BLCKBRRY:JSPR345:1:: | Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | AUR124 5 | 0.96894 | 0.92207 | -0.04687 |  | 0.925 | 1.05 | 0.035565 | P12:345:AECI:BLCKBRRY:JSPR345:1:: | Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | AUR124 5 | 0.96894 | 0.92207 | -0.04687 |  | 0.925 | 1.05 | 0.082596 | P12:345:AECI:BLCKBRRY:JSPR345:1:: | Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | AUR124 5 | 0.96894 | 0.92207 | -0.04687 |  | 0.925 | 1.05 | 0.038589 | P12:345:AECI:BLCKBRRY:JSPR345:1:: | Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | AUR124 5 | 0.96894 | 0.92207 | -0.04687 |  | 0.925 | 1.05 | 0.034208 | P12:345:AECI:BLCKBRRY:JSPR345:1:: | Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | AVOCA 5 | 0.98868 | 0.91867 | -0.070007 |  | 0.92 | 1.05 | 0.033596 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | AVOCA 5 | 0.98868 | 0.91867 | -0.070007 |  | 0.92 | 1.05 | 0.040193 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | AVOCA 5 | 0.98868 | 0.91867 | -0.070007 |  | 0.92 | 1.05 | 0.088122 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | AVOCA 5 | 0.98868 | 0.91867 | -0.070007 |  | 0.92 | 1.05 | 0.074664 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | AVOCA 5 | 0.98868 | 0.91867 | -0.070007 |  | 0.92 | 1.05 | 0.068051 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | AVOCA 5 | 0.98868 | 0.91867 | -0.070007 |  | 0.92 | 1.05 | 0.035565 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | AVOCA 5 | 0.98868 | 0.91867 | -0.070007 |  | 0.92 | 1.05 | 0.033904 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | AVOCA 5 | 0.98868 | 0.91867 | -0.070007 |  | 0.92 | 1.05 | 0.16366 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | AVOCA 5 | 0.98868 | 0.91867 | -0.070007 |  | 0.92 | 1.05 | 0.045569 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | AVOCA 5 | 0.98868 | 0.91867 | -0.070007 |  | 0.92 | 1.05 | 0.13458 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | AVOCA 5 | 0.98868 | 0.91867 | -0.070007 |  | 0.92 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | AVOCA 5 | 0.98868 | 0.91867 | -0.070007 |  | 0.92 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | AVOCA 5 | 0.98868 | 0.91867 | -0.070007 |  | 0.92 | 1.05 | 0.068426 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | AVOCA 5 | 0.98868 | 0.91867 | -0.070007 |  | 0.92 | 1.05 | 0.035223 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | AVOCA 5 | 0.98868 | 0.91867 | -0.070007 |  | 0.92 | 1.05 | 0.034504 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | AVOCA 5 | 0.98888 | 0.91989 | -0.068998 |  | 0.92 | 1.05 | 0.040193 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | AVOCA 5 | 0.98888 | 0.91989 | -0.068998 |  | 0.92 | 1.05 | 0.088122 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | AVOCA 5 | 0.98888 | 0.91989 | -0.068998 |  | 0.92 | 1.05 | 0.074664 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | AVOCA 5 | 0.98888 | 0.91989 | -0.068998 |  | 0.92 | 1.05 | 0.068051 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | AVOCA 5 | 0.98888 | 0.91989 | -0.068998 |  | 0.92 | 1.05 | 0.034774 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | AVOCA 5 | 0.98888 | 0.91989 | -0.068998 |  | 0.92 | 1.05 | 0.033904 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | AVOCA 5 | 0.98888 | 0.91989 | -0.068998 |  | 0.92 | 1.05 | 0.16366 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | AVOCA 5 | 0.98888 | 0.91989 | -0.068998 |  | 0.92 | 1.05 | 0.045569 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | AVOCA 5 | 0.98888 | 0.91989 | -0.068998 |  | 0.92 | 1.05 | 0.13458 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | AVOCA 5 | 0.98888 | 0.91989 | -0.068998 |  | 0.92 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | AVOCA 5 | 0.98888 | 0.91989 | -0.068998 |  | 0.92 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | AVOCA 5 | 0.98888 | 0.91989 | -0.068998 |  | 0.92 | 1.05 | 0.068426 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | AVOCA 5 | 0.98888 | 0.91989 | -0.068998 |  | 0.92 | 1.05 | 0.035223 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | AVOCA 5 | 0.98888 | 0.91989 | -0.068998 |  | 0.92 | 1.05 | 0.034504 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | BEECRK4 | 0.96336 | 0.92157 | -0.041791 |  | 0.93 | 1.05 | 0.091967 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | BEECRK4 | 0.96336 | 0.92157 | -0.041791 |  | 0.93 | 1.05 | 0.033356 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | BEECRK4 | 0.96336 | 0.92157 | -0.041791 |  | 0.93 | 1.05 | 0.044346 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | BEECRK4 | 0.96336 | 0.92157 | -0.041791 |  | 0.93 | 1.05 | 0.058536 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | BEECRK4 | 0.96336 | 0.92157 | -0.041791 |  | 0.93 | 1.05 | 0.059327 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | BEECRK4 | 0.96336 | 0.92157 | -0.041791 |  | 0.93 | 1.05 | 0.041874 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | BEECRK4 | 0.96336 | 0.92157 | -0.041791 |  | 0.93 | 1.05 | 0.046192 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | BEECRK4 | 0.96336 | 0.92157 | -0.041791 |  | 0.93 | 1.05 | 0.12754 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | BEECRK4 | 0.96336 | 0.92157 | -0.041791 |  | 0.93 | 1.05 | 0.047018 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | BEECRK4 | 0.96336 | 0.92157 | -0.041791 |  | 0.93 | 1.05 | 0.056662 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | BEECRK4 | 0.96336 | 0.92157 | -0.041791 |  | 0.93 | 1.05 | 0.056662 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | BEECRK4 | 0.96336 | 0.92157 | -0.041791 |  | 0.93 | 1.05 | 0.056727 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | BEECRK4 | 0.96336 | 0.92157 | -0.041791 |  | 0.93 | 1.05 | 0.074186 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | BEECRK4 | 0.96336 | 0.92157 | -0.041791 |  | 0.93 | 1.05 | 0.040839 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | BEECRK4 | 0.96336 | 0.92157 | -0.041791 |  | 0.93 | 1.05 | 0.03863 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | BEECRK4 | 0.96336 | 0.92157 | -0.041791 |  | 0.93 | 1.05 | 0.042285 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | BEECRK4 | 0.96336 | 0.92157 | -0.041791 |  | 0.93 | 1.05 | 0.042285 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | BEECRK4 | 0.96336 | 0.92157 | -0.041791 |  | 0.93 | 1.05 | 0.050204 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | BEECRK4 | 0.96336 | 0.92157 | -0.041791 |  | 0.93 | 1.05 | 0.058005 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | BEECRK4 | 0.96336 | 0.92157 | -0.041791 |  | 0.93 | 1.05 | 0.041735 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | BEECRK4 | 0.96336 | 0.92157 | -0.041791 |  | 0.93 | 1.05 | 0.057076 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | BEECRK4 | 0.96336 | 0.92157 | -0.041791 |  | 0.93 | 1.05 | 0.050111 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | BEECRK4 | 0.96336 | 0.92157 | -0.041791 |  | 0.93 | 1.05 | 0.06491 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | BEECRK4 | 0.96336 | 0.92157 | -0.041791 |  | 0.93 | 1.05 | 0.051051 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | BEECRK4 | 0.96336 | 0.92157 | -0.041791 |  | 0.93 | 1.05 | 0.036279 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | BEECRK4 | 0.97024 | 0.92936 | -0.040877 |  | 0.93 | 1.05 | 0.049206 | P23:345:WERE:N345-345-20:EHV: | Add 20 MVAR switched shunt at LIBERTY4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | BEECRK4 | 0.97024 | 0.92936 | -0.040877 |  | 0.93 | 1.05 | 0.056808 | P23:345:WERE:N345-345-20:EHV: | Add 20 MVAR switched shunt at LIBERTY4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | BEECRK4 | 0.97024 | 0.92936 | -0.040877 |  | 0.93 | 1.05 | 0.079992 | P23:345:WERE:N345-345-20:EHV: | Add 20 MVAR switched shunt at LIBERTY4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | BEECRK4 | 0.97024 | 0.92936 | -0.040877 |  | 0.93 | 1.05 | 0.085896 | P23:345:WERE:N345-345-20:EHV: | Add 20 MVAR switched shunt at LIBERTY4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | BEECRK4 | 0.97024 | 0.92936 | -0.040877 |  | 0.93 | 1.05 | 0.049659 | P23:345:WERE:N345-345-20:EHV: | Add 20 MVAR switched shunt at LIBERTY4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | BEECRK4 | 0.97024 | 0.92936 | -0.040877 |  | 0.93 | 1.05 | 0.11417 | P23:345:WERE:N345-345-20:EHV: | Add 20 MVAR switched shunt at LIBERTY4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | BEECRK4 | 0.97024 | 0.92936 | -0.040877 |  | 0.93 | 1.05 | 0.043555 | P23:345:WERE:N345-345-20:EHV: | Add 20 MVAR switched shunt at LIBERTY4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | BEECRK4 | 0.97024 | 0.92936 | -0.040877 |  | 0.93 | 1.05 | 0.045351 | P23:345:WERE:N345-345-20:EHV: | Add 20 MVAR switched shunt at LIBERTY4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | BEECRK4 | 0.97024 | 0.92936 | -0.040877 |  | 0.93 | 1.05 | 0.067102 | P23:345:WERE:N345-345-20:EHV: | Add 20 MVAR switched shunt at LIBERTY4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | BEECRK4 | 0.97024 | 0.92936 | -0.040877 |  | 0.93 | 1.05 | 0.05564 | P23:345:WERE:N345-345-20:EHV: | Add 20 MVAR switched shunt at LIBERTY4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | BEECRK4 | 0.97024 | 0.92936 | -0.040877 |  | 0.93 | 1.05 | 0.040761 | P23:345:WERE:N345-345-20:EHV: | Add 20 MVAR switched shunt at LIBERTY4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | BEECRK4 | 0.97024 | 0.92936 | -0.040877 |  | 0.93 | 1.05 | 0.4666 | P23:345:WERE:N345-345-20:EHV: | Add 20 MVAR switched shunt at LIBERTY4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | BEECRK4 | 0.97024 | 0.92936 | -0.040877 |  | 0.93 | 1.05 | 0.040761 | P23:345:WERE:N345-345-20:EHV: | Add 20 MVAR switched shunt at LIBERTY4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | BEECRK4 | 0.97024 | 0.92936 | -0.040877 |  | 0.93 | 1.05 | 0.038981 | P23:345:WERE:N345-345-20:EHV: | Add 20 MVAR switched shunt at LIBERTY4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | BEECRK4 | 0.97024 | 0.92936 | -0.040877 |  | 0.93 | 1.05 | 0.043527 | P23:345:WERE:N345-345-20:EHV: | Add 20 MVAR switched shunt at LIBERTY4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | BEECRK4 | 0.97024 | 0.92936 | -0.040877 |  | 0.93 | 1.05 | 0.070027 | P23:345:WERE:N345-345-20:EHV: | Add 20 MVAR switched shunt at LIBERTY4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | BEECRK4 | 0.97024 | 0.92936 | -0.040877 |  | 0.93 | 1.05 | 0.06871 | P23:345:WERE:N345-345-20:EHV: | Add 20 MVAR switched shunt at LIBERTY4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | BEECRK4 | 0.97024 | 0.92936 | -0.040877 |  | 0.93 | 1.05 | 0.059117 | P23:345:WERE:N345-345-20:EHV: | Add 20 MVAR switched shunt at LIBERTY4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | BEECRK4 | 0.97024 | 0.92936 | -0.040877 |  | 0.93 | 1.05 | 0.059117 | P23:345:WERE:N345-345-20:EHV: | Add 20 MVAR switched shunt at LIBERTY4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | BEECRK4 | 0.97024 | 0.92936 | -0.040877 |  | 0.93 | 1.05 | 0.094447 | P23:345:WERE:N345-345-20:EHV: | Add 20 MVAR switched shunt at LIBERTY4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | BEECRK4 | 0.97024 | 0.92936 | -0.040877 |  | 0.93 | 1.05 | 0.045445 | P23:345:WERE:N345-345-20:EHV: | Add 20 MVAR switched shunt at LIBERTY4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | BEECRK4 | 0.97024 | 0.92936 | -0.040877 |  | 0.93 | 1.05 | 0.044374 | P23:345:WERE:N345-345-20:EHV: | Add 20 MVAR switched shunt at LIBERTY4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | BEECRK4 | 0.97024 | 0.92936 | -0.040877 |  | 0.93 | 1.05 | 0.06597 | P23:345:WERE:N345-345-20:EHV: | Add 20 MVAR switched shunt at LIBERTY4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | BEECRK4 | 0.97024 | 0.92936 | -0.040877 |  | 0.93 | 1.05 | 0.048874 | P23:345:WERE:N345-345-20:EHV: | Add 20 MVAR switched shunt at LIBERTY4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | BEECRK4 | 0.97024 | 0.92936 | -0.040877 |  | 0.93 | 1.05 | 0.060524 | P23:345:WERE:N345-345-20:EHV: | Add 20 MVAR switched shunt at LIBERTY4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | BEECRK4 | 0.97024 | 0.92936 | -0.040877 |  | 0.93 | 1.05 | 0.04115 | P23:345:WERE:N345-345-20:EHV: | Add 20 MVAR switched shunt at LIBERTY4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | BEECRK4 | 0.97024 | 0.92936 | -0.040877 |  | 0.93 | 1.05 | 0.038988 | P23:345:WERE:N345-345-20:EHV: | Add 20 MVAR switched shunt at LIBERTY4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | BEECRK4 | 0.9735 | 0.92891 | -0.044596 |  | 0.93 | 1.05 | 0.035768 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | BEECRK4 | 0.9735 | 0.92891 | -0.044596 |  | 0.93 | 1.05 | 0.088718 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | BEECRK4 | 0.9735 | 0.92891 | -0.044596 |  | 0.93 | 1.05 | 0.031473 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | BEECRK4 | 0.9735 | 0.92891 | -0.044596 |  | 0.93 | 1.05 | 0.034941 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | BEECRK4 | 0.9735 | 0.92891 | -0.044596 |  | 0.93 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | BEECRK4 | 0.9735 | 0.92891 | -0.044596 |  | 0.93 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | BEECRK4 | 0.9735 | 0.92891 | -0.044596 |  | 0.93 | 1.05 | 0.049224 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | BEECRK4 | 0.9735 | 0.92891 | -0.044596 |  | 0.93 | 1.05 | 0.038981 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | BEECRK4 | 0.9735 | 0.92891 | -0.044596 |  | 0.93 | 1.05 | 0.040399 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | BEECRK4 | 0.9735 | 0.92891 | -0.044596 |  | 0.93 | 1.05 | 0.031912 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | BEECRK4 | 0.9735 | 0.92891 | -0.044596 |  | 0.93 | 1.05 | 0.034127 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | BEECRK4 | 0.9735 | 0.92891 | -0.044596 |  | 0.93 | 1.05 | 0.047318 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | BEECRK4 | 0.96896 | 0.9262 | -0.042758 |  | 0.93 | 1.05 | 0.040439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | BEECRK4 | 0.96896 | 0.9262 | -0.042758 |  | 0.93 | 1.05 | 0.034853 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | BEECRK4 | 0.96896 | 0.9262 | -0.042758 |  | 0.93 | 1.05 | 0.046783 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | BEECRK4 | 0.96896 | 0.9262 | -0.042758 |  | 0.93 | 1.05 | 0.047615 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | BEECRK4 | 0.96896 | 0.9262 | -0.042758 |  | 0.93 | 1.05 | 0.034938 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | BEECRK4 | 0.96896 | 0.9262 | -0.042758 |  | 0.93 | 1.05 | 0.037875 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | BEECRK4 | 0.96896 | 0.9262 | -0.042758 |  | 0.93 | 1.05 | 0.044022 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | BEECRK4 | 0.96896 | 0.9262 | -0.042758 |  | 0.93 | 1.05 | 0.030552 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | BEECRK4 | 0.96896 | 0.9262 | -0.042758 |  | 0.93 | 1.05 | 0.038531 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | BEECRK4 | 0.96896 | 0.9262 | -0.042758 |  | 0.93 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | BEECRK4 | 0.96896 | 0.9262 | -0.042758 |  | 0.93 | 1.05 | 0.062491 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | BEECRK4 | 0.96896 | 0.9262 | -0.042758 |  | 0.93 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | BEECRK4 | 0.96896 | 0.9262 | -0.042758 |  | 0.93 | 1.05 | 0.038129 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | BEECRK4 | 0.96896 | 0.9262 | -0.042758 |  | 0.93 | 1.05 | 0.038066 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | BEECRK4 | 0.96896 | 0.9262 | -0.042758 |  | 0.93 | 1.05 | 0.034955 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | BEECRK4 | 0.96896 | 0.9262 | -0.042758 |  | 0.93 | 1.05 | 0.06281 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | BEECRK4 | 0.96896 | 0.9262 | -0.042758 |  | 0.93 | 1.05 | 0.045309 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | BEECRK4 | 0.96896 | 0.9262 | -0.042758 |  | 0.93 | 1.05 | 0.035805 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | BEECRK4 | 0.96896 | 0.9262 | -0.042758 |  | 0.93 | 1.05 | 0.032364 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | BEECRK4 | 0.96896 | 0.9262 | -0.042758 |  | 0.93 | 1.05 | 0.031815 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | BEECRK4 | 0.96896 | 0.9262 | -0.042758 |  | 0.93 | 1.05 | 0.033886 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | BEECRK4 | 0.96896 | 0.9262 | -0.042758 |  | 0.93 | 1.05 | 0.035554 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | BEECRK4 | 0.97217 | 0.92248 | -0.049697 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | BEECRK4 | 0.97217 | 0.92248 | -0.049697 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | BEECRK4 | 0.97217 | 0.92248 | -0.049697 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | BEECRK4 | 0.97217 | 0.92248 | -0.049697 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | BEECRK4 | 0.97217 | 0.92248 | -0.049697 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | BEECRK4 | 0.97217 | 0.92248 | -0.049697 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | BEECRK4 | 0.97217 | 0.92248 | -0.049697 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | BEECRK4 | 0.97217 | 0.92248 | -0.049697 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | BEECRK4 | 0.97217 | 0.92248 | -0.049697 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | BEECRK4 | 0.97217 | 0.92248 | -0.049697 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | BEECRK4 | 0.97217 | 0.92248 | -0.049697 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | BEECRK4 | 0.97217 | 0.92248 | -0.049697 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | BEECRK4 | 0.97217 | 0.92248 | -0.049697 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | BEECRK4 | 0.97217 | 0.92248 | -0.049697 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | BEECRK4 | 0.97217 | 0.92248 | -0.049697 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | BEECRK4 | 0.97217 | 0.92248 | -0.049697 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | BEECRK4 | 0.97217 | 0.92248 | -0.049697 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | BEECRK4 | 0.97217 | 0.92248 | -0.049697 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | BEECRK4 | 0.97217 | 0.92248 | -0.049697 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | BEECRK4 | 0.97217 | 0.92248 | -0.049697 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | BEECRK4 | 0.97217 | 0.92248 | -0.049697 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | BEECRK4 | 0.97217 | 0.92248 | -0.049697 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | BEECRK4 | 0.97217 | 0.92248 | -0.049697 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | BEECRK4 | 0.97217 | 0.92248 | -0.049697 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | BEECRK4 | 0.97217 | 0.92248 | -0.049697 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | BELTONS5 | 0.9994 | 0.9231 | -0.076297 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | BELTONS5 | 0.9994 | 0.9231 | -0.076297 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | BELTONS5 | 0.9994 | 0.9231 | -0.076297 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | BELTONS5 | 0.9994 | 0.9231 | -0.076297 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | BELTONS5 | 0.9994 | 0.9231 | -0.076297 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | BELTONS5 | 0.9994 | 0.9231 | -0.076297 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | BELTONS5 | 0.9994 | 0.9231 | -0.076297 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | BELTONS5 | 0.9994 | 0.9231 | -0.076297 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | BELTONS5 | 0.9994 | 0.9231 | -0.076297 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | BELTONS5 | 0.9994 | 0.9231 | -0.076297 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | BELTONS5 | 0.9994 | 0.9231 | -0.076297 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | BELTONS5 | 0.9994 | 0.9231 | -0.076297 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | BELTONS5 | 0.9994 | 0.9231 | -0.076297 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | BELTONS5 | 0.9994 | 0.9231 | -0.076297 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | BELTONS5 | 0.9994 | 0.9231 | -0.076297 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | BELTONS5 | 0.9994 | 0.9231 | -0.076297 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | BELTONS5 | 0.9994 | 0.9231 | -0.076297 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | BELTONS5 | 0.9994 | 0.9231 | -0.076297 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | BELTONS5 | 0.9994 | 0.9231 | -0.076297 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | BELTONS5 | 0.9994 | 0.9231 | -0.076297 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | BELTONS5 | 0.9994 | 0.9231 | -0.076297 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | BELTONS5 | 0.9994 | 0.9231 | -0.076297 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | BELTONS5 | 0.9994 | 0.9231 | -0.076297 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | BELTONS5 | 0.9994 | 0.9231 | -0.076297 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | BELTONS5 | 0.9994 | 0.9231 | -0.076297 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | BENTLEY4 | 0.97139 | 0.92316 | -0.048226 |  | 0.93 | 1.05 | 0.044747 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | BENTLEY4 | 0.97139 | 0.92316 | -0.048226 |  | 0.93 | 1.05 | 0.063323 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | BENTLEY4 | 0.97139 | 0.92316 | -0.048226 |  | 0.93 | 1.05 | 0.043143 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | BENTLEY4 | 0.97139 | 0.92316 | -0.048226 |  | 0.93 | 1.05 | 0.038771 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | BENTLEY4 | 0.97139 | 0.92316 | -0.048226 |  | 0.93 | 1.05 | 0.038438 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | BENTLEY4 | 0.97139 | 0.92316 | -0.048226 |  | 0.93 | 1.05 | 0.04552 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | BENTLEY4 | 0.97139 | 0.92316 | -0.048226 |  | 0.93 | 1.05 | 0.03158 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | BENTLEY4 | 0.97139 | 0.92316 | -0.048226 |  | 0.93 | 1.05 | 0.034131 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | BENTLEY4 | 0.97139 | 0.92316 | -0.048226 |  | 0.93 | 1.05 | 0.042547 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | BENTLEY4 | 0.97139 | 0.92316 | -0.048226 |  | 0.93 | 1.05 | 0.032964 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | BENTLEY4 | 0.97139 | 0.92316 | -0.048226 |  | 0.93 | 1.05 | 0.041072 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | BENTLEY4 | 0.97139 | 0.92316 | -0.048226 |  | 0.93 | 1.05 | 0.069811 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | BENTLEY4 | 0.97139 | 0.92316 | -0.048226 |  | 0.93 | 1.05 | 0.041072 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | BENTLEY4 | 0.97139 | 0.92316 | -0.048226 |  | 0.93 | 1.05 | 0.042352 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | BENTLEY4 | 0.97139 | 0.92316 | -0.048226 |  | 0.93 | 1.05 | 0.041773 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | BENTLEY4 | 0.97139 | 0.92316 | -0.048226 |  | 0.93 | 1.05 | 0.048747 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | BENTLEY4 | 0.97139 | 0.92316 | -0.048226 |  | 0.93 | 1.05 | 0.044283 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | BENTLEY4 | 0.97139 | 0.92316 | -0.048226 |  | 0.93 | 1.05 | 0.039667 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | BENTLEY4 | 0.97139 | 0.92316 | -0.048226 |  | 0.93 | 1.05 | 0.031705 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | BENTLEY4 | 0.97139 | 0.92316 | -0.048226 |  | 0.93 | 1.05 | 0.036041 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | BENTLEY4 | 0.97139 | 0.92316 | -0.048226 |  | 0.93 | 1.05 | 0.035457 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | BENTLEY4 | 0.97139 | 0.92316 | -0.048226 |  | 0.93 | 1.05 | 0.0376 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | BENTLEY4 | 0.97139 | 0.92316 | -0.048226 |  | 0.93 | 1.05 | 0.039043 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | BENTLEY4 | 0.97166 | 0.92395 | -0.047708 |  | 0.93 | 1.05 | 0.044747 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | BENTLEY4 | 0.97166 | 0.92395 | -0.047708 |  | 0.93 | 1.05 | 0.038771 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | BENTLEY4 | 0.97166 | 0.92395 | -0.047708 |  | 0.93 | 1.05 | 0.038438 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | BENTLEY4 | 0.97166 | 0.92395 | -0.047708 |  | 0.93 | 1.05 | 0.030968 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | BENTLEY4 | 0.97166 | 0.92395 | -0.047708 |  | 0.93 | 1.05 | 0.03158 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | BENTLEY4 | 0.97166 | 0.92395 | -0.047708 |  | 0.93 | 1.05 | 0.034131 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | BENTLEY4 | 0.97166 | 0.92395 | -0.047708 |  | 0.93 | 1.05 | 0.040933 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | BENTLEY4 | 0.97166 | 0.92395 | -0.047708 |  | 0.93 | 1.05 | 0.032964 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | BENTLEY4 | 0.97166 | 0.92395 | -0.047708 |  | 0.93 | 1.05 | 0.041072 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | BENTLEY4 | 0.97166 | 0.92395 | -0.047708 |  | 0.93 | 1.05 | 0.041072 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | BENTLEY4 | 0.97166 | 0.92395 | -0.047708 |  | 0.93 | 1.05 | 0.042352 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | BENTLEY4 | 0.97166 | 0.92395 | -0.047708 |  | 0.93 | 1.05 | 0.041773 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | BENTLEY4 | 0.97166 | 0.92395 | -0.047708 |  | 0.93 | 1.05 | 0.039667 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | BENTLEY4 | 0.97166 | 0.92395 | -0.047708 |  | 0.93 | 1.05 | 0.031705 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | BENTLEY4 | 0.97166 | 0.92395 | -0.047708 |  | 0.93 | 1.05 | 0.036041 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | BENTLEY4 | 0.97166 | 0.92395 | -0.047708 |  | 0.93 | 1.05 | 0.035457 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | BENTLEY4 | 0.97166 | 0.92395 | -0.047708 |  | 0.93 | 1.05 | 0.0376 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | BENTLEY4 | 0.97166 | 0.92395 | -0.047708 |  | 0.93 | 1.05 | 0.039043 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | BENTLEY4 | 0.98759 | 0.92844 | -0.059148 |  | 0.93 | 1.05 | 0.040439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | BENTLEY4 | 0.98759 | 0.92844 | -0.059148 |  | 0.93 | 1.05 | 0.034853 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | BENTLEY4 | 0.98759 | 0.92844 | -0.059148 |  | 0.93 | 1.05 | 0.046783 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | BENTLEY4 | 0.98759 | 0.92844 | -0.059148 |  | 0.93 | 1.05 | 0.047615 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | BENTLEY4 | 0.98759 | 0.92844 | -0.059148 |  | 0.93 | 1.05 | 0.034938 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | BENTLEY4 | 0.98759 | 0.92844 | -0.059148 |  | 0.93 | 1.05 | 0.037875 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | BENTLEY4 | 0.98759 | 0.92844 | -0.059148 |  | 0.93 | 1.05 | 0.044022 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | BENTLEY4 | 0.98759 | 0.92844 | -0.059148 |  | 0.93 | 1.05 | 0.030552 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | BENTLEY4 | 0.98759 | 0.92844 | -0.059148 |  | 0.93 | 1.05 | 0.038531 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | BENTLEY4 | 0.98759 | 0.92844 | -0.059148 |  | 0.93 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | BENTLEY4 | 0.98759 | 0.92844 | -0.059148 |  | 0.93 | 1.05 | 0.062491 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | BENTLEY4 | 0.98759 | 0.92844 | -0.059148 |  | 0.93 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | BENTLEY4 | 0.98759 | 0.92844 | -0.059148 |  | 0.93 | 1.05 | 0.038129 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | BENTLEY4 | 0.98759 | 0.92844 | -0.059148 |  | 0.93 | 1.05 | 0.038066 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | BENTLEY4 | 0.98759 | 0.92844 | -0.059148 |  | 0.93 | 1.05 | 0.034955 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | BENTLEY4 | 0.98759 | 0.92844 | -0.059148 |  | 0.93 | 1.05 | 0.06281 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | BENTLEY4 | 0.98759 | 0.92844 | -0.059148 |  | 0.93 | 1.05 | 0.045309 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | BENTLEY4 | 0.98759 | 0.92844 | -0.059148 |  | 0.93 | 1.05 | 0.035805 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | BENTLEY4 | 0.98759 | 0.92844 | -0.059148 |  | 0.93 | 1.05 | 0.032364 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | BENTLEY4 | 0.98759 | 0.92844 | -0.059148 |  | 0.93 | 1.05 | 0.031815 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | BENTLEY4 | 0.98759 | 0.92844 | -0.059148 |  | 0.93 | 1.05 | 0.033886 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | BENTLEY4 | 0.98759 | 0.92844 | -0.059148 |  | 0.93 | 1.05 | 0.035554 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | BENTLEY4 | 0.98003 | 0.90537 | -0.074664 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | BENTLEY4 | 0.98003 | 0.90537 | -0.074664 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | BENTLEY4 | 0.98003 | 0.90537 | -0.074664 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | BENTLEY4 | 0.98003 | 0.90537 | -0.074664 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | BENTLEY4 | 0.98003 | 0.90537 | -0.074664 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | BENTLEY4 | 0.98003 | 0.90537 | -0.074664 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | BENTLEY4 | 0.98003 | 0.90537 | -0.074664 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | BENTLEY4 | 0.98003 | 0.90537 | -0.074664 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | BENTLEY4 | 0.98003 | 0.90537 | -0.074664 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | BENTLEY4 | 0.98003 | 0.90537 | -0.074664 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | BENTLEY4 | 0.98003 | 0.90537 | -0.074664 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | BENTLEY4 | 0.98003 | 0.90537 | -0.074664 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | BENTLEY4 | 0.98003 | 0.90537 | -0.074664 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | BENTLEY4 | 0.98003 | 0.90537 | -0.074664 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | BENTLEY4 | 0.98003 | 0.90537 | -0.074664 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | BENTLEY4 | 0.98003 | 0.90537 | -0.074664 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | BENTLEY4 | 0.98003 | 0.90537 | -0.074664 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | BENTLEY4 | 0.98003 | 0.90537 | -0.074664 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | BENTLEY4 | 0.98003 | 0.90537 | -0.074664 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | BENTLEY4 | 0.98003 | 0.90537 | -0.074664 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | BENTLEY4 | 0.98003 | 0.90537 | -0.074664 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | BENTLEY4 | 0.98003 | 0.90537 | -0.074664 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | BENTLEY4 | 0.98003 | 0.90537 | -0.074664 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | BENTLEY4 | 0.98003 | 0.90537 | -0.074664 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | BENTLEY4 | 0.98003 | 0.90537 | -0.074664 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | BENTVJ_5 | 0.98934 | 0.91906 | -0.070278 |  | 0.92 | 1.05 | 0.033596 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | BENTVJ_5 | 0.98934 | 0.91906 | -0.070278 |  | 0.92 | 1.05 | 0.040193 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | BENTVJ_5 | 0.98934 | 0.91906 | -0.070278 |  | 0.92 | 1.05 | 0.088122 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | BENTVJ_5 | 0.98934 | 0.91906 | -0.070278 |  | 0.92 | 1.05 | 0.074664 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | BENTVJ_5 | 0.98934 | 0.91906 | -0.070278 |  | 0.92 | 1.05 | 0.068051 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | BENTVJ_5 | 0.98934 | 0.91906 | -0.070278 |  | 0.92 | 1.05 | 0.035565 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | BENTVJ_5 | 0.98934 | 0.91906 | -0.070278 |  | 0.92 | 1.05 | 0.033904 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | BENTVJ_5 | 0.98934 | 0.91906 | -0.070278 |  | 0.92 | 1.05 | 0.16366 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | BENTVJ_5 | 0.98934 | 0.91906 | -0.070278 |  | 0.92 | 1.05 | 0.045569 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | BENTVJ_5 | 0.98934 | 0.91906 | -0.070278 |  | 0.92 | 1.05 | 0.13458 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | BENTVJ_5 | 0.98934 | 0.91906 | -0.070278 |  | 0.92 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | BENTVJ_5 | 0.98934 | 0.91906 | -0.070278 |  | 0.92 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | BENTVJ_5 | 0.98934 | 0.91906 | -0.070278 |  | 0.92 | 1.05 | 0.068426 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | BENTVJ_5 | 0.98934 | 0.91906 | -0.070278 |  | 0.92 | 1.05 | 0.035223 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | BENTVJ_5 | 0.98934 | 0.91906 | -0.070278 |  | 0.92 | 1.05 | 0.034504 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | BENT_SL5 | 0.98949 | 0.91928 | -0.070217 |  | 0.92 | 1.05 | 0.033596 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | BENT_SL5 | 0.98949 | 0.91928 | -0.070217 |  | 0.92 | 1.05 | 0.040193 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | BENT_SL5 | 0.98949 | 0.91928 | -0.070217 |  | 0.92 | 1.05 | 0.088122 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | BENT_SL5 | 0.98949 | 0.91928 | -0.070217 |  | 0.92 | 1.05 | 0.074664 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | BENT_SL5 | 0.98949 | 0.91928 | -0.070217 |  | 0.92 | 1.05 | 0.068051 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | BENT_SL5 | 0.98949 | 0.91928 | -0.070217 |  | 0.92 | 1.05 | 0.035565 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | BENT_SL5 | 0.98949 | 0.91928 | -0.070217 |  | 0.92 | 1.05 | 0.033904 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | BENT_SL5 | 0.98949 | 0.91928 | -0.070217 |  | 0.92 | 1.05 | 0.16366 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | BENT_SL5 | 0.98949 | 0.91928 | -0.070217 |  | 0.92 | 1.05 | 0.045569 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | BENT_SL5 | 0.98949 | 0.91928 | -0.070217 |  | 0.92 | 1.05 | 0.13458 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | BENT_SL5 | 0.98949 | 0.91928 | -0.070217 |  | 0.92 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | BENT_SL5 | 0.98949 | 0.91928 | -0.070217 |  | 0.92 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | BENT_SL5 | 0.98949 | 0.91928 | -0.070217 |  | 0.92 | 1.05 | 0.068426 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | BENT_SL5 | 0.98949 | 0.91928 | -0.070217 |  | 0.92 | 1.05 | 0.035223 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | BENT_SL5 | 0.98949 | 0.91928 | -0.070217 |  | 0.92 | 1.05 | 0.034504 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | BIRDHOL4 | 0.94414 | 0.91553 | -0.028604 |  | 0.92 | 1.05 | 0.038424 | Single 509752 INOLATP4 138 509790 CATOOSA4 138 1 | Add 57 MVAR switched shunt at GUAVA 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | BNSF 5 | 1.0031 | 0.9263 | -0.076815 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | BNSF 5 | 1.0031 | 0.9263 | -0.076815 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | BNSF 5 | 1.0031 | 0.9263 | -0.076815 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | BNSF 5 | 1.0031 | 0.9263 | -0.076815 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | BNSF 5 | 1.0031 | 0.9263 | -0.076815 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | BNSF 5 | 1.0031 | 0.9263 | -0.076815 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | BNSF 5 | 1.0031 | 0.9263 | -0.076815 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | BNSF 5 | 1.0031 | 0.9263 | -0.076815 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | BNSF 5 | 1.0031 | 0.9263 | -0.076815 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | BNSF 5 | 1.0031 | 0.9263 | -0.076815 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | BNSF 5 | 1.0031 | 0.9263 | -0.076815 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | BNSF 5 | 1.0031 | 0.9263 | -0.076815 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | BNSF 5 | 1.0031 | 0.9263 | -0.076815 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | BNSF 5 | 1.0031 | 0.9263 | -0.076815 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | BNSF 5 | 1.0031 | 0.9263 | -0.076815 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | BNSF 5 | 1.0031 | 0.9263 | -0.076815 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | BNSF 5 | 1.0031 | 0.9263 | -0.076815 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | BNSF 5 | 1.0031 | 0.9263 | -0.076815 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | BNSF 5 | 1.0031 | 0.9263 | -0.076815 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | BNSF 5 | 1.0031 | 0.9263 | -0.076815 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | BNSF 5 | 1.0031 | 0.9263 | -0.076815 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | BNSF 5 | 1.0031 | 0.9263 | -0.076815 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | BNSF 5 | 1.0031 | 0.9263 | -0.076815 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | BNSF 5 | 1.0031 | 0.9263 | -0.076815 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | BNSF 5 | 1.0031 | 0.9263 | -0.076815 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | BONITA 3 | 0.97065 | 0.92897 | -0.041674 |  | 0.93 | 1.05 | 0.036307 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | BONITA 3 | 0.97065 | 0.92897 | -0.041674 |  | 0.93 | 1.05 | 0.052743 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | BONITA 3 | 0.97065 | 0.92897 | -0.041674 |  | 0.93 | 1.05 | 0.039345 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | BONITA 3 | 0.97065 | 0.92897 | -0.041674 |  | 0.93 | 1.05 | 0.031366 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | BONITA 3 | 0.97065 | 0.92897 | -0.041674 |  | 0.93 | 1.05 | 0.041888 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | BONITA 3 | 0.97065 | 0.92897 | -0.041674 |  | 0.93 | 1.05 | 0.038797 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | BONITA 3 | 0.97065 | 0.92897 | -0.041674 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | BONITA 3 | 0.97065 | 0.92897 | -0.041674 |  | 0.93 | 1.05 | 0.067346 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | BONITA 3 | 0.97065 | 0.92897 | -0.041674 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | BONITA 3 | 0.97065 | 0.92897 | -0.041674 |  | 0.93 | 1.05 | 0.030851 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | BONITA 3 | 0.97065 | 0.92897 | -0.041674 |  | 0.93 | 1.05 | 0.032161 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | BONITA 3 | 0.97065 | 0.92897 | -0.041674 |  | 0.93 | 1.05 | 0.04067 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | BONITA 3 | 0.97065 | 0.92897 | -0.041674 |  | 0.93 | 1.05 | 0.040569 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | BONITA 3 | 0.97065 | 0.92897 | -0.041674 |  | 0.93 | 1.05 | 0.03086 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | BONITA 3 | 0.97065 | 0.92897 | -0.041674 |  | 0.93 | 1.05 | 0.033223 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | BONITA 3 | 0.97065 | 0.92897 | -0.041674 |  | 0.93 | 1.05 | 0.033733 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | BONITA 3 | 0.98596 | 0.91637 | -0.069593 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | BONITA 3 | 0.98596 | 0.91637 | -0.069593 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | BONITA 3 | 0.98596 | 0.91637 | -0.069593 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | BONITA 3 | 0.98596 | 0.91637 | -0.069593 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | BONITA 3 | 0.98596 | 0.91637 | -0.069593 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | BONITA 3 | 0.98596 | 0.91637 | -0.069593 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | BONITA 3 | 0.98596 | 0.91637 | -0.069593 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | BONITA 3 | 0.98596 | 0.91637 | -0.069593 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | BONITA 3 | 0.98596 | 0.91637 | -0.069593 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | BONITA 3 | 0.98596 | 0.91637 | -0.069593 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | BONITA 3 | 0.98596 | 0.91637 | -0.069593 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | BONITA 3 | 0.98596 | 0.91637 | -0.069593 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | BONITA 3 | 0.98596 | 0.91637 | -0.069593 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | BONITA 3 | 0.98596 | 0.91637 | -0.069593 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | BONITA 3 | 0.98596 | 0.91637 | -0.069593 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | BONITA 3 | 0.98596 | 0.91637 | -0.069593 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | BONITA 3 | 0.98596 | 0.91637 | -0.069593 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | BONITA 3 | 0.98596 | 0.91637 | -0.069593 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | BONITA 3 | 0.98596 | 0.91637 | -0.069593 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | BONITA 3 | 0.98596 | 0.91637 | -0.069593 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | BONITA 3 | 0.98596 | 0.91637 | -0.069593 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | BONITA 3 | 0.98596 | 0.91637 | -0.069593 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | BONITA 3 | 0.98596 | 0.91637 | -0.069593 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | BONITA 3 | 0.98596 | 0.91637 | -0.069593 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | BONITA 3 | 0.98596 | 0.91637 | -0.069593 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | BRKRIDG5 | 0.96643 | 0.92886 | -0.037576 |  | 0.93 | 1.05 | 0.036307 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | BRKRIDG5 | 0.96643 | 0.92886 | -0.037576 |  | 0.93 | 1.05 | 0.052743 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | BRKRIDG5 | 0.96643 | 0.92886 | -0.037576 |  | 0.93 | 1.05 | 0.039345 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | BRKRIDG5 | 0.96643 | 0.92886 | -0.037576 |  | 0.93 | 1.05 | 0.031366 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | BRKRIDG5 | 0.96643 | 0.92886 | -0.037576 |  | 0.93 | 1.05 | 0.041888 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | BRKRIDG5 | 0.96643 | 0.92886 | -0.037576 |  | 0.93 | 1.05 | 0.038797 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | BRKRIDG5 | 0.96643 | 0.92886 | -0.037576 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | BRKRIDG5 | 0.96643 | 0.92886 | -0.037576 |  | 0.93 | 1.05 | 0.067346 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | BRKRIDG5 | 0.96643 | 0.92886 | -0.037576 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | BRKRIDG5 | 0.96643 | 0.92886 | -0.037576 |  | 0.93 | 1.05 | 0.030851 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | BRKRIDG5 | 0.96643 | 0.92886 | -0.037576 |  | 0.93 | 1.05 | 0.032161 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | BRKRIDG5 | 0.96643 | 0.92886 | -0.037576 |  | 0.93 | 1.05 | 0.04067 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | BRKRIDG5 | 0.96643 | 0.92886 | -0.037576 |  | 0.93 | 1.05 | 0.040569 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | BRKRIDG5 | 0.96643 | 0.92886 | -0.037576 |  | 0.93 | 1.05 | 0.03086 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | BRKRIDG5 | 0.96643 | 0.92886 | -0.037576 |  | 0.93 | 1.05 | 0.033223 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | BRKRIDG5 | 0.96643 | 0.92886 | -0.037576 |  | 0.93 | 1.05 | 0.033733 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | BRKRIDG5 | 0.97765 | 0.91231 | -0.065336 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | BRKRIDG5 | 0.97765 | 0.91231 | -0.065336 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | BRKRIDG5 | 0.97765 | 0.91231 | -0.065336 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | BRKRIDG5 | 0.97765 | 0.91231 | -0.065336 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | BRKRIDG5 | 0.97765 | 0.91231 | -0.065336 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | BRKRIDG5 | 0.97765 | 0.91231 | -0.065336 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | BRKRIDG5 | 0.97765 | 0.91231 | -0.065336 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | BRKRIDG5 | 0.97765 | 0.91231 | -0.065336 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | BRKRIDG5 | 0.97765 | 0.91231 | -0.065336 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | BRKRIDG5 | 0.97765 | 0.91231 | -0.065336 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | BRKRIDG5 | 0.97765 | 0.91231 | -0.065336 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | BRKRIDG5 | 0.97765 | 0.91231 | -0.065336 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | BRKRIDG5 | 0.97765 | 0.91231 | -0.065336 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | BRKRIDG5 | 0.97765 | 0.91231 | -0.065336 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | BRKRIDG5 | 0.97765 | 0.91231 | -0.065336 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | BRKRIDG5 | 0.97765 | 0.91231 | -0.065336 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | BRKRIDG5 | 0.97765 | 0.91231 | -0.065336 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | BRKRIDG5 | 0.97765 | 0.91231 | -0.065336 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | BRKRIDG5 | 0.97765 | 0.91231 | -0.065336 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | BRKRIDG5 | 0.97765 | 0.91231 | -0.065336 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | BRKRIDG5 | 0.97765 | 0.91231 | -0.065336 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | BRKRIDG5 | 0.97765 | 0.91231 | -0.065336 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | BRKRIDG5 | 0.97765 | 0.91231 | -0.065336 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | BRKRIDG5 | 0.97765 | 0.91231 | -0.065336 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | BRKRIDG5 | 0.97765 | 0.91231 | -0.065336 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | BUCYRUS5 | 0.99463 | 0.90827 | -0.086363 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | BUCYRUS5 | 0.99463 | 0.90827 | -0.086363 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | BUCYRUS5 | 0.99463 | 0.90827 | -0.086363 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | BUCYRUS5 | 0.99463 | 0.90827 | -0.086363 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | BUCYRUS5 | 0.99463 | 0.90827 | -0.086363 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | BUCYRUS5 | 0.99463 | 0.90827 | -0.086363 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | BUCYRUS5 | 0.99463 | 0.90827 | -0.086363 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | BUCYRUS5 | 0.99463 | 0.90827 | -0.086363 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | BUCYRUS5 | 0.99463 | 0.90827 | -0.086363 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | BUCYRUS5 | 0.99463 | 0.90827 | -0.086363 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | BUCYRUS5 | 0.99463 | 0.90827 | -0.086363 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | BUCYRUS5 | 0.99463 | 0.90827 | -0.086363 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | BUCYRUS5 | 0.99463 | 0.90827 | -0.086363 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | BUCYRUS5 | 0.99463 | 0.90827 | -0.086363 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | BUCYRUS5 | 0.99463 | 0.90827 | -0.086363 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | BUCYRUS5 | 0.99463 | 0.90827 | -0.086363 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | BUCYRUS5 | 0.99463 | 0.90827 | -0.086363 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | BUCYRUS5 | 0.99463 | 0.90827 | -0.086363 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | BUCYRUS5 | 0.99463 | 0.90827 | -0.086363 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | BUCYRUS5 | 0.99463 | 0.90827 | -0.086363 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | BUCYRUS5 | 0.99463 | 0.90827 | -0.086363 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | BUCYRUS5 | 0.99463 | 0.90827 | -0.086363 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | BUCYRUS5 | 0.99463 | 0.90827 | -0.086363 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | BUCYRUS5 | 0.99463 | 0.90827 | -0.086363 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | BUCYRUS5 | 0.99463 | 0.90827 | -0.086363 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | BUFFALO4 | 0.98979 | 0.92083 | -0.068962 |  | 0.93 | 1.05 | 0.040439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | BUFFALO4 | 0.98979 | 0.92083 | -0.068962 |  | 0.93 | 1.05 | 0.034853 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | BUFFALO4 | 0.98979 | 0.92083 | -0.068962 |  | 0.93 | 1.05 | 0.046783 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | BUFFALO4 | 0.98979 | 0.92083 | -0.068962 |  | 0.93 | 1.05 | 0.047615 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | BUFFALO4 | 0.98979 | 0.92083 | -0.068962 |  | 0.93 | 1.05 | 0.034938 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | BUFFALO4 | 0.98979 | 0.92083 | -0.068962 |  | 0.93 | 1.05 | 0.037875 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | BUFFALO4 | 0.98979 | 0.92083 | -0.068962 |  | 0.93 | 1.05 | 0.044022 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | BUFFALO4 | 0.98979 | 0.92083 | -0.068962 |  | 0.93 | 1.05 | 0.030552 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | BUFFALO4 | 0.98979 | 0.92083 | -0.068962 |  | 0.93 | 1.05 | 0.038531 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | BUFFALO4 | 0.98979 | 0.92083 | -0.068962 |  | 0.93 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | BUFFALO4 | 0.98979 | 0.92083 | -0.068962 |  | 0.93 | 1.05 | 0.062491 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | BUFFALO4 | 0.98979 | 0.92083 | -0.068962 |  | 0.93 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | BUFFALO4 | 0.98979 | 0.92083 | -0.068962 |  | 0.93 | 1.05 | 0.038129 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | BUFFALO4 | 0.98979 | 0.92083 | -0.068962 |  | 0.93 | 1.05 | 0.038066 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | BUFFALO4 | 0.98979 | 0.92083 | -0.068962 |  | 0.93 | 1.05 | 0.034955 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | BUFFALO4 | 0.98979 | 0.92083 | -0.068962 |  | 0.93 | 1.05 | 0.06281 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | BUFFALO4 | 0.98979 | 0.92083 | -0.068962 |  | 0.93 | 1.05 | 0.045309 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | BUFFALO4 | 0.98979 | 0.92083 | -0.068962 |  | 0.93 | 1.05 | 0.035805 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | BUFFALO4 | 0.98979 | 0.92083 | -0.068962 |  | 0.93 | 1.05 | 0.032364 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | BUFFALO4 | 0.98979 | 0.92083 | -0.068962 |  | 0.93 | 1.05 | 0.031815 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | BUFFALO4 | 0.98979 | 0.92083 | -0.068962 |  | 0.93 | 1.05 | 0.033886 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | BUFFALO4 | 0.98979 | 0.92083 | -0.068962 |  | 0.93 | 1.05 | 0.035554 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | BUFFALO4 | 0.99048 | 0.92184 | -0.068634 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | BUFFALO4 | 0.99048 | 0.92184 | -0.068634 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | BUFFALO4 | 0.99048 | 0.92184 | -0.068634 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | BUFFALO4 | 0.99048 | 0.92184 | -0.068634 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | BUFFALO4 | 0.99048 | 0.92184 | -0.068634 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | BUFFALO4 | 0.99048 | 0.92184 | -0.068634 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | BUFFALO4 | 0.99048 | 0.92184 | -0.068634 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | BUFFALO4 | 0.99048 | 0.92184 | -0.068634 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | BUFFALO4 | 0.99048 | 0.92184 | -0.068634 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | BUFFALO4 | 0.99048 | 0.92184 | -0.068634 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | BUFFALO4 | 0.99048 | 0.92184 | -0.068634 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | BUFFALO4 | 0.99048 | 0.92184 | -0.068634 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | BUFFALO4 | 0.99048 | 0.92184 | -0.068634 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | BUFFALO4 | 0.99048 | 0.92184 | -0.068634 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | BUFFALO4 | 0.99048 | 0.92184 | -0.068634 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | BUFFALO4 | 0.99048 | 0.92184 | -0.068634 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | BUFFALO4 | 0.99048 | 0.92184 | -0.068634 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | BUFFALO4 | 0.99048 | 0.92184 | -0.068634 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | BUFFALO4 | 0.99048 | 0.92184 | -0.068634 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | BUFFALO4 | 0.99048 | 0.92184 | -0.068634 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | BUFFALO4 | 0.99048 | 0.92184 | -0.068634 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | BUFFALO4 | 0.99048 | 0.92184 | -0.068634 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | BUFFALO4 | 0.99048 | 0.92184 | -0.068634 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | BUFFALO4 | 0.99048 | 0.92184 | -0.068634 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | BUFFALO4 | 0.99048 | 0.92184 | -0.068634 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | BUFFALO7 | 0.9928 | 0.93273 | -0.060068 |  | 0.95 | 1.05 | 0.075186 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.02 MVAR switched shunt at BUFFALO7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | BUFFALO7 | 0.9928 | 0.93273 | -0.060068 |  | 0.95 | 1.05 | 0.031338 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.02 MVAR switched shunt at BUFFALO7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | BUFFALO7 | 0.9928 | 0.93273 | -0.060068 |  | 0.95 | 1.05 | 0.031338 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.02 MVAR switched shunt at BUFFALO7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | BUFFALO7 | 0.9928 | 0.93273 | -0.060068 |  | 0.95 | 1.05 | 0.031391 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.02 MVAR switched shunt at BUFFALO7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | BUFFALO7 | 0.9928 | 0.93273 | -0.060068 |  | 0.95 | 1.05 | 0.034523 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.02 MVAR switched shunt at BUFFALO7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | BUFFALO7 | 0.99268 | 0.93158 | -0.0611 |  | 0.95 | 1.05 | 0.075186 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | BUFFALO7 | 0.99268 | 0.93158 | -0.0611 |  | 0.95 | 1.05 | 0.031338 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | BUFFALO7 | 0.99268 | 0.93158 | -0.0611 |  | 0.95 | 1.05 | 0.031338 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | BUFFALO7 | 0.99268 | 0.93158 | -0.0611 |  | 0.95 | 1.05 | 0.031391 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | BUFFALO7 | 0.99268 | 0.93158 | -0.0611 |  | 0.95 | 1.05 | 0.034523 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | BUFFALO7 | 0.9904 | 0.93158 | -0.058829 |  | 0.95 | 1.05 | 0.035768 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | BUFFALO7 | 0.9904 | 0.93158 | -0.058829 |  | 0.95 | 1.05 | 0.088718 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | BUFFALO7 | 0.9904 | 0.93158 | -0.058829 |  | 0.95 | 1.05 | 0.031473 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | BUFFALO7 | 0.9904 | 0.93158 | -0.058829 |  | 0.95 | 1.05 | 0.034941 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | BUFFALO7 | 0.9904 | 0.93158 | -0.058829 |  | 0.95 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | BUFFALO7 | 0.9904 | 0.93158 | -0.058829 |  | 0.95 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | BUFFALO7 | 0.9904 | 0.93158 | -0.058829 |  | 0.95 | 1.05 | 0.049224 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | BUFFALO7 | 0.9904 | 0.93158 | -0.058829 |  | 0.95 | 1.05 | 0.038981 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | BUFFALO7 | 0.9904 | 0.93158 | -0.058829 |  | 0.95 | 1.05 | 0.040399 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | BUFFALO7 | 0.9904 | 0.93158 | -0.058829 |  | 0.95 | 1.05 | 0.031912 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | BUFFALO7 | 0.9904 | 0.93158 | -0.058829 |  | 0.95 | 1.05 | 0.034127 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | BUFFALO7 | 0.9904 | 0.93158 | -0.058829 |  | 0.95 | 1.05 | 0.047318 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | BUFFALO7 | 0.99024 | 0.91802 | -0.072216 |  | 0.95 | 1.05 | 0.040439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | BUFFALO7 | 0.99024 | 0.91802 | -0.072216 |  | 0.95 | 1.05 | 0.034853 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | BUFFALO7 | 0.99024 | 0.91802 | -0.072216 |  | 0.95 | 1.05 | 0.046783 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | BUFFALO7 | 0.99024 | 0.91802 | -0.072216 |  | 0.95 | 1.05 | 0.047615 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | BUFFALO7 | 0.99024 | 0.91802 | -0.072216 |  | 0.95 | 1.05 | 0.034938 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | BUFFALO7 | 0.99024 | 0.91802 | -0.072216 |  | 0.95 | 1.05 | 0.037875 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | BUFFALO7 | 0.99024 | 0.91802 | -0.072216 |  | 0.95 | 1.05 | 0.044022 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | BUFFALO7 | 0.99024 | 0.91802 | -0.072216 |  | 0.95 | 1.05 | 0.030552 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | BUFFALO7 | 0.99024 | 0.91802 | -0.072216 |  | 0.95 | 1.05 | 0.038531 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | BUFFALO7 | 0.99024 | 0.91802 | -0.072216 |  | 0.95 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | BUFFALO7 | 0.99024 | 0.91802 | -0.072216 |  | 0.95 | 1.05 | 0.062491 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | BUFFALO7 | 0.99024 | 0.91802 | -0.072216 |  | 0.95 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | BUFFALO7 | 0.99024 | 0.91802 | -0.072216 |  | 0.95 | 1.05 | 0.038129 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | BUFFALO7 | 0.99024 | 0.91802 | -0.072216 |  | 0.95 | 1.05 | 0.038066 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | BUFFALO7 | 0.99024 | 0.91802 | -0.072216 |  | 0.95 | 1.05 | 0.034955 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | BUFFALO7 | 0.99024 | 0.91802 | -0.072216 |  | 0.95 | 1.05 | 0.06281 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | BUFFALO7 | 0.99024 | 0.91802 | -0.072216 |  | 0.95 | 1.05 | 0.045309 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | BUFFALO7 | 0.99024 | 0.91802 | -0.072216 |  | 0.95 | 1.05 | 0.035805 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | BUFFALO7 | 0.99024 | 0.91802 | -0.072216 |  | 0.95 | 1.05 | 0.032364 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | BUFFALO7 | 0.99024 | 0.91802 | -0.072216 |  | 0.95 | 1.05 | 0.031815 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | BUFFALO7 | 0.99024 | 0.91802 | -0.072216 |  | 0.95 | 1.05 | 0.033886 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | BUFFALO7 | 0.99024 | 0.91802 | -0.072216 |  | 0.95 | 1.05 | 0.035554 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | BUFFALO7 | 0.99103 | 0.91955 | -0.071479 |  | 0.95 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | BUFFALO7 | 0.99103 | 0.91955 | -0.071479 |  | 0.95 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | BUFFALO7 | 0.99103 | 0.91955 | -0.071479 |  | 0.95 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | BUFFALO7 | 0.99103 | 0.91955 | -0.071479 |  | 0.95 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | BUFFALO7 | 0.99103 | 0.91955 | -0.071479 |  | 0.95 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | BUFFALO7 | 0.99103 | 0.91955 | -0.071479 |  | 0.95 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | BUFFALO7 | 0.99103 | 0.91955 | -0.071479 |  | 0.95 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | BUFFALO7 | 0.99103 | 0.91955 | -0.071479 |  | 0.95 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | BUFFALO7 | 0.99103 | 0.91955 | -0.071479 |  | 0.95 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | BUFFALO7 | 0.99103 | 0.91955 | -0.071479 |  | 0.95 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | BUFFALO7 | 0.99103 | 0.91955 | -0.071479 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | BUFFALO7 | 0.99103 | 0.91955 | -0.071479 |  | 0.95 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | BUFFALO7 | 0.99103 | 0.91955 | -0.071479 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | BUFFALO7 | 0.99103 | 0.91955 | -0.071479 |  | 0.95 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | BUFFALO7 | 0.99103 | 0.91955 | -0.071479 |  | 0.95 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | BUFFALO7 | 0.99103 | 0.91955 | -0.071479 |  | 0.95 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | BUFFALO7 | 0.99103 | 0.91955 | -0.071479 |  | 0.95 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | BUFFALO7 | 0.99103 | 0.91955 | -0.071479 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | BUFFALO7 | 0.99103 | 0.91955 | -0.071479 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | BUFFALO7 | 0.99103 | 0.91955 | -0.071479 |  | 0.95 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | BUFFALO7 | 0.99103 | 0.91955 | -0.071479 |  | 0.95 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | BUFFALO7 | 0.99103 | 0.91955 | -0.071479 |  | 0.95 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | BUFFALO7 | 0.99103 | 0.91955 | -0.071479 |  | 0.95 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | BUFFALO7 | 0.99103 | 0.91955 | -0.071479 |  | 0.95 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | BUFFALO7 | 0.99103 | 0.91955 | -0.071479 |  | 0.95 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | BUNKRDG5 | 0.99223 | 0.92915 | -0.063081 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | BUNKRDG5 | 0.99223 | 0.92915 | -0.063081 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | BUNKRDG5 | 0.99223 | 0.92915 | -0.063081 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | BUNKRDG5 | 0.99223 | 0.92915 | -0.063081 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | BUNKRDG5 | 0.99223 | 0.92915 | -0.063081 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | BUNKRDG5 | 0.99223 | 0.92915 | -0.063081 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | BUNKRDG5 | 0.99223 | 0.92915 | -0.063081 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | BUNKRDG5 | 0.99223 | 0.92915 | -0.063081 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | BUNKRDG5 | 0.99223 | 0.92915 | -0.063081 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | BUNKRDG5 | 0.99223 | 0.92915 | -0.063081 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | BUNKRDG5 | 0.99223 | 0.92915 | -0.063081 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | BUNKRDG5 | 0.99223 | 0.92915 | -0.063081 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | BUNKRDG5 | 0.99223 | 0.92915 | -0.063081 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | BUNKRDG5 | 0.99223 | 0.92915 | -0.063081 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | BUNKRDG5 | 0.99223 | 0.92915 | -0.063081 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | BUNKRDG5 | 0.99223 | 0.92915 | -0.063081 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | BUNKRDG5 | 0.99223 | 0.92915 | -0.063081 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | BUNKRDG5 | 0.99223 | 0.92915 | -0.063081 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | BUNKRDG5 | 0.99223 | 0.92915 | -0.063081 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | BUNKRDG5 | 0.99223 | 0.92915 | -0.063081 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | BUNKRDG5 | 0.99223 | 0.92915 | -0.063081 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | BUNKRDG5 | 0.99223 | 0.92915 | -0.063081 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | BUNKRDG5 | 0.99223 | 0.92915 | -0.063081 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | BUNKRDG5 | 0.99223 | 0.92915 | -0.063081 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | BUNKRDG5 | 0.99223 | 0.92915 | -0.063081 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | BURNS 7 | 1.0022 | 0.92998 | -0.072208 |  | 0.95 | 1.05 | 0.03053 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | BURNS 7 | 1.0022 | 0.92998 | -0.072208 |  | 0.95 | 1.05 | 0.044933 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | BURNS 7 | 1.0022 | 0.92998 | -0.072208 |  | 0.95 | 1.05 | 0.047811 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | BURNS 7 | 1.0022 | 0.92998 | -0.072208 |  | 0.95 | 1.05 | 0.09719 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | BURNS 7 | 1.0022 | 0.92998 | -0.072208 |  | 0.95 | 1.05 | 0.069376 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | BURNS 7 | 1.0022 | 0.92998 | -0.072208 |  | 0.95 | 1.05 | 0.04277 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | BURNS 7 | 1.0022 | 0.92998 | -0.072208 |  | 0.95 | 1.05 | 0.071112 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | BURNS 7 | 1.0022 | 0.92998 | -0.072208 |  | 0.95 | 1.05 | 0.039357 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | BURNS 7 | 1.0022 | 0.92998 | -0.072208 |  | 0.95 | 1.05 | 0.04035 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | BURNS 7 | 1.0022 | 0.92998 | -0.072208 |  | 0.95 | 1.05 | 0.052332 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | BURNS 7 | 1.0022 | 0.92998 | -0.072208 |  | 0.95 | 1.05 | 0.045944 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | BURNS 7 | 1.0022 | 0.92998 | -0.072208 |  | 0.95 | 1.05 | 0.038178 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | BURNS 7 | 1.0022 | 0.92998 | -0.072208 |  | 0.95 | 1.05 | 0.13469 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | BURNS 7 | 1.0022 | 0.92998 | -0.072208 |  | 0.95 | 1.05 | 0.03053 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | BURNS 7 | 1.0022 | 0.92998 | -0.072208 |  | 0.95 | 1.05 | 0.038178 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | BURNS 7 | 1.0022 | 0.92998 | -0.072208 |  | 0.95 | 1.05 | 0.037309 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | BURNS 7 | 1.0022 | 0.92998 | -0.072208 |  | 0.95 | 1.05 | 0.040075 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | BURNS 7 | 1.0022 | 0.92998 | -0.072208 |  | 0.95 | 1.05 | 0.053764 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | BURNS 7 | 1.0022 | 0.92998 | -0.072208 |  | 0.95 | 1.05 | 0.071762 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | BURNS 7 | 1.0022 | 0.92998 | -0.072208 |  | 0.95 | 1.05 | 0.047827 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | BURNS 7 | 1.0022 | 0.92998 | -0.072208 |  | 0.95 | 1.05 | 0.047827 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | BURNS 7 | 1.0022 | 0.92998 | -0.072208 |  | 0.95 | 1.05 | 0.070303 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | BURNS 7 | 1.0022 | 0.92998 | -0.072208 |  | 0.95 | 1.05 | 0.040614 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | BURNS 7 | 1.0022 | 0.92998 | -0.072208 |  | 0.95 | 1.05 | 0.039729 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | BURNS 7 | 1.0022 | 0.92998 | -0.072208 |  | 0.95 | 1.05 | 0.049662 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | BURNS 7 | 1.0022 | 0.92998 | -0.072208 |  | 0.95 | 1.05 | 0.042332 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | BURNS 7 | 1.0022 | 0.92998 | -0.072208 |  | 0.95 | 1.05 | 0.048722 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | BURNS 7 | 1.0022 | 0.92998 | -0.072208 |  | 0.95 | 1.05 | 0.038156 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | BURNS 7 | 1.0022 | 0.92998 | -0.072208 |  | 0.95 | 1.05 | 0.036794 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | BURNS 7 | 1.0033 | 0.94464 | -0.058673 |  | 0.95 | 1.05 | 0.075186 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | BURNS 7 | 1.0033 | 0.94464 | -0.058673 |  | 0.95 | 1.05 | 0.031338 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | BURNS 7 | 1.0033 | 0.94464 | -0.058673 |  | 0.95 | 1.05 | 0.031338 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | BURNS 7 | 1.0033 | 0.94464 | -0.058673 |  | 0.95 | 1.05 | 0.031391 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | BURNS 7 | 1.0033 | 0.94464 | -0.058673 |  | 0.95 | 1.05 | 0.034523 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | BURNS 7 | 1.0031 | 0.94012 | -0.062994 |  | 0.95 | 1.05 | 0.036307 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | BURNS 7 | 1.0031 | 0.94012 | -0.062994 |  | 0.95 | 1.05 | 0.052743 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | BURNS 7 | 1.0031 | 0.94012 | -0.062994 |  | 0.95 | 1.05 | 0.039345 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | BURNS 7 | 1.0031 | 0.94012 | -0.062994 |  | 0.95 | 1.05 | 0.031366 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | BURNS 7 | 1.0031 | 0.94012 | -0.062994 |  | 0.95 | 1.05 | 0.041888 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | BURNS 7 | 1.0031 | 0.94012 | -0.062994 |  | 0.95 | 1.05 | 0.038797 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | BURNS 7 | 1.0031 | 0.94012 | -0.062994 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | BURNS 7 | 1.0031 | 0.94012 | -0.062994 |  | 0.95 | 1.05 | 0.067346 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | BURNS 7 | 1.0031 | 0.94012 | -0.062994 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | BURNS 7 | 1.0031 | 0.94012 | -0.062994 |  | 0.95 | 1.05 | 0.030851 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | BURNS 7 | 1.0031 | 0.94012 | -0.062994 |  | 0.95 | 1.05 | 0.032161 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | BURNS 7 | 1.0031 | 0.94012 | -0.062994 |  | 0.95 | 1.05 | 0.04067 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | BURNS 7 | 1.0031 | 0.94012 | -0.062994 |  | 0.95 | 1.05 | 0.040569 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | BURNS 7 | 1.0031 | 0.94012 | -0.062994 |  | 0.95 | 1.05 | 0.03086 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | BURNS 7 | 1.0031 | 0.94012 | -0.062994 |  | 0.95 | 1.05 | 0.033223 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | BURNS 7 | 1.0031 | 0.94012 | -0.062994 |  | 0.95 | 1.05 | 0.033733 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | BURNS 7 | 0.99939 | 0.91787 | -0.081519 |  | 0.95 | 1.05 | 0.040439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | BURNS 7 | 0.99939 | 0.91787 | -0.081519 |  | 0.95 | 1.05 | 0.034853 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | BURNS 7 | 0.99939 | 0.91787 | -0.081519 |  | 0.95 | 1.05 | 0.046783 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | BURNS 7 | 0.99939 | 0.91787 | -0.081519 |  | 0.95 | 1.05 | 0.047615 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | BURNS 7 | 0.99939 | 0.91787 | -0.081519 |  | 0.95 | 1.05 | 0.034938 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | BURNS 7 | 0.99939 | 0.91787 | -0.081519 |  | 0.95 | 1.05 | 0.037875 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | BURNS 7 | 0.99939 | 0.91787 | -0.081519 |  | 0.95 | 1.05 | 0.044022 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | BURNS 7 | 0.99939 | 0.91787 | -0.081519 |  | 0.95 | 1.05 | 0.030552 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | BURNS 7 | 0.99939 | 0.91787 | -0.081519 |  | 0.95 | 1.05 | 0.038531 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | BURNS 7 | 0.99939 | 0.91787 | -0.081519 |  | 0.95 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | BURNS 7 | 0.99939 | 0.91787 | -0.081519 |  | 0.95 | 1.05 | 0.062491 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | BURNS 7 | 0.99939 | 0.91787 | -0.081519 |  | 0.95 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | BURNS 7 | 0.99939 | 0.91787 | -0.081519 |  | 0.95 | 1.05 | 0.038129 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | BURNS 7 | 0.99939 | 0.91787 | -0.081519 |  | 0.95 | 1.05 | 0.038066 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | BURNS 7 | 0.99939 | 0.91787 | -0.081519 |  | 0.95 | 1.05 | 0.034955 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | BURNS 7 | 0.99939 | 0.91787 | -0.081519 |  | 0.95 | 1.05 | 0.06281 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | BURNS 7 | 0.99939 | 0.91787 | -0.081519 |  | 0.95 | 1.05 | 0.045309 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | BURNS 7 | 0.99939 | 0.91787 | -0.081519 |  | 0.95 | 1.05 | 0.035805 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | BURNS 7 | 0.99939 | 0.91787 | -0.081519 |  | 0.95 | 1.05 | 0.032364 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | BURNS 7 | 0.99939 | 0.91787 | -0.081519 |  | 0.95 | 1.05 | 0.031815 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | BURNS 7 | 0.99939 | 0.91787 | -0.081519 |  | 0.95 | 1.05 | 0.033886 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | BURNS 7 | 0.99939 | 0.91787 | -0.081519 |  | 0.95 | 1.05 | 0.035554 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | BURNS 7 | 0.99875 | 0.9229 | -0.075852 |  | 0.95 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | BURNS 7 | 0.99875 | 0.9229 | -0.075852 |  | 0.95 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | BURNS 7 | 0.99875 | 0.9229 | -0.075852 |  | 0.95 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | BURNS 7 | 0.99875 | 0.9229 | -0.075852 |  | 0.95 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | BURNS 7 | 0.99875 | 0.9229 | -0.075852 |  | 0.95 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | BURNS 7 | 0.99875 | 0.9229 | -0.075852 |  | 0.95 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | BURNS 7 | 0.99875 | 0.9229 | -0.075852 |  | 0.95 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | BURNS 7 | 0.99875 | 0.9229 | -0.075852 |  | 0.95 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | BURNS 7 | 0.99875 | 0.9229 | -0.075852 |  | 0.95 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | BURNS 7 | 0.99875 | 0.9229 | -0.075852 |  | 0.95 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | BURNS 7 | 0.99875 | 0.9229 | -0.075852 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | BURNS 7 | 0.99875 | 0.9229 | -0.075852 |  | 0.95 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | BURNS 7 | 0.99875 | 0.9229 | -0.075852 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | BURNS 7 | 0.99875 | 0.9229 | -0.075852 |  | 0.95 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | BURNS 7 | 0.99875 | 0.9229 | -0.075852 |  | 0.95 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | BURNS 7 | 0.99875 | 0.9229 | -0.075852 |  | 0.95 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | BURNS 7 | 0.99875 | 0.9229 | -0.075852 |  | 0.95 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | BURNS 7 | 0.99875 | 0.9229 | -0.075852 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | BURNS 7 | 0.99875 | 0.9229 | -0.075852 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | BURNS 7 | 0.99875 | 0.9229 | -0.075852 |  | 0.95 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | BURNS 7 | 0.99875 | 0.9229 | -0.075852 |  | 0.95 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | BURNS 7 | 0.99875 | 0.9229 | -0.075852 |  | 0.95 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | BURNS 7 | 0.99875 | 0.9229 | -0.075852 |  | 0.95 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | BURNS 7 | 0.99875 | 0.9229 | -0.075852 |  | 0.95 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | BURNS 7 | 0.99875 | 0.9229 | -0.075852 |  | 0.95 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | CANEYRV7 | 0.98465 | 0.94967 | -0.03498 |  | 0.95 | 1.05 | 0.034914 | P23:345:WERE:WOLF-345-50:EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | CANEYRV7 | 0.98465 | 0.94967 | -0.03498 |  | 0.95 | 1.05 | 0.033648 | P23:345:WERE:WOLF-345-50:EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | CANEYRV7 | 0.98465 | 0.94967 | -0.03498 |  | 0.95 | 1.05 | 0.030226 | P23:345:WERE:WOLF-345-50:EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | CANEYRV7 | 0.98465 | 0.94967 | -0.03498 |  | 0.95 | 1.05 | 0.03107 | P23:345:WERE:WOLF-345-50:EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | CANEYRV7 | 0.99077 | 0.941 | -0.049765 |  | 0.95 | 1.05 | 0.035768 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | CANEYRV7 | 0.99077 | 0.941 | -0.049765 |  | 0.95 | 1.05 | 0.088718 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | CANEYRV7 | 0.99077 | 0.941 | -0.049765 |  | 0.95 | 1.05 | 0.031473 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | CANEYRV7 | 0.99077 | 0.941 | -0.049765 |  | 0.95 | 1.05 | 0.034941 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | CANEYRV7 | 0.99077 | 0.941 | -0.049765 |  | 0.95 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | CANEYRV7 | 0.99077 | 0.941 | -0.049765 |  | 0.95 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | CANEYRV7 | 0.99077 | 0.941 | -0.049765 |  | 0.95 | 1.05 | 0.049224 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | CANEYRV7 | 0.99077 | 0.941 | -0.049765 |  | 0.95 | 1.05 | 0.038981 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | CANEYRV7 | 0.99077 | 0.941 | -0.049765 |  | 0.95 | 1.05 | 0.040399 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | CANEYRV7 | 0.99077 | 0.941 | -0.049765 |  | 0.95 | 1.05 | 0.031912 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | CANEYRV7 | 0.99077 | 0.941 | -0.049765 |  | 0.95 | 1.05 | 0.034127 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | CANEYRV7 | 0.99077 | 0.941 | -0.049765 |  | 0.95 | 1.05 | 0.047318 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | CANEYRV7 | 0.9839 | 0.92897 | -0.054928 |  | 0.95 | 1.05 | 0.040439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | CANEYRV7 | 0.9839 | 0.92897 | -0.054928 |  | 0.95 | 1.05 | 0.034853 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | CANEYRV7 | 0.9839 | 0.92897 | -0.054928 |  | 0.95 | 1.05 | 0.046783 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | CANEYRV7 | 0.9839 | 0.92897 | -0.054928 |  | 0.95 | 1.05 | 0.047615 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | CANEYRV7 | 0.9839 | 0.92897 | -0.054928 |  | 0.95 | 1.05 | 0.034938 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | CANEYRV7 | 0.9839 | 0.92897 | -0.054928 |  | 0.95 | 1.05 | 0.037875 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | CANEYRV7 | 0.9839 | 0.92897 | -0.054928 |  | 0.95 | 1.05 | 0.044022 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | CANEYRV7 | 0.9839 | 0.92897 | -0.054928 |  | 0.95 | 1.05 | 0.030552 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | CANEYRV7 | 0.9839 | 0.92897 | -0.054928 |  | 0.95 | 1.05 | 0.038531 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | CANEYRV7 | 0.9839 | 0.92897 | -0.054928 |  | 0.95 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | CANEYRV7 | 0.9839 | 0.92897 | -0.054928 |  | 0.95 | 1.05 | 0.062491 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | CANEYRV7 | 0.9839 | 0.92897 | -0.054928 |  | 0.95 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | CANEYRV7 | 0.9839 | 0.92897 | -0.054928 |  | 0.95 | 1.05 | 0.038129 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | CANEYRV7 | 0.9839 | 0.92897 | -0.054928 |  | 0.95 | 1.05 | 0.038066 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | CANEYRV7 | 0.9839 | 0.92897 | -0.054928 |  | 0.95 | 1.05 | 0.034955 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | CANEYRV7 | 0.9839 | 0.92897 | -0.054928 |  | 0.95 | 1.05 | 0.06281 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | CANEYRV7 | 0.9839 | 0.92897 | -0.054928 |  | 0.95 | 1.05 | 0.045309 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | CANEYRV7 | 0.9839 | 0.92897 | -0.054928 |  | 0.95 | 1.05 | 0.035805 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | CANEYRV7 | 0.9839 | 0.92897 | -0.054928 |  | 0.95 | 1.05 | 0.032364 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | CANEYRV7 | 0.9839 | 0.92897 | -0.054928 |  | 0.95 | 1.05 | 0.031815 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | CANEYRV7 | 0.9839 | 0.92897 | -0.054928 |  | 0.95 | 1.05 | 0.033886 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | CANEYRV7 | 0.9839 | 0.92897 | -0.054928 |  | 0.95 | 1.05 | 0.035554 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | CANEYRV7 | 0.99325 | 0.93947 | -0.053782 |  | 0.95 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | CANEYRV7 | 0.99325 | 0.93947 | -0.053782 |  | 0.95 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | CANEYRV7 | 0.99325 | 0.93947 | -0.053782 |  | 0.95 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | CANEYRV7 | 0.99325 | 0.93947 | -0.053782 |  | 0.95 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | CANEYRV7 | 0.99325 | 0.93947 | -0.053782 |  | 0.95 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | CANEYRV7 | 0.99325 | 0.93947 | -0.053782 |  | 0.95 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | CANEYRV7 | 0.99325 | 0.93947 | -0.053782 |  | 0.95 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | CANEYRV7 | 0.99325 | 0.93947 | -0.053782 |  | 0.95 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | CANEYRV7 | 0.99325 | 0.93947 | -0.053782 |  | 0.95 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | CANEYRV7 | 0.99325 | 0.93947 | -0.053782 |  | 0.95 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | CANEYRV7 | 0.99325 | 0.93947 | -0.053782 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | CANEYRV7 | 0.99325 | 0.93947 | -0.053782 |  | 0.95 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | CANEYRV7 | 0.99325 | 0.93947 | -0.053782 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | CANEYRV7 | 0.99325 | 0.93947 | -0.053782 |  | 0.95 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | CANEYRV7 | 0.99325 | 0.93947 | -0.053782 |  | 0.95 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | CANEYRV7 | 0.99325 | 0.93947 | -0.053782 |  | 0.95 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | CANEYRV7 | 0.99325 | 0.93947 | -0.053782 |  | 0.95 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | CANEYRV7 | 0.99325 | 0.93947 | -0.053782 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | CANEYRV7 | 0.99325 | 0.93947 | -0.053782 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | CANEYRV7 | 0.99325 | 0.93947 | -0.053782 |  | 0.95 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | CANEYRV7 | 0.99325 | 0.93947 | -0.053782 |  | 0.95 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | CANEYRV7 | 0.99325 | 0.93947 | -0.053782 |  | 0.95 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | CANEYRV7 | 0.99325 | 0.93947 | -0.053782 |  | 0.95 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | CANEYRV7 | 0.99325 | 0.93947 | -0.053782 |  | 0.95 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | CANEYRV7 | 0.99325 | 0.93947 | -0.053782 |  | 0.95 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | CANEYWF7 | 0.98477 | 0.94979 | -0.034984 |  | 0.95 | 1.05 | 0.034914 | P23:345:WERE:WOLF-345-50:EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | CANEYWF7 | 0.98477 | 0.94979 | -0.034984 |  | 0.95 | 1.05 | 0.033648 | P23:345:WERE:WOLF-345-50:EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | CANEYWF7 | 0.98477 | 0.94979 | -0.034984 |  | 0.95 | 1.05 | 0.030226 | P23:345:WERE:WOLF-345-50:EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | CANEYWF7 | 0.98477 | 0.94979 | -0.034984 |  | 0.95 | 1.05 | 0.03107 | P23:345:WERE:WOLF-345-50:EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | CANEYWF7 | 0.99089 | 0.94112 | -0.049771 |  | 0.95 | 1.05 | 0.035768 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | CANEYWF7 | 0.99089 | 0.94112 | -0.049771 |  | 0.95 | 1.05 | 0.088718 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | CANEYWF7 | 0.99089 | 0.94112 | -0.049771 |  | 0.95 | 1.05 | 0.031473 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | CANEYWF7 | 0.99089 | 0.94112 | -0.049771 |  | 0.95 | 1.05 | 0.034941 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | CANEYWF7 | 0.99089 | 0.94112 | -0.049771 |  | 0.95 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | CANEYWF7 | 0.99089 | 0.94112 | -0.049771 |  | 0.95 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | CANEYWF7 | 0.99089 | 0.94112 | -0.049771 |  | 0.95 | 1.05 | 0.049224 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | CANEYWF7 | 0.99089 | 0.94112 | -0.049771 |  | 0.95 | 1.05 | 0.038981 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | CANEYWF7 | 0.99089 | 0.94112 | -0.049771 |  | 0.95 | 1.05 | 0.040399 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | CANEYWF7 | 0.99089 | 0.94112 | -0.049771 |  | 0.95 | 1.05 | 0.031912 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | CANEYWF7 | 0.99089 | 0.94112 | -0.049771 |  | 0.95 | 1.05 | 0.034127 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | CANEYWF7 | 0.99089 | 0.94112 | -0.049771 |  | 0.95 | 1.05 | 0.047318 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | CANEYWF7 | 0.98402 | 0.92908 | -0.054934 |  | 0.95 | 1.05 | 0.040439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | CANEYWF7 | 0.98402 | 0.92908 | -0.054934 |  | 0.95 | 1.05 | 0.034853 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | CANEYWF7 | 0.98402 | 0.92908 | -0.054934 |  | 0.95 | 1.05 | 0.046783 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | CANEYWF7 | 0.98402 | 0.92908 | -0.054934 |  | 0.95 | 1.05 | 0.047615 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | CANEYWF7 | 0.98402 | 0.92908 | -0.054934 |  | 0.95 | 1.05 | 0.034938 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | CANEYWF7 | 0.98402 | 0.92908 | -0.054934 |  | 0.95 | 1.05 | 0.037875 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | CANEYWF7 | 0.98402 | 0.92908 | -0.054934 |  | 0.95 | 1.05 | 0.044022 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | CANEYWF7 | 0.98402 | 0.92908 | -0.054934 |  | 0.95 | 1.05 | 0.030552 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | CANEYWF7 | 0.98402 | 0.92908 | -0.054934 |  | 0.95 | 1.05 | 0.038531 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | CANEYWF7 | 0.98402 | 0.92908 | -0.054934 |  | 0.95 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | CANEYWF7 | 0.98402 | 0.92908 | -0.054934 |  | 0.95 | 1.05 | 0.062491 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | CANEYWF7 | 0.98402 | 0.92908 | -0.054934 |  | 0.95 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | CANEYWF7 | 0.98402 | 0.92908 | -0.054934 |  | 0.95 | 1.05 | 0.038129 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | CANEYWF7 | 0.98402 | 0.92908 | -0.054934 |  | 0.95 | 1.05 | 0.038066 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | CANEYWF7 | 0.98402 | 0.92908 | -0.054934 |  | 0.95 | 1.05 | 0.034955 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | CANEYWF7 | 0.98402 | 0.92908 | -0.054934 |  | 0.95 | 1.05 | 0.06281 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | CANEYWF7 | 0.98402 | 0.92908 | -0.054934 |  | 0.95 | 1.05 | 0.045309 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | CANEYWF7 | 0.98402 | 0.92908 | -0.054934 |  | 0.95 | 1.05 | 0.035805 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | CANEYWF7 | 0.98402 | 0.92908 | -0.054934 |  | 0.95 | 1.05 | 0.032364 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | CANEYWF7 | 0.98402 | 0.92908 | -0.054934 |  | 0.95 | 1.05 | 0.031815 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | CANEYWF7 | 0.98402 | 0.92908 | -0.054934 |  | 0.95 | 1.05 | 0.033886 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | CANEYWF7 | 0.98402 | 0.92908 | -0.054934 |  | 0.95 | 1.05 | 0.035554 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | CANEYWF7 | 0.99335 | 0.93959 | -0.053762 |  | 0.95 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | CANEYWF7 | 0.99335 | 0.93959 | -0.053762 |  | 0.95 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | CANEYWF7 | 0.99335 | 0.93959 | -0.053762 |  | 0.95 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | CANEYWF7 | 0.99335 | 0.93959 | -0.053762 |  | 0.95 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | CANEYWF7 | 0.99335 | 0.93959 | -0.053762 |  | 0.95 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | CANEYWF7 | 0.99335 | 0.93959 | -0.053762 |  | 0.95 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | CANEYWF7 | 0.99335 | 0.93959 | -0.053762 |  | 0.95 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | CANEYWF7 | 0.99335 | 0.93959 | -0.053762 |  | 0.95 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | CANEYWF7 | 0.99335 | 0.93959 | -0.053762 |  | 0.95 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | CANEYWF7 | 0.99335 | 0.93959 | -0.053762 |  | 0.95 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | CANEYWF7 | 0.99335 | 0.93959 | -0.053762 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | CANEYWF7 | 0.99335 | 0.93959 | -0.053762 |  | 0.95 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | CANEYWF7 | 0.99335 | 0.93959 | -0.053762 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | CANEYWF7 | 0.99335 | 0.93959 | -0.053762 |  | 0.95 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | CANEYWF7 | 0.99335 | 0.93959 | -0.053762 |  | 0.95 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | CANEYWF7 | 0.99335 | 0.93959 | -0.053762 |  | 0.95 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | CANEYWF7 | 0.99335 | 0.93959 | -0.053762 |  | 0.95 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | CANEYWF7 | 0.99335 | 0.93959 | -0.053762 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | CANEYWF7 | 0.99335 | 0.93959 | -0.053762 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | CANEYWF7 | 0.99335 | 0.93959 | -0.053762 |  | 0.95 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | CANEYWF7 | 0.99335 | 0.93959 | -0.053762 |  | 0.95 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | CANEYWF7 | 0.99335 | 0.93959 | -0.053762 |  | 0.95 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | CANEYWF7 | 0.99335 | 0.93959 | -0.053762 |  | 0.95 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | CANEYWF7 | 0.99335 | 0.93959 | -0.053762 |  | 0.95 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | CANEYWF7 | 0.99335 | 0.93959 | -0.053762 |  | 0.95 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | CARB-KW 3 | 0.9854 | 0.92628 | -0.059128 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | CARB-KW 3 | 0.9854 | 0.92628 | -0.059128 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | CARB-KW 3 | 0.9854 | 0.92628 | -0.059128 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | CARB-KW 3 | 0.9854 | 0.92628 | -0.059128 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | CARB-KW 3 | 0.9854 | 0.92628 | -0.059128 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | CARB-KW 3 | 0.9854 | 0.92628 | -0.059128 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | CARB-KW 3 | 0.9854 | 0.92628 | -0.059128 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | CARB-KW 3 | 0.9854 | 0.92628 | -0.059128 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | CARB-KW 3 | 0.9854 | 0.92628 | -0.059128 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | CARB-KW 3 | 0.9854 | 0.92628 | -0.059128 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | CARB-KW 3 | 0.9854 | 0.92628 | -0.059128 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | CARB-KW 3 | 0.9854 | 0.92628 | -0.059128 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | CARB-KW 3 | 0.9854 | 0.92628 | -0.059128 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | CARB-KW 3 | 0.9854 | 0.92628 | -0.059128 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | CARB-KW 3 | 0.9854 | 0.92628 | -0.059128 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | CARB-KW 3 | 0.9854 | 0.92628 | -0.059128 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | CARB-KW 3 | 0.9854 | 0.92628 | -0.059128 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | CARB-KW 3 | 0.9854 | 0.92628 | -0.059128 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | CARB-KW 3 | 0.9854 | 0.92628 | -0.059128 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | CARB-KW 3 | 0.9854 | 0.92628 | -0.059128 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | CARB-KW 3 | 0.9854 | 0.92628 | -0.059128 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | CARB-KW 3 | 0.9854 | 0.92628 | -0.059128 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | CARB-KW 3 | 0.9854 | 0.92628 | -0.059128 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | CARB-KW 3 | 0.9854 | 0.92628 | -0.059128 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | CARB-KW 3 | 0.9854 | 0.92628 | -0.059128 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | CEDRCRK5 | 0.98774 | 0.92248 | -0.065255 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | CEDRCRK5 | 0.98774 | 0.92248 | -0.065255 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | CEDRCRK5 | 0.98774 | 0.92248 | -0.065255 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | CEDRCRK5 | 0.98774 | 0.92248 | -0.065255 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | CEDRCRK5 | 0.98774 | 0.92248 | -0.065255 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | CEDRCRK5 | 0.98774 | 0.92248 | -0.065255 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | CEDRCRK5 | 0.98774 | 0.92248 | -0.065255 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | CEDRCRK5 | 0.98774 | 0.92248 | -0.065255 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | CEDRCRK5 | 0.98774 | 0.92248 | -0.065255 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | CEDRCRK5 | 0.98774 | 0.92248 | -0.065255 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | CEDRCRK5 | 0.98774 | 0.92248 | -0.065255 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | CEDRCRK5 | 0.98774 | 0.92248 | -0.065255 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | CEDRCRK5 | 0.98774 | 0.92248 | -0.065255 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | CEDRCRK5 | 0.98774 | 0.92248 | -0.065255 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | CEDRCRK5 | 0.98774 | 0.92248 | -0.065255 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | CEDRCRK5 | 0.98774 | 0.92248 | -0.065255 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | CEDRCRK5 | 0.98774 | 0.92248 | -0.065255 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | CEDRCRK5 | 0.98774 | 0.92248 | -0.065255 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | CEDRCRK5 | 0.98774 | 0.92248 | -0.065255 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | CEDRCRK5 | 0.98774 | 0.92248 | -0.065255 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | CEDRCRK5 | 0.98774 | 0.92248 | -0.065255 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | CEDRCRK5 | 0.98774 | 0.92248 | -0.065255 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | CEDRCRK5 | 0.98774 | 0.92248 | -0.065255 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | CEDRCRK5 | 0.98774 | 0.92248 | -0.065255 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | CEDRCRK5 | 0.98774 | 0.92248 | -0.065255 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | CENTENL5 | 0.98735 | 0.92503 | -0.062318 |  | 0.93 | 1.05 | 0.036307 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | CENTENL5 | 0.98735 | 0.92503 | -0.062318 |  | 0.93 | 1.05 | 0.052743 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | CENTENL5 | 0.98735 | 0.92503 | -0.062318 |  | 0.93 | 1.05 | 0.039345 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | CENTENL5 | 0.98735 | 0.92503 | -0.062318 |  | 0.93 | 1.05 | 0.031366 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | CENTENL5 | 0.98735 | 0.92503 | -0.062318 |  | 0.93 | 1.05 | 0.041888 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | CENTENL5 | 0.98735 | 0.92503 | -0.062318 |  | 0.93 | 1.05 | 0.038797 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | CENTENL5 | 0.98735 | 0.92503 | -0.062318 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | CENTENL5 | 0.98735 | 0.92503 | -0.062318 |  | 0.93 | 1.05 | 0.067346 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | CENTENL5 | 0.98735 | 0.92503 | -0.062318 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | CENTENL5 | 0.98735 | 0.92503 | -0.062318 |  | 0.93 | 1.05 | 0.030851 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | CENTENL5 | 0.98735 | 0.92503 | -0.062318 |  | 0.93 | 1.05 | 0.032161 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | CENTENL5 | 0.98735 | 0.92503 | -0.062318 |  | 0.93 | 1.05 | 0.04067 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | CENTENL5 | 0.98735 | 0.92503 | -0.062318 |  | 0.93 | 1.05 | 0.040569 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | CENTENL5 | 0.98735 | 0.92503 | -0.062318 |  | 0.93 | 1.05 | 0.03086 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | CENTENL5 | 0.98735 | 0.92503 | -0.062318 |  | 0.93 | 1.05 | 0.033223 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | CENTENL5 | 0.98735 | 0.92503 | -0.062318 |  | 0.93 | 1.05 | 0.033733 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | CENTENL5 | 0.99759 | 0.92732 | -0.070269 |  | 0.93 | 1.05 | 0.036307 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | CENTENL5 | 0.99759 | 0.92732 | -0.070269 |  | 0.93 | 1.05 | 0.052743 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | CENTENL5 | 0.99759 | 0.92732 | -0.070269 |  | 0.93 | 1.05 | 0.039345 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | CENTENL5 | 0.99759 | 0.92732 | -0.070269 |  | 0.93 | 1.05 | 0.031366 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | CENTENL5 | 0.99759 | 0.92732 | -0.070269 |  | 0.93 | 1.05 | 0.041888 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | CENTENL5 | 0.99759 | 0.92732 | -0.070269 |  | 0.93 | 1.05 | 0.038797 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | CENTENL5 | 0.99759 | 0.92732 | -0.070269 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | CENTENL5 | 0.99759 | 0.92732 | -0.070269 |  | 0.93 | 1.05 | 0.067346 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | CENTENL5 | 0.99759 | 0.92732 | -0.070269 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | CENTENL5 | 0.99759 | 0.92732 | -0.070269 |  | 0.93 | 1.05 | 0.030851 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | CENTENL5 | 0.99759 | 0.92732 | -0.070269 |  | 0.93 | 1.05 | 0.032161 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | CENTENL5 | 0.99759 | 0.92732 | -0.070269 |  | 0.93 | 1.05 | 0.04067 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | CENTENL5 | 0.99759 | 0.92732 | -0.070269 |  | 0.93 | 1.05 | 0.040569 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | CENTENL5 | 0.99759 | 0.92732 | -0.070269 |  | 0.93 | 1.05 | 0.03086 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | CENTENL5 | 0.99759 | 0.92732 | -0.070269 |  | 0.93 | 1.05 | 0.033223 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | CENTENL5 | 0.99759 | 0.92732 | -0.070269 |  | 0.93 | 1.05 | 0.033733 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | CENTENL5 | 1.0004 | 0.90426 | -0.096135 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | CENTENL5 | 1.0004 | 0.90426 | -0.096135 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | CENTENL5 | 1.0004 | 0.90426 | -0.096135 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | CENTENL5 | 1.0004 | 0.90426 | -0.096135 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | CENTENL5 | 1.0004 | 0.90426 | -0.096135 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | CENTENL5 | 1.0004 | 0.90426 | -0.096135 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | CENTENL5 | 1.0004 | 0.90426 | -0.096135 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | CENTENL5 | 1.0004 | 0.90426 | -0.096135 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | CENTENL5 | 1.0004 | 0.90426 | -0.096135 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | CENTENL5 | 1.0004 | 0.90426 | -0.096135 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | CENTENL5 | 1.0004 | 0.90426 | -0.096135 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | CENTENL5 | 1.0004 | 0.90426 | -0.096135 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | CENTENL5 | 1.0004 | 0.90426 | -0.096135 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | CENTENL5 | 1.0004 | 0.90426 | -0.096135 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | CENTENL5 | 1.0004 | 0.90426 | -0.096135 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | CENTENL5 | 1.0004 | 0.90426 | -0.096135 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | CENTENL5 | 1.0004 | 0.90426 | -0.096135 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | CENTENL5 | 1.0004 | 0.90426 | -0.096135 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | CENTENL5 | 1.0004 | 0.90426 | -0.096135 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | CENTENL5 | 1.0004 | 0.90426 | -0.096135 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | CENTENL5 | 1.0004 | 0.90426 | -0.096135 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | CENTENL5 | 1.0004 | 0.90426 | -0.096135 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | CENTENL5 | 1.0004 | 0.90426 | -0.096135 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | CENTENL5 | 1.0004 | 0.90426 | -0.096135 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | CENTENL5 | 1.0004 | 0.90426 | -0.096135 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | CHAMSPR7 | 0.98517 | 0.91853 | -0.066644 |  | 0.92 | 1.05 | 0.035932 | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: | Add 0.11 MVAR switched shunt at CHAMSPR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | CHAMSPR7 | 0.98517 | 0.91853 | -0.066644 |  | 0.92 | 1.05 | 0.054461 | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: | Add 0.11 MVAR switched shunt at CHAMSPR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | CHAMSPR7 | 0.98517 | 0.91853 | -0.066644 |  | 0.92 | 1.05 | 0.068475 | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: | Add 0.11 MVAR switched shunt at CHAMSPR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | CHAMSPR7 | 0.98517 | 0.91853 | -0.066644 |  | 0.92 | 1.05 | 0.034821 | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: | Add 0.11 MVAR switched shunt at CHAMSPR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | CHAMSPR7 | 0.98517 | 0.91853 | -0.066644 |  | 0.92 | 1.05 | 0.1501 | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: | Add 0.11 MVAR switched shunt at CHAMSPR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | CHAMSPR7 | 0.98517 | 0.91853 | -0.066644 |  | 0.92 | 1.05 | 0.057116 | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: | Add 0.11 MVAR switched shunt at CHAMSPR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | CHAMSPR7 | 0.98476 | 0.91701 | -0.06774 |  | 0.92 | 1.05 | 0.035932 | P23:345:GRDA:TONNECE CB9580:::EHV: | Add 0.4 MVAR switched shunt at TONTITN7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | CHAMSPR7 | 0.98476 | 0.91701 | -0.06774 |  | 0.92 | 1.05 | 0.057432 | P23:345:GRDA:TONNECE CB9580:::EHV: | Add 0.4 MVAR switched shunt at TONTITN7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | CHAMSPR7 | 0.98476 | 0.91701 | -0.06774 |  | 0.92 | 1.05 | 0.068475 | P23:345:GRDA:TONNECE CB9580:::EHV: | Add 0.4 MVAR switched shunt at TONTITN7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | CHAMSPR7 | 0.98476 | 0.91701 | -0.06774 |  | 0.92 | 1.05 | 0.035744 | P23:345:GRDA:TONNECE CB9580:::EHV: | Add 0.4 MVAR switched shunt at TONTITN7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | CHAMSPR7 | 0.98476 | 0.91701 | -0.06774 |  | 0.92 | 1.05 | 0.1501 | P23:345:GRDA:TONNECE CB9580:::EHV: | Add 0.4 MVAR switched shunt at TONTITN7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | CHAMSPR7 | 0.98476 | 0.91701 | -0.06774 |  | 0.92 | 1.05 | 0.058419 | P23:345:GRDA:TONNECE CB9580:::EHV: | Add 0.4 MVAR switched shunt at TONTITN7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | CHOUTEA4 | 0.89053 | 0.86218 | -0.028345 |  | 0.92 | 1.05 | 0.038424 | Single 509752 INOLATP4 138 509790 CATOOSA4 138 1 | Add 57 MVAR switched shunt at GUAVA 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | CHOUTEA4 | 0.90309 | 0.87662 | -0.026473 |  | 0.92 | 1.05 | 0.038424 | Single 509752 INOLATP4 138 510442 GUAVA4 138 1 | Add 57 MVAR switched shunt at GUAVA 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | CLEARVW3 | 0.97116 | 0.92919 | -0.041969 |  | 0.93 | 1.05 | 0.036307 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | CLEARVW3 | 0.97116 | 0.92919 | -0.041969 |  | 0.93 | 1.05 | 0.052743 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | CLEARVW3 | 0.97116 | 0.92919 | -0.041969 |  | 0.93 | 1.05 | 0.039345 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | CLEARVW3 | 0.97116 | 0.92919 | -0.041969 |  | 0.93 | 1.05 | 0.031366 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | CLEARVW3 | 0.97116 | 0.92919 | -0.041969 |  | 0.93 | 1.05 | 0.041888 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | CLEARVW3 | 0.97116 | 0.92919 | -0.041969 |  | 0.93 | 1.05 | 0.038797 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | CLEARVW3 | 0.97116 | 0.92919 | -0.041969 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | CLEARVW3 | 0.97116 | 0.92919 | -0.041969 |  | 0.93 | 1.05 | 0.067346 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | CLEARVW3 | 0.97116 | 0.92919 | -0.041969 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | CLEARVW3 | 0.97116 | 0.92919 | -0.041969 |  | 0.93 | 1.05 | 0.030851 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | CLEARVW3 | 0.97116 | 0.92919 | -0.041969 |  | 0.93 | 1.05 | 0.032161 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | CLEARVW3 | 0.97116 | 0.92919 | -0.041969 |  | 0.93 | 1.05 | 0.04067 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | CLEARVW3 | 0.97116 | 0.92919 | -0.041969 |  | 0.93 | 1.05 | 0.040569 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | CLEARVW3 | 0.97116 | 0.92919 | -0.041969 |  | 0.93 | 1.05 | 0.03086 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | CLEARVW3 | 0.97116 | 0.92919 | -0.041969 |  | 0.93 | 1.05 | 0.033223 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | CLEARVW3 | 0.97116 | 0.92919 | -0.041969 |  | 0.93 | 1.05 | 0.033733 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | CLEARVW3 | 0.98692 | 0.92296 | -0.06396 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | CLEARVW3 | 0.98692 | 0.92296 | -0.06396 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | CLEARVW3 | 0.98692 | 0.92296 | -0.06396 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | CLEARVW3 | 0.98692 | 0.92296 | -0.06396 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | CLEARVW3 | 0.98692 | 0.92296 | -0.06396 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | CLEARVW3 | 0.98692 | 0.92296 | -0.06396 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | CLEARVW3 | 0.98692 | 0.92296 | -0.06396 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | CLEARVW3 | 0.98692 | 0.92296 | -0.06396 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | CLEARVW3 | 0.98692 | 0.92296 | -0.06396 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | CLEARVW3 | 0.98692 | 0.92296 | -0.06396 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | CLEARVW3 | 0.98692 | 0.92296 | -0.06396 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | CLEARVW3 | 0.98692 | 0.92296 | -0.06396 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | CLEARVW3 | 0.98692 | 0.92296 | -0.06396 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | CLEARVW3 | 0.98692 | 0.92296 | -0.06396 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | CLEARVW3 | 0.98692 | 0.92296 | -0.06396 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | CLEARVW3 | 0.98692 | 0.92296 | -0.06396 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | CLEARVW3 | 0.98692 | 0.92296 | -0.06396 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | CLEARVW3 | 0.98692 | 0.92296 | -0.06396 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | CLEARVW3 | 0.98692 | 0.92296 | -0.06396 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | CLEARVW3 | 0.98692 | 0.92296 | -0.06396 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | CLEARVW3 | 0.98692 | 0.92296 | -0.06396 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | CLEARVW3 | 0.98692 | 0.92296 | -0.06396 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | CLEARVW3 | 0.98692 | 0.92296 | -0.06396 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | CLEARVW3 | 0.98692 | 0.92296 | -0.06396 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | CLEARVW3 | 0.98692 | 0.92296 | -0.06396 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | CLINTON5 | 0.99137 | 0.91278 | -0.078595 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | CLINTON5 | 0.99137 | 0.91278 | -0.078595 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | CLINTON5 | 0.99137 | 0.91278 | -0.078595 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | CLINTON5 | 0.99137 | 0.91278 | -0.078595 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | CLINTON5 | 0.99137 | 0.91278 | -0.078595 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | CLINTON5 | 0.99137 | 0.91278 | -0.078595 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | CLINTON5 | 0.99137 | 0.91278 | -0.078595 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | CLINTON5 | 0.99137 | 0.91278 | -0.078595 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | CLINTON5 | 0.99137 | 0.91278 | -0.078595 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | CLINTON5 | 0.99137 | 0.91278 | -0.078595 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | CLINTON5 | 0.99137 | 0.91278 | -0.078595 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | CLINTON5 | 0.99137 | 0.91278 | -0.078595 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | CLINTON5 | 0.99137 | 0.91278 | -0.078595 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | CLINTON5 | 0.99137 | 0.91278 | -0.078595 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | CLINTON5 | 0.99137 | 0.91278 | -0.078595 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | CLINTON5 | 0.99137 | 0.91278 | -0.078595 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | CLINTON5 | 0.99137 | 0.91278 | -0.078595 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | CLINTON5 | 0.99137 | 0.91278 | -0.078595 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | CLINTON5 | 0.99137 | 0.91278 | -0.078595 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | CLINTON5 | 0.99137 | 0.91278 | -0.078595 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | CLINTON5 | 0.99137 | 0.91278 | -0.078595 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | CLINTON5 | 0.99137 | 0.91278 | -0.078595 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | CLINTON5 | 0.99137 | 0.91278 | -0.078595 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | CLINTON5 | 0.99137 | 0.91278 | -0.078595 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | CLINTON5 | 0.99137 | 0.91278 | -0.078595 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | CNTRVIL5 | 0.9888 | 0.90667 | -0.08213 |  | 0.93 | 1.05 | 0.03053 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | CNTRVIL5 | 0.9888 | 0.90667 | -0.08213 |  | 0.93 | 1.05 | 0.044933 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | CNTRVIL5 | 0.9888 | 0.90667 | -0.08213 |  | 0.93 | 1.05 | 0.047811 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | CNTRVIL5 | 0.9888 | 0.90667 | -0.08213 |  | 0.93 | 1.05 | 0.09719 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | CNTRVIL5 | 0.9888 | 0.90667 | -0.08213 |  | 0.93 | 1.05 | 0.069376 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | CNTRVIL5 | 0.9888 | 0.90667 | -0.08213 |  | 0.93 | 1.05 | 0.04277 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | CNTRVIL5 | 0.9888 | 0.90667 | -0.08213 |  | 0.93 | 1.05 | 0.071112 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | CNTRVIL5 | 0.9888 | 0.90667 | -0.08213 |  | 0.93 | 1.05 | 0.039357 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | CNTRVIL5 | 0.9888 | 0.90667 | -0.08213 |  | 0.93 | 1.05 | 0.04035 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | CNTRVIL5 | 0.9888 | 0.90667 | -0.08213 |  | 0.93 | 1.05 | 0.052332 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | CNTRVIL5 | 0.9888 | 0.90667 | -0.08213 |  | 0.93 | 1.05 | 0.045944 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | CNTRVIL5 | 0.9888 | 0.90667 | -0.08213 |  | 0.93 | 1.05 | 0.038178 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | CNTRVIL5 | 0.9888 | 0.90667 | -0.08213 |  | 0.93 | 1.05 | 0.13469 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | CNTRVIL5 | 0.9888 | 0.90667 | -0.08213 |  | 0.93 | 1.05 | 0.03053 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | CNTRVIL5 | 0.9888 | 0.90667 | -0.08213 |  | 0.93 | 1.05 | 0.038178 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | CNTRVIL5 | 0.9888 | 0.90667 | -0.08213 |  | 0.93 | 1.05 | 0.037309 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | CNTRVIL5 | 0.9888 | 0.90667 | -0.08213 |  | 0.93 | 1.05 | 0.040075 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | CNTRVIL5 | 0.9888 | 0.90667 | -0.08213 |  | 0.93 | 1.05 | 0.053764 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | CNTRVIL5 | 0.9888 | 0.90667 | -0.08213 |  | 0.93 | 1.05 | 0.071762 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | CNTRVIL5 | 0.9888 | 0.90667 | -0.08213 |  | 0.93 | 1.05 | 0.047827 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | CNTRVIL5 | 0.9888 | 0.90667 | -0.08213 |  | 0.93 | 1.05 | 0.047827 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | CNTRVIL5 | 0.9888 | 0.90667 | -0.08213 |  | 0.93 | 1.05 | 0.070303 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | CNTRVIL5 | 0.9888 | 0.90667 | -0.08213 |  | 0.93 | 1.05 | 0.040614 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | CNTRVIL5 | 0.9888 | 0.90667 | -0.08213 |  | 0.93 | 1.05 | 0.039729 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | CNTRVIL5 | 0.9888 | 0.90667 | -0.08213 |  | 0.93 | 1.05 | 0.049662 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | CNTRVIL5 | 0.9888 | 0.90667 | -0.08213 |  | 0.93 | 1.05 | 0.042332 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | CNTRVIL5 | 0.9888 | 0.90667 | -0.08213 |  | 0.93 | 1.05 | 0.048722 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | CNTRVIL5 | 0.9888 | 0.90667 | -0.08213 |  | 0.93 | 1.05 | 0.038156 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | CNTRVIL5 | 0.9888 | 0.90667 | -0.08213 |  | 0.93 | 1.05 | 0.036794 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | CNTRVIL5 | 0.98313 | 0.91637 | -0.066767 |  | 0.93 | 1.05 | 0.036307 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | CNTRVIL5 | 0.98313 | 0.91637 | -0.066767 |  | 0.93 | 1.05 | 0.052743 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | CNTRVIL5 | 0.98313 | 0.91637 | -0.066767 |  | 0.93 | 1.05 | 0.039345 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | CNTRVIL5 | 0.98313 | 0.91637 | -0.066767 |  | 0.93 | 1.05 | 0.031366 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | CNTRVIL5 | 0.98313 | 0.91637 | -0.066767 |  | 0.93 | 1.05 | 0.041888 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | CNTRVIL5 | 0.98313 | 0.91637 | -0.066767 |  | 0.93 | 1.05 | 0.038797 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | CNTRVIL5 | 0.98313 | 0.91637 | -0.066767 |  | 0.93 | 1.05 | 0.030557 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | CNTRVIL5 | 0.98313 | 0.91637 | -0.066767 |  | 0.93 | 1.05 | 0.067346 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | CNTRVIL5 | 0.98313 | 0.91637 | -0.066767 |  | 0.93 | 1.05 | 0.030557 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | CNTRVIL5 | 0.98313 | 0.91637 | -0.066767 |  | 0.93 | 1.05 | 0.030851 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | CNTRVIL5 | 0.98313 | 0.91637 | -0.066767 |  | 0.93 | 1.05 | 0.032161 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | CNTRVIL5 | 0.98313 | 0.91637 | -0.066767 |  | 0.93 | 1.05 | 0.04067 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | CNTRVIL5 | 0.98313 | 0.91637 | -0.066767 |  | 0.93 | 1.05 | 0.040569 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | CNTRVIL5 | 0.98313 | 0.91637 | -0.066767 |  | 0.93 | 1.05 | 0.03086 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | CNTRVIL5 | 0.98313 | 0.91637 | -0.066767 |  | 0.93 | 1.05 | 0.033223 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | CNTRVIL5 | 0.98313 | 0.91637 | -0.066767 |  | 0.93 | 1.05 | 0.033733 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | CNTRVIL5 | 0.97965 | 0.90875 | -0.070905 |  | 0.93 | 1.05 | 0.036307 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | CNTRVIL5 | 0.97965 | 0.90875 | -0.070905 |  | 0.93 | 1.05 | 0.052743 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | CNTRVIL5 | 0.97965 | 0.90875 | -0.070905 |  | 0.93 | 1.05 | 0.039345 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | CNTRVIL5 | 0.97965 | 0.90875 | -0.070905 |  | 0.93 | 1.05 | 0.031366 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | CNTRVIL5 | 0.97965 | 0.90875 | -0.070905 |  | 0.93 | 1.05 | 0.041888 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | CNTRVIL5 | 0.97965 | 0.90875 | -0.070905 |  | 0.93 | 1.05 | 0.038797 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | CNTRVIL5 | 0.97965 | 0.90875 | -0.070905 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | CNTRVIL5 | 0.97965 | 0.90875 | -0.070905 |  | 0.93 | 1.05 | 0.067346 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | CNTRVIL5 | 0.97965 | 0.90875 | -0.070905 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | CNTRVIL5 | 0.97965 | 0.90875 | -0.070905 |  | 0.93 | 1.05 | 0.030851 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | CNTRVIL5 | 0.97965 | 0.90875 | -0.070905 |  | 0.93 | 1.05 | 0.032161 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | CNTRVIL5 | 0.97965 | 0.90875 | -0.070905 |  | 0.93 | 1.05 | 0.04067 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | CNTRVIL5 | 0.97965 | 0.90875 | -0.070905 |  | 0.93 | 1.05 | 0.040569 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | CNTRVIL5 | 0.97965 | 0.90875 | -0.070905 |  | 0.93 | 1.05 | 0.03086 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | CNTRVIL5 | 0.97965 | 0.90875 | -0.070905 |  | 0.93 | 1.05 | 0.033223 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | CNTRVIL5 | 0.97965 | 0.90875 | -0.070905 |  | 0.93 | 1.05 | 0.033733 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | CNTRVIL5 | 0.98603 | 0.9067 | -0.079326 |  | 0.93 | 1.05 | 0.036307 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | CNTRVIL5 | 0.98603 | 0.9067 | -0.079326 |  | 0.93 | 1.05 | 0.052743 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | CNTRVIL5 | 0.98603 | 0.9067 | -0.079326 |  | 0.93 | 1.05 | 0.039345 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | CNTRVIL5 | 0.98603 | 0.9067 | -0.079326 |  | 0.93 | 1.05 | 0.031366 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | CNTRVIL5 | 0.98603 | 0.9067 | -0.079326 |  | 0.93 | 1.05 | 0.041888 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | CNTRVIL5 | 0.98603 | 0.9067 | -0.079326 |  | 0.93 | 1.05 | 0.038797 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | CNTRVIL5 | 0.98603 | 0.9067 | -0.079326 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | CNTRVIL5 | 0.98603 | 0.9067 | -0.079326 |  | 0.93 | 1.05 | 0.067346 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | CNTRVIL5 | 0.98603 | 0.9067 | -0.079326 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | CNTRVIL5 | 0.98603 | 0.9067 | -0.079326 |  | 0.93 | 1.05 | 0.030851 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | CNTRVIL5 | 0.98603 | 0.9067 | -0.079326 |  | 0.93 | 1.05 | 0.032161 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | CNTRVIL5 | 0.98603 | 0.9067 | -0.079326 |  | 0.93 | 1.05 | 0.04067 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | CNTRVIL5 | 0.98603 | 0.9067 | -0.079326 |  | 0.93 | 1.05 | 0.040569 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | CNTRVIL5 | 0.98603 | 0.9067 | -0.079326 |  | 0.93 | 1.05 | 0.03086 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | CNTRVIL5 | 0.98603 | 0.9067 | -0.079326 |  | 0.93 | 1.05 | 0.033223 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | CNTRVIL5 | 0.98603 | 0.9067 | -0.079326 |  | 0.93 | 1.05 | 0.033733 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | CNTRVIL5 | 0.98816 | 0.89462 | -0.093542 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | CNTRVIL5 | 0.98816 | 0.89462 | -0.093542 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | CNTRVIL5 | 0.98816 | 0.89462 | -0.093542 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | CNTRVIL5 | 0.98816 | 0.89462 | -0.093542 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | CNTRVIL5 | 0.98816 | 0.89462 | -0.093542 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | CNTRVIL5 | 0.98816 | 0.89462 | -0.093542 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | CNTRVIL5 | 0.98816 | 0.89462 | -0.093542 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | CNTRVIL5 | 0.98816 | 0.89462 | -0.093542 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | CNTRVIL5 | 0.98816 | 0.89462 | -0.093542 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | CNTRVIL5 | 0.98816 | 0.89462 | -0.093542 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | CNTRVIL5 | 0.98816 | 0.89462 | -0.093542 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | CNTRVIL5 | 0.98816 | 0.89462 | -0.093542 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | CNTRVIL5 | 0.98816 | 0.89462 | -0.093542 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | CNTRVIL5 | 0.98816 | 0.89462 | -0.093542 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | CNTRVIL5 | 0.98816 | 0.89462 | -0.093542 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | CNTRVIL5 | 0.98816 | 0.89462 | -0.093542 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | CNTRVIL5 | 0.98816 | 0.89462 | -0.093542 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | CNTRVIL5 | 0.98816 | 0.89462 | -0.093542 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | CNTRVIL5 | 0.98816 | 0.89462 | -0.093542 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | CNTRVIL5 | 0.98816 | 0.89462 | -0.093542 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | CNTRVIL5 | 0.98816 | 0.89462 | -0.093542 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | CNTRVIL5 | 0.98816 | 0.89462 | -0.093542 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | CNTRVIL5 | 0.98816 | 0.89462 | -0.093542 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | CNTRVIL5 | 0.98816 | 0.89462 | -0.093542 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | CNTRVIL5 | 0.98816 | 0.89462 | -0.093542 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | COLLEGE5 | 0.98283 | 0.91639 | -0.066439 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | COLLEGE5 | 0.98283 | 0.91639 | -0.066439 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | COLLEGE5 | 0.98283 | 0.91639 | -0.066439 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | COLLEGE5 | 0.98283 | 0.91639 | -0.066439 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | COLLEGE5 | 0.98283 | 0.91639 | -0.066439 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | COLLEGE5 | 0.98283 | 0.91639 | -0.066439 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | COLLEGE5 | 0.98283 | 0.91639 | -0.066439 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | COLLEGE5 | 0.98283 | 0.91639 | -0.066439 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | COLLEGE5 | 0.98283 | 0.91639 | -0.066439 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | COLLEGE5 | 0.98283 | 0.91639 | -0.066439 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | COLLEGE5 | 0.98283 | 0.91639 | -0.066439 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | COLLEGE5 | 0.98283 | 0.91639 | -0.066439 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | COLLEGE5 | 0.98283 | 0.91639 | -0.066439 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | COLLEGE5 | 0.98283 | 0.91639 | -0.066439 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | COLLEGE5 | 0.98283 | 0.91639 | -0.066439 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | COLLEGE5 | 0.98283 | 0.91639 | -0.066439 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | COLLEGE5 | 0.98283 | 0.91639 | -0.066439 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | COLLEGE5 | 0.98283 | 0.91639 | -0.066439 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | COLLEGE5 | 0.98283 | 0.91639 | -0.066439 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | COLLEGE5 | 0.98283 | 0.91639 | -0.066439 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | COLLEGE5 | 0.98283 | 0.91639 | -0.066439 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | COLLEGE5 | 0.98283 | 0.91639 | -0.066439 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | COLLEGE5 | 0.98283 | 0.91639 | -0.066439 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | COLLEGE5 | 0.98283 | 0.91639 | -0.066439 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | COLLEGE5 | 0.98283 | 0.91639 | -0.066439 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | COOYYAH4 | 0.9054 | 0.87785 | -0.027546 |  | 0.92 | 1.05 | 0.038424 | Single 509752 INOLATP4 138 509790 CATOOSA4 138 1 | Add 57 MVAR switched shunt at GUAVA 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | COOYYAH4 | 0.91664 | 0.8908 | -0.025842 |  | 0.92 | 1.05 | 0.038424 | Single 509752 INOLATP4 138 510442 GUAVA4 138 1 | Add 57 MVAR switched shunt at GUAVA 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | COWSKIN 4 | 0.96051 | 0.89765 | -0.062856 |  | 0.9 | 1.05 | 0.033596 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | COWSKIN 4 | 0.96051 | 0.89765 | -0.062856 |  | 0.9 | 1.05 | 0.040193 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | COWSKIN 4 | 0.96051 | 0.89765 | -0.062856 |  | 0.9 | 1.05 | 0.088122 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | COWSKIN 4 | 0.96051 | 0.89765 | -0.062856 |  | 0.9 | 1.05 | 0.074664 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | COWSKIN 4 | 0.96051 | 0.89765 | -0.062856 |  | 0.9 | 1.05 | 0.068051 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | COWSKIN 4 | 0.96051 | 0.89765 | -0.062856 |  | 0.9 | 1.05 | 0.035565 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | COWSKIN 4 | 0.96051 | 0.89765 | -0.062856 |  | 0.9 | 1.05 | 0.033904 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | COWSKIN 4 | 0.96051 | 0.89765 | -0.062856 |  | 0.9 | 1.05 | 0.16366 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | COWSKIN 4 | 0.96051 | 0.89765 | -0.062856 |  | 0.9 | 1.05 | 0.045569 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | COWSKIN 4 | 0.96051 | 0.89765 | -0.062856 |  | 0.9 | 1.05 | 0.13458 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | COWSKIN 4 | 0.96051 | 0.89765 | -0.062856 |  | 0.9 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | COWSKIN 4 | 0.96051 | 0.89765 | -0.062856 |  | 0.9 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | COWSKIN 4 | 0.96051 | 0.89765 | -0.062856 |  | 0.9 | 1.05 | 0.068426 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | COWSKIN 4 | 0.96051 | 0.89765 | -0.062856 |  | 0.9 | 1.05 | 0.035223 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | COWSKIN 4 | 0.96051 | 0.89765 | -0.062856 |  | 0.9 | 1.05 | 0.034504 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | COWSKIN 4 | 0.96063 | 0.8984 | -0.062226 |  | 0.9 | 1.05 | 0.040193 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | COWSKIN 4 | 0.96063 | 0.8984 | -0.062226 |  | 0.9 | 1.05 | 0.088122 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | COWSKIN 4 | 0.96063 | 0.8984 | -0.062226 |  | 0.9 | 1.05 | 0.074664 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | COWSKIN 4 | 0.96063 | 0.8984 | -0.062226 |  | 0.9 | 1.05 | 0.068051 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | COWSKIN 4 | 0.96063 | 0.8984 | -0.062226 |  | 0.9 | 1.05 | 0.034774 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | COWSKIN 4 | 0.96063 | 0.8984 | -0.062226 |  | 0.9 | 1.05 | 0.033904 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | COWSKIN 4 | 0.96063 | 0.8984 | -0.062226 |  | 0.9 | 1.05 | 0.16366 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | COWSKIN 4 | 0.96063 | 0.8984 | -0.062226 |  | 0.9 | 1.05 | 0.045569 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | COWSKIN 4 | 0.96063 | 0.8984 | -0.062226 |  | 0.9 | 1.05 | 0.13458 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | COWSKIN 4 | 0.96063 | 0.8984 | -0.062226 |  | 0.9 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | COWSKIN 4 | 0.96063 | 0.8984 | -0.062226 |  | 0.9 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | COWSKIN 4 | 0.96063 | 0.8984 | -0.062226 |  | 0.9 | 1.05 | 0.068426 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | COWSKIN 4 | 0.96063 | 0.8984 | -0.062226 |  | 0.9 | 1.05 | 0.035223 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | COWSKIN 4 | 0.96063 | 0.8984 | -0.062226 |  | 0.9 | 1.05 | 0.034504 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | COWSKIN2 | 0.95139 | 0.89063 | -0.060769 |  | 0.9 | 1.05 | 0.033596 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | COWSKIN2 | 0.95139 | 0.89063 | -0.060769 |  | 0.9 | 1.05 | 0.040193 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | COWSKIN2 | 0.95139 | 0.89063 | -0.060769 |  | 0.9 | 1.05 | 0.088122 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | COWSKIN2 | 0.95139 | 0.89063 | -0.060769 |  | 0.9 | 1.05 | 0.074664 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | COWSKIN2 | 0.95139 | 0.89063 | -0.060769 |  | 0.9 | 1.05 | 0.068051 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | COWSKIN2 | 0.95139 | 0.89063 | -0.060769 |  | 0.9 | 1.05 | 0.035565 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | COWSKIN2 | 0.95139 | 0.89063 | -0.060769 |  | 0.9 | 1.05 | 0.033904 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | COWSKIN2 | 0.95139 | 0.89063 | -0.060769 |  | 0.9 | 1.05 | 0.16366 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | COWSKIN2 | 0.95139 | 0.89063 | -0.060769 |  | 0.9 | 1.05 | 0.045569 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | COWSKIN2 | 0.95139 | 0.89063 | -0.060769 |  | 0.9 | 1.05 | 0.13458 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | COWSKIN2 | 0.95139 | 0.89063 | -0.060769 |  | 0.9 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | COWSKIN2 | 0.95139 | 0.89063 | -0.060769 |  | 0.9 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | COWSKIN2 | 0.95139 | 0.89063 | -0.060769 |  | 0.9 | 1.05 | 0.068426 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | COWSKIN2 | 0.95139 | 0.89063 | -0.060769 |  | 0.9 | 1.05 | 0.035223 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | COWSKIN2 | 0.95139 | 0.89063 | -0.060769 |  | 0.9 | 1.05 | 0.034504 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | COWSKIN2 | 0.9515 | 0.8914 | -0.060103 |  | 0.9 | 1.05 | 0.040193 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | COWSKIN2 | 0.9515 | 0.8914 | -0.060103 |  | 0.9 | 1.05 | 0.088122 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | COWSKIN2 | 0.9515 | 0.8914 | -0.060103 |  | 0.9 | 1.05 | 0.074664 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | COWSKIN2 | 0.9515 | 0.8914 | -0.060103 |  | 0.9 | 1.05 | 0.068051 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | COWSKIN2 | 0.9515 | 0.8914 | -0.060103 |  | 0.9 | 1.05 | 0.034774 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | COWSKIN2 | 0.9515 | 0.8914 | -0.060103 |  | 0.9 | 1.05 | 0.033904 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | COWSKIN2 | 0.9515 | 0.8914 | -0.060103 |  | 0.9 | 1.05 | 0.16366 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | COWSKIN2 | 0.9515 | 0.8914 | -0.060103 |  | 0.9 | 1.05 | 0.045569 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | COWSKIN2 | 0.9515 | 0.8914 | -0.060103 |  | 0.9 | 1.05 | 0.13458 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | COWSKIN2 | 0.9515 | 0.8914 | -0.060103 |  | 0.9 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | COWSKIN2 | 0.9515 | 0.8914 | -0.060103 |  | 0.9 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | COWSKIN2 | 0.9515 | 0.8914 | -0.060103 |  | 0.9 | 1.05 | 0.068426 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | COWSKIN2 | 0.9515 | 0.8914 | -0.060103 |  | 0.9 | 1.05 | 0.035223 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | COWSKIN2 | 0.9515 | 0.8914 | -0.060103 |  | 0.9 | 1.05 | 0.034504 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | COWSKIN2 | 0.95127 | 0.89497 | -0.056297 |  | 0.9 | 1.05 | 0.033596 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | COWSKIN2 | 0.95127 | 0.89497 | -0.056297 |  | 0.9 | 1.05 | 0.040193 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | COWSKIN2 | 0.95127 | 0.89497 | -0.056297 |  | 0.9 | 1.05 | 0.056051 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | COWSKIN2 | 0.95127 | 0.89497 | -0.056297 |  | 0.9 | 1.05 | 0.074664 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | COWSKIN2 | 0.95127 | 0.89497 | -0.056297 |  | 0.9 | 1.05 | 0.068051 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | COWSKIN2 | 0.95127 | 0.89497 | -0.056297 |  | 0.9 | 1.05 | 0.035565 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | COWSKIN2 | 0.95127 | 0.89497 | -0.056297 |  | 0.9 | 1.05 | 0.033904 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | COWSKIN2 | 0.95127 | 0.89497 | -0.056297 |  | 0.9 | 1.05 | 0.082596 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | COWSKIN2 | 0.95127 | 0.89497 | -0.056297 |  | 0.9 | 1.05 | 0.045569 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | COWSKIN2 | 0.95127 | 0.89497 | -0.056297 |  | 0.9 | 1.05 | 0.13458 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | COWSKIN2 | 0.95127 | 0.89497 | -0.056297 |  | 0.9 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | COWSKIN2 | 0.95127 | 0.89497 | -0.056297 |  | 0.9 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | COWSKIN2 | 0.95127 | 0.89497 | -0.056297 |  | 0.9 | 1.05 | 0.068426 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | COWSKIN2 | 0.95127 | 0.89497 | -0.056297 |  | 0.9 | 1.05 | 0.035223 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | COWSKIN2 | 0.95127 | 0.89497 | -0.056297 |  | 0.9 | 1.05 | 0.034504 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | COWSKIN2 | 0.94915 | 0.89589 | -0.053253 |  | 0.9 | 1.05 | 0.035932 | P23:345:GRDA:TONNECE CB9580:::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | COWSKIN2 | 0.94915 | 0.89589 | -0.053253 |  | 0.9 | 1.05 | 0.057432 | P23:345:GRDA:TONNECE CB9580:::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | COWSKIN2 | 0.94915 | 0.89589 | -0.053253 |  | 0.9 | 1.05 | 0.068475 | P23:345:GRDA:TONNECE CB9580:::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | COWSKIN2 | 0.94915 | 0.89589 | -0.053253 |  | 0.9 | 1.05 | 0.035744 | P23:345:GRDA:TONNECE CB9580:::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | COWSKIN2 | 0.94915 | 0.89589 | -0.053253 |  | 0.9 | 1.05 | 0.1501 | P23:345:GRDA:TONNECE CB9580:::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | COWSKIN2 | 0.94915 | 0.89589 | -0.053253 |  | 0.9 | 1.05 | 0.058419 | P23:345:GRDA:TONNECE CB9580:::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | COWSKIN2 | 0.95024 | 0.89851 | -0.051729 |  | 0.9 | 1.05 | 0.035932 | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: | Add 0.02 MVAR switched shunt at JAY 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | COWSKIN2 | 0.95024 | 0.89851 | -0.051729 |  | 0.9 | 1.05 | 0.054461 | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: | Add 0.02 MVAR switched shunt at JAY 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | COWSKIN2 | 0.95024 | 0.89851 | -0.051729 |  | 0.9 | 1.05 | 0.068475 | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: | Add 0.02 MVAR switched shunt at JAY 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | COWSKIN2 | 0.95024 | 0.89851 | -0.051729 |  | 0.9 | 1.05 | 0.034821 | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: | Add 0.02 MVAR switched shunt at JAY 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | COWSKIN2 | 0.95024 | 0.89851 | -0.051729 |  | 0.9 | 1.05 | 0.1501 | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: | Add 0.02 MVAR switched shunt at JAY 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | COWSKIN2 | 0.95024 | 0.89851 | -0.051729 |  | 0.9 | 1.05 | 0.057116 | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: | Add 0.02 MVAR switched shunt at JAY 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | CPK446 5 | 0.97134 | 0.91772 | -0.053619 |  | 0.925 | 1.05 | 0.033596 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | CPK446 5 | 0.97134 | 0.91772 | -0.053619 |  | 0.925 | 1.05 | 0.040193 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | CPK446 5 | 0.97134 | 0.91772 | -0.053619 |  | 0.925 | 1.05 | 0.088122 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | CPK446 5 | 0.97134 | 0.91772 | -0.053619 |  | 0.925 | 1.05 | 0.074664 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | CPK446 5 | 0.97134 | 0.91772 | -0.053619 |  | 0.925 | 1.05 | 0.068051 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | CPK446 5 | 0.97134 | 0.91772 | -0.053619 |  | 0.925 | 1.05 | 0.035565 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | CPK446 5 | 0.97134 | 0.91772 | -0.053619 |  | 0.925 | 1.05 | 0.033904 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | CPK446 5 | 0.97134 | 0.91772 | -0.053619 |  | 0.925 | 1.05 | 0.16366 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | CPK446 5 | 0.97134 | 0.91772 | -0.053619 |  | 0.925 | 1.05 | 0.045569 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | CPK446 5 | 0.97134 | 0.91772 | -0.053619 |  | 0.925 | 1.05 | 0.13458 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | CPK446 5 | 0.97134 | 0.91772 | -0.053619 |  | 0.925 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | CPK446 5 | 0.97134 | 0.91772 | -0.053619 |  | 0.925 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | CPK446 5 | 0.97134 | 0.91772 | -0.053619 |  | 0.925 | 1.05 | 0.068426 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | CPK446 5 | 0.97134 | 0.91772 | -0.053619 |  | 0.925 | 1.05 | 0.035223 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | CPK446 5 | 0.97134 | 0.91772 | -0.053619 |  | 0.925 | 1.05 | 0.034504 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | CPK446 5 | 0.97224 | 0.91997 | -0.052275 |  | 0.925 | 1.05 | 0.033596 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.2 MVAR switched shunt at GROVE 5 161 kV; Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | CPK446 5 | 0.97224 | 0.91997 | -0.052275 |  | 0.925 | 1.05 | 0.088122 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.2 MVAR switched shunt at GROVE 5 161 kV; Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | CPK446 5 | 0.97224 | 0.91997 | -0.052275 |  | 0.925 | 1.05 | 0.030897 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.2 MVAR switched shunt at GROVE 5 161 kV; Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | CPK446 5 | 0.97224 | 0.91997 | -0.052275 |  | 0.925 | 1.05 | 0.038719 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.2 MVAR switched shunt at GROVE 5 161 kV; Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | CPK446 5 | 0.97224 | 0.91997 | -0.052275 |  | 0.925 | 1.05 | 0.035565 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.2 MVAR switched shunt at GROVE 5 161 kV; Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | CPK446 5 | 0.97224 | 0.91997 | -0.052275 |  | 0.925 | 1.05 | 0.16366 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.2 MVAR switched shunt at GROVE 5 161 kV; Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | CPK446 5 | 0.97224 | 0.91997 | -0.052275 |  | 0.925 | 1.05 | 0.038589 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.2 MVAR switched shunt at GROVE 5 161 kV; Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | CPK446 5 | 0.97224 | 0.91997 | -0.052275 |  | 0.925 | 1.05 | 0.034208 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.2 MVAR switched shunt at GROVE 5 161 kV; Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | CPK446 5 | 0.97025 | 0.91806 | -0.052187 |  | 0.925 | 1.05 | 0.033596 | P23:345:AECI:7JASPER:1182::: | Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | CPK446 5 | 0.97025 | 0.91806 | -0.052187 |  | 0.925 | 1.05 | 0.056051 | P23:345:AECI:7JASPER:1182::: | Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | CPK446 5 | 0.97025 | 0.91806 | -0.052187 |  | 0.925 | 1.05 | 0.030897 | P23:345:AECI:7JASPER:1182::: | Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | CPK446 5 | 0.97025 | 0.91806 | -0.052187 |  | 0.925 | 1.05 | 0.038719 | P23:345:AECI:7JASPER:1182::: | Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | CPK446 5 | 0.97025 | 0.91806 | -0.052187 |  | 0.925 | 1.05 | 0.035565 | P23:345:AECI:7JASPER:1182::: | Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | CPK446 5 | 0.97025 | 0.91806 | -0.052187 |  | 0.925 | 1.05 | 0.082596 | P23:345:AECI:7JASPER:1182::: | Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | CPK446 5 | 0.97025 | 0.91806 | -0.052187 |  | 0.925 | 1.05 | 0.038589 | P23:345:AECI:7JASPER:1182::: | Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | CPK446 5 | 0.97025 | 0.91806 | -0.052187 |  | 0.925 | 1.05 | 0.034208 | P23:345:AECI:7JASPER:1182::: | Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | ASGI-2024-023 | CPK446 5 | 0.97212 | 0.91881 | -0.053313 |  | 0.925 | 1.05 | 0.079962 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | CPK446 5 | 0.97212 | 0.91881 | -0.053313 |  | 0.925 | 1.05 | 0.065323 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-068 | CPK446 5 | 0.97212 | 0.91881 | -0.053313 |  | 0.925 | 1.05 | 0.067422 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-071 | CPK446 5 | 0.97212 | 0.91881 | -0.053313 |  | 0.925 | 1.05 | 0.074668 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | CPK446 5 | 0.97212 | 0.91881 | -0.053313 |  | 0.925 | 1.05 | 0.053027 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-122 | CPK446 5 | 0.97212 | 0.91881 | -0.053313 |  | 0.925 | 1.05 | 0.082926 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-177 | CPK446 5 | 0.97212 | 0.91881 | -0.053313 |  | 0.925 | 1.05 | 0.084694 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-178 | CPK446 5 | 0.97212 | 0.91881 | -0.053313 |  | 0.925 | 1.05 | 0.078867 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | CPK446 5 | 0.97212 | 0.91881 | -0.053313 |  | 0.925 | 1.05 | 0.031571 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-220 | CPK446 5 | 0.97212 | 0.91881 | -0.053313 |  | 0.925 | 1.05 | 0.075331 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-232 | CPK446 5 | 0.97212 | 0.91881 | -0.053313 |  | 0.925 | 1.05 | 0.078906 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | CPK446 5 | 0.97212 | 0.91881 | -0.053313 |  | 0.925 | 1.05 | 0.065323 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | CPK446 5 | 0.97212 | 0.91881 | -0.053313 |  | 0.925 | 1.05 | 0.03431 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | CPK446 5 | 0.97212 | 0.91881 | -0.053313 |  | 0.925 | 1.05 | 0.031504 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | CPK446 5 | 0.97212 | 0.91881 | -0.053313 |  | 0.925 | 1.05 | 0.031504 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | CPK446 5 | 0.97212 | 0.91881 | -0.053313 |  | 0.925 | 1.05 | 0.030663 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | CPK446 5 | 0.97212 | 0.91881 | -0.053313 |  | 0.925 | 1.05 | 0.04269 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-376 | CPK446 5 | 0.97212 | 0.91881 | -0.053313 |  | 0.925 | 1.05 | 0.082476 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | CPK446 5 | 0.97456 | 0.91851 | -0.056048 |  | 0.925 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | CPK446 5 | 0.97456 | 0.91851 | -0.056048 |  | 0.925 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | CPK446 5 | 0.97456 | 0.91851 | -0.056048 |  | 0.925 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | CPK446 5 | 0.97456 | 0.91851 | -0.056048 |  | 0.925 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | CPK446 5 | 0.97456 | 0.91851 | -0.056048 |  | 0.925 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | CPK446 5 | 0.97456 | 0.91851 | -0.056048 |  | 0.925 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | CPK446 5 | 0.97456 | 0.91851 | -0.056048 |  | 0.925 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | CPK446 5 | 0.97456 | 0.91851 | -0.056048 |  | 0.925 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | CPK446 5 | 0.97456 | 0.91851 | -0.056048 |  | 0.925 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | CPK446 5 | 0.97456 | 0.91851 | -0.056048 |  | 0.925 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | CPK446 5 | 0.97456 | 0.91851 | -0.056048 |  | 0.925 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | CPK446 5 | 0.97456 | 0.91851 | -0.056048 |  | 0.925 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | CPK446 5 | 0.97456 | 0.91851 | -0.056048 |  | 0.925 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | CPK446 5 | 0.97456 | 0.91851 | -0.056048 |  | 0.925 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | CPK446 5 | 0.97456 | 0.91851 | -0.056048 |  | 0.925 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | CPK446 5 | 0.97456 | 0.91851 | -0.056048 |  | 0.925 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | CPK446 5 | 0.97456 | 0.91851 | -0.056048 |  | 0.925 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | CPK446 5 | 0.97456 | 0.91851 | -0.056048 |  | 0.925 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | CPK446 5 | 0.97456 | 0.91851 | -0.056048 |  | 0.925 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | CPK446 5 | 0.97456 | 0.91851 | -0.056048 |  | 0.925 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | CPK446 5 | 0.97456 | 0.91851 | -0.056048 |  | 0.925 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | CPK446 5 | 0.97456 | 0.91851 | -0.056048 |  | 0.925 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | CPK446 5 | 0.97456 | 0.91851 | -0.056048 |  | 0.925 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | CPK446 5 | 0.97456 | 0.91851 | -0.056048 |  | 0.925 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | CPK446 5 | 0.97456 | 0.91851 | -0.056048 |  | 0.925 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | CRAIG 5 | 0.98659 | 0.9231 | -0.063488 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | CRAIG 5 | 0.98659 | 0.9231 | -0.063488 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | CRAIG 5 | 0.98659 | 0.9231 | -0.063488 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | CRAIG 5 | 0.98659 | 0.9231 | -0.063488 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | CRAIG 5 | 0.98659 | 0.9231 | -0.063488 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | CRAIG 5 | 0.98659 | 0.9231 | -0.063488 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | CRAIG 5 | 0.98659 | 0.9231 | -0.063488 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | CRAIG 5 | 0.98659 | 0.9231 | -0.063488 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | CRAIG 5 | 0.98659 | 0.9231 | -0.063488 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | CRAIG 5 | 0.98659 | 0.9231 | -0.063488 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | CRAIG 5 | 0.98659 | 0.9231 | -0.063488 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | CRAIG 5 | 0.98659 | 0.9231 | -0.063488 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | CRAIG 5 | 0.98659 | 0.9231 | -0.063488 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | CRAIG 5 | 0.98659 | 0.9231 | -0.063488 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | CRAIG 5 | 0.98659 | 0.9231 | -0.063488 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | CRAIG 5 | 0.98659 | 0.9231 | -0.063488 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | CRAIG 5 | 0.98659 | 0.9231 | -0.063488 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | CRAIG 5 | 0.98659 | 0.9231 | -0.063488 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | CRAIG 5 | 0.98659 | 0.9231 | -0.063488 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | CRAIG 5 | 0.98659 | 0.9231 | -0.063488 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | CRAIG 5 | 0.98659 | 0.9231 | -0.063488 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | CRAIG 5 | 0.98659 | 0.9231 | -0.063488 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | CRAIG 5 | 0.98659 | 0.9231 | -0.063488 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | CRAIG 5 | 0.98659 | 0.9231 | -0.063488 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | CRAIG 5 | 0.98659 | 0.9231 | -0.063488 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | CRAIG 7 | 0.97428 | 0.9419 | -0.032371 |  | 0.95 | 1.05 | 0.036307 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | CRAIG 7 | 0.97428 | 0.9419 | -0.032371 |  | 0.95 | 1.05 | 0.052743 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | CRAIG 7 | 0.97428 | 0.9419 | -0.032371 |  | 0.95 | 1.05 | 0.039345 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | CRAIG 7 | 0.97428 | 0.9419 | -0.032371 |  | 0.95 | 1.05 | 0.031366 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | CRAIG 7 | 0.97428 | 0.9419 | -0.032371 |  | 0.95 | 1.05 | 0.041888 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | CRAIG 7 | 0.97428 | 0.9419 | -0.032371 |  | 0.95 | 1.05 | 0.038797 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | CRAIG 7 | 0.97428 | 0.9419 | -0.032371 |  | 0.95 | 1.05 | 0.030557 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | CRAIG 7 | 0.97428 | 0.9419 | -0.032371 |  | 0.95 | 1.05 | 0.067346 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | CRAIG 7 | 0.97428 | 0.9419 | -0.032371 |  | 0.95 | 1.05 | 0.030557 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | CRAIG 7 | 0.97428 | 0.9419 | -0.032371 |  | 0.95 | 1.05 | 0.030851 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | CRAIG 7 | 0.97428 | 0.9419 | -0.032371 |  | 0.95 | 1.05 | 0.032161 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | CRAIG 7 | 0.97428 | 0.9419 | -0.032371 |  | 0.95 | 1.05 | 0.04067 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | CRAIG 7 | 0.97428 | 0.9419 | -0.032371 |  | 0.95 | 1.05 | 0.040569 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | CRAIG 7 | 0.97428 | 0.9419 | -0.032371 |  | 0.95 | 1.05 | 0.03086 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | CRAIG 7 | 0.97428 | 0.9419 | -0.032371 |  | 0.95 | 1.05 | 0.033223 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | CRAIG 7 | 0.97428 | 0.9419 | -0.032371 |  | 0.95 | 1.05 | 0.033733 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | CRAIG 7 | 0.96925 | 0.93159 | -0.037658 |  | 0.95 | 1.05 | 0.036307 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | CRAIG 7 | 0.96925 | 0.93159 | -0.037658 |  | 0.95 | 1.05 | 0.052743 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | CRAIG 7 | 0.96925 | 0.93159 | -0.037658 |  | 0.95 | 1.05 | 0.039345 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | CRAIG 7 | 0.96925 | 0.93159 | -0.037658 |  | 0.95 | 1.05 | 0.031366 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | CRAIG 7 | 0.96925 | 0.93159 | -0.037658 |  | 0.95 | 1.05 | 0.041888 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | CRAIG 7 | 0.96925 | 0.93159 | -0.037658 |  | 0.95 | 1.05 | 0.038797 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | CRAIG 7 | 0.96925 | 0.93159 | -0.037658 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | CRAIG 7 | 0.96925 | 0.93159 | -0.037658 |  | 0.95 | 1.05 | 0.067346 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | CRAIG 7 | 0.96925 | 0.93159 | -0.037658 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | CRAIG 7 | 0.96925 | 0.93159 | -0.037658 |  | 0.95 | 1.05 | 0.030851 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | CRAIG 7 | 0.96925 | 0.93159 | -0.037658 |  | 0.95 | 1.05 | 0.032161 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | CRAIG 7 | 0.96925 | 0.93159 | -0.037658 |  | 0.95 | 1.05 | 0.04067 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | CRAIG 7 | 0.96925 | 0.93159 | -0.037658 |  | 0.95 | 1.05 | 0.040569 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | CRAIG 7 | 0.96925 | 0.93159 | -0.037658 |  | 0.95 | 1.05 | 0.03086 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | CRAIG 7 | 0.96925 | 0.93159 | -0.037658 |  | 0.95 | 1.05 | 0.033223 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | CRAIG 7 | 0.96925 | 0.93159 | -0.037658 |  | 0.95 | 1.05 | 0.033733 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | CRAIG 7 | 0.9781 | 0.93462 | -0.04348 |  | 0.95 | 1.05 | 0.036307 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | CRAIG 7 | 0.9781 | 0.93462 | -0.04348 |  | 0.95 | 1.05 | 0.052743 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | CRAIG 7 | 0.9781 | 0.93462 | -0.04348 |  | 0.95 | 1.05 | 0.039345 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | CRAIG 7 | 0.9781 | 0.93462 | -0.04348 |  | 0.95 | 1.05 | 0.031366 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | CRAIG 7 | 0.9781 | 0.93462 | -0.04348 |  | 0.95 | 1.05 | 0.041888 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | CRAIG 7 | 0.9781 | 0.93462 | -0.04348 |  | 0.95 | 1.05 | 0.038797 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | CRAIG 7 | 0.9781 | 0.93462 | -0.04348 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | CRAIG 7 | 0.9781 | 0.93462 | -0.04348 |  | 0.95 | 1.05 | 0.067346 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | CRAIG 7 | 0.9781 | 0.93462 | -0.04348 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | CRAIG 7 | 0.9781 | 0.93462 | -0.04348 |  | 0.95 | 1.05 | 0.030851 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | CRAIG 7 | 0.9781 | 0.93462 | -0.04348 |  | 0.95 | 1.05 | 0.032161 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | CRAIG 7 | 0.9781 | 0.93462 | -0.04348 |  | 0.95 | 1.05 | 0.04067 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | CRAIG 7 | 0.9781 | 0.93462 | -0.04348 |  | 0.95 | 1.05 | 0.040569 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | CRAIG 7 | 0.9781 | 0.93462 | -0.04348 |  | 0.95 | 1.05 | 0.03086 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | CRAIG 7 | 0.9781 | 0.93462 | -0.04348 |  | 0.95 | 1.05 | 0.033223 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | CRAIG 7 | 0.9781 | 0.93462 | -0.04348 |  | 0.95 | 1.05 | 0.033733 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | CRAIG 7 | 0.98367 | 0.92502 | -0.058648 |  | 0.95 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | CRAIG 7 | 0.98367 | 0.92502 | -0.058648 |  | 0.95 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | CRAIG 7 | 0.98367 | 0.92502 | -0.058648 |  | 0.95 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | CRAIG 7 | 0.98367 | 0.92502 | -0.058648 |  | 0.95 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | CRAIG 7 | 0.98367 | 0.92502 | -0.058648 |  | 0.95 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | CRAIG 7 | 0.98367 | 0.92502 | -0.058648 |  | 0.95 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | CRAIG 7 | 0.98367 | 0.92502 | -0.058648 |  | 0.95 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | CRAIG 7 | 0.98367 | 0.92502 | -0.058648 |  | 0.95 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | CRAIG 7 | 0.98367 | 0.92502 | -0.058648 |  | 0.95 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | CRAIG 7 | 0.98367 | 0.92502 | -0.058648 |  | 0.95 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | CRAIG 7 | 0.98367 | 0.92502 | -0.058648 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | CRAIG 7 | 0.98367 | 0.92502 | -0.058648 |  | 0.95 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | CRAIG 7 | 0.98367 | 0.92502 | -0.058648 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | CRAIG 7 | 0.98367 | 0.92502 | -0.058648 |  | 0.95 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | CRAIG 7 | 0.98367 | 0.92502 | -0.058648 |  | 0.95 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | CRAIG 7 | 0.98367 | 0.92502 | -0.058648 |  | 0.95 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | CRAIG 7 | 0.98367 | 0.92502 | -0.058648 |  | 0.95 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | CRAIG 7 | 0.98367 | 0.92502 | -0.058648 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | CRAIG 7 | 0.98367 | 0.92502 | -0.058648 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | CRAIG 7 | 0.98367 | 0.92502 | -0.058648 |  | 0.95 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | CRAIG 7 | 0.98367 | 0.92502 | -0.058648 |  | 0.95 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | CRAIG 7 | 0.98367 | 0.92502 | -0.058648 |  | 0.95 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | CRAIG 7 | 0.98367 | 0.92502 | -0.058648 |  | 0.95 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | CRAIG 7 | 0.98367 | 0.92502 | -0.058648 |  | 0.95 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | CRAIG 7 | 0.98367 | 0.92502 | -0.058648 |  | 0.95 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | CRAIG 7 | 0.97365 | 0.94061 | -0.033038 |  | 0.95 | 1.05 | 0.036307 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | CRAIG 7 | 0.97365 | 0.94061 | -0.033038 |  | 0.95 | 1.05 | 0.052743 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | CRAIG 7 | 0.97365 | 0.94061 | -0.033038 |  | 0.95 | 1.05 | 0.039345 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | CRAIG 7 | 0.97365 | 0.94061 | -0.033038 |  | 0.95 | 1.05 | 0.031366 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | CRAIG 7 | 0.97365 | 0.94061 | -0.033038 |  | 0.95 | 1.05 | 0.041888 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | CRAIG 7 | 0.97365 | 0.94061 | -0.033038 |  | 0.95 | 1.05 | 0.038797 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | CRAIG 7 | 0.97365 | 0.94061 | -0.033038 |  | 0.95 | 1.05 | 0.030557 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | CRAIG 7 | 0.97365 | 0.94061 | -0.033038 |  | 0.95 | 1.05 | 0.067346 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | CRAIG 7 | 0.97365 | 0.94061 | -0.033038 |  | 0.95 | 1.05 | 0.030557 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | CRAIG 7 | 0.97365 | 0.94061 | -0.033038 |  | 0.95 | 1.05 | 0.030851 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | CRAIG 7 | 0.97365 | 0.94061 | -0.033038 |  | 0.95 | 1.05 | 0.032161 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | CRAIG 7 | 0.97365 | 0.94061 | -0.033038 |  | 0.95 | 1.05 | 0.04067 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | CRAIG 7 | 0.97365 | 0.94061 | -0.033038 |  | 0.95 | 1.05 | 0.040569 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | CRAIG 7 | 0.97365 | 0.94061 | -0.033038 |  | 0.95 | 1.05 | 0.03086 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | CRAIG 7 | 0.97365 | 0.94061 | -0.033038 |  | 0.95 | 1.05 | 0.033223 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | CRAIG 7 | 0.97365 | 0.94061 | -0.033038 |  | 0.95 | 1.05 | 0.033733 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | CRAIG_CAP 5 | 0.98766 | 0.92411 | -0.063557 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | CRAIG_CAP 5 | 0.98766 | 0.92411 | -0.063557 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | CRAIG_CAP 5 | 0.98766 | 0.92411 | -0.063557 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | CRAIG_CAP 5 | 0.98766 | 0.92411 | -0.063557 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | CRAIG_CAP 5 | 0.98766 | 0.92411 | -0.063557 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | CRAIG_CAP 5 | 0.98766 | 0.92411 | -0.063557 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | CRAIG_CAP 5 | 0.98766 | 0.92411 | -0.063557 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | CRAIG_CAP 5 | 0.98766 | 0.92411 | -0.063557 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | CRAIG_CAP 5 | 0.98766 | 0.92411 | -0.063557 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | CRAIG_CAP 5 | 0.98766 | 0.92411 | -0.063557 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | CRAIG_CAP 5 | 0.98766 | 0.92411 | -0.063557 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | CRAIG_CAP 5 | 0.98766 | 0.92411 | -0.063557 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | CRAIG_CAP 5 | 0.98766 | 0.92411 | -0.063557 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | CRAIG_CAP 5 | 0.98766 | 0.92411 | -0.063557 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | CRAIG_CAP 5 | 0.98766 | 0.92411 | -0.063557 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | CRAIG_CAP 5 | 0.98766 | 0.92411 | -0.063557 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | CRAIG_CAP 5 | 0.98766 | 0.92411 | -0.063557 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | CRAIG_CAP 5 | 0.98766 | 0.92411 | -0.063557 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | CRAIG_CAP 5 | 0.98766 | 0.92411 | -0.063557 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | CRAIG_CAP 5 | 0.98766 | 0.92411 | -0.063557 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | CRAIG_CAP 5 | 0.98766 | 0.92411 | -0.063557 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | CRAIG_CAP 5 | 0.98766 | 0.92411 | -0.063557 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | CRAIG_CAP 5 | 0.98766 | 0.92411 | -0.063557 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | CRAIG_CAP 5 | 0.98766 | 0.92411 | -0.063557 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | CRAIG_CAP 5 | 0.98766 | 0.92411 | -0.063557 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | CRAWFOR2 | 0.96868 | 0.92927 | -0.039409 |  | 0.93 | 1.05 | 0.040439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | CRAWFOR2 | 0.96868 | 0.92927 | -0.039409 |  | 0.93 | 1.05 | 0.034853 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | CRAWFOR2 | 0.96868 | 0.92927 | -0.039409 |  | 0.93 | 1.05 | 0.046783 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | CRAWFOR2 | 0.96868 | 0.92927 | -0.039409 |  | 0.93 | 1.05 | 0.047615 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | CRAWFOR2 | 0.96868 | 0.92927 | -0.039409 |  | 0.93 | 1.05 | 0.034938 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | CRAWFOR2 | 0.96868 | 0.92927 | -0.039409 |  | 0.93 | 1.05 | 0.037875 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | CRAWFOR2 | 0.96868 | 0.92927 | -0.039409 |  | 0.93 | 1.05 | 0.044022 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | CRAWFOR2 | 0.96868 | 0.92927 | -0.039409 |  | 0.93 | 1.05 | 0.030552 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | CRAWFOR2 | 0.96868 | 0.92927 | -0.039409 |  | 0.93 | 1.05 | 0.038531 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | CRAWFOR2 | 0.96868 | 0.92927 | -0.039409 |  | 0.93 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | CRAWFOR2 | 0.96868 | 0.92927 | -0.039409 |  | 0.93 | 1.05 | 0.062491 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | CRAWFOR2 | 0.96868 | 0.92927 | -0.039409 |  | 0.93 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | CRAWFOR2 | 0.96868 | 0.92927 | -0.039409 |  | 0.93 | 1.05 | 0.038129 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | CRAWFOR2 | 0.96868 | 0.92927 | -0.039409 |  | 0.93 | 1.05 | 0.038066 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | CRAWFOR2 | 0.96868 | 0.92927 | -0.039409 |  | 0.93 | 1.05 | 0.034955 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | CRAWFOR2 | 0.96868 | 0.92927 | -0.039409 |  | 0.93 | 1.05 | 0.06281 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | CRAWFOR2 | 0.96868 | 0.92927 | -0.039409 |  | 0.93 | 1.05 | 0.045309 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | CRAWFOR2 | 0.96868 | 0.92927 | -0.039409 |  | 0.93 | 1.05 | 0.035805 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | CRAWFOR2 | 0.96868 | 0.92927 | -0.039409 |  | 0.93 | 1.05 | 0.032364 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | CRAWFOR2 | 0.96868 | 0.92927 | -0.039409 |  | 0.93 | 1.05 | 0.031815 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | CRAWFOR2 | 0.96868 | 0.92927 | -0.039409 |  | 0.93 | 1.05 | 0.033886 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | CRAWFOR2 | 0.96868 | 0.92927 | -0.039409 |  | 0.93 | 1.05 | 0.035554 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | CRAWFOR2 | 0.97005 | 0.91899 | -0.051062 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | CRAWFOR2 | 0.97005 | 0.91899 | -0.051062 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | CRAWFOR2 | 0.97005 | 0.91899 | -0.051062 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | CRAWFOR2 | 0.97005 | 0.91899 | -0.051062 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | CRAWFOR2 | 0.97005 | 0.91899 | -0.051062 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | CRAWFOR2 | 0.97005 | 0.91899 | -0.051062 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | CRAWFOR2 | 0.97005 | 0.91899 | -0.051062 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | CRAWFOR2 | 0.97005 | 0.91899 | -0.051062 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | CRAWFOR2 | 0.97005 | 0.91899 | -0.051062 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | CRAWFOR2 | 0.97005 | 0.91899 | -0.051062 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | CRAWFOR2 | 0.97005 | 0.91899 | -0.051062 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | CRAWFOR2 | 0.97005 | 0.91899 | -0.051062 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | CRAWFOR2 | 0.97005 | 0.91899 | -0.051062 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | CRAWFOR2 | 0.97005 | 0.91899 | -0.051062 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | CRAWFOR2 | 0.97005 | 0.91899 | -0.051062 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | CRAWFOR2 | 0.97005 | 0.91899 | -0.051062 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | CRAWFOR2 | 0.97005 | 0.91899 | -0.051062 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | CRAWFOR2 | 0.97005 | 0.91899 | -0.051062 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | CRAWFOR2 | 0.97005 | 0.91899 | -0.051062 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | CRAWFOR2 | 0.97005 | 0.91899 | -0.051062 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | CRAWFOR2 | 0.97005 | 0.91899 | -0.051062 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | CRAWFOR2 | 0.97005 | 0.91899 | -0.051062 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | CRAWFOR2 | 0.97005 | 0.91899 | -0.051062 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | CRAWFOR2 | 0.97005 | 0.91899 | -0.051062 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | CRAWFOR2 | 0.97005 | 0.91899 | -0.051062 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | ASGI-2024-023 | DAD368 5 | 0.9843 | 0.92285 | -0.061443 |  | 0.925 | 1.05 | 0.079962 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | DAD368 5 | 0.9843 | 0.92285 | -0.061443 |  | 0.925 | 1.05 | 0.065323 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-068 | DAD368 5 | 0.9843 | 0.92285 | -0.061443 |  | 0.925 | 1.05 | 0.067422 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-071 | DAD368 5 | 0.9843 | 0.92285 | -0.061443 |  | 0.925 | 1.05 | 0.074668 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | DAD368 5 | 0.9843 | 0.92285 | -0.061443 |  | 0.925 | 1.05 | 0.053027 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-122 | DAD368 5 | 0.9843 | 0.92285 | -0.061443 |  | 0.925 | 1.05 | 0.082926 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-177 | DAD368 5 | 0.9843 | 0.92285 | -0.061443 |  | 0.925 | 1.05 | 0.084694 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-178 | DAD368 5 | 0.9843 | 0.92285 | -0.061443 |  | 0.925 | 1.05 | 0.078867 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | DAD368 5 | 0.9843 | 0.92285 | -0.061443 |  | 0.925 | 1.05 | 0.031571 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-220 | DAD368 5 | 0.9843 | 0.92285 | -0.061443 |  | 0.925 | 1.05 | 0.075331 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-232 | DAD368 5 | 0.9843 | 0.92285 | -0.061443 |  | 0.925 | 1.05 | 0.078906 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | DAD368 5 | 0.9843 | 0.92285 | -0.061443 |  | 0.925 | 1.05 | 0.065323 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | DAD368 5 | 0.9843 | 0.92285 | -0.061443 |  | 0.925 | 1.05 | 0.03431 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | DAD368 5 | 0.9843 | 0.92285 | -0.061443 |  | 0.925 | 1.05 | 0.031504 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | DAD368 5 | 0.9843 | 0.92285 | -0.061443 |  | 0.925 | 1.05 | 0.031504 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | DAD368 5 | 0.9843 | 0.92285 | -0.061443 |  | 0.925 | 1.05 | 0.030663 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | DAD368 5 | 0.9843 | 0.92285 | -0.061443 |  | 0.925 | 1.05 | 0.04269 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-376 | DAD368 5 | 0.9843 | 0.92285 | -0.061443 |  | 0.925 | 1.05 | 0.082476 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | DAD368 5 | 0.98613 | 0.91516 | -0.070973 |  | 0.925 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | DAD368 5 | 0.98613 | 0.91516 | -0.070973 |  | 0.925 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | DAD368 5 | 0.98613 | 0.91516 | -0.070973 |  | 0.925 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | DAD368 5 | 0.98613 | 0.91516 | -0.070973 |  | 0.925 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | DAD368 5 | 0.98613 | 0.91516 | -0.070973 |  | 0.925 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | DAD368 5 | 0.98613 | 0.91516 | -0.070973 |  | 0.925 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | DAD368 5 | 0.98613 | 0.91516 | -0.070973 |  | 0.925 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | DAD368 5 | 0.98613 | 0.91516 | -0.070973 |  | 0.925 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | DAD368 5 | 0.98613 | 0.91516 | -0.070973 |  | 0.925 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | DAD368 5 | 0.98613 | 0.91516 | -0.070973 |  | 0.925 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | DAD368 5 | 0.98613 | 0.91516 | -0.070973 |  | 0.925 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | DAD368 5 | 0.98613 | 0.91516 | -0.070973 |  | 0.925 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | DAD368 5 | 0.98613 | 0.91516 | -0.070973 |  | 0.925 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | DAD368 5 | 0.98613 | 0.91516 | -0.070973 |  | 0.925 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | DAD368 5 | 0.98613 | 0.91516 | -0.070973 |  | 0.925 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | DAD368 5 | 0.98613 | 0.91516 | -0.070973 |  | 0.925 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | DAD368 5 | 0.98613 | 0.91516 | -0.070973 |  | 0.925 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | DAD368 5 | 0.98613 | 0.91516 | -0.070973 |  | 0.925 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | DAD368 5 | 0.98613 | 0.91516 | -0.070973 |  | 0.925 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | DAD368 5 | 0.98613 | 0.91516 | -0.070973 |  | 0.925 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | DAD368 5 | 0.98613 | 0.91516 | -0.070973 |  | 0.925 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | DAD368 5 | 0.98613 | 0.91516 | -0.070973 |  | 0.925 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | DAD368 5 | 0.98613 | 0.91516 | -0.070973 |  | 0.925 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | DAD368 5 | 0.98613 | 0.91516 | -0.070973 |  | 0.925 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | DAD368 5 | 0.98613 | 0.91516 | -0.070973 |  | 0.925 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | DAKOTA_5 | 0.99239 | 0.91859 | -0.073801 |  | 0.93 | 1.05 | 0.03053 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | DAKOTA_5 | 0.99239 | 0.91859 | -0.073801 |  | 0.93 | 1.05 | 0.044933 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | DAKOTA_5 | 0.99239 | 0.91859 | -0.073801 |  | 0.93 | 1.05 | 0.047811 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | DAKOTA_5 | 0.99239 | 0.91859 | -0.073801 |  | 0.93 | 1.05 | 0.09719 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | DAKOTA_5 | 0.99239 | 0.91859 | -0.073801 |  | 0.93 | 1.05 | 0.069376 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | DAKOTA_5 | 0.99239 | 0.91859 | -0.073801 |  | 0.93 | 1.05 | 0.04277 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | DAKOTA_5 | 0.99239 | 0.91859 | -0.073801 |  | 0.93 | 1.05 | 0.071112 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | DAKOTA_5 | 0.99239 | 0.91859 | -0.073801 |  | 0.93 | 1.05 | 0.039357 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | DAKOTA_5 | 0.99239 | 0.91859 | -0.073801 |  | 0.93 | 1.05 | 0.04035 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | DAKOTA_5 | 0.99239 | 0.91859 | -0.073801 |  | 0.93 | 1.05 | 0.052332 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | DAKOTA_5 | 0.99239 | 0.91859 | -0.073801 |  | 0.93 | 1.05 | 0.045944 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | DAKOTA_5 | 0.99239 | 0.91859 | -0.073801 |  | 0.93 | 1.05 | 0.038178 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | DAKOTA_5 | 0.99239 | 0.91859 | -0.073801 |  | 0.93 | 1.05 | 0.13469 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | DAKOTA_5 | 0.99239 | 0.91859 | -0.073801 |  | 0.93 | 1.05 | 0.03053 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | DAKOTA_5 | 0.99239 | 0.91859 | -0.073801 |  | 0.93 | 1.05 | 0.038178 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | DAKOTA_5 | 0.99239 | 0.91859 | -0.073801 |  | 0.93 | 1.05 | 0.037309 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | DAKOTA_5 | 0.99239 | 0.91859 | -0.073801 |  | 0.93 | 1.05 | 0.040075 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | DAKOTA_5 | 0.99239 | 0.91859 | -0.073801 |  | 0.93 | 1.05 | 0.053764 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | DAKOTA_5 | 0.99239 | 0.91859 | -0.073801 |  | 0.93 | 1.05 | 0.071762 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | DAKOTA_5 | 0.99239 | 0.91859 | -0.073801 |  | 0.93 | 1.05 | 0.047827 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | DAKOTA_5 | 0.99239 | 0.91859 | -0.073801 |  | 0.93 | 1.05 | 0.047827 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | DAKOTA_5 | 0.99239 | 0.91859 | -0.073801 |  | 0.93 | 1.05 | 0.070303 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | DAKOTA_5 | 0.99239 | 0.91859 | -0.073801 |  | 0.93 | 1.05 | 0.040614 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | DAKOTA_5 | 0.99239 | 0.91859 | -0.073801 |  | 0.93 | 1.05 | 0.039729 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | DAKOTA_5 | 0.99239 | 0.91859 | -0.073801 |  | 0.93 | 1.05 | 0.049662 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | DAKOTA_5 | 0.99239 | 0.91859 | -0.073801 |  | 0.93 | 1.05 | 0.042332 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | DAKOTA_5 | 0.99239 | 0.91859 | -0.073801 |  | 0.93 | 1.05 | 0.048722 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | DAKOTA_5 | 0.99239 | 0.91859 | -0.073801 |  | 0.93 | 1.05 | 0.038156 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | DAKOTA_5 | 0.99239 | 0.91859 | -0.073801 |  | 0.93 | 1.05 | 0.036794 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | DAKOTA_5 | 0.98604 | 0.92431 | -0.061733 |  | 0.93 | 1.05 | 0.036307 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | DAKOTA_5 | 0.98604 | 0.92431 | -0.061733 |  | 0.93 | 1.05 | 0.052743 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | DAKOTA_5 | 0.98604 | 0.92431 | -0.061733 |  | 0.93 | 1.05 | 0.039345 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | DAKOTA_5 | 0.98604 | 0.92431 | -0.061733 |  | 0.93 | 1.05 | 0.031366 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | DAKOTA_5 | 0.98604 | 0.92431 | -0.061733 |  | 0.93 | 1.05 | 0.041888 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | DAKOTA_5 | 0.98604 | 0.92431 | -0.061733 |  | 0.93 | 1.05 | 0.038797 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | DAKOTA_5 | 0.98604 | 0.92431 | -0.061733 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | DAKOTA_5 | 0.98604 | 0.92431 | -0.061733 |  | 0.93 | 1.05 | 0.067346 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | DAKOTA_5 | 0.98604 | 0.92431 | -0.061733 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | DAKOTA_5 | 0.98604 | 0.92431 | -0.061733 |  | 0.93 | 1.05 | 0.030851 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | DAKOTA_5 | 0.98604 | 0.92431 | -0.061733 |  | 0.93 | 1.05 | 0.032161 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | DAKOTA_5 | 0.98604 | 0.92431 | -0.061733 |  | 0.93 | 1.05 | 0.04067 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | DAKOTA_5 | 0.98604 | 0.92431 | -0.061733 |  | 0.93 | 1.05 | 0.040569 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | DAKOTA_5 | 0.98604 | 0.92431 | -0.061733 |  | 0.93 | 1.05 | 0.03086 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | DAKOTA_5 | 0.98604 | 0.92431 | -0.061733 |  | 0.93 | 1.05 | 0.033223 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | DAKOTA_5 | 0.98604 | 0.92431 | -0.061733 |  | 0.93 | 1.05 | 0.033733 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | DAKOTA_5 | 0.9901 | 0.92084 | -0.069264 |  | 0.93 | 1.05 | 0.036307 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | DAKOTA_5 | 0.9901 | 0.92084 | -0.069264 |  | 0.93 | 1.05 | 0.052743 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | DAKOTA_5 | 0.9901 | 0.92084 | -0.069264 |  | 0.93 | 1.05 | 0.039345 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | DAKOTA_5 | 0.9901 | 0.92084 | -0.069264 |  | 0.93 | 1.05 | 0.031366 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | DAKOTA_5 | 0.9901 | 0.92084 | -0.069264 |  | 0.93 | 1.05 | 0.041888 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | DAKOTA_5 | 0.9901 | 0.92084 | -0.069264 |  | 0.93 | 1.05 | 0.038797 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | DAKOTA_5 | 0.9901 | 0.92084 | -0.069264 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | DAKOTA_5 | 0.9901 | 0.92084 | -0.069264 |  | 0.93 | 1.05 | 0.067346 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | DAKOTA_5 | 0.9901 | 0.92084 | -0.069264 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | DAKOTA_5 | 0.9901 | 0.92084 | -0.069264 |  | 0.93 | 1.05 | 0.030851 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | DAKOTA_5 | 0.9901 | 0.92084 | -0.069264 |  | 0.93 | 1.05 | 0.032161 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | DAKOTA_5 | 0.9901 | 0.92084 | -0.069264 |  | 0.93 | 1.05 | 0.04067 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | DAKOTA_5 | 0.9901 | 0.92084 | -0.069264 |  | 0.93 | 1.05 | 0.040569 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | DAKOTA_5 | 0.9901 | 0.92084 | -0.069264 |  | 0.93 | 1.05 | 0.03086 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | DAKOTA_5 | 0.9901 | 0.92084 | -0.069264 |  | 0.93 | 1.05 | 0.033223 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | DAKOTA_5 | 0.9901 | 0.92084 | -0.069264 |  | 0.93 | 1.05 | 0.033733 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | DAKOTA_5 | 0.99125 | 0.91873 | -0.072525 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | DAKOTA_5 | 0.99125 | 0.91873 | -0.072525 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | DAKOTA_5 | 0.99125 | 0.91873 | -0.072525 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | DAKOTA_5 | 0.99125 | 0.91873 | -0.072525 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | DAKOTA_5 | 0.99125 | 0.91873 | -0.072525 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | DAKOTA_5 | 0.99125 | 0.91873 | -0.072525 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | DAKOTA_5 | 0.99125 | 0.91873 | -0.072525 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | DAKOTA_5 | 0.99125 | 0.91873 | -0.072525 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | DAKOTA_5 | 0.99125 | 0.91873 | -0.072525 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | DAKOTA_5 | 0.99125 | 0.91873 | -0.072525 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | DAKOTA_5 | 0.99125 | 0.91873 | -0.072525 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | DAKOTA_5 | 0.99125 | 0.91873 | -0.072525 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | DAKOTA_5 | 0.99125 | 0.91873 | -0.072525 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | DAKOTA_5 | 0.99125 | 0.91873 | -0.072525 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | DAKOTA_5 | 0.99125 | 0.91873 | -0.072525 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | DAKOTA_5 | 0.99125 | 0.91873 | -0.072525 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | DAKOTA_5 | 0.99125 | 0.91873 | -0.072525 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | DAKOTA_5 | 0.99125 | 0.91873 | -0.072525 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | DAKOTA_5 | 0.99125 | 0.91873 | -0.072525 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | DAKOTA_5 | 0.99125 | 0.91873 | -0.072525 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | DAKOTA_5 | 0.99125 | 0.91873 | -0.072525 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | DAKOTA_5 | 0.99125 | 0.91873 | -0.072525 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | DAKOTA_5 | 0.99125 | 0.91873 | -0.072525 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | DAKOTA_5 | 0.99125 | 0.91873 | -0.072525 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | DAKOTA_5 | 0.99125 | 0.91873 | -0.072525 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | EAST ST3 | 0.95963 | 0.86149 | -0.098141 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | EAST ST3 | 0.95963 | 0.86149 | -0.098141 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | EAST ST3 | 0.95963 | 0.86149 | -0.098141 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | EAST ST3 | 0.95963 | 0.86149 | -0.098141 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | EAST ST3 | 0.95963 | 0.86149 | -0.098141 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | EAST ST3 | 0.95963 | 0.86149 | -0.098141 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | EAST ST3 | 0.95963 | 0.86149 | -0.098141 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | EAST ST3 | 0.95963 | 0.86149 | -0.098141 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | EAST ST3 | 0.95963 | 0.86149 | -0.098141 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | EAST ST3 | 0.95963 | 0.86149 | -0.098141 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | EAST ST3 | 0.95963 | 0.86149 | -0.098141 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | EAST ST3 | 0.95963 | 0.86149 | -0.098141 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | EAST ST3 | 0.95963 | 0.86149 | -0.098141 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | EAST ST3 | 0.95963 | 0.86149 | -0.098141 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | EAST ST3 | 0.95963 | 0.86149 | -0.098141 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | EAST ST3 | 0.95963 | 0.86149 | -0.098141 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | EAST ST3 | 0.95963 | 0.86149 | -0.098141 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | EAST ST3 | 0.95963 | 0.86149 | -0.098141 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | EAST ST3 | 0.95963 | 0.86149 | -0.098141 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | EAST ST3 | 0.95963 | 0.86149 | -0.098141 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | EAST ST3 | 0.95963 | 0.86149 | -0.098141 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | EAST ST3 | 0.95963 | 0.86149 | -0.098141 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | EAST ST3 | 0.95963 | 0.86149 | -0.098141 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | EAST ST3 | 0.95963 | 0.86149 | -0.098141 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | EAST ST3 | 0.95963 | 0.86149 | -0.098141 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | EDWRDVL5 | 0.98149 | 0.92632 | -0.055171 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | EDWRDVL5 | 0.98149 | 0.92632 | -0.055171 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | EDWRDVL5 | 0.98149 | 0.92632 | -0.055171 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | EDWRDVL5 | 0.98149 | 0.92632 | -0.055171 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | EDWRDVL5 | 0.98149 | 0.92632 | -0.055171 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | EDWRDVL5 | 0.98149 | 0.92632 | -0.055171 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | EDWRDVL5 | 0.98149 | 0.92632 | -0.055171 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | EDWRDVL5 | 0.98149 | 0.92632 | -0.055171 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | EDWRDVL5 | 0.98149 | 0.92632 | -0.055171 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | EDWRDVL5 | 0.98149 | 0.92632 | -0.055171 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | EDWRDVL5 | 0.98149 | 0.92632 | -0.055171 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | EDWRDVL5 | 0.98149 | 0.92632 | -0.055171 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | EDWRDVL5 | 0.98149 | 0.92632 | -0.055171 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | EDWRDVL5 | 0.98149 | 0.92632 | -0.055171 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | EDWRDVL5 | 0.98149 | 0.92632 | -0.055171 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | EDWRDVL5 | 0.98149 | 0.92632 | -0.055171 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | EDWRDVL5 | 0.98149 | 0.92632 | -0.055171 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | EDWRDVL5 | 0.98149 | 0.92632 | -0.055171 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | EDWRDVL5 | 0.98149 | 0.92632 | -0.055171 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | EDWRDVL5 | 0.98149 | 0.92632 | -0.055171 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | EDWRDVL5 | 0.98149 | 0.92632 | -0.055171 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | EDWRDVL5 | 0.98149 | 0.92632 | -0.055171 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | EDWRDVL5 | 0.98149 | 0.92632 | -0.055171 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | EDWRDVL5 | 0.98149 | 0.92632 | -0.055171 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | EDWRDVL5 | 0.98149 | 0.92632 | -0.055171 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | EEUREKA3 | 0.98309 | 0.90795 | -0.075144 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | EEUREKA3 | 0.98309 | 0.90795 | -0.075144 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | EEUREKA3 | 0.98309 | 0.90795 | -0.075144 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | EEUREKA3 | 0.98309 | 0.90795 | -0.075144 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | EEUREKA3 | 0.98309 | 0.90795 | -0.075144 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | EEUREKA3 | 0.98309 | 0.90795 | -0.075144 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | EEUREKA3 | 0.98309 | 0.90795 | -0.075144 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | EEUREKA3 | 0.98309 | 0.90795 | -0.075144 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | EEUREKA3 | 0.98309 | 0.90795 | -0.075144 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | EEUREKA3 | 0.98309 | 0.90795 | -0.075144 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | EEUREKA3 | 0.98309 | 0.90795 | -0.075144 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | EEUREKA3 | 0.98309 | 0.90795 | -0.075144 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | EEUREKA3 | 0.98309 | 0.90795 | -0.075144 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | EEUREKA3 | 0.98309 | 0.90795 | -0.075144 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | EEUREKA3 | 0.98309 | 0.90795 | -0.075144 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | EEUREKA3 | 0.98309 | 0.90795 | -0.075144 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | EEUREKA3 | 0.98309 | 0.90795 | -0.075144 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | EEUREKA3 | 0.98309 | 0.90795 | -0.075144 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | EEUREKA3 | 0.98309 | 0.90795 | -0.075144 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | EEUREKA3 | 0.98309 | 0.90795 | -0.075144 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | EEUREKA3 | 0.98309 | 0.90795 | -0.075144 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | EEUREKA3 | 0.98309 | 0.90795 | -0.075144 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | EEUREKA3 | 0.98309 | 0.90795 | -0.075144 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | EEUREKA3 | 0.98309 | 0.90795 | -0.075144 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | EEUREKA3 | 0.98309 | 0.90795 | -0.075144 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | ELKRVR17 | 0.98064 | 0.94315 | -0.037496 |  | 0.95 | 1.05 | 0.034914 | P23:345:WERE:WOLF-345-50:EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | ELKRVR17 | 0.98064 | 0.94315 | -0.037496 |  | 0.95 | 1.05 | 0.033648 | P23:345:WERE:WOLF-345-50:EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | ELKRVR17 | 0.98064 | 0.94315 | -0.037496 |  | 0.95 | 1.05 | 0.030226 | P23:345:WERE:WOLF-345-50:EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | ELKRVR17 | 0.98064 | 0.94315 | -0.037496 |  | 0.95 | 1.05 | 0.03107 | P23:345:WERE:WOLF-345-50:EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | ELKRVR17 | 0.98701 | 0.93354 | -0.053469 |  | 0.95 | 1.05 | 0.035768 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | ELKRVR17 | 0.98701 | 0.93354 | -0.053469 |  | 0.95 | 1.05 | 0.088718 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | ELKRVR17 | 0.98701 | 0.93354 | -0.053469 |  | 0.95 | 1.05 | 0.031473 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | ELKRVR17 | 0.98701 | 0.93354 | -0.053469 |  | 0.95 | 1.05 | 0.034941 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | ELKRVR17 | 0.98701 | 0.93354 | -0.053469 |  | 0.95 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | ELKRVR17 | 0.98701 | 0.93354 | -0.053469 |  | 0.95 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | ELKRVR17 | 0.98701 | 0.93354 | -0.053469 |  | 0.95 | 1.05 | 0.049224 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | ELKRVR17 | 0.98701 | 0.93354 | -0.053469 |  | 0.95 | 1.05 | 0.038981 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | ELKRVR17 | 0.98701 | 0.93354 | -0.053469 |  | 0.95 | 1.05 | 0.040399 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | ELKRVR17 | 0.98701 | 0.93354 | -0.053469 |  | 0.95 | 1.05 | 0.031912 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | ELKRVR17 | 0.98701 | 0.93354 | -0.053469 |  | 0.95 | 1.05 | 0.034127 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | ELKRVR17 | 0.98701 | 0.93354 | -0.053469 |  | 0.95 | 1.05 | 0.047318 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | ELKRVR17 | 0.97997 | 0.92068 | -0.059287 |  | 0.95 | 1.05 | 0.040439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | ELKRVR17 | 0.97997 | 0.92068 | -0.059287 |  | 0.95 | 1.05 | 0.034853 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | ELKRVR17 | 0.97997 | 0.92068 | -0.059287 |  | 0.95 | 1.05 | 0.046783 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | ELKRVR17 | 0.97997 | 0.92068 | -0.059287 |  | 0.95 | 1.05 | 0.047615 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | ELKRVR17 | 0.97997 | 0.92068 | -0.059287 |  | 0.95 | 1.05 | 0.034938 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | ELKRVR17 | 0.97997 | 0.92068 | -0.059287 |  | 0.95 | 1.05 | 0.037875 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | ELKRVR17 | 0.97997 | 0.92068 | -0.059287 |  | 0.95 | 1.05 | 0.044022 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | ELKRVR17 | 0.97997 | 0.92068 | -0.059287 |  | 0.95 | 1.05 | 0.030552 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | ELKRVR17 | 0.97997 | 0.92068 | -0.059287 |  | 0.95 | 1.05 | 0.038531 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | ELKRVR17 | 0.97997 | 0.92068 | -0.059287 |  | 0.95 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | ELKRVR17 | 0.97997 | 0.92068 | -0.059287 |  | 0.95 | 1.05 | 0.062491 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | ELKRVR17 | 0.97997 | 0.92068 | -0.059287 |  | 0.95 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | ELKRVR17 | 0.97997 | 0.92068 | -0.059287 |  | 0.95 | 1.05 | 0.038129 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | ELKRVR17 | 0.97997 | 0.92068 | -0.059287 |  | 0.95 | 1.05 | 0.038066 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | ELKRVR17 | 0.97997 | 0.92068 | -0.059287 |  | 0.95 | 1.05 | 0.034955 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | ELKRVR17 | 0.97997 | 0.92068 | -0.059287 |  | 0.95 | 1.05 | 0.06281 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | ELKRVR17 | 0.97997 | 0.92068 | -0.059287 |  | 0.95 | 1.05 | 0.045309 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | ELKRVR17 | 0.97997 | 0.92068 | -0.059287 |  | 0.95 | 1.05 | 0.035805 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | ELKRVR17 | 0.97997 | 0.92068 | -0.059287 |  | 0.95 | 1.05 | 0.032364 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | ELKRVR17 | 0.97997 | 0.92068 | -0.059287 |  | 0.95 | 1.05 | 0.031815 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | ELKRVR17 | 0.97997 | 0.92068 | -0.059287 |  | 0.95 | 1.05 | 0.033886 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | ELKRVR17 | 0.97997 | 0.92068 | -0.059287 |  | 0.95 | 1.05 | 0.035554 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | ELKRVR17 | 0.99037 | 0.93466 | -0.055711 |  | 0.95 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | ELKRVR17 | 0.99037 | 0.93466 | -0.055711 |  | 0.95 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | ELKRVR17 | 0.99037 | 0.93466 | -0.055711 |  | 0.95 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | ELKRVR17 | 0.99037 | 0.93466 | -0.055711 |  | 0.95 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | ELKRVR17 | 0.99037 | 0.93466 | -0.055711 |  | 0.95 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | ELKRVR17 | 0.99037 | 0.93466 | -0.055711 |  | 0.95 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | ELKRVR17 | 0.99037 | 0.93466 | -0.055711 |  | 0.95 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | ELKRVR17 | 0.99037 | 0.93466 | -0.055711 |  | 0.95 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | ELKRVR17 | 0.99037 | 0.93466 | -0.055711 |  | 0.95 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | ELKRVR17 | 0.99037 | 0.93466 | -0.055711 |  | 0.95 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | ELKRVR17 | 0.99037 | 0.93466 | -0.055711 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | ELKRVR17 | 0.99037 | 0.93466 | -0.055711 |  | 0.95 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | ELKRVR17 | 0.99037 | 0.93466 | -0.055711 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | ELKRVR17 | 0.99037 | 0.93466 | -0.055711 |  | 0.95 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | ELKRVR17 | 0.99037 | 0.93466 | -0.055711 |  | 0.95 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | ELKRVR17 | 0.99037 | 0.93466 | -0.055711 |  | 0.95 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | ELKRVR17 | 0.99037 | 0.93466 | -0.055711 |  | 0.95 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | ELKRVR17 | 0.99037 | 0.93466 | -0.055711 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | ELKRVR17 | 0.99037 | 0.93466 | -0.055711 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | ELKRVR17 | 0.99037 | 0.93466 | -0.055711 |  | 0.95 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | ELKRVR17 | 0.99037 | 0.93466 | -0.055711 |  | 0.95 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | ELKRVR17 | 0.99037 | 0.93466 | -0.055711 |  | 0.95 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | ELKRVR17 | 0.99037 | 0.93466 | -0.055711 |  | 0.95 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | ELKRVR17 | 0.99037 | 0.93466 | -0.055711 |  | 0.95 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | ELKRVR17 | 0.99037 | 0.93466 | -0.055711 |  | 0.95 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | EUDORA 3 | 0.96936 | 0.92902 | -0.040339 |  | 0.93 | 1.05 | 0.036307 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | EUDORA 3 | 0.96936 | 0.92902 | -0.040339 |  | 0.93 | 1.05 | 0.052743 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | EUDORA 3 | 0.96936 | 0.92902 | -0.040339 |  | 0.93 | 1.05 | 0.039345 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | EUDORA 3 | 0.96936 | 0.92902 | -0.040339 |  | 0.93 | 1.05 | 0.031366 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | EUDORA 3 | 0.96936 | 0.92902 | -0.040339 |  | 0.93 | 1.05 | 0.041888 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | EUDORA 3 | 0.96936 | 0.92902 | -0.040339 |  | 0.93 | 1.05 | 0.038797 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | EUDORA 3 | 0.96936 | 0.92902 | -0.040339 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | EUDORA 3 | 0.96936 | 0.92902 | -0.040339 |  | 0.93 | 1.05 | 0.067346 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | EUDORA 3 | 0.96936 | 0.92902 | -0.040339 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | EUDORA 3 | 0.96936 | 0.92902 | -0.040339 |  | 0.93 | 1.05 | 0.030851 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | EUDORA 3 | 0.96936 | 0.92902 | -0.040339 |  | 0.93 | 1.05 | 0.032161 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | EUDORA 3 | 0.96936 | 0.92902 | -0.040339 |  | 0.93 | 1.05 | 0.04067 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | EUDORA 3 | 0.96936 | 0.92902 | -0.040339 |  | 0.93 | 1.05 | 0.040569 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | EUDORA 3 | 0.96936 | 0.92902 | -0.040339 |  | 0.93 | 1.05 | 0.03086 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | EUDORA 3 | 0.96936 | 0.92902 | -0.040339 |  | 0.93 | 1.05 | 0.033223 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | EUDORA 3 | 0.96936 | 0.92902 | -0.040339 |  | 0.93 | 1.05 | 0.033733 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | EUDORA 3 | 0.98348 | 0.92671 | -0.056777 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | EUDORA 3 | 0.98348 | 0.92671 | -0.056777 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | EUDORA 3 | 0.98348 | 0.92671 | -0.056777 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | EUDORA 3 | 0.98348 | 0.92671 | -0.056777 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | EUDORA 3 | 0.98348 | 0.92671 | -0.056777 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | EUDORA 3 | 0.98348 | 0.92671 | -0.056777 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | EUDORA 3 | 0.98348 | 0.92671 | -0.056777 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | EUDORA 3 | 0.98348 | 0.92671 | -0.056777 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | EUDORA 3 | 0.98348 | 0.92671 | -0.056777 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | EUDORA 3 | 0.98348 | 0.92671 | -0.056777 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | EUDORA 3 | 0.98348 | 0.92671 | -0.056777 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | EUDORA 3 | 0.98348 | 0.92671 | -0.056777 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | EUDORA 3 | 0.98348 | 0.92671 | -0.056777 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | EUDORA 3 | 0.98348 | 0.92671 | -0.056777 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | EUDORA 3 | 0.98348 | 0.92671 | -0.056777 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | EUDORA 3 | 0.98348 | 0.92671 | -0.056777 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | EUDORA 3 | 0.98348 | 0.92671 | -0.056777 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | EUDORA 3 | 0.98348 | 0.92671 | -0.056777 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | EUDORA 3 | 0.98348 | 0.92671 | -0.056777 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | EUDORA 3 | 0.98348 | 0.92671 | -0.056777 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | EUDORA 3 | 0.98348 | 0.92671 | -0.056777 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | EUDORA 3 | 0.98348 | 0.92671 | -0.056777 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | EUDORA 3 | 0.98348 | 0.92671 | -0.056777 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | EUDORA 3 | 0.98348 | 0.92671 | -0.056777 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | EUDORA 3 | 0.98348 | 0.92671 | -0.056777 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | EXPCLAR4 | 0.90486 | 0.87729 | -0.027567 |  | 0.92 | 1.05 | 0.038424 | Single 509752 INOLATP4 138 509790 CATOOSA4 138 1 | Add 57 MVAR switched shunt at GUAVA 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | EXPCLAR4 | 0.91611 | 0.89025 | -0.025861 |  | 0.92 | 1.05 | 0.038424 | Single 509752 INOLATP4 138 510442 GUAVA4 138 1 | Add 57 MVAR switched shunt at GUAVA 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | EXPED WF7 | 1.0055 | 0.93303 | -0.072445 |  | 0.95 | 1.05 | 0.03053 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | EXPED WF7 | 1.0055 | 0.93303 | -0.072445 |  | 0.95 | 1.05 | 0.044933 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | EXPED WF7 | 1.0055 | 0.93303 | -0.072445 |  | 0.95 | 1.05 | 0.047811 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | EXPED WF7 | 1.0055 | 0.93303 | -0.072445 |  | 0.95 | 1.05 | 0.09719 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | EXPED WF7 | 1.0055 | 0.93303 | -0.072445 |  | 0.95 | 1.05 | 0.069376 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | EXPED WF7 | 1.0055 | 0.93303 | -0.072445 |  | 0.95 | 1.05 | 0.04277 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | EXPED WF7 | 1.0055 | 0.93303 | -0.072445 |  | 0.95 | 1.05 | 0.071112 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | EXPED WF7 | 1.0055 | 0.93303 | -0.072445 |  | 0.95 | 1.05 | 0.039357 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | EXPED WF7 | 1.0055 | 0.93303 | -0.072445 |  | 0.95 | 1.05 | 0.04035 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | EXPED WF7 | 1.0055 | 0.93303 | -0.072445 |  | 0.95 | 1.05 | 0.052332 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | EXPED WF7 | 1.0055 | 0.93303 | -0.072445 |  | 0.95 | 1.05 | 0.045944 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | EXPED WF7 | 1.0055 | 0.93303 | -0.072445 |  | 0.95 | 1.05 | 0.038178 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | EXPED WF7 | 1.0055 | 0.93303 | -0.072445 |  | 0.95 | 1.05 | 0.13469 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | EXPED WF7 | 1.0055 | 0.93303 | -0.072445 |  | 0.95 | 1.05 | 0.03053 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | EXPED WF7 | 1.0055 | 0.93303 | -0.072445 |  | 0.95 | 1.05 | 0.038178 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | EXPED WF7 | 1.0055 | 0.93303 | -0.072445 |  | 0.95 | 1.05 | 0.037309 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | EXPED WF7 | 1.0055 | 0.93303 | -0.072445 |  | 0.95 | 1.05 | 0.040075 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | EXPED WF7 | 1.0055 | 0.93303 | -0.072445 |  | 0.95 | 1.05 | 0.053764 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | EXPED WF7 | 1.0055 | 0.93303 | -0.072445 |  | 0.95 | 1.05 | 0.071762 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | EXPED WF7 | 1.0055 | 0.93303 | -0.072445 |  | 0.95 | 1.05 | 0.047827 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | EXPED WF7 | 1.0055 | 0.93303 | -0.072445 |  | 0.95 | 1.05 | 0.047827 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | EXPED WF7 | 1.0055 | 0.93303 | -0.072445 |  | 0.95 | 1.05 | 0.070303 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | EXPED WF7 | 1.0055 | 0.93303 | -0.072445 |  | 0.95 | 1.05 | 0.040614 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | EXPED WF7 | 1.0055 | 0.93303 | -0.072445 |  | 0.95 | 1.05 | 0.039729 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | EXPED WF7 | 1.0055 | 0.93303 | -0.072445 |  | 0.95 | 1.05 | 0.049662 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | EXPED WF7 | 1.0055 | 0.93303 | -0.072445 |  | 0.95 | 1.05 | 0.042332 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | EXPED WF7 | 1.0055 | 0.93303 | -0.072445 |  | 0.95 | 1.05 | 0.048722 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | EXPED WF7 | 1.0055 | 0.93303 | -0.072445 |  | 0.95 | 1.05 | 0.038156 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | EXPED WF7 | 1.0055 | 0.93303 | -0.072445 |  | 0.95 | 1.05 | 0.036794 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | EXPED WF7 | 1.0066 | 0.94774 | -0.058866 |  | 0.95 | 1.05 | 0.075186 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | EXPED WF7 | 1.0066 | 0.94774 | -0.058866 |  | 0.95 | 1.05 | 0.031338 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | EXPED WF7 | 1.0066 | 0.94774 | -0.058866 |  | 0.95 | 1.05 | 0.031338 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | EXPED WF7 | 1.0066 | 0.94774 | -0.058866 |  | 0.95 | 1.05 | 0.031391 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | EXPED WF7 | 1.0066 | 0.94774 | -0.058866 |  | 0.95 | 1.05 | 0.034523 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | EXPED WF7 | 1.0064 | 0.9432 | -0.063201 |  | 0.95 | 1.05 | 0.036307 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | EXPED WF7 | 1.0064 | 0.9432 | -0.063201 |  | 0.95 | 1.05 | 0.052743 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | EXPED WF7 | 1.0064 | 0.9432 | -0.063201 |  | 0.95 | 1.05 | 0.039345 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | EXPED WF7 | 1.0064 | 0.9432 | -0.063201 |  | 0.95 | 1.05 | 0.031366 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | EXPED WF7 | 1.0064 | 0.9432 | -0.063201 |  | 0.95 | 1.05 | 0.041888 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | EXPED WF7 | 1.0064 | 0.9432 | -0.063201 |  | 0.95 | 1.05 | 0.038797 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | EXPED WF7 | 1.0064 | 0.9432 | -0.063201 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | EXPED WF7 | 1.0064 | 0.9432 | -0.063201 |  | 0.95 | 1.05 | 0.067346 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | EXPED WF7 | 1.0064 | 0.9432 | -0.063201 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | EXPED WF7 | 1.0064 | 0.9432 | -0.063201 |  | 0.95 | 1.05 | 0.030851 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | EXPED WF7 | 1.0064 | 0.9432 | -0.063201 |  | 0.95 | 1.05 | 0.032161 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | EXPED WF7 | 1.0064 | 0.9432 | -0.063201 |  | 0.95 | 1.05 | 0.04067 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | EXPED WF7 | 1.0064 | 0.9432 | -0.063201 |  | 0.95 | 1.05 | 0.040569 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | EXPED WF7 | 1.0064 | 0.9432 | -0.063201 |  | 0.95 | 1.05 | 0.03086 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | EXPED WF7 | 1.0064 | 0.9432 | -0.063201 |  | 0.95 | 1.05 | 0.033223 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | EXPED WF7 | 1.0064 | 0.9432 | -0.063201 |  | 0.95 | 1.05 | 0.033733 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | EXPED WF7 | 1.0027 | 0.92088 | -0.081787 |  | 0.95 | 1.05 | 0.040439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | EXPED WF7 | 1.0027 | 0.92088 | -0.081787 |  | 0.95 | 1.05 | 0.034853 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | EXPED WF7 | 1.0027 | 0.92088 | -0.081787 |  | 0.95 | 1.05 | 0.046783 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | EXPED WF7 | 1.0027 | 0.92088 | -0.081787 |  | 0.95 | 1.05 | 0.047615 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | EXPED WF7 | 1.0027 | 0.92088 | -0.081787 |  | 0.95 | 1.05 | 0.034938 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | EXPED WF7 | 1.0027 | 0.92088 | -0.081787 |  | 0.95 | 1.05 | 0.037875 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | EXPED WF7 | 1.0027 | 0.92088 | -0.081787 |  | 0.95 | 1.05 | 0.044022 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | EXPED WF7 | 1.0027 | 0.92088 | -0.081787 |  | 0.95 | 1.05 | 0.030552 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | EXPED WF7 | 1.0027 | 0.92088 | -0.081787 |  | 0.95 | 1.05 | 0.038531 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | EXPED WF7 | 1.0027 | 0.92088 | -0.081787 |  | 0.95 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | EXPED WF7 | 1.0027 | 0.92088 | -0.081787 |  | 0.95 | 1.05 | 0.062491 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | EXPED WF7 | 1.0027 | 0.92088 | -0.081787 |  | 0.95 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | EXPED WF7 | 1.0027 | 0.92088 | -0.081787 |  | 0.95 | 1.05 | 0.038129 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | EXPED WF7 | 1.0027 | 0.92088 | -0.081787 |  | 0.95 | 1.05 | 0.038066 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | EXPED WF7 | 1.0027 | 0.92088 | -0.081787 |  | 0.95 | 1.05 | 0.034955 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | EXPED WF7 | 1.0027 | 0.92088 | -0.081787 |  | 0.95 | 1.05 | 0.06281 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | EXPED WF7 | 1.0027 | 0.92088 | -0.081787 |  | 0.95 | 1.05 | 0.045309 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | EXPED WF7 | 1.0027 | 0.92088 | -0.081787 |  | 0.95 | 1.05 | 0.035805 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | EXPED WF7 | 1.0027 | 0.92088 | -0.081787 |  | 0.95 | 1.05 | 0.032364 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | EXPED WF7 | 1.0027 | 0.92088 | -0.081787 |  | 0.95 | 1.05 | 0.031815 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | EXPED WF7 | 1.0027 | 0.92088 | -0.081787 |  | 0.95 | 1.05 | 0.033886 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | EXPED WF7 | 1.0027 | 0.92088 | -0.081787 |  | 0.95 | 1.05 | 0.035554 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | EXPED WF7 | 1.002 | 0.92593 | -0.076101 |  | 0.95 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | EXPED WF7 | 1.002 | 0.92593 | -0.076101 |  | 0.95 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | EXPED WF7 | 1.002 | 0.92593 | -0.076101 |  | 0.95 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | EXPED WF7 | 1.002 | 0.92593 | -0.076101 |  | 0.95 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | EXPED WF7 | 1.002 | 0.92593 | -0.076101 |  | 0.95 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | EXPED WF7 | 1.002 | 0.92593 | -0.076101 |  | 0.95 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | EXPED WF7 | 1.002 | 0.92593 | -0.076101 |  | 0.95 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | EXPED WF7 | 1.002 | 0.92593 | -0.076101 |  | 0.95 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | EXPED WF7 | 1.002 | 0.92593 | -0.076101 |  | 0.95 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | EXPED WF7 | 1.002 | 0.92593 | -0.076101 |  | 0.95 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | EXPED WF7 | 1.002 | 0.92593 | -0.076101 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | EXPED WF7 | 1.002 | 0.92593 | -0.076101 |  | 0.95 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | EXPED WF7 | 1.002 | 0.92593 | -0.076101 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | EXPED WF7 | 1.002 | 0.92593 | -0.076101 |  | 0.95 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | EXPED WF7 | 1.002 | 0.92593 | -0.076101 |  | 0.95 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | EXPED WF7 | 1.002 | 0.92593 | -0.076101 |  | 0.95 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | EXPED WF7 | 1.002 | 0.92593 | -0.076101 |  | 0.95 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | EXPED WF7 | 1.002 | 0.92593 | -0.076101 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | EXPED WF7 | 1.002 | 0.92593 | -0.076101 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | EXPED WF7 | 1.002 | 0.92593 | -0.076101 |  | 0.95 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | EXPED WF7 | 1.002 | 0.92593 | -0.076101 |  | 0.95 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | EXPED WF7 | 1.002 | 0.92593 | -0.076101 |  | 0.95 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | EXPED WF7 | 1.002 | 0.92593 | -0.076101 |  | 0.95 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | EXPED WF7 | 1.002 | 0.92593 | -0.076101 |  | 0.95 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | EXPED WF7 | 1.002 | 0.92593 | -0.076101 |  | 0.95 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | FINNEY 7 | 1.0336 | 1.0551 | 0.0215 |  | 0.9 | 1.05 | 0.06238 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | FLORENC3 | 0.9767 | 0.89521 | -0.081487 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | FLORENC3 | 0.9767 | 0.89521 | -0.081487 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | FLORENC3 | 0.9767 | 0.89521 | -0.081487 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | FLORENC3 | 0.9767 | 0.89521 | -0.081487 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | FLORENC3 | 0.9767 | 0.89521 | -0.081487 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | FLORENC3 | 0.9767 | 0.89521 | -0.081487 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | FLORENC3 | 0.9767 | 0.89521 | -0.081487 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | FLORENC3 | 0.9767 | 0.89521 | -0.081487 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | FLORENC3 | 0.9767 | 0.89521 | -0.081487 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | FLORENC3 | 0.9767 | 0.89521 | -0.081487 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | FLORENC3 | 0.9767 | 0.89521 | -0.081487 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | FLORENC3 | 0.9767 | 0.89521 | -0.081487 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | FLORENC3 | 0.9767 | 0.89521 | -0.081487 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | FLORENC3 | 0.9767 | 0.89521 | -0.081487 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | FLORENC3 | 0.9767 | 0.89521 | -0.081487 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | FLORENC3 | 0.9767 | 0.89521 | -0.081487 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | FLORENC3 | 0.9767 | 0.89521 | -0.081487 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | FLORENC3 | 0.9767 | 0.89521 | -0.081487 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | FLORENC3 | 0.9767 | 0.89521 | -0.081487 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | FLORENC3 | 0.9767 | 0.89521 | -0.081487 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | FLORENC3 | 0.9767 | 0.89521 | -0.081487 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | FLORENC3 | 0.9767 | 0.89521 | -0.081487 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | FLORENC3 | 0.9767 | 0.89521 | -0.081487 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | FLORENC3 | 0.9767 | 0.89521 | -0.081487 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | FLORENC3 | 0.9767 | 0.89521 | -0.081487 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | FOREST 5 | 0.98927 | 0.92684 | -0.062426 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | FOREST 5 | 0.98927 | 0.92684 | -0.062426 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | FOREST 5 | 0.98927 | 0.92684 | -0.062426 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | FOREST 5 | 0.98927 | 0.92684 | -0.062426 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | FOREST 5 | 0.98927 | 0.92684 | -0.062426 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | FOREST 5 | 0.98927 | 0.92684 | -0.062426 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | FOREST 5 | 0.98927 | 0.92684 | -0.062426 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | FOREST 5 | 0.98927 | 0.92684 | -0.062426 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | FOREST 5 | 0.98927 | 0.92684 | -0.062426 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | FOREST 5 | 0.98927 | 0.92684 | -0.062426 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | FOREST 5 | 0.98927 | 0.92684 | -0.062426 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | FOREST 5 | 0.98927 | 0.92684 | -0.062426 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | FOREST 5 | 0.98927 | 0.92684 | -0.062426 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | FOREST 5 | 0.98927 | 0.92684 | -0.062426 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | FOREST 5 | 0.98927 | 0.92684 | -0.062426 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | FOREST 5 | 0.98927 | 0.92684 | -0.062426 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | FOREST 5 | 0.98927 | 0.92684 | -0.062426 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | FOREST 5 | 0.98927 | 0.92684 | -0.062426 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | FOREST 5 | 0.98927 | 0.92684 | -0.062426 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | FOREST 5 | 0.98927 | 0.92684 | -0.062426 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | FOREST 5 | 0.98927 | 0.92684 | -0.062426 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | FOREST 5 | 0.98927 | 0.92684 | -0.062426 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | FOREST 5 | 0.98927 | 0.92684 | -0.062426 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | FOREST 5 | 0.98927 | 0.92684 | -0.062426 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | FOREST 5 | 0.98927 | 0.92684 | -0.062426 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | FR4 XMF1 345 | 0.99723 | 0.91996 | -0.077272 |  | 0.95 | 1.05 | 0.091967 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | FR4 XMF1 345 | 0.99723 | 0.91996 | -0.077272 |  | 0.95 | 1.05 | 0.033356 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | FR4 XMF1 345 | 0.99723 | 0.91996 | -0.077272 |  | 0.95 | 1.05 | 0.044346 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | FR4 XMF1 345 | 0.99723 | 0.91996 | -0.077272 |  | 0.95 | 1.05 | 0.058536 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | FR4 XMF1 345 | 0.99723 | 0.91996 | -0.077272 |  | 0.95 | 1.05 | 0.059327 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | FR4 XMF1 345 | 0.99723 | 0.91996 | -0.077272 |  | 0.95 | 1.05 | 0.041874 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | FR4 XMF1 345 | 0.99723 | 0.91996 | -0.077272 |  | 0.95 | 1.05 | 0.046192 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | FR4 XMF1 345 | 0.99723 | 0.91996 | -0.077272 |  | 0.95 | 1.05 | 0.12754 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | FR4 XMF1 345 | 0.99723 | 0.91996 | -0.077272 |  | 0.95 | 1.05 | 0.047018 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | FR4 XMF1 345 | 0.99723 | 0.91996 | -0.077272 |  | 0.95 | 1.05 | 0.056662 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | FR4 XMF1 345 | 0.99723 | 0.91996 | -0.077272 |  | 0.95 | 1.05 | 0.056662 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | FR4 XMF1 345 | 0.99723 | 0.91996 | -0.077272 |  | 0.95 | 1.05 | 0.056727 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | FR4 XMF1 345 | 0.99723 | 0.91996 | -0.077272 |  | 0.95 | 1.05 | 0.074186 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | FR4 XMF1 345 | 0.99723 | 0.91996 | -0.077272 |  | 0.95 | 1.05 | 0.040839 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | FR4 XMF1 345 | 0.99723 | 0.91996 | -0.077272 |  | 0.95 | 1.05 | 0.03863 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | FR4 XMF1 345 | 0.99723 | 0.91996 | -0.077272 |  | 0.95 | 1.05 | 0.042285 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | FR4 XMF1 345 | 0.99723 | 0.91996 | -0.077272 |  | 0.95 | 1.05 | 0.042285 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | FR4 XMF1 345 | 0.99723 | 0.91996 | -0.077272 |  | 0.95 | 1.05 | 0.050204 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | FR4 XMF1 345 | 0.99723 | 0.91996 | -0.077272 |  | 0.95 | 1.05 | 0.058005 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | FR4 XMF1 345 | 0.99723 | 0.91996 | -0.077272 |  | 0.95 | 1.05 | 0.041735 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | FR4 XMF1 345 | 0.99723 | 0.91996 | -0.077272 |  | 0.95 | 1.05 | 0.057076 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | FR4 XMF1 345 | 0.99723 | 0.91996 | -0.077272 |  | 0.95 | 1.05 | 0.050111 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | FR4 XMF1 345 | 0.99723 | 0.91996 | -0.077272 |  | 0.95 | 1.05 | 0.06491 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | FR4 XMF1 345 | 0.99723 | 0.91996 | -0.077272 |  | 0.95 | 1.05 | 0.051051 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | FR4 XMF1 345 | 0.99723 | 0.91996 | -0.077272 |  | 0.95 | 1.05 | 0.036279 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | FR4 XMF1 345 | 0.99984 | 0.94734 | -0.052505 |  | 0.95 | 1.05 | 0.091967 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | FR4 XMF1 345 | 0.99984 | 0.94734 | -0.052505 |  | 0.95 | 1.05 | 0.033356 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | FR4 XMF1 345 | 0.99984 | 0.94734 | -0.052505 |  | 0.95 | 1.05 | 0.044346 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | FR4 XMF1 345 | 0.99984 | 0.94734 | -0.052505 |  | 0.95 | 1.05 | 0.058536 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | FR4 XMF1 345 | 0.99984 | 0.94734 | -0.052505 |  | 0.95 | 1.05 | 0.059327 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | FR4 XMF1 345 | 0.99984 | 0.94734 | -0.052505 |  | 0.95 | 1.05 | 0.041874 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | FR4 XMF1 345 | 0.99984 | 0.94734 | -0.052505 |  | 0.95 | 1.05 | 0.046192 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | FR4 XMF1 345 | 0.99984 | 0.94734 | -0.052505 |  | 0.95 | 1.05 | 0.12754 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | FR4 XMF1 345 | 0.99984 | 0.94734 | -0.052505 |  | 0.95 | 1.05 | 0.047018 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | FR4 XMF1 345 | 0.99984 | 0.94734 | -0.052505 |  | 0.95 | 1.05 | 0.056662 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | FR4 XMF1 345 | 0.99984 | 0.94734 | -0.052505 |  | 0.95 | 1.05 | 0.056662 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | FR4 XMF1 345 | 0.99984 | 0.94734 | -0.052505 |  | 0.95 | 1.05 | 0.056727 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | FR4 XMF1 345 | 0.99984 | 0.94734 | -0.052505 |  | 0.95 | 1.05 | 0.074186 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | FR4 XMF1 345 | 0.99984 | 0.94734 | -0.052505 |  | 0.95 | 1.05 | 0.040839 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | FR4 XMF1 345 | 0.99984 | 0.94734 | -0.052505 |  | 0.95 | 1.05 | 0.03863 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | FR4 XMF1 345 | 0.99984 | 0.94734 | -0.052505 |  | 0.95 | 1.05 | 0.042285 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | FR4 XMF1 345 | 0.99984 | 0.94734 | -0.052505 |  | 0.95 | 1.05 | 0.042285 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | FR4 XMF1 345 | 0.99984 | 0.94734 | -0.052505 |  | 0.95 | 1.05 | 0.050204 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | FR4 XMF1 345 | 0.99984 | 0.94734 | -0.052505 |  | 0.95 | 1.05 | 0.058005 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | FR4 XMF1 345 | 0.99984 | 0.94734 | -0.052505 |  | 0.95 | 1.05 | 0.041735 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | FR4 XMF1 345 | 0.99984 | 0.94734 | -0.052505 |  | 0.95 | 1.05 | 0.057076 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | FR4 XMF1 345 | 0.99984 | 0.94734 | -0.052505 |  | 0.95 | 1.05 | 0.050111 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | FR4 XMF1 345 | 0.99984 | 0.94734 | -0.052505 |  | 0.95 | 1.05 | 0.06491 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | FR4 XMF1 345 | 0.99984 | 0.94734 | -0.052505 |  | 0.95 | 1.05 | 0.051051 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | FR4 XMF1 345 | 0.99984 | 0.94734 | -0.052505 |  | 0.95 | 1.05 | 0.036279 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | FR4 XMF1 345 | 0.99981 | 0.91417 | -0.085641 |  | 0.95 | 1.05 | 0.035768 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | FR4 XMF1 345 | 0.99981 | 0.91417 | -0.085641 |  | 0.95 | 1.05 | 0.088718 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | FR4 XMF1 345 | 0.99981 | 0.91417 | -0.085641 |  | 0.95 | 1.05 | 0.031473 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | FR4 XMF1 345 | 0.99981 | 0.91417 | -0.085641 |  | 0.95 | 1.05 | 0.034941 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | FR4 XMF1 345 | 0.99981 | 0.91417 | -0.085641 |  | 0.95 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | FR4 XMF1 345 | 0.99981 | 0.91417 | -0.085641 |  | 0.95 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | FR4 XMF1 345 | 0.99981 | 0.91417 | -0.085641 |  | 0.95 | 1.05 | 0.049224 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | FR4 XMF1 345 | 0.99981 | 0.91417 | -0.085641 |  | 0.95 | 1.05 | 0.038981 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | FR4 XMF1 345 | 0.99981 | 0.91417 | -0.085641 |  | 0.95 | 1.05 | 0.040399 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | FR4 XMF1 345 | 0.99981 | 0.91417 | -0.085641 |  | 0.95 | 1.05 | 0.031912 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | FR4 XMF1 345 | 0.99981 | 0.91417 | -0.085641 |  | 0.95 | 1.05 | 0.034127 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | FR4 XMF1 345 | 0.99981 | 0.91417 | -0.085641 |  | 0.95 | 1.05 | 0.047318 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | FR4 XMF1 345 | 1.002 | 0.93744 | -0.064553 |  | 0.95 | 1.05 | 0.040439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | FR4 XMF1 345 | 1.002 | 0.93744 | -0.064553 |  | 0.95 | 1.05 | 0.034853 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | FR4 XMF1 345 | 1.002 | 0.93744 | -0.064553 |  | 0.95 | 1.05 | 0.046783 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | FR4 XMF1 345 | 1.002 | 0.93744 | -0.064553 |  | 0.95 | 1.05 | 0.047615 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | FR4 XMF1 345 | 1.002 | 0.93744 | -0.064553 |  | 0.95 | 1.05 | 0.034938 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | FR4 XMF1 345 | 1.002 | 0.93744 | -0.064553 |  | 0.95 | 1.05 | 0.037875 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | FR4 XMF1 345 | 1.002 | 0.93744 | -0.064553 |  | 0.95 | 1.05 | 0.044022 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | FR4 XMF1 345 | 1.002 | 0.93744 | -0.064553 |  | 0.95 | 1.05 | 0.030552 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | FR4 XMF1 345 | 1.002 | 0.93744 | -0.064553 |  | 0.95 | 1.05 | 0.038531 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | FR4 XMF1 345 | 1.002 | 0.93744 | -0.064553 |  | 0.95 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | FR4 XMF1 345 | 1.002 | 0.93744 | -0.064553 |  | 0.95 | 1.05 | 0.062491 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | FR4 XMF1 345 | 1.002 | 0.93744 | -0.064553 |  | 0.95 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | FR4 XMF1 345 | 1.002 | 0.93744 | -0.064553 |  | 0.95 | 1.05 | 0.038129 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | FR4 XMF1 345 | 1.002 | 0.93744 | -0.064553 |  | 0.95 | 1.05 | 0.038066 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | FR4 XMF1 345 | 1.002 | 0.93744 | -0.064553 |  | 0.95 | 1.05 | 0.034955 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | FR4 XMF1 345 | 1.002 | 0.93744 | -0.064553 |  | 0.95 | 1.05 | 0.06281 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | FR4 XMF1 345 | 1.002 | 0.93744 | -0.064553 |  | 0.95 | 1.05 | 0.045309 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | FR4 XMF1 345 | 1.002 | 0.93744 | -0.064553 |  | 0.95 | 1.05 | 0.035805 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | FR4 XMF1 345 | 1.002 | 0.93744 | -0.064553 |  | 0.95 | 1.05 | 0.032364 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | FR4 XMF1 345 | 1.002 | 0.93744 | -0.064553 |  | 0.95 | 1.05 | 0.031815 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | FR4 XMF1 345 | 1.002 | 0.93744 | -0.064553 |  | 0.95 | 1.05 | 0.033886 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | FR4 XMF1 345 | 1.002 | 0.93744 | -0.064553 |  | 0.95 | 1.05 | 0.035554 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | FR4 XMF1 345 | 1.0027 | 0.94912 | -0.053603 |  | 0.95 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | FR4 XMF1 345 | 1.0027 | 0.94912 | -0.053603 |  | 0.95 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | FR4 XMF1 345 | 1.0027 | 0.94912 | -0.053603 |  | 0.95 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | FR4 XMF1 345 | 1.0027 | 0.94912 | -0.053603 |  | 0.95 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | FR4 XMF1 345 | 1.0027 | 0.94912 | -0.053603 |  | 0.95 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | FR4 XMF1 345 | 1.0027 | 0.94912 | -0.053603 |  | 0.95 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | FR4 XMF1 345 | 1.0027 | 0.94912 | -0.053603 |  | 0.95 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | FR4 XMF1 345 | 1.0027 | 0.94912 | -0.053603 |  | 0.95 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | FR4 XMF1 345 | 1.0027 | 0.94912 | -0.053603 |  | 0.95 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | FR4 XMF1 345 | 1.0027 | 0.94912 | -0.053603 |  | 0.95 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | FR4 XMF1 345 | 1.0027 | 0.94912 | -0.053603 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | FR4 XMF1 345 | 1.0027 | 0.94912 | -0.053603 |  | 0.95 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | FR4 XMF1 345 | 1.0027 | 0.94912 | -0.053603 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | FR4 XMF1 345 | 1.0027 | 0.94912 | -0.053603 |  | 0.95 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | FR4 XMF1 345 | 1.0027 | 0.94912 | -0.053603 |  | 0.95 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | FR4 XMF1 345 | 1.0027 | 0.94912 | -0.053603 |  | 0.95 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | FR4 XMF1 345 | 1.0027 | 0.94912 | -0.053603 |  | 0.95 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | FR4 XMF1 345 | 1.0027 | 0.94912 | -0.053603 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | FR4 XMF1 345 | 1.0027 | 0.94912 | -0.053603 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | FR4 XMF1 345 | 1.0027 | 0.94912 | -0.053603 |  | 0.95 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | FR4 XMF1 345 | 1.0027 | 0.94912 | -0.053603 |  | 0.95 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | FR4 XMF1 345 | 1.0027 | 0.94912 | -0.053603 |  | 0.95 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | FR4 XMF1 345 | 1.0027 | 0.94912 | -0.053603 |  | 0.95 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | FR4 XMF1 345 | 1.0027 | 0.94912 | -0.053603 |  | 0.95 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | FR4 XMF1 345 | 1.0027 | 0.94912 | -0.053603 |  | 0.95 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | FR4345KV-TAP | 0.99716 | 0.91989 | -0.077267 |  | 0.95 | 1.05 | 0.091967 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | FR4345KV-TAP | 0.99716 | 0.91989 | -0.077267 |  | 0.95 | 1.05 | 0.033356 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | FR4345KV-TAP | 0.99716 | 0.91989 | -0.077267 |  | 0.95 | 1.05 | 0.044346 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | FR4345KV-TAP | 0.99716 | 0.91989 | -0.077267 |  | 0.95 | 1.05 | 0.058536 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | FR4345KV-TAP | 0.99716 | 0.91989 | -0.077267 |  | 0.95 | 1.05 | 0.059327 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | FR4345KV-TAP | 0.99716 | 0.91989 | -0.077267 |  | 0.95 | 1.05 | 0.041874 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | FR4345KV-TAP | 0.99716 | 0.91989 | -0.077267 |  | 0.95 | 1.05 | 0.046192 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | FR4345KV-TAP | 0.99716 | 0.91989 | -0.077267 |  | 0.95 | 1.05 | 0.12754 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | FR4345KV-TAP | 0.99716 | 0.91989 | -0.077267 |  | 0.95 | 1.05 | 0.047018 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | FR4345KV-TAP | 0.99716 | 0.91989 | -0.077267 |  | 0.95 | 1.05 | 0.056662 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | FR4345KV-TAP | 0.99716 | 0.91989 | -0.077267 |  | 0.95 | 1.05 | 0.056662 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | FR4345KV-TAP | 0.99716 | 0.91989 | -0.077267 |  | 0.95 | 1.05 | 0.056727 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | FR4345KV-TAP | 0.99716 | 0.91989 | -0.077267 |  | 0.95 | 1.05 | 0.074186 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | FR4345KV-TAP | 0.99716 | 0.91989 | -0.077267 |  | 0.95 | 1.05 | 0.040839 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | FR4345KV-TAP | 0.99716 | 0.91989 | -0.077267 |  | 0.95 | 1.05 | 0.03863 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | FR4345KV-TAP | 0.99716 | 0.91989 | -0.077267 |  | 0.95 | 1.05 | 0.042285 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | FR4345KV-TAP | 0.99716 | 0.91989 | -0.077267 |  | 0.95 | 1.05 | 0.042285 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | FR4345KV-TAP | 0.99716 | 0.91989 | -0.077267 |  | 0.95 | 1.05 | 0.050204 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | FR4345KV-TAP | 0.99716 | 0.91989 | -0.077267 |  | 0.95 | 1.05 | 0.058005 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | FR4345KV-TAP | 0.99716 | 0.91989 | -0.077267 |  | 0.95 | 1.05 | 0.041735 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | FR4345KV-TAP | 0.99716 | 0.91989 | -0.077267 |  | 0.95 | 1.05 | 0.057076 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | FR4345KV-TAP | 0.99716 | 0.91989 | -0.077267 |  | 0.95 | 1.05 | 0.050111 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | FR4345KV-TAP | 0.99716 | 0.91989 | -0.077267 |  | 0.95 | 1.05 | 0.06491 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | FR4345KV-TAP | 0.99716 | 0.91989 | -0.077267 |  | 0.95 | 1.05 | 0.051051 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | FR4345KV-TAP | 0.99716 | 0.91989 | -0.077267 |  | 0.95 | 1.05 | 0.036279 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | FR4345KV-TAP | 0.99977 | 0.94727 | -0.052502 |  | 0.95 | 1.05 | 0.091967 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | FR4345KV-TAP | 0.99977 | 0.94727 | -0.052502 |  | 0.95 | 1.05 | 0.033356 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | FR4345KV-TAP | 0.99977 | 0.94727 | -0.052502 |  | 0.95 | 1.05 | 0.044346 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | FR4345KV-TAP | 0.99977 | 0.94727 | -0.052502 |  | 0.95 | 1.05 | 0.058536 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | FR4345KV-TAP | 0.99977 | 0.94727 | -0.052502 |  | 0.95 | 1.05 | 0.059327 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | FR4345KV-TAP | 0.99977 | 0.94727 | -0.052502 |  | 0.95 | 1.05 | 0.041874 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | FR4345KV-TAP | 0.99977 | 0.94727 | -0.052502 |  | 0.95 | 1.05 | 0.046192 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | FR4345KV-TAP | 0.99977 | 0.94727 | -0.052502 |  | 0.95 | 1.05 | 0.12754 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | FR4345KV-TAP | 0.99977 | 0.94727 | -0.052502 |  | 0.95 | 1.05 | 0.047018 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | FR4345KV-TAP | 0.99977 | 0.94727 | -0.052502 |  | 0.95 | 1.05 | 0.056662 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | FR4345KV-TAP | 0.99977 | 0.94727 | -0.052502 |  | 0.95 | 1.05 | 0.056662 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | FR4345KV-TAP | 0.99977 | 0.94727 | -0.052502 |  | 0.95 | 1.05 | 0.056727 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | FR4345KV-TAP | 0.99977 | 0.94727 | -0.052502 |  | 0.95 | 1.05 | 0.074186 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | FR4345KV-TAP | 0.99977 | 0.94727 | -0.052502 |  | 0.95 | 1.05 | 0.040839 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | FR4345KV-TAP | 0.99977 | 0.94727 | -0.052502 |  | 0.95 | 1.05 | 0.03863 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | FR4345KV-TAP | 0.99977 | 0.94727 | -0.052502 |  | 0.95 | 1.05 | 0.042285 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | FR4345KV-TAP | 0.99977 | 0.94727 | -0.052502 |  | 0.95 | 1.05 | 0.042285 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | FR4345KV-TAP | 0.99977 | 0.94727 | -0.052502 |  | 0.95 | 1.05 | 0.050204 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | FR4345KV-TAP | 0.99977 | 0.94727 | -0.052502 |  | 0.95 | 1.05 | 0.058005 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | FR4345KV-TAP | 0.99977 | 0.94727 | -0.052502 |  | 0.95 | 1.05 | 0.041735 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | FR4345KV-TAP | 0.99977 | 0.94727 | -0.052502 |  | 0.95 | 1.05 | 0.057076 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | FR4345KV-TAP | 0.99977 | 0.94727 | -0.052502 |  | 0.95 | 1.05 | 0.050111 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | FR4345KV-TAP | 0.99977 | 0.94727 | -0.052502 |  | 0.95 | 1.05 | 0.06491 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | FR4345KV-TAP | 0.99977 | 0.94727 | -0.052502 |  | 0.95 | 1.05 | 0.051051 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | FR4345KV-TAP | 0.99977 | 0.94727 | -0.052502 |  | 0.95 | 1.05 | 0.036279 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | FR4345KV-TAP | 0.99974 | 0.9141 | -0.085635 |  | 0.95 | 1.05 | 0.035768 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | FR4345KV-TAP | 0.99974 | 0.9141 | -0.085635 |  | 0.95 | 1.05 | 0.088718 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | FR4345KV-TAP | 0.99974 | 0.9141 | -0.085635 |  | 0.95 | 1.05 | 0.031473 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | FR4345KV-TAP | 0.99974 | 0.9141 | -0.085635 |  | 0.95 | 1.05 | 0.034941 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | FR4345KV-TAP | 0.99974 | 0.9141 | -0.085635 |  | 0.95 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | FR4345KV-TAP | 0.99974 | 0.9141 | -0.085635 |  | 0.95 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | FR4345KV-TAP | 0.99974 | 0.9141 | -0.085635 |  | 0.95 | 1.05 | 0.049224 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | FR4345KV-TAP | 0.99974 | 0.9141 | -0.085635 |  | 0.95 | 1.05 | 0.038981 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | FR4345KV-TAP | 0.99974 | 0.9141 | -0.085635 |  | 0.95 | 1.05 | 0.040399 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | FR4345KV-TAP | 0.99974 | 0.9141 | -0.085635 |  | 0.95 | 1.05 | 0.031912 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | FR4345KV-TAP | 0.99974 | 0.9141 | -0.085635 |  | 0.95 | 1.05 | 0.034127 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | FR4345KV-TAP | 0.99974 | 0.9141 | -0.085635 |  | 0.95 | 1.05 | 0.047318 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | FR4345KV-TAP | 1.0019 | 0.93737 | -0.064549 |  | 0.95 | 1.05 | 0.040439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | FR4345KV-TAP | 1.0019 | 0.93737 | -0.064549 |  | 0.95 | 1.05 | 0.034853 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | FR4345KV-TAP | 1.0019 | 0.93737 | -0.064549 |  | 0.95 | 1.05 | 0.046783 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | FR4345KV-TAP | 1.0019 | 0.93737 | -0.064549 |  | 0.95 | 1.05 | 0.047615 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | FR4345KV-TAP | 1.0019 | 0.93737 | -0.064549 |  | 0.95 | 1.05 | 0.034938 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | FR4345KV-TAP | 1.0019 | 0.93737 | -0.064549 |  | 0.95 | 1.05 | 0.037875 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | FR4345KV-TAP | 1.0019 | 0.93737 | -0.064549 |  | 0.95 | 1.05 | 0.044022 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | FR4345KV-TAP | 1.0019 | 0.93737 | -0.064549 |  | 0.95 | 1.05 | 0.030552 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | FR4345KV-TAP | 1.0019 | 0.93737 | -0.064549 |  | 0.95 | 1.05 | 0.038531 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | FR4345KV-TAP | 1.0019 | 0.93737 | -0.064549 |  | 0.95 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | FR4345KV-TAP | 1.0019 | 0.93737 | -0.064549 |  | 0.95 | 1.05 | 0.062491 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | FR4345KV-TAP | 1.0019 | 0.93737 | -0.064549 |  | 0.95 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | FR4345KV-TAP | 1.0019 | 0.93737 | -0.064549 |  | 0.95 | 1.05 | 0.038129 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | FR4345KV-TAP | 1.0019 | 0.93737 | -0.064549 |  | 0.95 | 1.05 | 0.038066 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | FR4345KV-TAP | 1.0019 | 0.93737 | -0.064549 |  | 0.95 | 1.05 | 0.034955 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | FR4345KV-TAP | 1.0019 | 0.93737 | -0.064549 |  | 0.95 | 1.05 | 0.06281 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | FR4345KV-TAP | 1.0019 | 0.93737 | -0.064549 |  | 0.95 | 1.05 | 0.045309 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | FR4345KV-TAP | 1.0019 | 0.93737 | -0.064549 |  | 0.95 | 1.05 | 0.035805 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | FR4345KV-TAP | 1.0019 | 0.93737 | -0.064549 |  | 0.95 | 1.05 | 0.032364 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | FR4345KV-TAP | 1.0019 | 0.93737 | -0.064549 |  | 0.95 | 1.05 | 0.031815 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | FR4345KV-TAP | 1.0019 | 0.93737 | -0.064549 |  | 0.95 | 1.05 | 0.033886 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | FR4345KV-TAP | 1.0019 | 0.93737 | -0.064549 |  | 0.95 | 1.05 | 0.035554 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | FR4345KV-TAP | 1.0027 | 0.94906 | -0.053599 |  | 0.95 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | FR4345KV-TAP | 1.0027 | 0.94906 | -0.053599 |  | 0.95 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | FR4345KV-TAP | 1.0027 | 0.94906 | -0.053599 |  | 0.95 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | FR4345KV-TAP | 1.0027 | 0.94906 | -0.053599 |  | 0.95 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | FR4345KV-TAP | 1.0027 | 0.94906 | -0.053599 |  | 0.95 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | FR4345KV-TAP | 1.0027 | 0.94906 | -0.053599 |  | 0.95 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | FR4345KV-TAP | 1.0027 | 0.94906 | -0.053599 |  | 0.95 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | FR4345KV-TAP | 1.0027 | 0.94906 | -0.053599 |  | 0.95 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | FR4345KV-TAP | 1.0027 | 0.94906 | -0.053599 |  | 0.95 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | FR4345KV-TAP | 1.0027 | 0.94906 | -0.053599 |  | 0.95 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | FR4345KV-TAP | 1.0027 | 0.94906 | -0.053599 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | FR4345KV-TAP | 1.0027 | 0.94906 | -0.053599 |  | 0.95 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | FR4345KV-TAP | 1.0027 | 0.94906 | -0.053599 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | FR4345KV-TAP | 1.0027 | 0.94906 | -0.053599 |  | 0.95 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | FR4345KV-TAP | 1.0027 | 0.94906 | -0.053599 |  | 0.95 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | FR4345KV-TAP | 1.0027 | 0.94906 | -0.053599 |  | 0.95 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | FR4345KV-TAP | 1.0027 | 0.94906 | -0.053599 |  | 0.95 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | FR4345KV-TAP | 1.0027 | 0.94906 | -0.053599 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | FR4345KV-TAP | 1.0027 | 0.94906 | -0.053599 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | FR4345KV-TAP | 1.0027 | 0.94906 | -0.053599 |  | 0.95 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | FR4345KV-TAP | 1.0027 | 0.94906 | -0.053599 |  | 0.95 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | FR4345KV-TAP | 1.0027 | 0.94906 | -0.053599 |  | 0.95 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | FR4345KV-TAP | 1.0027 | 0.94906 | -0.053599 |  | 0.95 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | FR4345KV-TAP | 1.0027 | 0.94906 | -0.053599 |  | 0.95 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | FR4345KV-TAP | 1.0027 | 0.94906 | -0.053599 |  | 0.95 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | G15052_1 | 0.96181 | 0.90848 | -0.053338 |  | 0.95 | 1.05 | 0.034914 | P23:345:WERE:WOLF-345-50:EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | G15052_1 | 0.96181 | 0.90848 | -0.053338 |  | 0.95 | 1.05 | 0.033648 | P23:345:WERE:WOLF-345-50:EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | G15052_1 | 0.96181 | 0.90848 | -0.053338 |  | 0.95 | 1.05 | 0.030226 | P23:345:WERE:WOLF-345-50:EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | G15052_1 | 0.96181 | 0.90848 | -0.053338 |  | 0.95 | 1.05 | 0.03107 | P23:345:WERE:WOLF-345-50:EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | G15052_1 | 0.96036 | 0.90869 | -0.051672 |  | 0.95 | 1.05 | 0.086438 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | G15052_1 | 0.96036 | 0.90869 | -0.051672 |  | 0.95 | 1.05 | 0.030745 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | G15052_1 | 0.96036 | 0.90869 | -0.051672 |  | 0.95 | 1.05 | 0.068467 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | G15052_1 | 0.96036 | 0.90869 | -0.051672 |  | 0.95 | 1.05 | 0.035987 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | G15052_1 | 0.96036 | 0.90869 | -0.051672 |  | 0.95 | 1.05 | 0.035544 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | G15052_1 | 0.96036 | 0.90869 | -0.051672 |  | 0.95 | 1.05 | 0.049119 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | G15052_1 | 0.96036 | 0.90869 | -0.051672 |  | 0.95 | 1.05 | 0.055003 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | G15052_1 | 0.96036 | 0.90869 | -0.051672 |  | 0.95 | 1.05 | 0.063546 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | G15052_1 | 0.96036 | 0.90869 | -0.051672 |  | 0.95 | 1.05 | 0.051632 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | G15052_1 | 0.96036 | 0.90869 | -0.051672 |  | 0.95 | 1.05 | 0.075715 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | G15052_1 | 0.96036 | 0.90869 | -0.051672 |  | 0.95 | 1.05 | 0.075715 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | G15052_1 | 0.96036 | 0.90869 | -0.051672 |  | 0.95 | 1.05 | 0.081345 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | G15052_1 | 0.96036 | 0.90869 | -0.051672 |  | 0.95 | 1.05 | 0.076095 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | G15052_1 | 0.96036 | 0.90869 | -0.051672 |  | 0.95 | 1.05 | 0.036132 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | G15052_1 | 0.96036 | 0.90869 | -0.051672 |  | 0.95 | 1.05 | 0.042821 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | G15052_1 | 0.96036 | 0.90869 | -0.051672 |  | 0.95 | 1.05 | 0.042821 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | G15052_1 | 0.96036 | 0.90869 | -0.051672 |  | 0.95 | 1.05 | 0.032833 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | G15052_1 | 0.96036 | 0.90869 | -0.051672 |  | 0.95 | 1.05 | 0.071192 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | G15052_1 | 0.96036 | 0.90869 | -0.051672 |  | 0.95 | 1.05 | 0.048915 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | G15052_1 | 0.96036 | 0.90869 | -0.051672 |  | 0.95 | 1.05 | 0.058485 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | G15052_1 | 0.96036 | 0.90869 | -0.051672 |  | 0.95 | 1.05 | 0.058513 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | G15052_1 | 0.96036 | 0.90869 | -0.051672 |  | 0.95 | 1.05 | 0.063019 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | G15052_1 | 0.96036 | 0.90869 | -0.051672 |  | 0.95 | 1.05 | 0.066289 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | G15052_1 | 0.96036 | 0.90869 | -0.051672 |  | 0.95 | 1.05 | 0.042335 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | G15052_1 | 0.96051 | 0.90918 | -0.05133 |  | 0.95 | 1.05 | 0.086438 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | G15052_1 | 0.96051 | 0.90918 | -0.05133 |  | 0.95 | 1.05 | 0.030745 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | G15052_1 | 0.96051 | 0.90918 | -0.05133 |  | 0.95 | 1.05 | 0.068467 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | G15052_1 | 0.96051 | 0.90918 | -0.05133 |  | 0.95 | 1.05 | 0.035987 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | G15052_1 | 0.96051 | 0.90918 | -0.05133 |  | 0.95 | 1.05 | 0.035544 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | G15052_1 | 0.96051 | 0.90918 | -0.05133 |  | 0.95 | 1.05 | 0.049119 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | G15052_1 | 0.96051 | 0.90918 | -0.05133 |  | 0.95 | 1.05 | 0.055003 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | G15052_1 | 0.96051 | 0.90918 | -0.05133 |  | 0.95 | 1.05 | 0.063546 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | G15052_1 | 0.96051 | 0.90918 | -0.05133 |  | 0.95 | 1.05 | 0.051632 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | G15052_1 | 0.96051 | 0.90918 | -0.05133 |  | 0.95 | 1.05 | 0.075715 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | G15052_1 | 0.96051 | 0.90918 | -0.05133 |  | 0.95 | 1.05 | 0.075715 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | G15052_1 | 0.96051 | 0.90918 | -0.05133 |  | 0.95 | 1.05 | 0.081345 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | G15052_1 | 0.96051 | 0.90918 | -0.05133 |  | 0.95 | 1.05 | 0.076095 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | G15052_1 | 0.96051 | 0.90918 | -0.05133 |  | 0.95 | 1.05 | 0.036132 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | G15052_1 | 0.96051 | 0.90918 | -0.05133 |  | 0.95 | 1.05 | 0.042821 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | G15052_1 | 0.96051 | 0.90918 | -0.05133 |  | 0.95 | 1.05 | 0.042821 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | G15052_1 | 0.96051 | 0.90918 | -0.05133 |  | 0.95 | 1.05 | 0.032833 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | G15052_1 | 0.96051 | 0.90918 | -0.05133 |  | 0.95 | 1.05 | 0.071192 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | G15052_1 | 0.96051 | 0.90918 | -0.05133 |  | 0.95 | 1.05 | 0.048915 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | G15052_1 | 0.96051 | 0.90918 | -0.05133 |  | 0.95 | 1.05 | 0.058485 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | G15052_1 | 0.96051 | 0.90918 | -0.05133 |  | 0.95 | 1.05 | 0.058513 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | G15052_1 | 0.96051 | 0.90918 | -0.05133 |  | 0.95 | 1.05 | 0.063019 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | G15052_1 | 0.96051 | 0.90918 | -0.05133 |  | 0.95 | 1.05 | 0.066289 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | G15052_1 | 0.96051 | 0.90918 | -0.05133 |  | 0.95 | 1.05 | 0.042335 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | G15052_1 | 0.96211 | 0.87593 | -0.086179 |  | 0.95 | 1.05 | 0.035768 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | G15052_1 | 0.96211 | 0.87593 | -0.086179 |  | 0.95 | 1.05 | 0.088718 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | G15052_1 | 0.96211 | 0.87593 | -0.086179 |  | 0.95 | 1.05 | 0.031473 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | G15052_1 | 0.96211 | 0.87593 | -0.086179 |  | 0.95 | 1.05 | 0.034941 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | G15052_1 | 0.96211 | 0.87593 | -0.086179 |  | 0.95 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | G15052_1 | 0.96211 | 0.87593 | -0.086179 |  | 0.95 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | G15052_1 | 0.96211 | 0.87593 | -0.086179 |  | 0.95 | 1.05 | 0.049224 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | G15052_1 | 0.96211 | 0.87593 | -0.086179 |  | 0.95 | 1.05 | 0.038981 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | G15052_1 | 0.96211 | 0.87593 | -0.086179 |  | 0.95 | 1.05 | 0.040399 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | G15052_1 | 0.96211 | 0.87593 | -0.086179 |  | 0.95 | 1.05 | 0.031912 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | G15052_1 | 0.96211 | 0.87593 | -0.086179 |  | 0.95 | 1.05 | 0.034127 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | G15052_1 | 0.96211 | 0.87593 | -0.086179 |  | 0.95 | 1.05 | 0.047318 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | G15052_1 | 0.96163 | 0.88443 | -0.077199 |  | 0.95 | 1.05 | 0.040439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | G15052_1 | 0.96163 | 0.88443 | -0.077199 |  | 0.95 | 1.05 | 0.034853 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | G15052_1 | 0.96163 | 0.88443 | -0.077199 |  | 0.95 | 1.05 | 0.046783 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | G15052_1 | 0.96163 | 0.88443 | -0.077199 |  | 0.95 | 1.05 | 0.047615 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | G15052_1 | 0.96163 | 0.88443 | -0.077199 |  | 0.95 | 1.05 | 0.034938 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | G15052_1 | 0.96163 | 0.88443 | -0.077199 |  | 0.95 | 1.05 | 0.037875 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | G15052_1 | 0.96163 | 0.88443 | -0.077199 |  | 0.95 | 1.05 | 0.044022 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | G15052_1 | 0.96163 | 0.88443 | -0.077199 |  | 0.95 | 1.05 | 0.030552 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | G15052_1 | 0.96163 | 0.88443 | -0.077199 |  | 0.95 | 1.05 | 0.038531 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | G15052_1 | 0.96163 | 0.88443 | -0.077199 |  | 0.95 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | G15052_1 | 0.96163 | 0.88443 | -0.077199 |  | 0.95 | 1.05 | 0.062491 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | G15052_1 | 0.96163 | 0.88443 | -0.077199 |  | 0.95 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | G15052_1 | 0.96163 | 0.88443 | -0.077199 |  | 0.95 | 1.05 | 0.038129 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | G15052_1 | 0.96163 | 0.88443 | -0.077199 |  | 0.95 | 1.05 | 0.038066 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | G15052_1 | 0.96163 | 0.88443 | -0.077199 |  | 0.95 | 1.05 | 0.034955 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | G15052_1 | 0.96163 | 0.88443 | -0.077199 |  | 0.95 | 1.05 | 0.06281 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | G15052_1 | 0.96163 | 0.88443 | -0.077199 |  | 0.95 | 1.05 | 0.045309 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | G15052_1 | 0.96163 | 0.88443 | -0.077199 |  | 0.95 | 1.05 | 0.035805 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | G15052_1 | 0.96163 | 0.88443 | -0.077199 |  | 0.95 | 1.05 | 0.032364 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | G15052_1 | 0.96163 | 0.88443 | -0.077199 |  | 0.95 | 1.05 | 0.031815 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | G15052_1 | 0.96163 | 0.88443 | -0.077199 |  | 0.95 | 1.05 | 0.033886 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | G15052_1 | 0.96163 | 0.88443 | -0.077199 |  | 0.95 | 1.05 | 0.035554 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | G15052_T | 0.97509 | 0.94557 | -0.029523 |  | 0.95 | 1.05 | 0.091967 | System Intact | Add 45 MVAR SVC at G15052_T 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | G15052_T | 0.97509 | 0.94557 | -0.029523 |  | 0.95 | 1.05 | 0.033356 | System Intact | Add 45 MVAR SVC at G15052_T 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | G15052_T | 0.97509 | 0.94557 | -0.029523 |  | 0.95 | 1.05 | 0.044346 | System Intact | Add 45 MVAR SVC at G15052_T 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | G15052_T | 0.97509 | 0.94557 | -0.029523 |  | 0.95 | 1.05 | 0.058536 | System Intact | Add 45 MVAR SVC at G15052_T 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | G15052_T | 0.97509 | 0.94557 | -0.029523 |  | 0.95 | 1.05 | 0.059327 | System Intact | Add 45 MVAR SVC at G15052_T 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | G15052_T | 0.97509 | 0.94557 | -0.029523 |  | 0.95 | 1.05 | 0.041874 | System Intact | Add 45 MVAR SVC at G15052_T 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | G15052_T | 0.97509 | 0.94557 | -0.029523 |  | 0.95 | 1.05 | 0.046192 | System Intact | Add 45 MVAR SVC at G15052_T 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | G15052_T | 0.97509 | 0.94557 | -0.029523 |  | 0.95 | 1.05 | 0.12754 | System Intact | Add 45 MVAR SVC at G15052_T 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | G15052_T | 0.97509 | 0.94557 | -0.029523 |  | 0.95 | 1.05 | 0.047018 | System Intact | Add 45 MVAR SVC at G15052_T 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | G15052_T | 0.97509 | 0.94557 | -0.029523 |  | 0.95 | 1.05 | 0.056662 | System Intact | Add 45 MVAR SVC at G15052_T 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | G15052_T | 0.97509 | 0.94557 | -0.029523 |  | 0.95 | 1.05 | 0.056662 | System Intact | Add 45 MVAR SVC at G15052_T 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | G15052_T | 0.97509 | 0.94557 | -0.029523 |  | 0.95 | 1.05 | 0.056727 | System Intact | Add 45 MVAR SVC at G15052_T 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | G15052_T | 0.97509 | 0.94557 | -0.029523 |  | 0.95 | 1.05 | 0.074186 | System Intact | Add 45 MVAR SVC at G15052_T 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | G15052_T | 0.97509 | 0.94557 | -0.029523 |  | 0.95 | 1.05 | 0.040839 | System Intact | Add 45 MVAR SVC at G15052_T 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | G15052_T | 0.97509 | 0.94557 | -0.029523 |  | 0.95 | 1.05 | 0.03863 | System Intact | Add 45 MVAR SVC at G15052_T 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | G15052_T | 0.97509 | 0.94557 | -0.029523 |  | 0.95 | 1.05 | 0.042285 | System Intact | Add 45 MVAR SVC at G15052_T 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | G15052_T | 0.97509 | 0.94557 | -0.029523 |  | 0.95 | 1.05 | 0.042285 | System Intact | Add 45 MVAR SVC at G15052_T 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | G15052_T | 0.97509 | 0.94557 | -0.029523 |  | 0.95 | 1.05 | 0.050204 | System Intact | Add 45 MVAR SVC at G15052_T 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | G15052_T | 0.97509 | 0.94557 | -0.029523 |  | 0.95 | 1.05 | 0.058005 | System Intact | Add 45 MVAR SVC at G15052_T 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | G15052_T | 0.97509 | 0.94557 | -0.029523 |  | 0.95 | 1.05 | 0.041735 | System Intact | Add 45 MVAR SVC at G15052_T 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | G15052_T | 0.97509 | 0.94557 | -0.029523 |  | 0.95 | 1.05 | 0.057076 | System Intact | Add 45 MVAR SVC at G15052_T 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | G15052_T | 0.97509 | 0.94557 | -0.029523 |  | 0.95 | 1.05 | 0.050111 | System Intact | Add 45 MVAR SVC at G15052_T 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | G15052_T | 0.97509 | 0.94557 | -0.029523 |  | 0.95 | 1.05 | 0.06491 | System Intact | Add 45 MVAR SVC at G15052_T 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | G15052_T | 0.97509 | 0.94557 | -0.029523 |  | 0.95 | 1.05 | 0.051051 | System Intact | Add 45 MVAR SVC at G15052_T 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | G15052_T | 0.97509 | 0.94557 | -0.029523 |  | 0.95 | 1.05 | 0.036279 | System Intact | Add 45 MVAR SVC at G15052_T 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | G15052_T | 0.96181 | 0.90848 | -0.053338 |  | 0.95 | 1.05 | 0.034914 | P23:345:WERE:WOLF-345-50:EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | G15052_T | 0.96181 | 0.90848 | -0.053338 |  | 0.95 | 1.05 | 0.033648 | P23:345:WERE:WOLF-345-50:EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | G15052_T | 0.96181 | 0.90848 | -0.053338 |  | 0.95 | 1.05 | 0.030226 | P23:345:WERE:WOLF-345-50:EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | G15052_T | 0.96181 | 0.90848 | -0.053338 |  | 0.95 | 1.05 | 0.03107 | P23:345:WERE:WOLF-345-50:EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | G15052_T | 0.96036 | 0.90869 | -0.051672 |  | 0.95 | 1.05 | 0.086438 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | G15052_T | 0.96036 | 0.90869 | -0.051672 |  | 0.95 | 1.05 | 0.030745 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | G15052_T | 0.96036 | 0.90869 | -0.051672 |  | 0.95 | 1.05 | 0.068467 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | G15052_T | 0.96036 | 0.90869 | -0.051672 |  | 0.95 | 1.05 | 0.035987 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | G15052_T | 0.96036 | 0.90869 | -0.051672 |  | 0.95 | 1.05 | 0.035544 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | G15052_T | 0.96036 | 0.90869 | -0.051672 |  | 0.95 | 1.05 | 0.049119 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | G15052_T | 0.96036 | 0.90869 | -0.051672 |  | 0.95 | 1.05 | 0.055003 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | G15052_T | 0.96036 | 0.90869 | -0.051672 |  | 0.95 | 1.05 | 0.063546 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | G15052_T | 0.96036 | 0.90869 | -0.051672 |  | 0.95 | 1.05 | 0.051632 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | G15052_T | 0.96036 | 0.90869 | -0.051672 |  | 0.95 | 1.05 | 0.075715 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | G15052_T | 0.96036 | 0.90869 | -0.051672 |  | 0.95 | 1.05 | 0.075715 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | G15052_T | 0.96036 | 0.90869 | -0.051672 |  | 0.95 | 1.05 | 0.081345 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | G15052_T | 0.96036 | 0.90869 | -0.051672 |  | 0.95 | 1.05 | 0.076095 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | G15052_T | 0.96036 | 0.90869 | -0.051672 |  | 0.95 | 1.05 | 0.036132 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | G15052_T | 0.96036 | 0.90869 | -0.051672 |  | 0.95 | 1.05 | 0.042821 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | G15052_T | 0.96036 | 0.90869 | -0.051672 |  | 0.95 | 1.05 | 0.042821 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | G15052_T | 0.96036 | 0.90869 | -0.051672 |  | 0.95 | 1.05 | 0.032833 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | G15052_T | 0.96036 | 0.90869 | -0.051672 |  | 0.95 | 1.05 | 0.071192 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | G15052_T | 0.96036 | 0.90869 | -0.051672 |  | 0.95 | 1.05 | 0.048915 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | G15052_T | 0.96036 | 0.90869 | -0.051672 |  | 0.95 | 1.05 | 0.058485 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | G15052_T | 0.96036 | 0.90869 | -0.051672 |  | 0.95 | 1.05 | 0.058513 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | G15052_T | 0.96036 | 0.90869 | -0.051672 |  | 0.95 | 1.05 | 0.063019 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | G15052_T | 0.96036 | 0.90869 | -0.051672 |  | 0.95 | 1.05 | 0.066289 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | G15052_T | 0.96036 | 0.90869 | -0.051672 |  | 0.95 | 1.05 | 0.042335 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | G15052_T | 0.96051 | 0.90918 | -0.05133 |  | 0.95 | 1.05 | 0.086438 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | G15052_T | 0.96051 | 0.90918 | -0.05133 |  | 0.95 | 1.05 | 0.030745 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | G15052_T | 0.96051 | 0.90918 | -0.05133 |  | 0.95 | 1.05 | 0.068467 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | G15052_T | 0.96051 | 0.90918 | -0.05133 |  | 0.95 | 1.05 | 0.035987 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | G15052_T | 0.96051 | 0.90918 | -0.05133 |  | 0.95 | 1.05 | 0.035544 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | G15052_T | 0.96051 | 0.90918 | -0.05133 |  | 0.95 | 1.05 | 0.049119 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | G15052_T | 0.96051 | 0.90918 | -0.05133 |  | 0.95 | 1.05 | 0.055003 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | G15052_T | 0.96051 | 0.90918 | -0.05133 |  | 0.95 | 1.05 | 0.063546 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | G15052_T | 0.96051 | 0.90918 | -0.05133 |  | 0.95 | 1.05 | 0.051632 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | G15052_T | 0.96051 | 0.90918 | -0.05133 |  | 0.95 | 1.05 | 0.075715 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | G15052_T | 0.96051 | 0.90918 | -0.05133 |  | 0.95 | 1.05 | 0.075715 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | G15052_T | 0.96051 | 0.90918 | -0.05133 |  | 0.95 | 1.05 | 0.081345 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | G15052_T | 0.96051 | 0.90918 | -0.05133 |  | 0.95 | 1.05 | 0.076095 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | G15052_T | 0.96051 | 0.90918 | -0.05133 |  | 0.95 | 1.05 | 0.036132 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | G15052_T | 0.96051 | 0.90918 | -0.05133 |  | 0.95 | 1.05 | 0.042821 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | G15052_T | 0.96051 | 0.90918 | -0.05133 |  | 0.95 | 1.05 | 0.042821 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | G15052_T | 0.96051 | 0.90918 | -0.05133 |  | 0.95 | 1.05 | 0.032833 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | G15052_T | 0.96051 | 0.90918 | -0.05133 |  | 0.95 | 1.05 | 0.071192 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | G15052_T | 0.96051 | 0.90918 | -0.05133 |  | 0.95 | 1.05 | 0.048915 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | G15052_T | 0.96051 | 0.90918 | -0.05133 |  | 0.95 | 1.05 | 0.058485 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | G15052_T | 0.96051 | 0.90918 | -0.05133 |  | 0.95 | 1.05 | 0.058513 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | G15052_T | 0.96051 | 0.90918 | -0.05133 |  | 0.95 | 1.05 | 0.063019 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | G15052_T | 0.96051 | 0.90918 | -0.05133 |  | 0.95 | 1.05 | 0.066289 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | G15052_T | 0.96051 | 0.90918 | -0.05133 |  | 0.95 | 1.05 | 0.042335 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | G15052_T | 0.96211 | 0.87593 | -0.086179 |  | 0.95 | 1.05 | 0.035768 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | G15052_T | 0.96211 | 0.87593 | -0.086179 |  | 0.95 | 1.05 | 0.088718 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | G15052_T | 0.96211 | 0.87593 | -0.086179 |  | 0.95 | 1.05 | 0.031473 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | G15052_T | 0.96211 | 0.87593 | -0.086179 |  | 0.95 | 1.05 | 0.034941 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | G15052_T | 0.96211 | 0.87593 | -0.086179 |  | 0.95 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | G15052_T | 0.96211 | 0.87593 | -0.086179 |  | 0.95 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | G15052_T | 0.96211 | 0.87593 | -0.086179 |  | 0.95 | 1.05 | 0.049224 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | G15052_T | 0.96211 | 0.87593 | -0.086179 |  | 0.95 | 1.05 | 0.038981 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | G15052_T | 0.96211 | 0.87593 | -0.086179 |  | 0.95 | 1.05 | 0.040399 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | G15052_T | 0.96211 | 0.87593 | -0.086179 |  | 0.95 | 1.05 | 0.031912 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | G15052_T | 0.96211 | 0.87593 | -0.086179 |  | 0.95 | 1.05 | 0.034127 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | G15052_T | 0.96211 | 0.87593 | -0.086179 |  | 0.95 | 1.05 | 0.047318 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | G15052_T | 0.96163 | 0.88443 | -0.077199 |  | 0.95 | 1.05 | 0.040439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | G15052_T | 0.96163 | 0.88443 | -0.077199 |  | 0.95 | 1.05 | 0.034853 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | G15052_T | 0.96163 | 0.88443 | -0.077199 |  | 0.95 | 1.05 | 0.046783 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | G15052_T | 0.96163 | 0.88443 | -0.077199 |  | 0.95 | 1.05 | 0.047615 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | G15052_T | 0.96163 | 0.88443 | -0.077199 |  | 0.95 | 1.05 | 0.034938 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | G15052_T | 0.96163 | 0.88443 | -0.077199 |  | 0.95 | 1.05 | 0.037875 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | G15052_T | 0.96163 | 0.88443 | -0.077199 |  | 0.95 | 1.05 | 0.044022 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | G15052_T | 0.96163 | 0.88443 | -0.077199 |  | 0.95 | 1.05 | 0.030552 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | G15052_T | 0.96163 | 0.88443 | -0.077199 |  | 0.95 | 1.05 | 0.038531 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | G15052_T | 0.96163 | 0.88443 | -0.077199 |  | 0.95 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | G15052_T | 0.96163 | 0.88443 | -0.077199 |  | 0.95 | 1.05 | 0.062491 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | G15052_T | 0.96163 | 0.88443 | -0.077199 |  | 0.95 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | G15052_T | 0.96163 | 0.88443 | -0.077199 |  | 0.95 | 1.05 | 0.038129 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | G15052_T | 0.96163 | 0.88443 | -0.077199 |  | 0.95 | 1.05 | 0.038066 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | G15052_T | 0.96163 | 0.88443 | -0.077199 |  | 0.95 | 1.05 | 0.034955 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | G15052_T | 0.96163 | 0.88443 | -0.077199 |  | 0.95 | 1.05 | 0.06281 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | G15052_T | 0.96163 | 0.88443 | -0.077199 |  | 0.95 | 1.05 | 0.045309 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | G15052_T | 0.96163 | 0.88443 | -0.077199 |  | 0.95 | 1.05 | 0.035805 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | G15052_T | 0.96163 | 0.88443 | -0.077199 |  | 0.95 | 1.05 | 0.032364 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | G15052_T | 0.96163 | 0.88443 | -0.077199 |  | 0.95 | 1.05 | 0.031815 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | G15052_T | 0.96163 | 0.88443 | -0.077199 |  | 0.95 | 1.05 | 0.033886 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | G15052_T | 0.96163 | 0.88443 | -0.077199 |  | 0.95 | 1.05 | 0.035554 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | G16-111-TAP | 0.98779 | 0.91968 | -0.068113 |  | 0.95 | 1.05 | 0.03053 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | G16-111-TAP | 0.98779 | 0.91968 | -0.068113 |  | 0.95 | 1.05 | 0.044933 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | G16-111-TAP | 0.98779 | 0.91968 | -0.068113 |  | 0.95 | 1.05 | 0.047811 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | G16-111-TAP | 0.98779 | 0.91968 | -0.068113 |  | 0.95 | 1.05 | 0.09719 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | G16-111-TAP | 0.98779 | 0.91968 | -0.068113 |  | 0.95 | 1.05 | 0.069376 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | G16-111-TAP | 0.98779 | 0.91968 | -0.068113 |  | 0.95 | 1.05 | 0.04277 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | G16-111-TAP | 0.98779 | 0.91968 | -0.068113 |  | 0.95 | 1.05 | 0.071112 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | G16-111-TAP | 0.98779 | 0.91968 | -0.068113 |  | 0.95 | 1.05 | 0.039357 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | G16-111-TAP | 0.98779 | 0.91968 | -0.068113 |  | 0.95 | 1.05 | 0.04035 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | G16-111-TAP | 0.98779 | 0.91968 | -0.068113 |  | 0.95 | 1.05 | 0.052332 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | G16-111-TAP | 0.98779 | 0.91968 | -0.068113 |  | 0.95 | 1.05 | 0.045944 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | G16-111-TAP | 0.98779 | 0.91968 | -0.068113 |  | 0.95 | 1.05 | 0.038178 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | G16-111-TAP | 0.98779 | 0.91968 | -0.068113 |  | 0.95 | 1.05 | 0.13469 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | G16-111-TAP | 0.98779 | 0.91968 | -0.068113 |  | 0.95 | 1.05 | 0.03053 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | G16-111-TAP | 0.98779 | 0.91968 | -0.068113 |  | 0.95 | 1.05 | 0.038178 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | G16-111-TAP | 0.98779 | 0.91968 | -0.068113 |  | 0.95 | 1.05 | 0.037309 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | G16-111-TAP | 0.98779 | 0.91968 | -0.068113 |  | 0.95 | 1.05 | 0.040075 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | G16-111-TAP | 0.98779 | 0.91968 | -0.068113 |  | 0.95 | 1.05 | 0.053764 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | G16-111-TAP | 0.98779 | 0.91968 | -0.068113 |  | 0.95 | 1.05 | 0.071762 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | G16-111-TAP | 0.98779 | 0.91968 | -0.068113 |  | 0.95 | 1.05 | 0.047827 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | G16-111-TAP | 0.98779 | 0.91968 | -0.068113 |  | 0.95 | 1.05 | 0.047827 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | G16-111-TAP | 0.98779 | 0.91968 | -0.068113 |  | 0.95 | 1.05 | 0.070303 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | G16-111-TAP | 0.98779 | 0.91968 | -0.068113 |  | 0.95 | 1.05 | 0.040614 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | G16-111-TAP | 0.98779 | 0.91968 | -0.068113 |  | 0.95 | 1.05 | 0.039729 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | G16-111-TAP | 0.98779 | 0.91968 | -0.068113 |  | 0.95 | 1.05 | 0.049662 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | G16-111-TAP | 0.98779 | 0.91968 | -0.068113 |  | 0.95 | 1.05 | 0.042332 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | G16-111-TAP | 0.98779 | 0.91968 | -0.068113 |  | 0.95 | 1.05 | 0.048722 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | G16-111-TAP | 0.98779 | 0.91968 | -0.068113 |  | 0.95 | 1.05 | 0.038156 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | G16-111-TAP | 0.98779 | 0.91968 | -0.068113 |  | 0.95 | 1.05 | 0.036794 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | G16-111-TAP | 0.98746 | 0.92453 | -0.062929 |  | 0.95 | 1.05 | 0.075186 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | G16-111-TAP | 0.98746 | 0.92453 | -0.062929 |  | 0.95 | 1.05 | 0.031338 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | G16-111-TAP | 0.98746 | 0.92453 | -0.062929 |  | 0.95 | 1.05 | 0.031338 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | G16-111-TAP | 0.98746 | 0.92453 | -0.062929 |  | 0.95 | 1.05 | 0.031391 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | G16-111-TAP | 0.98746 | 0.92453 | -0.062929 |  | 0.95 | 1.05 | 0.034523 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | G16-111-TAP | 0.98635 | 0.92494 | -0.061419 |  | 0.95 | 1.05 | 0.06238 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | G16-111-TAP | 0.98873 | 0.91613 | -0.072602 |  | 0.95 | 1.05 | 0.040439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | G16-111-TAP | 0.98873 | 0.91613 | -0.072602 |  | 0.95 | 1.05 | 0.034853 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | G16-111-TAP | 0.98873 | 0.91613 | -0.072602 |  | 0.95 | 1.05 | 0.046783 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | G16-111-TAP | 0.98873 | 0.91613 | -0.072602 |  | 0.95 | 1.05 | 0.047615 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | G16-111-TAP | 0.98873 | 0.91613 | -0.072602 |  | 0.95 | 1.05 | 0.034938 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | G16-111-TAP | 0.98873 | 0.91613 | -0.072602 |  | 0.95 | 1.05 | 0.037875 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | G16-111-TAP | 0.98873 | 0.91613 | -0.072602 |  | 0.95 | 1.05 | 0.044022 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | G16-111-TAP | 0.98873 | 0.91613 | -0.072602 |  | 0.95 | 1.05 | 0.030552 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | G16-111-TAP | 0.98873 | 0.91613 | -0.072602 |  | 0.95 | 1.05 | 0.038531 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | G16-111-TAP | 0.98873 | 0.91613 | -0.072602 |  | 0.95 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | G16-111-TAP | 0.98873 | 0.91613 | -0.072602 |  | 0.95 | 1.05 | 0.062491 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | G16-111-TAP | 0.98873 | 0.91613 | -0.072602 |  | 0.95 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | G16-111-TAP | 0.98873 | 0.91613 | -0.072602 |  | 0.95 | 1.05 | 0.038129 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | G16-111-TAP | 0.98873 | 0.91613 | -0.072602 |  | 0.95 | 1.05 | 0.038066 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | G16-111-TAP | 0.98873 | 0.91613 | -0.072602 |  | 0.95 | 1.05 | 0.034955 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | G16-111-TAP | 0.98873 | 0.91613 | -0.072602 |  | 0.95 | 1.05 | 0.06281 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | G16-111-TAP | 0.98873 | 0.91613 | -0.072602 |  | 0.95 | 1.05 | 0.045309 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | G16-111-TAP | 0.98873 | 0.91613 | -0.072602 |  | 0.95 | 1.05 | 0.035805 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | G16-111-TAP | 0.98873 | 0.91613 | -0.072602 |  | 0.95 | 1.05 | 0.032364 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | G16-111-TAP | 0.98873 | 0.91613 | -0.072602 |  | 0.95 | 1.05 | 0.031815 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | G16-111-TAP | 0.98873 | 0.91613 | -0.072602 |  | 0.95 | 1.05 | 0.033886 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | G16-111-TAP | 0.98873 | 0.91613 | -0.072602 |  | 0.95 | 1.05 | 0.035554 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | G16-111-TAP | 0.973 | 0.87098 | -0.10202 |  | 0.95 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | G16-111-TAP | 0.973 | 0.87098 | -0.10202 |  | 0.95 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | G16-111-TAP | 0.973 | 0.87098 | -0.10202 |  | 0.95 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | G16-111-TAP | 0.973 | 0.87098 | -0.10202 |  | 0.95 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | G16-111-TAP | 0.973 | 0.87098 | -0.10202 |  | 0.95 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | G16-111-TAP | 0.973 | 0.87098 | -0.10202 |  | 0.95 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | G16-111-TAP | 0.973 | 0.87098 | -0.10202 |  | 0.95 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | G16-111-TAP | 0.973 | 0.87098 | -0.10202 |  | 0.95 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | G16-111-TAP | 0.973 | 0.87098 | -0.10202 |  | 0.95 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | G16-111-TAP | 0.973 | 0.87098 | -0.10202 |  | 0.95 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | G16-111-TAP | 0.973 | 0.87098 | -0.10202 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | G16-111-TAP | 0.973 | 0.87098 | -0.10202 |  | 0.95 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | G16-111-TAP | 0.973 | 0.87098 | -0.10202 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | G16-111-TAP | 0.973 | 0.87098 | -0.10202 |  | 0.95 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | G16-111-TAP | 0.973 | 0.87098 | -0.10202 |  | 0.95 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | G16-111-TAP | 0.973 | 0.87098 | -0.10202 |  | 0.95 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | G16-111-TAP | 0.973 | 0.87098 | -0.10202 |  | 0.95 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | G16-111-TAP | 0.973 | 0.87098 | -0.10202 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | G16-111-TAP | 0.973 | 0.87098 | -0.10202 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | G16-111-TAP | 0.973 | 0.87098 | -0.10202 |  | 0.95 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | G16-111-TAP | 0.973 | 0.87098 | -0.10202 |  | 0.95 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | G16-111-TAP | 0.973 | 0.87098 | -0.10202 |  | 0.95 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | G16-111-TAP | 0.973 | 0.87098 | -0.10202 |  | 0.95 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | G16-111-TAP | 0.973 | 0.87098 | -0.10202 |  | 0.95 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | G16-111-TAP | 0.973 | 0.87098 | -0.10202 |  | 0.95 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | G17-108-TAP | 0.99286 | 0.91474 | -0.078112 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | G17-108-TAP | 0.99286 | 0.91474 | -0.078112 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | G17-108-TAP | 0.99286 | 0.91474 | -0.078112 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | G17-108-TAP | 0.99286 | 0.91474 | -0.078112 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | G17-108-TAP | 0.99286 | 0.91474 | -0.078112 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | G17-108-TAP | 0.99286 | 0.91474 | -0.078112 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | G17-108-TAP | 0.99286 | 0.91474 | -0.078112 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | G17-108-TAP | 0.99286 | 0.91474 | -0.078112 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | G17-108-TAP | 0.99286 | 0.91474 | -0.078112 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | G17-108-TAP | 0.99286 | 0.91474 | -0.078112 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | G17-108-TAP | 0.99286 | 0.91474 | -0.078112 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | G17-108-TAP | 0.99286 | 0.91474 | -0.078112 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | G17-108-TAP | 0.99286 | 0.91474 | -0.078112 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | G17-108-TAP | 0.99286 | 0.91474 | -0.078112 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | G17-108-TAP | 0.99286 | 0.91474 | -0.078112 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | G17-108-TAP | 0.99286 | 0.91474 | -0.078112 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | G17-108-TAP | 0.99286 | 0.91474 | -0.078112 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | G17-108-TAP | 0.99286 | 0.91474 | -0.078112 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | G17-108-TAP | 0.99286 | 0.91474 | -0.078112 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | G17-108-TAP | 0.99286 | 0.91474 | -0.078112 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | G17-108-TAP | 0.99286 | 0.91474 | -0.078112 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | G17-108-TAP | 0.99286 | 0.91474 | -0.078112 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | G17-108-TAP | 0.99286 | 0.91474 | -0.078112 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | G17-108-TAP | 0.99286 | 0.91474 | -0.078112 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | G17-108-TAP | 0.99286 | 0.91474 | -0.078112 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | G18-128-TAP | 0.97975 | 0.89202 | -0.087736 |  | 0.95 | 1.05 | 0.091967 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | G18-128-TAP | 0.97975 | 0.89202 | -0.087736 |  | 0.95 | 1.05 | 0.033356 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | G18-128-TAP | 0.97975 | 0.89202 | -0.087736 |  | 0.95 | 1.05 | 0.044346 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | G18-128-TAP | 0.97975 | 0.89202 | -0.087736 |  | 0.95 | 1.05 | 0.058536 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | G18-128-TAP | 0.97975 | 0.89202 | -0.087736 |  | 0.95 | 1.05 | 0.059327 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | G18-128-TAP | 0.97975 | 0.89202 | -0.087736 |  | 0.95 | 1.05 | 0.041874 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | G18-128-TAP | 0.97975 | 0.89202 | -0.087736 |  | 0.95 | 1.05 | 0.046192 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | G18-128-TAP | 0.97975 | 0.89202 | -0.087736 |  | 0.95 | 1.05 | 0.12754 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | G18-128-TAP | 0.97975 | 0.89202 | -0.087736 |  | 0.95 | 1.05 | 0.047018 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | G18-128-TAP | 0.97975 | 0.89202 | -0.087736 |  | 0.95 | 1.05 | 0.056662 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | G18-128-TAP | 0.97975 | 0.89202 | -0.087736 |  | 0.95 | 1.05 | 0.056662 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | G18-128-TAP | 0.97975 | 0.89202 | -0.087736 |  | 0.95 | 1.05 | 0.056727 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | G18-128-TAP | 0.97975 | 0.89202 | -0.087736 |  | 0.95 | 1.05 | 0.074186 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | G18-128-TAP | 0.97975 | 0.89202 | -0.087736 |  | 0.95 | 1.05 | 0.040839 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | G18-128-TAP | 0.97975 | 0.89202 | -0.087736 |  | 0.95 | 1.05 | 0.03863 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | G18-128-TAP | 0.97975 | 0.89202 | -0.087736 |  | 0.95 | 1.05 | 0.042285 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | G18-128-TAP | 0.97975 | 0.89202 | -0.087736 |  | 0.95 | 1.05 | 0.042285 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | G18-128-TAP | 0.97975 | 0.89202 | -0.087736 |  | 0.95 | 1.05 | 0.050204 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | G18-128-TAP | 0.97975 | 0.89202 | -0.087736 |  | 0.95 | 1.05 | 0.058005 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | G18-128-TAP | 0.97975 | 0.89202 | -0.087736 |  | 0.95 | 1.05 | 0.041735 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | G18-128-TAP | 0.97975 | 0.89202 | -0.087736 |  | 0.95 | 1.05 | 0.057076 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | G18-128-TAP | 0.97975 | 0.89202 | -0.087736 |  | 0.95 | 1.05 | 0.050111 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | G18-128-TAP | 0.97975 | 0.89202 | -0.087736 |  | 0.95 | 1.05 | 0.06491 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | G18-128-TAP | 0.97975 | 0.89202 | -0.087736 |  | 0.95 | 1.05 | 0.051051 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | G18-128-TAP | 0.97975 | 0.89202 | -0.087736 |  | 0.95 | 1.05 | 0.036279 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | G18-128-TAP | 0.98592 | 0.91976 | -0.066153 |  | 0.95 | 1.05 | 0.091967 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | G18-128-TAP | 0.98592 | 0.91976 | -0.066153 |  | 0.95 | 1.05 | 0.033356 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | G18-128-TAP | 0.98592 | 0.91976 | -0.066153 |  | 0.95 | 1.05 | 0.044346 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | G18-128-TAP | 0.98592 | 0.91976 | -0.066153 |  | 0.95 | 1.05 | 0.058536 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | G18-128-TAP | 0.98592 | 0.91976 | -0.066153 |  | 0.95 | 1.05 | 0.059327 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | G18-128-TAP | 0.98592 | 0.91976 | -0.066153 |  | 0.95 | 1.05 | 0.041874 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | G18-128-TAP | 0.98592 | 0.91976 | -0.066153 |  | 0.95 | 1.05 | 0.046192 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | G18-128-TAP | 0.98592 | 0.91976 | -0.066153 |  | 0.95 | 1.05 | 0.12754 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | G18-128-TAP | 0.98592 | 0.91976 | -0.066153 |  | 0.95 | 1.05 | 0.047018 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | G18-128-TAP | 0.98592 | 0.91976 | -0.066153 |  | 0.95 | 1.05 | 0.056662 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | G18-128-TAP | 0.98592 | 0.91976 | -0.066153 |  | 0.95 | 1.05 | 0.056662 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | G18-128-TAP | 0.98592 | 0.91976 | -0.066153 |  | 0.95 | 1.05 | 0.056727 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | G18-128-TAP | 0.98592 | 0.91976 | -0.066153 |  | 0.95 | 1.05 | 0.074186 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | G18-128-TAP | 0.98592 | 0.91976 | -0.066153 |  | 0.95 | 1.05 | 0.040839 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | G18-128-TAP | 0.98592 | 0.91976 | -0.066153 |  | 0.95 | 1.05 | 0.03863 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | G18-128-TAP | 0.98592 | 0.91976 | -0.066153 |  | 0.95 | 1.05 | 0.042285 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | G18-128-TAP | 0.98592 | 0.91976 | -0.066153 |  | 0.95 | 1.05 | 0.042285 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | G18-128-TAP | 0.98592 | 0.91976 | -0.066153 |  | 0.95 | 1.05 | 0.050204 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | G18-128-TAP | 0.98592 | 0.91976 | -0.066153 |  | 0.95 | 1.05 | 0.058005 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | G18-128-TAP | 0.98592 | 0.91976 | -0.066153 |  | 0.95 | 1.05 | 0.041735 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | G18-128-TAP | 0.98592 | 0.91976 | -0.066153 |  | 0.95 | 1.05 | 0.057076 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | G18-128-TAP | 0.98592 | 0.91976 | -0.066153 |  | 0.95 | 1.05 | 0.050111 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | G18-128-TAP | 0.98592 | 0.91976 | -0.066153 |  | 0.95 | 1.05 | 0.06491 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | G18-128-TAP | 0.98592 | 0.91976 | -0.066153 |  | 0.95 | 1.05 | 0.051051 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | G18-128-TAP | 0.98592 | 0.91976 | -0.066153 |  | 0.95 | 1.05 | 0.036279 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | G18-128-TAP | 0.98906 | 0.93054 | -0.05852 |  | 0.95 | 1.05 | 0.091967 | P42:345:OKGE:SB_OPKY7308:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | G18-128-TAP | 0.98906 | 0.93054 | -0.05852 |  | 0.95 | 1.05 | 0.033356 | P42:345:OKGE:SB_OPKY7308:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | G18-128-TAP | 0.98906 | 0.93054 | -0.05852 |  | 0.95 | 1.05 | 0.044346 | P42:345:OKGE:SB_OPKY7308:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | G18-128-TAP | 0.98906 | 0.93054 | -0.05852 |  | 0.95 | 1.05 | 0.058536 | P42:345:OKGE:SB_OPKY7308:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | G18-128-TAP | 0.98906 | 0.93054 | -0.05852 |  | 0.95 | 1.05 | 0.059327 | P42:345:OKGE:SB_OPKY7308:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | G18-128-TAP | 0.98906 | 0.93054 | -0.05852 |  | 0.95 | 1.05 | 0.041874 | P42:345:OKGE:SB_OPKY7308:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | G18-128-TAP | 0.98906 | 0.93054 | -0.05852 |  | 0.95 | 1.05 | 0.046192 | P42:345:OKGE:SB_OPKY7308:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | G18-128-TAP | 0.98906 | 0.93054 | -0.05852 |  | 0.95 | 1.05 | 0.12754 | P42:345:OKGE:SB_OPKY7308:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | G18-128-TAP | 0.98906 | 0.93054 | -0.05852 |  | 0.95 | 1.05 | 0.047018 | P42:345:OKGE:SB_OPKY7308:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | G18-128-TAP | 0.98906 | 0.93054 | -0.05852 |  | 0.95 | 1.05 | 0.056662 | P42:345:OKGE:SB_OPKY7308:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | G18-128-TAP | 0.98906 | 0.93054 | -0.05852 |  | 0.95 | 1.05 | 0.056662 | P42:345:OKGE:SB_OPKY7308:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | G18-128-TAP | 0.98906 | 0.93054 | -0.05852 |  | 0.95 | 1.05 | 0.056727 | P42:345:OKGE:SB_OPKY7308:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | G18-128-TAP | 0.98906 | 0.93054 | -0.05852 |  | 0.95 | 1.05 | 0.074186 | P42:345:OKGE:SB_OPKY7308:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | G18-128-TAP | 0.98906 | 0.93054 | -0.05852 |  | 0.95 | 1.05 | 0.040839 | P42:345:OKGE:SB_OPKY7308:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | G18-128-TAP | 0.98906 | 0.93054 | -0.05852 |  | 0.95 | 1.05 | 0.03863 | P42:345:OKGE:SB_OPKY7308:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | G18-128-TAP | 0.98906 | 0.93054 | -0.05852 |  | 0.95 | 1.05 | 0.042285 | P42:345:OKGE:SB_OPKY7308:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | G18-128-TAP | 0.98906 | 0.93054 | -0.05852 |  | 0.95 | 1.05 | 0.042285 | P42:345:OKGE:SB_OPKY7308:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | G18-128-TAP | 0.98906 | 0.93054 | -0.05852 |  | 0.95 | 1.05 | 0.050204 | P42:345:OKGE:SB_OPKY7308:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | G18-128-TAP | 0.98906 | 0.93054 | -0.05852 |  | 0.95 | 1.05 | 0.058005 | P42:345:OKGE:SB_OPKY7308:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | G18-128-TAP | 0.98906 | 0.93054 | -0.05852 |  | 0.95 | 1.05 | 0.041735 | P42:345:OKGE:SB_OPKY7308:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | G18-128-TAP | 0.98906 | 0.93054 | -0.05852 |  | 0.95 | 1.05 | 0.057076 | P42:345:OKGE:SB_OPKY7308:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | G18-128-TAP | 0.98906 | 0.93054 | -0.05852 |  | 0.95 | 1.05 | 0.050111 | P42:345:OKGE:SB_OPKY7308:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | G18-128-TAP | 0.98906 | 0.93054 | -0.05852 |  | 0.95 | 1.05 | 0.06491 | P42:345:OKGE:SB_OPKY7308:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | G18-128-TAP | 0.98906 | 0.93054 | -0.05852 |  | 0.95 | 1.05 | 0.051051 | P42:345:OKGE:SB_OPKY7308:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | G18-128-TAP | 0.98906 | 0.93054 | -0.05852 |  | 0.95 | 1.05 | 0.036279 | P42:345:OKGE:SB_OPKY7308:::EHV: | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | G18-128-TAP | 0.98638 | 0.88757 | -0.098805 |  | 0.95 | 1.05 | 0.035768 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | G18-128-TAP | 0.98638 | 0.88757 | -0.098805 |  | 0.95 | 1.05 | 0.088718 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | G18-128-TAP | 0.98638 | 0.88757 | -0.098805 |  | 0.95 | 1.05 | 0.031473 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | G18-128-TAP | 0.98638 | 0.88757 | -0.098805 |  | 0.95 | 1.05 | 0.034941 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | G18-128-TAP | 0.98638 | 0.88757 | -0.098805 |  | 0.95 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | G18-128-TAP | 0.98638 | 0.88757 | -0.098805 |  | 0.95 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | G18-128-TAP | 0.98638 | 0.88757 | -0.098805 |  | 0.95 | 1.05 | 0.049224 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | G18-128-TAP | 0.98638 | 0.88757 | -0.098805 |  | 0.95 | 1.05 | 0.038981 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | G18-128-TAP | 0.98638 | 0.88757 | -0.098805 |  | 0.95 | 1.05 | 0.040399 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | G18-128-TAP | 0.98638 | 0.88757 | -0.098805 |  | 0.95 | 1.05 | 0.031912 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | G18-128-TAP | 0.98638 | 0.88757 | -0.098805 |  | 0.95 | 1.05 | 0.034127 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | G18-128-TAP | 0.98638 | 0.88757 | -0.098805 |  | 0.95 | 1.05 | 0.047318 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | G18-128-TAP | 0.9955 | 0.91953 | -0.075974 |  | 0.95 | 1.05 | 0.040439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | G18-128-TAP | 0.9955 | 0.91953 | -0.075974 |  | 0.95 | 1.05 | 0.034853 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | G18-128-TAP | 0.9955 | 0.91953 | -0.075974 |  | 0.95 | 1.05 | 0.046783 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | G18-128-TAP | 0.9955 | 0.91953 | -0.075974 |  | 0.95 | 1.05 | 0.047615 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | G18-128-TAP | 0.9955 | 0.91953 | -0.075974 |  | 0.95 | 1.05 | 0.034938 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | G18-128-TAP | 0.9955 | 0.91953 | -0.075974 |  | 0.95 | 1.05 | 0.037875 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | G18-128-TAP | 0.9955 | 0.91953 | -0.075974 |  | 0.95 | 1.05 | 0.044022 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | G18-128-TAP | 0.9955 | 0.91953 | -0.075974 |  | 0.95 | 1.05 | 0.030552 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | G18-128-TAP | 0.9955 | 0.91953 | -0.075974 |  | 0.95 | 1.05 | 0.038531 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | G18-128-TAP | 0.9955 | 0.91953 | -0.075974 |  | 0.95 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | G18-128-TAP | 0.9955 | 0.91953 | -0.075974 |  | 0.95 | 1.05 | 0.062491 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | G18-128-TAP | 0.9955 | 0.91953 | -0.075974 |  | 0.95 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | G18-128-TAP | 0.9955 | 0.91953 | -0.075974 |  | 0.95 | 1.05 | 0.038129 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | G18-128-TAP | 0.9955 | 0.91953 | -0.075974 |  | 0.95 | 1.05 | 0.038066 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | G18-128-TAP | 0.9955 | 0.91953 | -0.075974 |  | 0.95 | 1.05 | 0.034955 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | G18-128-TAP | 0.9955 | 0.91953 | -0.075974 |  | 0.95 | 1.05 | 0.06281 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | G18-128-TAP | 0.9955 | 0.91953 | -0.075974 |  | 0.95 | 1.05 | 0.045309 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | G18-128-TAP | 0.9955 | 0.91953 | -0.075974 |  | 0.95 | 1.05 | 0.035805 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | G18-128-TAP | 0.9955 | 0.91953 | -0.075974 |  | 0.95 | 1.05 | 0.032364 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | G18-128-TAP | 0.9955 | 0.91953 | -0.075974 |  | 0.95 | 1.05 | 0.031815 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | G18-128-TAP | 0.9955 | 0.91953 | -0.075974 |  | 0.95 | 1.05 | 0.033886 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | G18-128-TAP | 0.9955 | 0.91953 | -0.075974 |  | 0.95 | 1.05 | 0.035554 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | G20-007-TAP | 0.99483 | 0.93043 | -0.064397 |  | 0.95 | 1.05 | 0.03053 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | G20-007-TAP | 0.99483 | 0.93043 | -0.064397 |  | 0.95 | 1.05 | 0.044933 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | G20-007-TAP | 0.99483 | 0.93043 | -0.064397 |  | 0.95 | 1.05 | 0.047811 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | G20-007-TAP | 0.99483 | 0.93043 | -0.064397 |  | 0.95 | 1.05 | 0.09719 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | G20-007-TAP | 0.99483 | 0.93043 | -0.064397 |  | 0.95 | 1.05 | 0.069376 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | G20-007-TAP | 0.99483 | 0.93043 | -0.064397 |  | 0.95 | 1.05 | 0.04277 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | G20-007-TAP | 0.99483 | 0.93043 | -0.064397 |  | 0.95 | 1.05 | 0.071112 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | G20-007-TAP | 0.99483 | 0.93043 | -0.064397 |  | 0.95 | 1.05 | 0.039357 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | G20-007-TAP | 0.99483 | 0.93043 | -0.064397 |  | 0.95 | 1.05 | 0.04035 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | G20-007-TAP | 0.99483 | 0.93043 | -0.064397 |  | 0.95 | 1.05 | 0.052332 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | G20-007-TAP | 0.99483 | 0.93043 | -0.064397 |  | 0.95 | 1.05 | 0.045944 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | G20-007-TAP | 0.99483 | 0.93043 | -0.064397 |  | 0.95 | 1.05 | 0.038178 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | G20-007-TAP | 0.99483 | 0.93043 | -0.064397 |  | 0.95 | 1.05 | 0.13469 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | G20-007-TAP | 0.99483 | 0.93043 | -0.064397 |  | 0.95 | 1.05 | 0.03053 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | G20-007-TAP | 0.99483 | 0.93043 | -0.064397 |  | 0.95 | 1.05 | 0.038178 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | G20-007-TAP | 0.99483 | 0.93043 | -0.064397 |  | 0.95 | 1.05 | 0.037309 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | G20-007-TAP | 0.99483 | 0.93043 | -0.064397 |  | 0.95 | 1.05 | 0.040075 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | G20-007-TAP | 0.99483 | 0.93043 | -0.064397 |  | 0.95 | 1.05 | 0.053764 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | G20-007-TAP | 0.99483 | 0.93043 | -0.064397 |  | 0.95 | 1.05 | 0.071762 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | G20-007-TAP | 0.99483 | 0.93043 | -0.064397 |  | 0.95 | 1.05 | 0.047827 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | G20-007-TAP | 0.99483 | 0.93043 | -0.064397 |  | 0.95 | 1.05 | 0.047827 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | G20-007-TAP | 0.99483 | 0.93043 | -0.064397 |  | 0.95 | 1.05 | 0.070303 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | G20-007-TAP | 0.99483 | 0.93043 | -0.064397 |  | 0.95 | 1.05 | 0.040614 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | G20-007-TAP | 0.99483 | 0.93043 | -0.064397 |  | 0.95 | 1.05 | 0.039729 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | G20-007-TAP | 0.99483 | 0.93043 | -0.064397 |  | 0.95 | 1.05 | 0.049662 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | G20-007-TAP | 0.99483 | 0.93043 | -0.064397 |  | 0.95 | 1.05 | 0.042332 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | G20-007-TAP | 0.99483 | 0.93043 | -0.064397 |  | 0.95 | 1.05 | 0.048722 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | G20-007-TAP | 0.99483 | 0.93043 | -0.064397 |  | 0.95 | 1.05 | 0.038156 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | G20-007-TAP | 0.99483 | 0.93043 | -0.064397 |  | 0.95 | 1.05 | 0.036794 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | G20-007-TAP | 1.0051 | 0.93496 | -0.070136 |  | 0.95 | 1.05 | 0.036307 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | G20-007-TAP | 1.0051 | 0.93496 | -0.070136 |  | 0.95 | 1.05 | 0.052743 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | G20-007-TAP | 1.0051 | 0.93496 | -0.070136 |  | 0.95 | 1.05 | 0.039345 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | G20-007-TAP | 1.0051 | 0.93496 | -0.070136 |  | 0.95 | 1.05 | 0.031366 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | G20-007-TAP | 1.0051 | 0.93496 | -0.070136 |  | 0.95 | 1.05 | 0.041888 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | G20-007-TAP | 1.0051 | 0.93496 | -0.070136 |  | 0.95 | 1.05 | 0.038797 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | G20-007-TAP | 1.0051 | 0.93496 | -0.070136 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | G20-007-TAP | 1.0051 | 0.93496 | -0.070136 |  | 0.95 | 1.05 | 0.067346 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | G20-007-TAP | 1.0051 | 0.93496 | -0.070136 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | G20-007-TAP | 1.0051 | 0.93496 | -0.070136 |  | 0.95 | 1.05 | 0.030851 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | G20-007-TAP | 1.0051 | 0.93496 | -0.070136 |  | 0.95 | 1.05 | 0.032161 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | G20-007-TAP | 1.0051 | 0.93496 | -0.070136 |  | 0.95 | 1.05 | 0.04067 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | G20-007-TAP | 1.0051 | 0.93496 | -0.070136 |  | 0.95 | 1.05 | 0.040569 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | G20-007-TAP | 1.0051 | 0.93496 | -0.070136 |  | 0.95 | 1.05 | 0.03086 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | G20-007-TAP | 1.0051 | 0.93496 | -0.070136 |  | 0.95 | 1.05 | 0.033223 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | G20-007-TAP | 1.0051 | 0.93496 | -0.070136 |  | 0.95 | 1.05 | 0.033733 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | G20-007-TAP | 1.0026 | 0.8826 | -0.12001 |  | 0.95 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | G20-007-TAP | 1.0026 | 0.8826 | -0.12001 |  | 0.95 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | G20-007-TAP | 1.0026 | 0.8826 | -0.12001 |  | 0.95 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | G20-007-TAP | 1.0026 | 0.8826 | -0.12001 |  | 0.95 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | G20-007-TAP | 1.0026 | 0.8826 | -0.12001 |  | 0.95 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | G20-007-TAP | 1.0026 | 0.8826 | -0.12001 |  | 0.95 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | G20-007-TAP | 1.0026 | 0.8826 | -0.12001 |  | 0.95 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | G20-007-TAP | 1.0026 | 0.8826 | -0.12001 |  | 0.95 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | G20-007-TAP | 1.0026 | 0.8826 | -0.12001 |  | 0.95 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | G20-007-TAP | 1.0026 | 0.8826 | -0.12001 |  | 0.95 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | G20-007-TAP | 1.0026 | 0.8826 | -0.12001 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | G20-007-TAP | 1.0026 | 0.8826 | -0.12001 |  | 0.95 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | G20-007-TAP | 1.0026 | 0.8826 | -0.12001 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | G20-007-TAP | 1.0026 | 0.8826 | -0.12001 |  | 0.95 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | G20-007-TAP | 1.0026 | 0.8826 | -0.12001 |  | 0.95 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | G20-007-TAP | 1.0026 | 0.8826 | -0.12001 |  | 0.95 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | G20-007-TAP | 1.0026 | 0.8826 | -0.12001 |  | 0.95 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | G20-007-TAP | 1.0026 | 0.8826 | -0.12001 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | G20-007-TAP | 1.0026 | 0.8826 | -0.12001 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | G20-007-TAP | 1.0026 | 0.8826 | -0.12001 |  | 0.95 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | G20-007-TAP | 1.0026 | 0.8826 | -0.12001 |  | 0.95 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | G20-007-TAP | 1.0026 | 0.8826 | -0.12001 |  | 0.95 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | G20-007-TAP | 1.0026 | 0.8826 | -0.12001 |  | 0.95 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | G20-007-TAP | 1.0026 | 0.8826 | -0.12001 |  | 0.95 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | G20-007-TAP | 1.0026 | 0.8826 | -0.12001 |  | 0.95 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | G20-072-TAP | 0.99362 | 0.92593 | -0.067687 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | G20-072-TAP | 0.99362 | 0.92593 | -0.067687 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | G20-072-TAP | 0.99362 | 0.92593 | -0.067687 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | G20-072-TAP | 0.99362 | 0.92593 | -0.067687 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | G20-072-TAP | 0.99362 | 0.92593 | -0.067687 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | G20-072-TAP | 0.99362 | 0.92593 | -0.067687 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | G20-072-TAP | 0.99362 | 0.92593 | -0.067687 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | G20-072-TAP | 0.99362 | 0.92593 | -0.067687 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | G20-072-TAP | 0.99362 | 0.92593 | -0.067687 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | G20-072-TAP | 0.99362 | 0.92593 | -0.067687 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | G20-072-TAP | 0.99362 | 0.92593 | -0.067687 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | G20-072-TAP | 0.99362 | 0.92593 | -0.067687 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | G20-072-TAP | 0.99362 | 0.92593 | -0.067687 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | G20-072-TAP | 0.99362 | 0.92593 | -0.067687 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | G20-072-TAP | 0.99362 | 0.92593 | -0.067687 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | G20-072-TAP | 0.99362 | 0.92593 | -0.067687 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | G20-072-TAP | 0.99362 | 0.92593 | -0.067687 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | G20-072-TAP | 0.99362 | 0.92593 | -0.067687 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | G20-072-TAP | 0.99362 | 0.92593 | -0.067687 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | G20-072-TAP | 0.99362 | 0.92593 | -0.067687 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | G20-072-TAP | 0.99362 | 0.92593 | -0.067687 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | G20-072-TAP | 0.99362 | 0.92593 | -0.067687 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | G20-072-TAP | 0.99362 | 0.92593 | -0.067687 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | G20-072-TAP | 0.99362 | 0.92593 | -0.067687 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | G20-072-TAP | 0.99362 | 0.92593 | -0.067687 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | G20-073-TAP | 1.0074 | 0.91747 | -0.089885 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | G20-073-TAP | 1.0074 | 0.91747 | -0.089885 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | G20-073-TAP | 1.0074 | 0.91747 | -0.089885 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | G20-073-TAP | 1.0074 | 0.91747 | -0.089885 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | G20-073-TAP | 1.0074 | 0.91747 | -0.089885 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | G20-073-TAP | 1.0074 | 0.91747 | -0.089885 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | G20-073-TAP | 1.0074 | 0.91747 | -0.089885 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | G20-073-TAP | 1.0074 | 0.91747 | -0.089885 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | G20-073-TAP | 1.0074 | 0.91747 | -0.089885 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | G20-073-TAP | 1.0074 | 0.91747 | -0.089885 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | G20-073-TAP | 1.0074 | 0.91747 | -0.089885 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | G20-073-TAP | 1.0074 | 0.91747 | -0.089885 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | G20-073-TAP | 1.0074 | 0.91747 | -0.089885 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | G20-073-TAP | 1.0074 | 0.91747 | -0.089885 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | G20-073-TAP | 1.0074 | 0.91747 | -0.089885 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | G20-073-TAP | 1.0074 | 0.91747 | -0.089885 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | G20-073-TAP | 1.0074 | 0.91747 | -0.089885 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | G20-073-TAP | 1.0074 | 0.91747 | -0.089885 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | G20-073-TAP | 1.0074 | 0.91747 | -0.089885 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | G20-073-TAP | 1.0074 | 0.91747 | -0.089885 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | G20-073-TAP | 1.0074 | 0.91747 | -0.089885 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | G20-073-TAP | 1.0074 | 0.91747 | -0.089885 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | G20-073-TAP | 1.0074 | 0.91747 | -0.089885 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | G20-073-TAP | 1.0074 | 0.91747 | -0.089885 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | G20-073-TAP | 1.0074 | 0.91747 | -0.089885 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | G20-092-TAP | 0.93719 | 0.91176 | -0.025429 |  | 0.92 | 1.05 | 0.038424 | Single 509752 INOLATP4 138 509790 CATOOSA4 138 1 | Add 57 MVAR switched shunt at GUAVA 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | G21-029-TAP | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.03053 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | G21-029-TAP | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.044933 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | G21-029-TAP | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.047811 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | G21-029-TAP | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.09719 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | G21-029-TAP | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.069376 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | G21-029-TAP | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.04277 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | G21-029-TAP | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.071112 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | G21-029-TAP | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.039357 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | G21-029-TAP | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.04035 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | G21-029-TAP | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.052332 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | G21-029-TAP | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.045944 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | G21-029-TAP | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.038178 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | G21-029-TAP | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.13469 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | G21-029-TAP | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.03053 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | G21-029-TAP | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.038178 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | G21-029-TAP | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.037309 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | G21-029-TAP | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.040075 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | G21-029-TAP | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.053764 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | G21-029-TAP | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.071762 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | G21-029-TAP | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.047827 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | G21-029-TAP | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.047827 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | G21-029-TAP | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.070303 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | G21-029-TAP | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.040614 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | G21-029-TAP | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.039729 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | G21-029-TAP | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.049662 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | G21-029-TAP | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.042332 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | G21-029-TAP | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.048722 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | G21-029-TAP | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.038156 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | G21-029-TAP | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.036794 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | G21-029-TAP | 0.96836 | 0.92888 | -0.039481 |  | 0.95 | 1.05 | 0.036307 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | G21-029-TAP | 0.96836 | 0.92888 | -0.039481 |  | 0.95 | 1.05 | 0.052743 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | G21-029-TAP | 0.96836 | 0.92888 | -0.039481 |  | 0.95 | 1.05 | 0.039345 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | G21-029-TAP | 0.96836 | 0.92888 | -0.039481 |  | 0.95 | 1.05 | 0.031366 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | G21-029-TAP | 0.96836 | 0.92888 | -0.039481 |  | 0.95 | 1.05 | 0.041888 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | G21-029-TAP | 0.96836 | 0.92888 | -0.039481 |  | 0.95 | 1.05 | 0.038797 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | G21-029-TAP | 0.96836 | 0.92888 | -0.039481 |  | 0.95 | 1.05 | 0.030557 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | G21-029-TAP | 0.96836 | 0.92888 | -0.039481 |  | 0.95 | 1.05 | 0.067346 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | G21-029-TAP | 0.96836 | 0.92888 | -0.039481 |  | 0.95 | 1.05 | 0.030557 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | G21-029-TAP | 0.96836 | 0.92888 | -0.039481 |  | 0.95 | 1.05 | 0.030851 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | G21-029-TAP | 0.96836 | 0.92888 | -0.039481 |  | 0.95 | 1.05 | 0.032161 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | G21-029-TAP | 0.96836 | 0.92888 | -0.039481 |  | 0.95 | 1.05 | 0.04067 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | G21-029-TAP | 0.96836 | 0.92888 | -0.039481 |  | 0.95 | 1.05 | 0.040569 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | G21-029-TAP | 0.96836 | 0.92888 | -0.039481 |  | 0.95 | 1.05 | 0.03086 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | G21-029-TAP | 0.96836 | 0.92888 | -0.039481 |  | 0.95 | 1.05 | 0.033223 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | G21-029-TAP | 0.96836 | 0.92888 | -0.039481 |  | 0.95 | 1.05 | 0.033733 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | G21-029-TAP | 0.97297 | 0.91992 | -0.053049 |  | 0.95 | 1.05 | 0.036307 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | G21-029-TAP | 0.97297 | 0.91992 | -0.053049 |  | 0.95 | 1.05 | 0.052743 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | G21-029-TAP | 0.97297 | 0.91992 | -0.053049 |  | 0.95 | 1.05 | 0.039345 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | G21-029-TAP | 0.97297 | 0.91992 | -0.053049 |  | 0.95 | 1.05 | 0.031366 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | G21-029-TAP | 0.97297 | 0.91992 | -0.053049 |  | 0.95 | 1.05 | 0.041888 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | G21-029-TAP | 0.97297 | 0.91992 | -0.053049 |  | 0.95 | 1.05 | 0.038797 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | G21-029-TAP | 0.97297 | 0.91992 | -0.053049 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | G21-029-TAP | 0.97297 | 0.91992 | -0.053049 |  | 0.95 | 1.05 | 0.067346 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | G21-029-TAP | 0.97297 | 0.91992 | -0.053049 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | G21-029-TAP | 0.97297 | 0.91992 | -0.053049 |  | 0.95 | 1.05 | 0.030851 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | G21-029-TAP | 0.97297 | 0.91992 | -0.053049 |  | 0.95 | 1.05 | 0.032161 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | G21-029-TAP | 0.97297 | 0.91992 | -0.053049 |  | 0.95 | 1.05 | 0.04067 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | G21-029-TAP | 0.97297 | 0.91992 | -0.053049 |  | 0.95 | 1.05 | 0.040569 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | G21-029-TAP | 0.97297 | 0.91992 | -0.053049 |  | 0.95 | 1.05 | 0.03086 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | G21-029-TAP | 0.97297 | 0.91992 | -0.053049 |  | 0.95 | 1.05 | 0.033223 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | G21-029-TAP | 0.97297 | 0.91992 | -0.053049 |  | 0.95 | 1.05 | 0.033733 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | G21-029-TAP | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | G21-029-TAP | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | G21-029-TAP | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | G21-029-TAP | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | G21-029-TAP | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | G21-029-TAP | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | G21-029-TAP | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | G21-029-TAP | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | G21-029-TAP | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | G21-029-TAP | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | G21-029-TAP | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | G21-029-TAP | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | G21-029-TAP | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | G21-029-TAP | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | G21-029-TAP | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | G21-029-TAP | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | G21-029-TAP | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | G21-029-TAP | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | G21-029-TAP | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | G21-029-TAP | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | G21-029-TAP | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | G21-029-TAP | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | G21-029-TAP | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | G21-029-TAP | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | G21-029-TAP | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | G21-096-TAP | 0.99739 | 0.92248 | -0.074906 |  | 0.95 | 1.05 | 0.040439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | G21-096-TAP | 0.99739 | 0.92248 | -0.074906 |  | 0.95 | 1.05 | 0.034853 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | G21-096-TAP | 0.99739 | 0.92248 | -0.074906 |  | 0.95 | 1.05 | 0.046783 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | G21-096-TAP | 0.99739 | 0.92248 | -0.074906 |  | 0.95 | 1.05 | 0.047615 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | G21-096-TAP | 0.99739 | 0.92248 | -0.074906 |  | 0.95 | 1.05 | 0.034938 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | G21-096-TAP | 0.99739 | 0.92248 | -0.074906 |  | 0.95 | 1.05 | 0.037875 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | G21-096-TAP | 0.99739 | 0.92248 | -0.074906 |  | 0.95 | 1.05 | 0.044022 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | G21-096-TAP | 0.99739 | 0.92248 | -0.074906 |  | 0.95 | 1.05 | 0.030552 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | G21-096-TAP | 0.99739 | 0.92248 | -0.074906 |  | 0.95 | 1.05 | 0.038531 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | G21-096-TAP | 0.99739 | 0.92248 | -0.074906 |  | 0.95 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | G21-096-TAP | 0.99739 | 0.92248 | -0.074906 |  | 0.95 | 1.05 | 0.062491 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | G21-096-TAP | 0.99739 | 0.92248 | -0.074906 |  | 0.95 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | G21-096-TAP | 0.99739 | 0.92248 | -0.074906 |  | 0.95 | 1.05 | 0.038129 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | G21-096-TAP | 0.99739 | 0.92248 | -0.074906 |  | 0.95 | 1.05 | 0.038066 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | G21-096-TAP | 0.99739 | 0.92248 | -0.074906 |  | 0.95 | 1.05 | 0.034955 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | G21-096-TAP | 0.99739 | 0.92248 | -0.074906 |  | 0.95 | 1.05 | 0.06281 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | G21-096-TAP | 0.99739 | 0.92248 | -0.074906 |  | 0.95 | 1.05 | 0.045309 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | G21-096-TAP | 0.99739 | 0.92248 | -0.074906 |  | 0.95 | 1.05 | 0.035805 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | G21-096-TAP | 0.99739 | 0.92248 | -0.074906 |  | 0.95 | 1.05 | 0.032364 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | G21-096-TAP | 0.99739 | 0.92248 | -0.074906 |  | 0.95 | 1.05 | 0.031815 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | G21-096-TAP | 0.99739 | 0.92248 | -0.074906 |  | 0.95 | 1.05 | 0.033886 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | G21-096-TAP | 0.99739 | 0.92248 | -0.074906 |  | 0.95 | 1.05 | 0.035554 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | G22-007-TAP | 0.96384 | 0.86895 | -0.094885 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | G22-007-TAP | 0.96384 | 0.86895 | -0.094885 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | G22-007-TAP | 0.96384 | 0.86895 | -0.094885 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | G22-007-TAP | 0.96384 | 0.86895 | -0.094885 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | G22-007-TAP | 0.96384 | 0.86895 | -0.094885 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | G22-007-TAP | 0.96384 | 0.86895 | -0.094885 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | G22-007-TAP | 0.96384 | 0.86895 | -0.094885 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | G22-007-TAP | 0.96384 | 0.86895 | -0.094885 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | G22-007-TAP | 0.96384 | 0.86895 | -0.094885 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | G22-007-TAP | 0.96384 | 0.86895 | -0.094885 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | G22-007-TAP | 0.96384 | 0.86895 | -0.094885 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | G22-007-TAP | 0.96384 | 0.86895 | -0.094885 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | G22-007-TAP | 0.96384 | 0.86895 | -0.094885 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | G22-007-TAP | 0.96384 | 0.86895 | -0.094885 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | G22-007-TAP | 0.96384 | 0.86895 | -0.094885 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | G22-007-TAP | 0.96384 | 0.86895 | -0.094885 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | G22-007-TAP | 0.96384 | 0.86895 | -0.094885 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | G22-007-TAP | 0.96384 | 0.86895 | -0.094885 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | G22-007-TAP | 0.96384 | 0.86895 | -0.094885 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | G22-007-TAP | 0.96384 | 0.86895 | -0.094885 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | G22-007-TAP | 0.96384 | 0.86895 | -0.094885 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | G22-007-TAP | 0.96384 | 0.86895 | -0.094885 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | G22-007-TAP | 0.96384 | 0.86895 | -0.094885 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | G22-007-TAP | 0.96384 | 0.86895 | -0.094885 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | G22-007-TAP | 0.96384 | 0.86895 | -0.094885 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | ASGI-2024-023 | G22-013-TAP | 1.0053 | 0.94276 | -0.062556 |  | 0.95 | 1.05 | 0.079962 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | G22-013-TAP | 1.0053 | 0.94276 | -0.062556 |  | 0.95 | 1.05 | 0.065323 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-068 | G22-013-TAP | 1.0053 | 0.94276 | -0.062556 |  | 0.95 | 1.05 | 0.067422 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-071 | G22-013-TAP | 1.0053 | 0.94276 | -0.062556 |  | 0.95 | 1.05 | 0.074668 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | G22-013-TAP | 1.0053 | 0.94276 | -0.062556 |  | 0.95 | 1.05 | 0.053027 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-122 | G22-013-TAP | 1.0053 | 0.94276 | -0.062556 |  | 0.95 | 1.05 | 0.082926 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-177 | G22-013-TAP | 1.0053 | 0.94276 | -0.062556 |  | 0.95 | 1.05 | 0.084694 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-178 | G22-013-TAP | 1.0053 | 0.94276 | -0.062556 |  | 0.95 | 1.05 | 0.078867 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | G22-013-TAP | 1.0053 | 0.94276 | -0.062556 |  | 0.95 | 1.05 | 0.031571 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-220 | G22-013-TAP | 1.0053 | 0.94276 | -0.062556 |  | 0.95 | 1.05 | 0.075331 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-232 | G22-013-TAP | 1.0053 | 0.94276 | -0.062556 |  | 0.95 | 1.05 | 0.078906 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | G22-013-TAP | 1.0053 | 0.94276 | -0.062556 |  | 0.95 | 1.05 | 0.065323 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | G22-013-TAP | 1.0053 | 0.94276 | -0.062556 |  | 0.95 | 1.05 | 0.03431 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | G22-013-TAP | 1.0053 | 0.94276 | -0.062556 |  | 0.95 | 1.05 | 0.031504 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | G22-013-TAP | 1.0053 | 0.94276 | -0.062556 |  | 0.95 | 1.05 | 0.031504 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | G22-013-TAP | 1.0053 | 0.94276 | -0.062556 |  | 0.95 | 1.05 | 0.030663 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | G22-013-TAP | 1.0053 | 0.94276 | -0.062556 |  | 0.95 | 1.05 | 0.04269 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-376 | G22-013-TAP | 1.0053 | 0.94276 | -0.062556 |  | 0.95 | 1.05 | 0.082476 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | G22-013-TAP | 1.0014 | 0.94262 | -0.05878 |  | 0.95 | 1.05 | 0.040439 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | G22-013-TAP | 1.0014 | 0.94262 | -0.05878 |  | 0.95 | 1.05 | 0.034938 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | G22-013-TAP | 1.0014 | 0.94262 | -0.05878 |  | 0.95 | 1.05 | 0.037875 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | G22-013-TAP | 1.0014 | 0.94262 | -0.05878 |  | 0.95 | 1.05 | 0.030552 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | G22-013-TAP | 1.0014 | 0.94262 | -0.05878 |  | 0.95 | 1.05 | 0.038531 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | G22-013-TAP | 1.0014 | 0.94262 | -0.05878 |  | 0.95 | 1.05 | 0.037118 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | G22-013-TAP | 1.0014 | 0.94262 | -0.05878 |  | 0.95 | 1.05 | 0.037118 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | G22-013-TAP | 1.0014 | 0.94262 | -0.05878 |  | 0.95 | 1.05 | 0.038129 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | G22-013-TAP | 1.0014 | 0.94262 | -0.05878 |  | 0.95 | 1.05 | 0.038066 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | G22-013-TAP | 1.0014 | 0.94262 | -0.05878 |  | 0.95 | 1.05 | 0.035805 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | G22-013-TAP | 1.0014 | 0.94262 | -0.05878 |  | 0.95 | 1.05 | 0.032364 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | G22-013-TAP | 1.0014 | 0.94262 | -0.05878 |  | 0.95 | 1.05 | 0.031815 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | G22-013-TAP | 1.0014 | 0.94262 | -0.05878 |  | 0.95 | 1.05 | 0.033886 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | G22-013-TAP | 1.0014 | 0.94262 | -0.05878 |  | 0.95 | 1.05 | 0.035554 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | G22-013-TAP | 1.0013 | 0.9454 | -0.055938 |  | 0.95 | 1.05 | 0.039728 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | G22-013-TAP | 1.0013 | 0.9454 | -0.055938 |  | 0.95 | 1.05 | 0.034227 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | G22-013-TAP | 1.0013 | 0.9454 | -0.055938 |  | 0.95 | 1.05 | 0.037164 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | G22-013-TAP | 1.0013 | 0.9454 | -0.055938 |  | 0.95 | 1.05 | 0.03782 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | G22-013-TAP | 1.0013 | 0.9454 | -0.055938 |  | 0.95 | 1.05 | 0.036407 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | G22-013-TAP | 1.0013 | 0.9454 | -0.055938 |  | 0.95 | 1.05 | 0.036407 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | G22-013-TAP | 1.0013 | 0.9454 | -0.055938 |  | 0.95 | 1.05 | 0.037418 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | G22-013-TAP | 1.0013 | 0.9454 | -0.055938 |  | 0.95 | 1.05 | 0.037355 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | G22-013-TAP | 1.0013 | 0.9454 | -0.055938 |  | 0.95 | 1.05 | 0.035094 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | G22-013-TAP | 1.0013 | 0.9454 | -0.055938 |  | 0.95 | 1.05 | 0.031652 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | G22-013-TAP | 1.0013 | 0.9454 | -0.055938 |  | 0.95 | 1.05 | 0.031104 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | G22-013-TAP | 1.0013 | 0.9454 | -0.055938 |  | 0.95 | 1.05 | 0.033175 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | G22-013-TAP | 1.0013 | 0.9454 | -0.055938 |  | 0.95 | 1.05 | 0.034843 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | G22-013-TAP | 1.0015 | 0.94147 | -0.060015 |  | 0.95 | 1.05 | 0.040439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | G22-013-TAP | 1.0015 | 0.94147 | -0.060015 |  | 0.95 | 1.05 | 0.034853 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | G22-013-TAP | 1.0015 | 0.94147 | -0.060015 |  | 0.95 | 1.05 | 0.046783 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | G22-013-TAP | 1.0015 | 0.94147 | -0.060015 |  | 0.95 | 1.05 | 0.047615 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | G22-013-TAP | 1.0015 | 0.94147 | -0.060015 |  | 0.95 | 1.05 | 0.034938 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | G22-013-TAP | 1.0015 | 0.94147 | -0.060015 |  | 0.95 | 1.05 | 0.037875 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | G22-013-TAP | 1.0015 | 0.94147 | -0.060015 |  | 0.95 | 1.05 | 0.044022 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | G22-013-TAP | 1.0015 | 0.94147 | -0.060015 |  | 0.95 | 1.05 | 0.030552 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | G22-013-TAP | 1.0015 | 0.94147 | -0.060015 |  | 0.95 | 1.05 | 0.038531 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | G22-013-TAP | 1.0015 | 0.94147 | -0.060015 |  | 0.95 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | G22-013-TAP | 1.0015 | 0.94147 | -0.060015 |  | 0.95 | 1.05 | 0.062491 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | G22-013-TAP | 1.0015 | 0.94147 | -0.060015 |  | 0.95 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | G22-013-TAP | 1.0015 | 0.94147 | -0.060015 |  | 0.95 | 1.05 | 0.038129 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | G22-013-TAP | 1.0015 | 0.94147 | -0.060015 |  | 0.95 | 1.05 | 0.038066 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | G22-013-TAP | 1.0015 | 0.94147 | -0.060015 |  | 0.95 | 1.05 | 0.034955 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | G22-013-TAP | 1.0015 | 0.94147 | -0.060015 |  | 0.95 | 1.05 | 0.06281 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | G22-013-TAP | 1.0015 | 0.94147 | -0.060015 |  | 0.95 | 1.05 | 0.045309 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | G22-013-TAP | 1.0015 | 0.94147 | -0.060015 |  | 0.95 | 1.05 | 0.035805 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | G22-013-TAP | 1.0015 | 0.94147 | -0.060015 |  | 0.95 | 1.05 | 0.032364 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | G22-013-TAP | 1.0015 | 0.94147 | -0.060015 |  | 0.95 | 1.05 | 0.031815 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | G22-013-TAP | 1.0015 | 0.94147 | -0.060015 |  | 0.95 | 1.05 | 0.033886 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | G22-013-TAP | 1.0015 | 0.94147 | -0.060015 |  | 0.95 | 1.05 | 0.035554 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | G22-013-TAP | 1.0022 | 0.88966 | -0.11254 |  | 0.95 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | G22-013-TAP | 1.0022 | 0.88966 | -0.11254 |  | 0.95 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | G22-013-TAP | 1.0022 | 0.88966 | -0.11254 |  | 0.95 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | G22-013-TAP | 1.0022 | 0.88966 | -0.11254 |  | 0.95 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | G22-013-TAP | 1.0022 | 0.88966 | -0.11254 |  | 0.95 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | G22-013-TAP | 1.0022 | 0.88966 | -0.11254 |  | 0.95 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | G22-013-TAP | 1.0022 | 0.88966 | -0.11254 |  | 0.95 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | G22-013-TAP | 1.0022 | 0.88966 | -0.11254 |  | 0.95 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | G22-013-TAP | 1.0022 | 0.88966 | -0.11254 |  | 0.95 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | G22-013-TAP | 1.0022 | 0.88966 | -0.11254 |  | 0.95 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | G22-013-TAP | 1.0022 | 0.88966 | -0.11254 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | G22-013-TAP | 1.0022 | 0.88966 | -0.11254 |  | 0.95 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | G22-013-TAP | 1.0022 | 0.88966 | -0.11254 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | G22-013-TAP | 1.0022 | 0.88966 | -0.11254 |  | 0.95 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | G22-013-TAP | 1.0022 | 0.88966 | -0.11254 |  | 0.95 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | G22-013-TAP | 1.0022 | 0.88966 | -0.11254 |  | 0.95 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | G22-013-TAP | 1.0022 | 0.88966 | -0.11254 |  | 0.95 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | G22-013-TAP | 1.0022 | 0.88966 | -0.11254 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | G22-013-TAP | 1.0022 | 0.88966 | -0.11254 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | G22-013-TAP | 1.0022 | 0.88966 | -0.11254 |  | 0.95 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | G22-013-TAP | 1.0022 | 0.88966 | -0.11254 |  | 0.95 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | G22-013-TAP | 1.0022 | 0.88966 | -0.11254 |  | 0.95 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | G22-013-TAP | 1.0022 | 0.88966 | -0.11254 |  | 0.95 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | G22-013-TAP | 1.0022 | 0.88966 | -0.11254 |  | 0.95 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | G22-013-TAP | 1.0022 | 0.88966 | -0.11254 |  | 0.95 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | G23-220-TAP | 0.99132 | 0.92973 | -0.061586 |  | 0.95 | 1.05 | 0.039728 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | G23-220-TAP | 0.99132 | 0.92973 | -0.061586 |  | 0.95 | 1.05 | 0.040762 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | G23-220-TAP | 0.99132 | 0.92973 | -0.061586 |  | 0.95 | 1.05 | 0.030778 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | G23-220-TAP | 0.99132 | 0.92973 | -0.061586 |  | 0.95 | 1.05 | 0.034227 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | G23-220-TAP | 0.99132 | 0.92973 | -0.061586 |  | 0.95 | 1.05 | 0.037164 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | G23-220-TAP | 0.99132 | 0.92973 | -0.061586 |  | 0.95 | 1.05 | 0.031937 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | G23-220-TAP | 0.99132 | 0.92973 | -0.061586 |  | 0.95 | 1.05 | 0.03782 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | G23-220-TAP | 0.99132 | 0.92973 | -0.061586 |  | 0.95 | 1.05 | 0.036407 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | G23-220-TAP | 0.99132 | 0.92973 | -0.061586 |  | 0.95 | 1.05 | 0.053181 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | G23-220-TAP | 0.99132 | 0.92973 | -0.061586 |  | 0.95 | 1.05 | 0.036407 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | G23-220-TAP | 0.99132 | 0.92973 | -0.061586 |  | 0.95 | 1.05 | 0.037418 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | G23-220-TAP | 0.99132 | 0.92973 | -0.061586 |  | 0.95 | 1.05 | 0.037355 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | G23-220-TAP | 0.99132 | 0.92973 | -0.061586 |  | 0.95 | 1.05 | 0.032533 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | G23-220-TAP | 0.99132 | 0.92973 | -0.061586 |  | 0.95 | 1.05 | 0.031326 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | G23-220-TAP | 0.99132 | 0.92973 | -0.061586 |  | 0.95 | 1.05 | 0.035094 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | G23-220-TAP | 0.99132 | 0.92973 | -0.061586 |  | 0.95 | 1.05 | 0.031652 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | G23-220-TAP | 0.99132 | 0.92973 | -0.061586 |  | 0.95 | 1.05 | 0.031104 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | G23-220-TAP | 0.99132 | 0.92973 | -0.061586 |  | 0.95 | 1.05 | 0.033175 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | G23-220-TAP | 0.99132 | 0.92973 | -0.061586 |  | 0.95 | 1.05 | 0.034843 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | G23-220-TAP | 0.99498 | 0.93081 | -0.064164 |  | 0.95 | 1.05 | 0.03053 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | G23-220-TAP | 0.99498 | 0.93081 | -0.064164 |  | 0.95 | 1.05 | 0.044933 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | G23-220-TAP | 0.99498 | 0.93081 | -0.064164 |  | 0.95 | 1.05 | 0.047811 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | G23-220-TAP | 0.99498 | 0.93081 | -0.064164 |  | 0.95 | 1.05 | 0.09719 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | G23-220-TAP | 0.99498 | 0.93081 | -0.064164 |  | 0.95 | 1.05 | 0.069376 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | G23-220-TAP | 0.99498 | 0.93081 | -0.064164 |  | 0.95 | 1.05 | 0.04277 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | G23-220-TAP | 0.99498 | 0.93081 | -0.064164 |  | 0.95 | 1.05 | 0.071112 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | G23-220-TAP | 0.99498 | 0.93081 | -0.064164 |  | 0.95 | 1.05 | 0.039357 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | G23-220-TAP | 0.99498 | 0.93081 | -0.064164 |  | 0.95 | 1.05 | 0.04035 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | G23-220-TAP | 0.99498 | 0.93081 | -0.064164 |  | 0.95 | 1.05 | 0.052332 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | G23-220-TAP | 0.99498 | 0.93081 | -0.064164 |  | 0.95 | 1.05 | 0.045944 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | G23-220-TAP | 0.99498 | 0.93081 | -0.064164 |  | 0.95 | 1.05 | 0.038178 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | G23-220-TAP | 0.99498 | 0.93081 | -0.064164 |  | 0.95 | 1.05 | 0.13469 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | G23-220-TAP | 0.99498 | 0.93081 | -0.064164 |  | 0.95 | 1.05 | 0.03053 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | G23-220-TAP | 0.99498 | 0.93081 | -0.064164 |  | 0.95 | 1.05 | 0.038178 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | G23-220-TAP | 0.99498 | 0.93081 | -0.064164 |  | 0.95 | 1.05 | 0.037309 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | G23-220-TAP | 0.99498 | 0.93081 | -0.064164 |  | 0.95 | 1.05 | 0.040075 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | G23-220-TAP | 0.99498 | 0.93081 | -0.064164 |  | 0.95 | 1.05 | 0.053764 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | G23-220-TAP | 0.99498 | 0.93081 | -0.064164 |  | 0.95 | 1.05 | 0.071762 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | G23-220-TAP | 0.99498 | 0.93081 | -0.064164 |  | 0.95 | 1.05 | 0.047827 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | G23-220-TAP | 0.99498 | 0.93081 | -0.064164 |  | 0.95 | 1.05 | 0.047827 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | G23-220-TAP | 0.99498 | 0.93081 | -0.064164 |  | 0.95 | 1.05 | 0.070303 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | G23-220-TAP | 0.99498 | 0.93081 | -0.064164 |  | 0.95 | 1.05 | 0.040614 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | G23-220-TAP | 0.99498 | 0.93081 | -0.064164 |  | 0.95 | 1.05 | 0.039729 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | G23-220-TAP | 0.99498 | 0.93081 | -0.064164 |  | 0.95 | 1.05 | 0.049662 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | G23-220-TAP | 0.99498 | 0.93081 | -0.064164 |  | 0.95 | 1.05 | 0.042332 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | G23-220-TAP | 0.99498 | 0.93081 | -0.064164 |  | 0.95 | 1.05 | 0.048722 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | G23-220-TAP | 0.99498 | 0.93081 | -0.064164 |  | 0.95 | 1.05 | 0.038156 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | G23-220-TAP | 0.99498 | 0.93081 | -0.064164 |  | 0.95 | 1.05 | 0.036794 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | G23-220-TAP | 0.99126 | 0.9358 | -0.055463 |  | 0.95 | 1.05 | 0.036307 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | G23-220-TAP | 0.99126 | 0.9358 | -0.055463 |  | 0.95 | 1.05 | 0.052743 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | G23-220-TAP | 0.99126 | 0.9358 | -0.055463 |  | 0.95 | 1.05 | 0.039345 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | G23-220-TAP | 0.99126 | 0.9358 | -0.055463 |  | 0.95 | 1.05 | 0.031366 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | G23-220-TAP | 0.99126 | 0.9358 | -0.055463 |  | 0.95 | 1.05 | 0.041888 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | G23-220-TAP | 0.99126 | 0.9358 | -0.055463 |  | 0.95 | 1.05 | 0.038797 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | G23-220-TAP | 0.99126 | 0.9358 | -0.055463 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | G23-220-TAP | 0.99126 | 0.9358 | -0.055463 |  | 0.95 | 1.05 | 0.067346 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | G23-220-TAP | 0.99126 | 0.9358 | -0.055463 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | G23-220-TAP | 0.99126 | 0.9358 | -0.055463 |  | 0.95 | 1.05 | 0.030851 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | G23-220-TAP | 0.99126 | 0.9358 | -0.055463 |  | 0.95 | 1.05 | 0.032161 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | G23-220-TAP | 0.99126 | 0.9358 | -0.055463 |  | 0.95 | 1.05 | 0.04067 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | G23-220-TAP | 0.99126 | 0.9358 | -0.055463 |  | 0.95 | 1.05 | 0.040569 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | G23-220-TAP | 0.99126 | 0.9358 | -0.055463 |  | 0.95 | 1.05 | 0.03086 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | G23-220-TAP | 0.99126 | 0.9358 | -0.055463 |  | 0.95 | 1.05 | 0.033223 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | G23-220-TAP | 0.99126 | 0.9358 | -0.055463 |  | 0.95 | 1.05 | 0.033733 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | G23-220-TAP | 0.99303 | 0.92766 | -0.065366 |  | 0.95 | 1.05 | 0.036307 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | G23-220-TAP | 0.99303 | 0.92766 | -0.065366 |  | 0.95 | 1.05 | 0.052743 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | G23-220-TAP | 0.99303 | 0.92766 | -0.065366 |  | 0.95 | 1.05 | 0.039345 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | G23-220-TAP | 0.99303 | 0.92766 | -0.065366 |  | 0.95 | 1.05 | 0.031366 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | G23-220-TAP | 0.99303 | 0.92766 | -0.065366 |  | 0.95 | 1.05 | 0.041888 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | G23-220-TAP | 0.99303 | 0.92766 | -0.065366 |  | 0.95 | 1.05 | 0.038797 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | G23-220-TAP | 0.99303 | 0.92766 | -0.065366 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | G23-220-TAP | 0.99303 | 0.92766 | -0.065366 |  | 0.95 | 1.05 | 0.067346 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | G23-220-TAP | 0.99303 | 0.92766 | -0.065366 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | G23-220-TAP | 0.99303 | 0.92766 | -0.065366 |  | 0.95 | 1.05 | 0.030851 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | G23-220-TAP | 0.99303 | 0.92766 | -0.065366 |  | 0.95 | 1.05 | 0.032161 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | G23-220-TAP | 0.99303 | 0.92766 | -0.065366 |  | 0.95 | 1.05 | 0.04067 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | G23-220-TAP | 0.99303 | 0.92766 | -0.065366 |  | 0.95 | 1.05 | 0.040569 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | G23-220-TAP | 0.99303 | 0.92766 | -0.065366 |  | 0.95 | 1.05 | 0.03086 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | G23-220-TAP | 0.99303 | 0.92766 | -0.065366 |  | 0.95 | 1.05 | 0.033223 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | G23-220-TAP | 0.99303 | 0.92766 | -0.065366 |  | 0.95 | 1.05 | 0.033733 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | G23-220-TAP | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | G23-220-TAP | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | G23-220-TAP | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | G23-220-TAP | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | G23-220-TAP | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | G23-220-TAP | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | G23-220-TAP | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | G23-220-TAP | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | G23-220-TAP | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | G23-220-TAP | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | G23-220-TAP | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | G23-220-TAP | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | G23-220-TAP | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | G23-220-TAP | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | G23-220-TAP | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | G23-220-TAP | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | G23-220-TAP | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | G23-220-TAP | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | G23-220-TAP | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | G23-220-TAP | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | G23-220-TAP | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | G23-220-TAP | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | G23-220-TAP | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | G23-220-TAP | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | G23-220-TAP | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | G23-221-TAP | 0.99221 | 0.93069 | -0.061519 |  | 0.95 | 1.05 | 0.039728 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | G23-221-TAP | 0.99221 | 0.93069 | -0.061519 |  | 0.95 | 1.05 | 0.040762 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | G23-221-TAP | 0.99221 | 0.93069 | -0.061519 |  | 0.95 | 1.05 | 0.030778 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | G23-221-TAP | 0.99221 | 0.93069 | -0.061519 |  | 0.95 | 1.05 | 0.034227 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | G23-221-TAP | 0.99221 | 0.93069 | -0.061519 |  | 0.95 | 1.05 | 0.037164 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | G23-221-TAP | 0.99221 | 0.93069 | -0.061519 |  | 0.95 | 1.05 | 0.031937 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | G23-221-TAP | 0.99221 | 0.93069 | -0.061519 |  | 0.95 | 1.05 | 0.03782 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | G23-221-TAP | 0.99221 | 0.93069 | -0.061519 |  | 0.95 | 1.05 | 0.036407 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | G23-221-TAP | 0.99221 | 0.93069 | -0.061519 |  | 0.95 | 1.05 | 0.053181 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | G23-221-TAP | 0.99221 | 0.93069 | -0.061519 |  | 0.95 | 1.05 | 0.036407 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | G23-221-TAP | 0.99221 | 0.93069 | -0.061519 |  | 0.95 | 1.05 | 0.037418 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | G23-221-TAP | 0.99221 | 0.93069 | -0.061519 |  | 0.95 | 1.05 | 0.037355 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | G23-221-TAP | 0.99221 | 0.93069 | -0.061519 |  | 0.95 | 1.05 | 0.032533 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | G23-221-TAP | 0.99221 | 0.93069 | -0.061519 |  | 0.95 | 1.05 | 0.031326 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | G23-221-TAP | 0.99221 | 0.93069 | -0.061519 |  | 0.95 | 1.05 | 0.035094 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | G23-221-TAP | 0.99221 | 0.93069 | -0.061519 |  | 0.95 | 1.05 | 0.031652 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | G23-221-TAP | 0.99221 | 0.93069 | -0.061519 |  | 0.95 | 1.05 | 0.031104 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | G23-221-TAP | 0.99221 | 0.93069 | -0.061519 |  | 0.95 | 1.05 | 0.033175 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | G23-221-TAP | 0.99221 | 0.93069 | -0.061519 |  | 0.95 | 1.05 | 0.034843 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | G23-221-TAP | 0.99565 | 0.93146 | -0.064187 |  | 0.95 | 1.05 | 0.03053 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | G23-221-TAP | 0.99565 | 0.93146 | -0.064187 |  | 0.95 | 1.05 | 0.044933 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | G23-221-TAP | 0.99565 | 0.93146 | -0.064187 |  | 0.95 | 1.05 | 0.047811 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | G23-221-TAP | 0.99565 | 0.93146 | -0.064187 |  | 0.95 | 1.05 | 0.09719 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | G23-221-TAP | 0.99565 | 0.93146 | -0.064187 |  | 0.95 | 1.05 | 0.069376 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | G23-221-TAP | 0.99565 | 0.93146 | -0.064187 |  | 0.95 | 1.05 | 0.04277 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | G23-221-TAP | 0.99565 | 0.93146 | -0.064187 |  | 0.95 | 1.05 | 0.071112 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | G23-221-TAP | 0.99565 | 0.93146 | -0.064187 |  | 0.95 | 1.05 | 0.039357 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | G23-221-TAP | 0.99565 | 0.93146 | -0.064187 |  | 0.95 | 1.05 | 0.04035 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | G23-221-TAP | 0.99565 | 0.93146 | -0.064187 |  | 0.95 | 1.05 | 0.052332 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | G23-221-TAP | 0.99565 | 0.93146 | -0.064187 |  | 0.95 | 1.05 | 0.045944 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | G23-221-TAP | 0.99565 | 0.93146 | -0.064187 |  | 0.95 | 1.05 | 0.038178 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | G23-221-TAP | 0.99565 | 0.93146 | -0.064187 |  | 0.95 | 1.05 | 0.13469 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | G23-221-TAP | 0.99565 | 0.93146 | -0.064187 |  | 0.95 | 1.05 | 0.03053 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | G23-221-TAP | 0.99565 | 0.93146 | -0.064187 |  | 0.95 | 1.05 | 0.038178 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | G23-221-TAP | 0.99565 | 0.93146 | -0.064187 |  | 0.95 | 1.05 | 0.037309 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | G23-221-TAP | 0.99565 | 0.93146 | -0.064187 |  | 0.95 | 1.05 | 0.040075 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | G23-221-TAP | 0.99565 | 0.93146 | -0.064187 |  | 0.95 | 1.05 | 0.053764 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | G23-221-TAP | 0.99565 | 0.93146 | -0.064187 |  | 0.95 | 1.05 | 0.071762 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | G23-221-TAP | 0.99565 | 0.93146 | -0.064187 |  | 0.95 | 1.05 | 0.047827 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | G23-221-TAP | 0.99565 | 0.93146 | -0.064187 |  | 0.95 | 1.05 | 0.047827 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | G23-221-TAP | 0.99565 | 0.93146 | -0.064187 |  | 0.95 | 1.05 | 0.070303 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | G23-221-TAP | 0.99565 | 0.93146 | -0.064187 |  | 0.95 | 1.05 | 0.040614 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | G23-221-TAP | 0.99565 | 0.93146 | -0.064187 |  | 0.95 | 1.05 | 0.039729 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | G23-221-TAP | 0.99565 | 0.93146 | -0.064187 |  | 0.95 | 1.05 | 0.049662 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | G23-221-TAP | 0.99565 | 0.93146 | -0.064187 |  | 0.95 | 1.05 | 0.042332 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | G23-221-TAP | 0.99565 | 0.93146 | -0.064187 |  | 0.95 | 1.05 | 0.048722 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | G23-221-TAP | 0.99565 | 0.93146 | -0.064187 |  | 0.95 | 1.05 | 0.038156 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | G23-221-TAP | 0.99565 | 0.93146 | -0.064187 |  | 0.95 | 1.05 | 0.036794 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | G23-221-TAP | 0.99222 | 0.93695 | -0.05527 |  | 0.95 | 1.05 | 0.036307 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | G23-221-TAP | 0.99222 | 0.93695 | -0.05527 |  | 0.95 | 1.05 | 0.052743 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | G23-221-TAP | 0.99222 | 0.93695 | -0.05527 |  | 0.95 | 1.05 | 0.039345 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | G23-221-TAP | 0.99222 | 0.93695 | -0.05527 |  | 0.95 | 1.05 | 0.031366 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | G23-221-TAP | 0.99222 | 0.93695 | -0.05527 |  | 0.95 | 1.05 | 0.041888 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | G23-221-TAP | 0.99222 | 0.93695 | -0.05527 |  | 0.95 | 1.05 | 0.038797 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | G23-221-TAP | 0.99222 | 0.93695 | -0.05527 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | G23-221-TAP | 0.99222 | 0.93695 | -0.05527 |  | 0.95 | 1.05 | 0.067346 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | G23-221-TAP | 0.99222 | 0.93695 | -0.05527 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | G23-221-TAP | 0.99222 | 0.93695 | -0.05527 |  | 0.95 | 1.05 | 0.030851 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | G23-221-TAP | 0.99222 | 0.93695 | -0.05527 |  | 0.95 | 1.05 | 0.032161 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | G23-221-TAP | 0.99222 | 0.93695 | -0.05527 |  | 0.95 | 1.05 | 0.04067 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | G23-221-TAP | 0.99222 | 0.93695 | -0.05527 |  | 0.95 | 1.05 | 0.040569 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | G23-221-TAP | 0.99222 | 0.93695 | -0.05527 |  | 0.95 | 1.05 | 0.03086 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | G23-221-TAP | 0.99222 | 0.93695 | -0.05527 |  | 0.95 | 1.05 | 0.033223 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | G23-221-TAP | 0.99222 | 0.93695 | -0.05527 |  | 0.95 | 1.05 | 0.033733 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | G23-221-TAP | 0.99384 | 0.92866 | -0.065176 |  | 0.95 | 1.05 | 0.036307 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | G23-221-TAP | 0.99384 | 0.92866 | -0.065176 |  | 0.95 | 1.05 | 0.052743 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | G23-221-TAP | 0.99384 | 0.92866 | -0.065176 |  | 0.95 | 1.05 | 0.039345 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | G23-221-TAP | 0.99384 | 0.92866 | -0.065176 |  | 0.95 | 1.05 | 0.031366 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | G23-221-TAP | 0.99384 | 0.92866 | -0.065176 |  | 0.95 | 1.05 | 0.041888 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | G23-221-TAP | 0.99384 | 0.92866 | -0.065176 |  | 0.95 | 1.05 | 0.038797 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | G23-221-TAP | 0.99384 | 0.92866 | -0.065176 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | G23-221-TAP | 0.99384 | 0.92866 | -0.065176 |  | 0.95 | 1.05 | 0.067346 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | G23-221-TAP | 0.99384 | 0.92866 | -0.065176 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | G23-221-TAP | 0.99384 | 0.92866 | -0.065176 |  | 0.95 | 1.05 | 0.030851 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | G23-221-TAP | 0.99384 | 0.92866 | -0.065176 |  | 0.95 | 1.05 | 0.032161 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | G23-221-TAP | 0.99384 | 0.92866 | -0.065176 |  | 0.95 | 1.05 | 0.04067 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | G23-221-TAP | 0.99384 | 0.92866 | -0.065176 |  | 0.95 | 1.05 | 0.040569 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | G23-221-TAP | 0.99384 | 0.92866 | -0.065176 |  | 0.95 | 1.05 | 0.03086 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | G23-221-TAP | 0.99384 | 0.92866 | -0.065176 |  | 0.95 | 1.05 | 0.033223 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | G23-221-TAP | 0.99384 | 0.92866 | -0.065176 |  | 0.95 | 1.05 | 0.033733 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | G23-221-TAP | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | G23-221-TAP | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | G23-221-TAP | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | G23-221-TAP | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | G23-221-TAP | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | G23-221-TAP | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | G23-221-TAP | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | G23-221-TAP | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | G23-221-TAP | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | G23-221-TAP | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | G23-221-TAP | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | G23-221-TAP | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | G23-221-TAP | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | G23-221-TAP | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | G23-221-TAP | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | G23-221-TAP | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | G23-221-TAP | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | G23-221-TAP | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | G23-221-TAP | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | G23-221-TAP | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | G23-221-TAP | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | G23-221-TAP | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | G23-221-TAP | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | G23-221-TAP | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | G23-221-TAP | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | ASGI-2024-023 | G24-076-TAP | 1.0053 | 0.94283 | -0.062494 |  | 0.95 | 1.05 | 0.079962 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | G24-076-TAP | 1.0053 | 0.94283 | -0.062494 |  | 0.95 | 1.05 | 0.065323 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-068 | G24-076-TAP | 1.0053 | 0.94283 | -0.062494 |  | 0.95 | 1.05 | 0.067422 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-071 | G24-076-TAP | 1.0053 | 0.94283 | -0.062494 |  | 0.95 | 1.05 | 0.074668 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | G24-076-TAP | 1.0053 | 0.94283 | -0.062494 |  | 0.95 | 1.05 | 0.053027 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-122 | G24-076-TAP | 1.0053 | 0.94283 | -0.062494 |  | 0.95 | 1.05 | 0.082926 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-177 | G24-076-TAP | 1.0053 | 0.94283 | -0.062494 |  | 0.95 | 1.05 | 0.084694 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-178 | G24-076-TAP | 1.0053 | 0.94283 | -0.062494 |  | 0.95 | 1.05 | 0.078867 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | G24-076-TAP | 1.0053 | 0.94283 | -0.062494 |  | 0.95 | 1.05 | 0.031571 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-220 | G24-076-TAP | 1.0053 | 0.94283 | -0.062494 |  | 0.95 | 1.05 | 0.075331 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-232 | G24-076-TAP | 1.0053 | 0.94283 | -0.062494 |  | 0.95 | 1.05 | 0.078906 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | G24-076-TAP | 1.0053 | 0.94283 | -0.062494 |  | 0.95 | 1.05 | 0.065323 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | G24-076-TAP | 1.0053 | 0.94283 | -0.062494 |  | 0.95 | 1.05 | 0.03431 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | G24-076-TAP | 1.0053 | 0.94283 | -0.062494 |  | 0.95 | 1.05 | 0.031504 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | G24-076-TAP | 1.0053 | 0.94283 | -0.062494 |  | 0.95 | 1.05 | 0.031504 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | G24-076-TAP | 1.0053 | 0.94283 | -0.062494 |  | 0.95 | 1.05 | 0.030663 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | G24-076-TAP | 1.0053 | 0.94283 | -0.062494 |  | 0.95 | 1.05 | 0.04269 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-376 | G24-076-TAP | 1.0053 | 0.94283 | -0.062494 |  | 0.95 | 1.05 | 0.082476 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | G24-076-TAP | 1.0014 | 0.94255 | -0.058884 |  | 0.95 | 1.05 | 0.040439 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | G24-076-TAP | 1.0014 | 0.94255 | -0.058884 |  | 0.95 | 1.05 | 0.034938 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | G24-076-TAP | 1.0014 | 0.94255 | -0.058884 |  | 0.95 | 1.05 | 0.037875 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | G24-076-TAP | 1.0014 | 0.94255 | -0.058884 |  | 0.95 | 1.05 | 0.030552 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | G24-076-TAP | 1.0014 | 0.94255 | -0.058884 |  | 0.95 | 1.05 | 0.038531 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | G24-076-TAP | 1.0014 | 0.94255 | -0.058884 |  | 0.95 | 1.05 | 0.037118 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | G24-076-TAP | 1.0014 | 0.94255 | -0.058884 |  | 0.95 | 1.05 | 0.037118 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | G24-076-TAP | 1.0014 | 0.94255 | -0.058884 |  | 0.95 | 1.05 | 0.038129 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | G24-076-TAP | 1.0014 | 0.94255 | -0.058884 |  | 0.95 | 1.05 | 0.038066 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | G24-076-TAP | 1.0014 | 0.94255 | -0.058884 |  | 0.95 | 1.05 | 0.035805 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | G24-076-TAP | 1.0014 | 0.94255 | -0.058884 |  | 0.95 | 1.05 | 0.032364 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | G24-076-TAP | 1.0014 | 0.94255 | -0.058884 |  | 0.95 | 1.05 | 0.031815 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | G24-076-TAP | 1.0014 | 0.94255 | -0.058884 |  | 0.95 | 1.05 | 0.033886 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | G24-076-TAP | 1.0014 | 0.94255 | -0.058884 |  | 0.95 | 1.05 | 0.035554 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | G24-076-TAP | 1.0014 | 0.94533 | -0.056037 |  | 0.95 | 1.05 | 0.039728 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | G24-076-TAP | 1.0014 | 0.94533 | -0.056037 |  | 0.95 | 1.05 | 0.034227 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | G24-076-TAP | 1.0014 | 0.94533 | -0.056037 |  | 0.95 | 1.05 | 0.037164 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | G24-076-TAP | 1.0014 | 0.94533 | -0.056037 |  | 0.95 | 1.05 | 0.03782 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | G24-076-TAP | 1.0014 | 0.94533 | -0.056037 |  | 0.95 | 1.05 | 0.036407 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | G24-076-TAP | 1.0014 | 0.94533 | -0.056037 |  | 0.95 | 1.05 | 0.036407 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | G24-076-TAP | 1.0014 | 0.94533 | -0.056037 |  | 0.95 | 1.05 | 0.037418 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | G24-076-TAP | 1.0014 | 0.94533 | -0.056037 |  | 0.95 | 1.05 | 0.037355 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | G24-076-TAP | 1.0014 | 0.94533 | -0.056037 |  | 0.95 | 1.05 | 0.035094 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | G24-076-TAP | 1.0014 | 0.94533 | -0.056037 |  | 0.95 | 1.05 | 0.031652 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | G24-076-TAP | 1.0014 | 0.94533 | -0.056037 |  | 0.95 | 1.05 | 0.031104 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | G24-076-TAP | 1.0014 | 0.94533 | -0.056037 |  | 0.95 | 1.05 | 0.033175 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | G24-076-TAP | 1.0014 | 0.94533 | -0.056037 |  | 0.95 | 1.05 | 0.034843 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | G24-076-TAP | 1.0015 | 0.94087 | -0.060606 |  | 0.95 | 1.05 | 0.040439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | G24-076-TAP | 1.0015 | 0.94087 | -0.060606 |  | 0.95 | 1.05 | 0.034853 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | G24-076-TAP | 1.0015 | 0.94087 | -0.060606 |  | 0.95 | 1.05 | 0.046783 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | G24-076-TAP | 1.0015 | 0.94087 | -0.060606 |  | 0.95 | 1.05 | 0.047615 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | G24-076-TAP | 1.0015 | 0.94087 | -0.060606 |  | 0.95 | 1.05 | 0.034938 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | G24-076-TAP | 1.0015 | 0.94087 | -0.060606 |  | 0.95 | 1.05 | 0.037875 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | G24-076-TAP | 1.0015 | 0.94087 | -0.060606 |  | 0.95 | 1.05 | 0.044022 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | G24-076-TAP | 1.0015 | 0.94087 | -0.060606 |  | 0.95 | 1.05 | 0.030552 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | G24-076-TAP | 1.0015 | 0.94087 | -0.060606 |  | 0.95 | 1.05 | 0.038531 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | G24-076-TAP | 1.0015 | 0.94087 | -0.060606 |  | 0.95 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | G24-076-TAP | 1.0015 | 0.94087 | -0.060606 |  | 0.95 | 1.05 | 0.062491 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | G24-076-TAP | 1.0015 | 0.94087 | -0.060606 |  | 0.95 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | G24-076-TAP | 1.0015 | 0.94087 | -0.060606 |  | 0.95 | 1.05 | 0.038129 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | G24-076-TAP | 1.0015 | 0.94087 | -0.060606 |  | 0.95 | 1.05 | 0.038066 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | G24-076-TAP | 1.0015 | 0.94087 | -0.060606 |  | 0.95 | 1.05 | 0.034955 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | G24-076-TAP | 1.0015 | 0.94087 | -0.060606 |  | 0.95 | 1.05 | 0.06281 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | G24-076-TAP | 1.0015 | 0.94087 | -0.060606 |  | 0.95 | 1.05 | 0.045309 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | G24-076-TAP | 1.0015 | 0.94087 | -0.060606 |  | 0.95 | 1.05 | 0.035805 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | G24-076-TAP | 1.0015 | 0.94087 | -0.060606 |  | 0.95 | 1.05 | 0.032364 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | G24-076-TAP | 1.0015 | 0.94087 | -0.060606 |  | 0.95 | 1.05 | 0.031815 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | G24-076-TAP | 1.0015 | 0.94087 | -0.060606 |  | 0.95 | 1.05 | 0.033886 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | G24-076-TAP | 1.0015 | 0.94087 | -0.060606 |  | 0.95 | 1.05 | 0.035554 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | G24-076-TAP | 1.0023 | 0.89079 | -0.11147 |  | 0.95 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | G24-076-TAP | 1.0023 | 0.89079 | -0.11147 |  | 0.95 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | G24-076-TAP | 1.0023 | 0.89079 | -0.11147 |  | 0.95 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | G24-076-TAP | 1.0023 | 0.89079 | -0.11147 |  | 0.95 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | G24-076-TAP | 1.0023 | 0.89079 | -0.11147 |  | 0.95 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | G24-076-TAP | 1.0023 | 0.89079 | -0.11147 |  | 0.95 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | G24-076-TAP | 1.0023 | 0.89079 | -0.11147 |  | 0.95 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | G24-076-TAP | 1.0023 | 0.89079 | -0.11147 |  | 0.95 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | G24-076-TAP | 1.0023 | 0.89079 | -0.11147 |  | 0.95 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | G24-076-TAP | 1.0023 | 0.89079 | -0.11147 |  | 0.95 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | G24-076-TAP | 1.0023 | 0.89079 | -0.11147 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | G24-076-TAP | 1.0023 | 0.89079 | -0.11147 |  | 0.95 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | G24-076-TAP | 1.0023 | 0.89079 | -0.11147 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | G24-076-TAP | 1.0023 | 0.89079 | -0.11147 |  | 0.95 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | G24-076-TAP | 1.0023 | 0.89079 | -0.11147 |  | 0.95 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | G24-076-TAP | 1.0023 | 0.89079 | -0.11147 |  | 0.95 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | G24-076-TAP | 1.0023 | 0.89079 | -0.11147 |  | 0.95 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | G24-076-TAP | 1.0023 | 0.89079 | -0.11147 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | G24-076-TAP | 1.0023 | 0.89079 | -0.11147 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | G24-076-TAP | 1.0023 | 0.89079 | -0.11147 |  | 0.95 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | G24-076-TAP | 1.0023 | 0.89079 | -0.11147 |  | 0.95 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | G24-076-TAP | 1.0023 | 0.89079 | -0.11147 |  | 0.95 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | G24-076-TAP | 1.0023 | 0.89079 | -0.11147 |  | 0.95 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | G24-076-TAP | 1.0023 | 0.89079 | -0.11147 |  | 0.95 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | G24-076-TAP | 1.0023 | 0.89079 | -0.11147 |  | 0.95 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | G24-125-TAP | 0.9898 | 0.94281 | -0.046985 |  | 0.95 | 1.05 | 0.040439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | G24-125-TAP | 0.9898 | 0.94281 | -0.046985 |  | 0.95 | 1.05 | 0.034853 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | G24-125-TAP | 0.9898 | 0.94281 | -0.046985 |  | 0.95 | 1.05 | 0.046783 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | G24-125-TAP | 0.9898 | 0.94281 | -0.046985 |  | 0.95 | 1.05 | 0.047615 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | G24-125-TAP | 0.9898 | 0.94281 | -0.046985 |  | 0.95 | 1.05 | 0.034938 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | G24-125-TAP | 0.9898 | 0.94281 | -0.046985 |  | 0.95 | 1.05 | 0.037875 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | G24-125-TAP | 0.9898 | 0.94281 | -0.046985 |  | 0.95 | 1.05 | 0.044022 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | G24-125-TAP | 0.9898 | 0.94281 | -0.046985 |  | 0.95 | 1.05 | 0.030552 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | G24-125-TAP | 0.9898 | 0.94281 | -0.046985 |  | 0.95 | 1.05 | 0.038531 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | G24-125-TAP | 0.9898 | 0.94281 | -0.046985 |  | 0.95 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | G24-125-TAP | 0.9898 | 0.94281 | -0.046985 |  | 0.95 | 1.05 | 0.062491 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | G24-125-TAP | 0.9898 | 0.94281 | -0.046985 |  | 0.95 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | G24-125-TAP | 0.9898 | 0.94281 | -0.046985 |  | 0.95 | 1.05 | 0.038129 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | G24-125-TAP | 0.9898 | 0.94281 | -0.046985 |  | 0.95 | 1.05 | 0.038066 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | G24-125-TAP | 0.9898 | 0.94281 | -0.046985 |  | 0.95 | 1.05 | 0.034955 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | G24-125-TAP | 0.9898 | 0.94281 | -0.046985 |  | 0.95 | 1.05 | 0.06281 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | G24-125-TAP | 0.9898 | 0.94281 | -0.046985 |  | 0.95 | 1.05 | 0.045309 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | G24-125-TAP | 0.9898 | 0.94281 | -0.046985 |  | 0.95 | 1.05 | 0.035805 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | G24-125-TAP | 0.9898 | 0.94281 | -0.046985 |  | 0.95 | 1.05 | 0.032364 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | G24-125-TAP | 0.9898 | 0.94281 | -0.046985 |  | 0.95 | 1.05 | 0.031815 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | G24-125-TAP | 0.9898 | 0.94281 | -0.046985 |  | 0.95 | 1.05 | 0.033886 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | G24-125-TAP | 0.9898 | 0.94281 | -0.046985 |  | 0.95 | 1.05 | 0.035554 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | G24-125-TAP | 0.99752 | 0.94702 | -0.050503 |  | 0.95 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | G24-125-TAP | 0.99752 | 0.94702 | -0.050503 |  | 0.95 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | G24-125-TAP | 0.99752 | 0.94702 | -0.050503 |  | 0.95 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | G24-125-TAP | 0.99752 | 0.94702 | -0.050503 |  | 0.95 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | G24-125-TAP | 0.99752 | 0.94702 | -0.050503 |  | 0.95 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | G24-125-TAP | 0.99752 | 0.94702 | -0.050503 |  | 0.95 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | G24-125-TAP | 0.99752 | 0.94702 | -0.050503 |  | 0.95 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | G24-125-TAP | 0.99752 | 0.94702 | -0.050503 |  | 0.95 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | G24-125-TAP | 0.99752 | 0.94702 | -0.050503 |  | 0.95 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | G24-125-TAP | 0.99752 | 0.94702 | -0.050503 |  | 0.95 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | G24-125-TAP | 0.99752 | 0.94702 | -0.050503 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | G24-125-TAP | 0.99752 | 0.94702 | -0.050503 |  | 0.95 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | G24-125-TAP | 0.99752 | 0.94702 | -0.050503 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | G24-125-TAP | 0.99752 | 0.94702 | -0.050503 |  | 0.95 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | G24-125-TAP | 0.99752 | 0.94702 | -0.050503 |  | 0.95 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | G24-125-TAP | 0.99752 | 0.94702 | -0.050503 |  | 0.95 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | G24-125-TAP | 0.99752 | 0.94702 | -0.050503 |  | 0.95 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | G24-125-TAP | 0.99752 | 0.94702 | -0.050503 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | G24-125-TAP | 0.99752 | 0.94702 | -0.050503 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | G24-125-TAP | 0.99752 | 0.94702 | -0.050503 |  | 0.95 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | G24-125-TAP | 0.99752 | 0.94702 | -0.050503 |  | 0.95 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | G24-125-TAP | 0.99752 | 0.94702 | -0.050503 |  | 0.95 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | G24-125-TAP | 0.99752 | 0.94702 | -0.050503 |  | 0.95 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | G24-125-TAP | 0.99752 | 0.94702 | -0.050503 |  | 0.95 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | G24-125-TAP | 0.99752 | 0.94702 | -0.050503 |  | 0.95 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | G24-129-TAP | 0.99901 | 0.94242 | -0.056593 |  | 0.95 | 1.05 | 0.040439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | G24-129-TAP | 0.99901 | 0.94242 | -0.056593 |  | 0.95 | 1.05 | 0.034853 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | G24-129-TAP | 0.99901 | 0.94242 | -0.056593 |  | 0.95 | 1.05 | 0.046783 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | G24-129-TAP | 0.99901 | 0.94242 | -0.056593 |  | 0.95 | 1.05 | 0.047615 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | G24-129-TAP | 0.99901 | 0.94242 | -0.056593 |  | 0.95 | 1.05 | 0.034938 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | G24-129-TAP | 0.99901 | 0.94242 | -0.056593 |  | 0.95 | 1.05 | 0.037875 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | G24-129-TAP | 0.99901 | 0.94242 | -0.056593 |  | 0.95 | 1.05 | 0.044022 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | G24-129-TAP | 0.99901 | 0.94242 | -0.056593 |  | 0.95 | 1.05 | 0.030552 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | G24-129-TAP | 0.99901 | 0.94242 | -0.056593 |  | 0.95 | 1.05 | 0.038531 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | G24-129-TAP | 0.99901 | 0.94242 | -0.056593 |  | 0.95 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | G24-129-TAP | 0.99901 | 0.94242 | -0.056593 |  | 0.95 | 1.05 | 0.062491 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | G24-129-TAP | 0.99901 | 0.94242 | -0.056593 |  | 0.95 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | G24-129-TAP | 0.99901 | 0.94242 | -0.056593 |  | 0.95 | 1.05 | 0.038129 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | G24-129-TAP | 0.99901 | 0.94242 | -0.056593 |  | 0.95 | 1.05 | 0.038066 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | G24-129-TAP | 0.99901 | 0.94242 | -0.056593 |  | 0.95 | 1.05 | 0.034955 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | G24-129-TAP | 0.99901 | 0.94242 | -0.056593 |  | 0.95 | 1.05 | 0.06281 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | G24-129-TAP | 0.99901 | 0.94242 | -0.056593 |  | 0.95 | 1.05 | 0.045309 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | G24-129-TAP | 0.99901 | 0.94242 | -0.056593 |  | 0.95 | 1.05 | 0.035805 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | G24-129-TAP | 0.99901 | 0.94242 | -0.056593 |  | 0.95 | 1.05 | 0.032364 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | G24-129-TAP | 0.99901 | 0.94242 | -0.056593 |  | 0.95 | 1.05 | 0.031815 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | G24-129-TAP | 0.99901 | 0.94242 | -0.056593 |  | 0.95 | 1.05 | 0.033886 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | G24-129-TAP | 0.99901 | 0.94242 | -0.056593 |  | 0.95 | 1.05 | 0.035554 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | G24-129-TAP | 1.0035 | 0.93555 | -0.067953 |  | 0.95 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | G24-129-TAP | 1.0035 | 0.93555 | -0.067953 |  | 0.95 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | G24-129-TAP | 1.0035 | 0.93555 | -0.067953 |  | 0.95 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | G24-129-TAP | 1.0035 | 0.93555 | -0.067953 |  | 0.95 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | G24-129-TAP | 1.0035 | 0.93555 | -0.067953 |  | 0.95 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | G24-129-TAP | 1.0035 | 0.93555 | -0.067953 |  | 0.95 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | G24-129-TAP | 1.0035 | 0.93555 | -0.067953 |  | 0.95 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | G24-129-TAP | 1.0035 | 0.93555 | -0.067953 |  | 0.95 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | G24-129-TAP | 1.0035 | 0.93555 | -0.067953 |  | 0.95 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | G24-129-TAP | 1.0035 | 0.93555 | -0.067953 |  | 0.95 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | G24-129-TAP | 1.0035 | 0.93555 | -0.067953 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | G24-129-TAP | 1.0035 | 0.93555 | -0.067953 |  | 0.95 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | G24-129-TAP | 1.0035 | 0.93555 | -0.067953 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | G24-129-TAP | 1.0035 | 0.93555 | -0.067953 |  | 0.95 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | G24-129-TAP | 1.0035 | 0.93555 | -0.067953 |  | 0.95 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | G24-129-TAP | 1.0035 | 0.93555 | -0.067953 |  | 0.95 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | G24-129-TAP | 1.0035 | 0.93555 | -0.067953 |  | 0.95 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | G24-129-TAP | 1.0035 | 0.93555 | -0.067953 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | G24-129-TAP | 1.0035 | 0.93555 | -0.067953 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | G24-129-TAP | 1.0035 | 0.93555 | -0.067953 |  | 0.95 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | G24-129-TAP | 1.0035 | 0.93555 | -0.067953 |  | 0.95 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | G24-129-TAP | 1.0035 | 0.93555 | -0.067953 |  | 0.95 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | G24-129-TAP | 1.0035 | 0.93555 | -0.067953 |  | 0.95 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | G24-129-TAP | 1.0035 | 0.93555 | -0.067953 |  | 0.95 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | G24-129-TAP | 1.0035 | 0.93555 | -0.067953 |  | 0.95 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | G24-276-TAP | 0.97119 | 0.93543 | -0.035757 |  | 0.95 | 1.05 | 0.039728 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | G24-276-TAP | 0.97119 | 0.93543 | -0.035757 |  | 0.95 | 1.05 | 0.040762 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | G24-276-TAP | 0.97119 | 0.93543 | -0.035757 |  | 0.95 | 1.05 | 0.030778 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | G24-276-TAP | 0.97119 | 0.93543 | -0.035757 |  | 0.95 | 1.05 | 0.034227 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | G24-276-TAP | 0.97119 | 0.93543 | -0.035757 |  | 0.95 | 1.05 | 0.037164 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | G24-276-TAP | 0.97119 | 0.93543 | -0.035757 |  | 0.95 | 1.05 | 0.031937 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | G24-276-TAP | 0.97119 | 0.93543 | -0.035757 |  | 0.95 | 1.05 | 0.03782 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | G24-276-TAP | 0.97119 | 0.93543 | -0.035757 |  | 0.95 | 1.05 | 0.036407 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | G24-276-TAP | 0.97119 | 0.93543 | -0.035757 |  | 0.95 | 1.05 | 0.053181 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | G24-276-TAP | 0.97119 | 0.93543 | -0.035757 |  | 0.95 | 1.05 | 0.036407 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | G24-276-TAP | 0.97119 | 0.93543 | -0.035757 |  | 0.95 | 1.05 | 0.037418 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | G24-276-TAP | 0.97119 | 0.93543 | -0.035757 |  | 0.95 | 1.05 | 0.037355 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | G24-276-TAP | 0.97119 | 0.93543 | -0.035757 |  | 0.95 | 1.05 | 0.032533 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | G24-276-TAP | 0.97119 | 0.93543 | -0.035757 |  | 0.95 | 1.05 | 0.031326 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | G24-276-TAP | 0.97119 | 0.93543 | -0.035757 |  | 0.95 | 1.05 | 0.035094 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | G24-276-TAP | 0.97119 | 0.93543 | -0.035757 |  | 0.95 | 1.05 | 0.031652 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | G24-276-TAP | 0.97119 | 0.93543 | -0.035757 |  | 0.95 | 1.05 | 0.031104 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | G24-276-TAP | 0.97119 | 0.93543 | -0.035757 |  | 0.95 | 1.05 | 0.033175 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | G24-276-TAP | 0.97119 | 0.93543 | -0.035757 |  | 0.95 | 1.05 | 0.034843 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | G24-276-TAP | 0.96785 | 0.9307 | -0.037148 |  | 0.95 | 1.05 | 0.036307 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | G24-276-TAP | 0.96785 | 0.9307 | -0.037148 |  | 0.95 | 1.05 | 0.052743 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | G24-276-TAP | 0.96785 | 0.9307 | -0.037148 |  | 0.95 | 1.05 | 0.039345 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | G24-276-TAP | 0.96785 | 0.9307 | -0.037148 |  | 0.95 | 1.05 | 0.031366 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | G24-276-TAP | 0.96785 | 0.9307 | -0.037148 |  | 0.95 | 1.05 | 0.041888 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | G24-276-TAP | 0.96785 | 0.9307 | -0.037148 |  | 0.95 | 1.05 | 0.038797 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | G24-276-TAP | 0.96785 | 0.9307 | -0.037148 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | G24-276-TAP | 0.96785 | 0.9307 | -0.037148 |  | 0.95 | 1.05 | 0.067346 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | G24-276-TAP | 0.96785 | 0.9307 | -0.037148 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | G24-276-TAP | 0.96785 | 0.9307 | -0.037148 |  | 0.95 | 1.05 | 0.030851 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | G24-276-TAP | 0.96785 | 0.9307 | -0.037148 |  | 0.95 | 1.05 | 0.032161 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | G24-276-TAP | 0.96785 | 0.9307 | -0.037148 |  | 0.95 | 1.05 | 0.04067 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | G24-276-TAP | 0.96785 | 0.9307 | -0.037148 |  | 0.95 | 1.05 | 0.040569 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | G24-276-TAP | 0.96785 | 0.9307 | -0.037148 |  | 0.95 | 1.05 | 0.03086 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | G24-276-TAP | 0.96785 | 0.9307 | -0.037148 |  | 0.95 | 1.05 | 0.033223 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | G24-276-TAP | 0.96785 | 0.9307 | -0.037148 |  | 0.95 | 1.05 | 0.033733 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | G24-276-TAP | 0.97263 | 0.92971 | -0.042924 |  | 0.95 | 1.05 | 0.036307 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | G24-276-TAP | 0.97263 | 0.92971 | -0.042924 |  | 0.95 | 1.05 | 0.052743 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | G24-276-TAP | 0.97263 | 0.92971 | -0.042924 |  | 0.95 | 1.05 | 0.039345 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | G24-276-TAP | 0.97263 | 0.92971 | -0.042924 |  | 0.95 | 1.05 | 0.031366 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | G24-276-TAP | 0.97263 | 0.92971 | -0.042924 |  | 0.95 | 1.05 | 0.041888 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | G24-276-TAP | 0.97263 | 0.92971 | -0.042924 |  | 0.95 | 1.05 | 0.038797 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | G24-276-TAP | 0.97263 | 0.92971 | -0.042924 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | G24-276-TAP | 0.97263 | 0.92971 | -0.042924 |  | 0.95 | 1.05 | 0.067346 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | G24-276-TAP | 0.97263 | 0.92971 | -0.042924 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | G24-276-TAP | 0.97263 | 0.92971 | -0.042924 |  | 0.95 | 1.05 | 0.030851 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | G24-276-TAP | 0.97263 | 0.92971 | -0.042924 |  | 0.95 | 1.05 | 0.032161 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | G24-276-TAP | 0.97263 | 0.92971 | -0.042924 |  | 0.95 | 1.05 | 0.04067 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | G24-276-TAP | 0.97263 | 0.92971 | -0.042924 |  | 0.95 | 1.05 | 0.040569 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | G24-276-TAP | 0.97263 | 0.92971 | -0.042924 |  | 0.95 | 1.05 | 0.03086 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | G24-276-TAP | 0.97263 | 0.92971 | -0.042924 |  | 0.95 | 1.05 | 0.033223 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | G24-276-TAP | 0.97263 | 0.92971 | -0.042924 |  | 0.95 | 1.05 | 0.033733 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | G24-276-TAP | 0.97735 | 0.93344 | -0.043915 |  | 0.95 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | G24-276-TAP | 0.97735 | 0.93344 | -0.043915 |  | 0.95 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | G24-276-TAP | 0.97735 | 0.93344 | -0.043915 |  | 0.95 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | G24-276-TAP | 0.97735 | 0.93344 | -0.043915 |  | 0.95 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | G24-276-TAP | 0.97735 | 0.93344 | -0.043915 |  | 0.95 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | G24-276-TAP | 0.97735 | 0.93344 | -0.043915 |  | 0.95 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | G24-276-TAP | 0.97735 | 0.93344 | -0.043915 |  | 0.95 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | G24-276-TAP | 0.97735 | 0.93344 | -0.043915 |  | 0.95 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | G24-276-TAP | 0.97735 | 0.93344 | -0.043915 |  | 0.95 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | G24-276-TAP | 0.97735 | 0.93344 | -0.043915 |  | 0.95 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | G24-276-TAP | 0.97735 | 0.93344 | -0.043915 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | G24-276-TAP | 0.97735 | 0.93344 | -0.043915 |  | 0.95 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | G24-276-TAP | 0.97735 | 0.93344 | -0.043915 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | G24-276-TAP | 0.97735 | 0.93344 | -0.043915 |  | 0.95 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | G24-276-TAP | 0.97735 | 0.93344 | -0.043915 |  | 0.95 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | G24-276-TAP | 0.97735 | 0.93344 | -0.043915 |  | 0.95 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | G24-276-TAP | 0.97735 | 0.93344 | -0.043915 |  | 0.95 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | G24-276-TAP | 0.97735 | 0.93344 | -0.043915 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | G24-276-TAP | 0.97735 | 0.93344 | -0.043915 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | G24-276-TAP | 0.97735 | 0.93344 | -0.043915 |  | 0.95 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | G24-276-TAP | 0.97735 | 0.93344 | -0.043915 |  | 0.95 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | G24-276-TAP | 0.97735 | 0.93344 | -0.043915 |  | 0.95 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | G24-276-TAP | 0.97735 | 0.93344 | -0.043915 |  | 0.95 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | G24-276-TAP | 0.97735 | 0.93344 | -0.043915 |  | 0.95 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | G24-276-TAP | 0.97735 | 0.93344 | -0.043915 |  | 0.95 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | G24-276-TAP | 0.96999 | 0.93826 | -0.031731 |  | 0.95 | 1.05 | 0.036307 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | G24-276-TAP | 0.96999 | 0.93826 | -0.031731 |  | 0.95 | 1.05 | 0.052743 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | G24-276-TAP | 0.96999 | 0.93826 | -0.031731 |  | 0.95 | 1.05 | 0.039345 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | G24-276-TAP | 0.96999 | 0.93826 | -0.031731 |  | 0.95 | 1.05 | 0.031366 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | G24-276-TAP | 0.96999 | 0.93826 | -0.031731 |  | 0.95 | 1.05 | 0.041888 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | G24-276-TAP | 0.96999 | 0.93826 | -0.031731 |  | 0.95 | 1.05 | 0.038797 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | G24-276-TAP | 0.96999 | 0.93826 | -0.031731 |  | 0.95 | 1.05 | 0.030557 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | G24-276-TAP | 0.96999 | 0.93826 | -0.031731 |  | 0.95 | 1.05 | 0.067346 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | G24-276-TAP | 0.96999 | 0.93826 | -0.031731 |  | 0.95 | 1.05 | 0.030557 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | G24-276-TAP | 0.96999 | 0.93826 | -0.031731 |  | 0.95 | 1.05 | 0.030851 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | G24-276-TAP | 0.96999 | 0.93826 | -0.031731 |  | 0.95 | 1.05 | 0.032161 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | G24-276-TAP | 0.96999 | 0.93826 | -0.031731 |  | 0.95 | 1.05 | 0.04067 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | G24-276-TAP | 0.96999 | 0.93826 | -0.031731 |  | 0.95 | 1.05 | 0.040569 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | G24-276-TAP | 0.96999 | 0.93826 | -0.031731 |  | 0.95 | 1.05 | 0.03086 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | G24-276-TAP | 0.96999 | 0.93826 | -0.031731 |  | 0.95 | 1.05 | 0.033223 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | G24-276-TAP | 0.96999 | 0.93826 | -0.031731 |  | 0.95 | 1.05 | 0.033733 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GARDNER5 | 0.9956 | 0.91947 | -0.076135 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GARDNER5 | 0.9956 | 0.91947 | -0.076135 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GARDNER5 | 0.9956 | 0.91947 | -0.076135 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GARDNER5 | 0.9956 | 0.91947 | -0.076135 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GARDNER5 | 0.9956 | 0.91947 | -0.076135 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | GARDNER5 | 0.9956 | 0.91947 | -0.076135 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GARDNER5 | 0.9956 | 0.91947 | -0.076135 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | GARDNER5 | 0.9956 | 0.91947 | -0.076135 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GARDNER5 | 0.9956 | 0.91947 | -0.076135 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | GARDNER5 | 0.9956 | 0.91947 | -0.076135 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GARDNER5 | 0.9956 | 0.91947 | -0.076135 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GARDNER5 | 0.9956 | 0.91947 | -0.076135 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GARDNER5 | 0.9956 | 0.91947 | -0.076135 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GARDNER5 | 0.9956 | 0.91947 | -0.076135 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GARDNER5 | 0.9956 | 0.91947 | -0.076135 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GARDNER5 | 0.9956 | 0.91947 | -0.076135 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GARDNER5 | 0.9956 | 0.91947 | -0.076135 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | GARDNER5 | 0.9956 | 0.91947 | -0.076135 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | GARDNER5 | 0.9956 | 0.91947 | -0.076135 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GARDNER5 | 0.9956 | 0.91947 | -0.076135 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GARDNER5 | 0.9956 | 0.91947 | -0.076135 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GARDNER5 | 0.9956 | 0.91947 | -0.076135 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GARDNER5 | 0.9956 | 0.91947 | -0.076135 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GARDNER5 | 0.9956 | 0.91947 | -0.076135 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GARDNER5 | 0.9956 | 0.91947 | -0.076135 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GATZ 2 | 0.9829 | 0.92721 | -0.055681 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GATZ 2 | 0.9829 | 0.92721 | -0.055681 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GATZ 2 | 0.9829 | 0.92721 | -0.055681 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GATZ 2 | 0.9829 | 0.92721 | -0.055681 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GATZ 2 | 0.9829 | 0.92721 | -0.055681 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | GATZ 2 | 0.9829 | 0.92721 | -0.055681 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GATZ 2 | 0.9829 | 0.92721 | -0.055681 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | GATZ 2 | 0.9829 | 0.92721 | -0.055681 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GATZ 2 | 0.9829 | 0.92721 | -0.055681 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | GATZ 2 | 0.9829 | 0.92721 | -0.055681 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GATZ 2 | 0.9829 | 0.92721 | -0.055681 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GATZ 2 | 0.9829 | 0.92721 | -0.055681 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GATZ 2 | 0.9829 | 0.92721 | -0.055681 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GATZ 2 | 0.9829 | 0.92721 | -0.055681 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GATZ 2 | 0.9829 | 0.92721 | -0.055681 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GATZ 2 | 0.9829 | 0.92721 | -0.055681 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GATZ 2 | 0.9829 | 0.92721 | -0.055681 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | GATZ 2 | 0.9829 | 0.92721 | -0.055681 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | GATZ 2 | 0.9829 | 0.92721 | -0.055681 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GATZ 2 | 0.9829 | 0.92721 | -0.055681 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GATZ 2 | 0.9829 | 0.92721 | -0.055681 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GATZ 2 | 0.9829 | 0.92721 | -0.055681 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GATZ 2 | 0.9829 | 0.92721 | -0.055681 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GATZ 2 | 0.9829 | 0.92721 | -0.055681 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GATZ 2 | 0.9829 | 0.92721 | -0.055681 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEARY 7 | 1.0031 | 0.9323 | -0.070838 |  | 0.95 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GEARY 7 | 1.0031 | 0.9323 | -0.070838 |  | 0.95 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEARY 7 | 1.0031 | 0.9323 | -0.070838 |  | 0.95 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEARY 7 | 1.0031 | 0.9323 | -0.070838 |  | 0.95 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEARY 7 | 1.0031 | 0.9323 | -0.070838 |  | 0.95 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | GEARY 7 | 1.0031 | 0.9323 | -0.070838 |  | 0.95 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEARY 7 | 1.0031 | 0.9323 | -0.070838 |  | 0.95 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | GEARY 7 | 1.0031 | 0.9323 | -0.070838 |  | 0.95 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEARY 7 | 1.0031 | 0.9323 | -0.070838 |  | 0.95 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | GEARY 7 | 1.0031 | 0.9323 | -0.070838 |  | 0.95 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEARY 7 | 1.0031 | 0.9323 | -0.070838 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEARY 7 | 1.0031 | 0.9323 | -0.070838 |  | 0.95 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEARY 7 | 1.0031 | 0.9323 | -0.070838 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEARY 7 | 1.0031 | 0.9323 | -0.070838 |  | 0.95 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEARY 7 | 1.0031 | 0.9323 | -0.070838 |  | 0.95 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GEARY 7 | 1.0031 | 0.9323 | -0.070838 |  | 0.95 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEARY 7 | 1.0031 | 0.9323 | -0.070838 |  | 0.95 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | GEARY 7 | 1.0031 | 0.9323 | -0.070838 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | GEARY 7 | 1.0031 | 0.9323 | -0.070838 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEARY 7 | 1.0031 | 0.9323 | -0.070838 |  | 0.95 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEARY 7 | 1.0031 | 0.9323 | -0.070838 |  | 0.95 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEARY 7 | 1.0031 | 0.9323 | -0.070838 |  | 0.95 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEARY 7 | 1.0031 | 0.9323 | -0.070838 |  | 0.95 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEARY 7 | 1.0031 | 0.9323 | -0.070838 |  | 0.95 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEARY 7 | 1.0031 | 0.9323 | -0.070838 |  | 0.95 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | GEN-2016-073 | 0.99756 | 0.9372 | -0.060356 |  | 0.95 | 1.05 | 0.075186 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.02 MVAR switched shunt at BUFFALO7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2016-073 | 0.99756 | 0.9372 | -0.060356 |  | 0.95 | 1.05 | 0.031338 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.02 MVAR switched shunt at BUFFALO7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2016-073 | 0.99756 | 0.9372 | -0.060356 |  | 0.95 | 1.05 | 0.031338 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.02 MVAR switched shunt at BUFFALO7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2016-073 | 0.99756 | 0.9372 | -0.060356 |  | 0.95 | 1.05 | 0.031391 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.02 MVAR switched shunt at BUFFALO7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2016-073 | 0.99756 | 0.9372 | -0.060356 |  | 0.95 | 1.05 | 0.034523 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.02 MVAR switched shunt at BUFFALO7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | GEN-2016-073 | 0.99743 | 0.93604 | -0.061393 |  | 0.95 | 1.05 | 0.075186 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2016-073 | 0.99743 | 0.93604 | -0.061393 |  | 0.95 | 1.05 | 0.031338 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2016-073 | 0.99743 | 0.93604 | -0.061393 |  | 0.95 | 1.05 | 0.031338 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2016-073 | 0.99743 | 0.93604 | -0.061393 |  | 0.95 | 1.05 | 0.031391 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2016-073 | 0.99743 | 0.93604 | -0.061393 |  | 0.95 | 1.05 | 0.034523 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2016-073 | 0.99515 | 0.93604 | -0.059111 |  | 0.95 | 1.05 | 0.035768 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | GEN-2016-073 | 0.99515 | 0.93604 | -0.059111 |  | 0.95 | 1.05 | 0.088718 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | GEN-2016-073 | 0.99515 | 0.93604 | -0.059111 |  | 0.95 | 1.05 | 0.031473 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | GEN-2016-073 | 0.99515 | 0.93604 | -0.059111 |  | 0.95 | 1.05 | 0.034941 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2016-073 | 0.99515 | 0.93604 | -0.059111 |  | 0.95 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2016-073 | 0.99515 | 0.93604 | -0.059111 |  | 0.95 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2016-073 | 0.99515 | 0.93604 | -0.059111 |  | 0.95 | 1.05 | 0.049224 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2016-073 | 0.99515 | 0.93604 | -0.059111 |  | 0.95 | 1.05 | 0.038981 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2016-073 | 0.99515 | 0.93604 | -0.059111 |  | 0.95 | 1.05 | 0.040399 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | GEN-2016-073 | 0.99515 | 0.93604 | -0.059111 |  | 0.95 | 1.05 | 0.031912 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEN-2016-073 | 0.99515 | 0.93604 | -0.059111 |  | 0.95 | 1.05 | 0.034127 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2016-073 | 0.99515 | 0.93604 | -0.059111 |  | 0.95 | 1.05 | 0.047318 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2016-073 | 0.99498 | 0.92242 | -0.072562 |  | 0.95 | 1.05 | 0.040439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GEN-2016-073 | 0.99498 | 0.92242 | -0.072562 |  | 0.95 | 1.05 | 0.034853 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2016-073 | 0.99498 | 0.92242 | -0.072562 |  | 0.95 | 1.05 | 0.046783 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2016-073 | 0.99498 | 0.92242 | -0.072562 |  | 0.95 | 1.05 | 0.047615 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2016-073 | 0.99498 | 0.92242 | -0.072562 |  | 0.95 | 1.05 | 0.034938 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | GEN-2016-073 | 0.99498 | 0.92242 | -0.072562 |  | 0.95 | 1.05 | 0.037875 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2016-073 | 0.99498 | 0.92242 | -0.072562 |  | 0.95 | 1.05 | 0.044022 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | GEN-2016-073 | 0.99498 | 0.92242 | -0.072562 |  | 0.95 | 1.05 | 0.030552 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2016-073 | 0.99498 | 0.92242 | -0.072562 |  | 0.95 | 1.05 | 0.038531 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2016-073 | 0.99498 | 0.92242 | -0.072562 |  | 0.95 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2016-073 | 0.99498 | 0.92242 | -0.072562 |  | 0.95 | 1.05 | 0.062491 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2016-073 | 0.99498 | 0.92242 | -0.072562 |  | 0.95 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2016-073 | 0.99498 | 0.92242 | -0.072562 |  | 0.95 | 1.05 | 0.038129 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2016-073 | 0.99498 | 0.92242 | -0.072562 |  | 0.95 | 1.05 | 0.038066 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GEN-2016-073 | 0.99498 | 0.92242 | -0.072562 |  | 0.95 | 1.05 | 0.034955 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2016-073 | 0.99498 | 0.92242 | -0.072562 |  | 0.95 | 1.05 | 0.06281 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2016-073 | 0.99498 | 0.92242 | -0.072562 |  | 0.95 | 1.05 | 0.045309 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2016-073 | 0.99498 | 0.92242 | -0.072562 |  | 0.95 | 1.05 | 0.035805 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2016-073 | 0.99498 | 0.92242 | -0.072562 |  | 0.95 | 1.05 | 0.032364 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEN-2016-073 | 0.99498 | 0.92242 | -0.072562 |  | 0.95 | 1.05 | 0.031815 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2016-073 | 0.99498 | 0.92242 | -0.072562 |  | 0.95 | 1.05 | 0.033886 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2016-073 | 0.99498 | 0.92242 | -0.072562 |  | 0.95 | 1.05 | 0.035554 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2016-073 | 0.99578 | 0.92395 | -0.071822 |  | 0.95 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GEN-2016-073 | 0.99578 | 0.92395 | -0.071822 |  | 0.95 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2016-073 | 0.99578 | 0.92395 | -0.071822 |  | 0.95 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2016-073 | 0.99578 | 0.92395 | -0.071822 |  | 0.95 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2016-073 | 0.99578 | 0.92395 | -0.071822 |  | 0.95 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | GEN-2016-073 | 0.99578 | 0.92395 | -0.071822 |  | 0.95 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2016-073 | 0.99578 | 0.92395 | -0.071822 |  | 0.95 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | GEN-2016-073 | 0.99578 | 0.92395 | -0.071822 |  | 0.95 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2016-073 | 0.99578 | 0.92395 | -0.071822 |  | 0.95 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | GEN-2016-073 | 0.99578 | 0.92395 | -0.071822 |  | 0.95 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2016-073 | 0.99578 | 0.92395 | -0.071822 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2016-073 | 0.99578 | 0.92395 | -0.071822 |  | 0.95 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2016-073 | 0.99578 | 0.92395 | -0.071822 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2016-073 | 0.99578 | 0.92395 | -0.071822 |  | 0.95 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2016-073 | 0.99578 | 0.92395 | -0.071822 |  | 0.95 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GEN-2016-073 | 0.99578 | 0.92395 | -0.071822 |  | 0.95 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2016-073 | 0.99578 | 0.92395 | -0.071822 |  | 0.95 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | GEN-2016-073 | 0.99578 | 0.92395 | -0.071822 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | GEN-2016-073 | 0.99578 | 0.92395 | -0.071822 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2016-073 | 0.99578 | 0.92395 | -0.071822 |  | 0.95 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2016-073 | 0.99578 | 0.92395 | -0.071822 |  | 0.95 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2016-073 | 0.99578 | 0.92395 | -0.071822 |  | 0.95 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEN-2016-073 | 0.99578 | 0.92395 | -0.071822 |  | 0.95 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2016-073 | 0.99578 | 0.92395 | -0.071822 |  | 0.95 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2016-073 | 0.99578 | 0.92395 | -0.071822 |  | 0.95 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | GEN-2016-111 | 0.9887 | 0.92053 | -0.068176 |  | 0.95 | 1.05 | 0.03053 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2016-111 | 0.9887 | 0.92053 | -0.068176 |  | 0.95 | 1.05 | 0.044933 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GEN-2016-111 | 0.9887 | 0.92053 | -0.068176 |  | 0.95 | 1.05 | 0.047811 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2016-111 | 0.9887 | 0.92053 | -0.068176 |  | 0.95 | 1.05 | 0.09719 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2016-111 | 0.9887 | 0.92053 | -0.068176 |  | 0.95 | 1.05 | 0.069376 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2016-111 | 0.9887 | 0.92053 | -0.068176 |  | 0.95 | 1.05 | 0.04277 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2016-111 | 0.9887 | 0.92053 | -0.068176 |  | 0.95 | 1.05 | 0.071112 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | GEN-2016-111 | 0.9887 | 0.92053 | -0.068176 |  | 0.95 | 1.05 | 0.039357 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | GEN-2016-111 | 0.9887 | 0.92053 | -0.068176 |  | 0.95 | 1.05 | 0.04035 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2016-111 | 0.9887 | 0.92053 | -0.068176 |  | 0.95 | 1.05 | 0.052332 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | GEN-2016-111 | 0.9887 | 0.92053 | -0.068176 |  | 0.95 | 1.05 | 0.045944 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2016-111 | 0.9887 | 0.92053 | -0.068176 |  | 0.95 | 1.05 | 0.038178 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2016-111 | 0.9887 | 0.92053 | -0.068176 |  | 0.95 | 1.05 | 0.13469 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | GEN-2016-111 | 0.9887 | 0.92053 | -0.068176 |  | 0.95 | 1.05 | 0.03053 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2016-111 | 0.9887 | 0.92053 | -0.068176 |  | 0.95 | 1.05 | 0.038178 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2016-111 | 0.9887 | 0.92053 | -0.068176 |  | 0.95 | 1.05 | 0.037309 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2016-111 | 0.9887 | 0.92053 | -0.068176 |  | 0.95 | 1.05 | 0.040075 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GEN-2016-111 | 0.9887 | 0.92053 | -0.068176 |  | 0.95 | 1.05 | 0.053764 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2016-111 | 0.9887 | 0.92053 | -0.068176 |  | 0.95 | 1.05 | 0.071762 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | GEN-2016-111 | 0.9887 | 0.92053 | -0.068176 |  | 0.95 | 1.05 | 0.047827 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | GEN-2016-111 | 0.9887 | 0.92053 | -0.068176 |  | 0.95 | 1.05 | 0.047827 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2016-111 | 0.9887 | 0.92053 | -0.068176 |  | 0.95 | 1.05 | 0.070303 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2016-111 | 0.9887 | 0.92053 | -0.068176 |  | 0.95 | 1.05 | 0.040614 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | GEN-2016-111 | 0.9887 | 0.92053 | -0.068176 |  | 0.95 | 1.05 | 0.039729 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2016-111 | 0.9887 | 0.92053 | -0.068176 |  | 0.95 | 1.05 | 0.049662 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEN-2016-111 | 0.9887 | 0.92053 | -0.068176 |  | 0.95 | 1.05 | 0.042332 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2016-111 | 0.9887 | 0.92053 | -0.068176 |  | 0.95 | 1.05 | 0.048722 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2016-111 | 0.9887 | 0.92053 | -0.068176 |  | 0.95 | 1.05 | 0.038156 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | GEN-2016-111 | 0.9887 | 0.92053 | -0.068176 |  | 0.95 | 1.05 | 0.036794 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | GEN-2016-111 | 0.98838 | 0.92539 | -0.062987 |  | 0.95 | 1.05 | 0.075186 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2016-111 | 0.98838 | 0.92539 | -0.062987 |  | 0.95 | 1.05 | 0.031338 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2016-111 | 0.98838 | 0.92539 | -0.062987 |  | 0.95 | 1.05 | 0.031338 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2016-111 | 0.98838 | 0.92539 | -0.062987 |  | 0.95 | 1.05 | 0.031391 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2016-111 | 0.98838 | 0.92539 | -0.062987 |  | 0.95 | 1.05 | 0.034523 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | GEN-2016-111 | 0.98727 | 0.92579 | -0.061476 |  | 0.95 | 1.05 | 0.06238 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2016-111 | 0.98965 | 0.91698 | -0.072669 |  | 0.95 | 1.05 | 0.040439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GEN-2016-111 | 0.98965 | 0.91698 | -0.072669 |  | 0.95 | 1.05 | 0.034853 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2016-111 | 0.98965 | 0.91698 | -0.072669 |  | 0.95 | 1.05 | 0.046783 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2016-111 | 0.98965 | 0.91698 | -0.072669 |  | 0.95 | 1.05 | 0.047615 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2016-111 | 0.98965 | 0.91698 | -0.072669 |  | 0.95 | 1.05 | 0.034938 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | GEN-2016-111 | 0.98965 | 0.91698 | -0.072669 |  | 0.95 | 1.05 | 0.037875 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2016-111 | 0.98965 | 0.91698 | -0.072669 |  | 0.95 | 1.05 | 0.044022 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | GEN-2016-111 | 0.98965 | 0.91698 | -0.072669 |  | 0.95 | 1.05 | 0.030552 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2016-111 | 0.98965 | 0.91698 | -0.072669 |  | 0.95 | 1.05 | 0.038531 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2016-111 | 0.98965 | 0.91698 | -0.072669 |  | 0.95 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2016-111 | 0.98965 | 0.91698 | -0.072669 |  | 0.95 | 1.05 | 0.062491 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2016-111 | 0.98965 | 0.91698 | -0.072669 |  | 0.95 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2016-111 | 0.98965 | 0.91698 | -0.072669 |  | 0.95 | 1.05 | 0.038129 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2016-111 | 0.98965 | 0.91698 | -0.072669 |  | 0.95 | 1.05 | 0.038066 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GEN-2016-111 | 0.98965 | 0.91698 | -0.072669 |  | 0.95 | 1.05 | 0.034955 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2016-111 | 0.98965 | 0.91698 | -0.072669 |  | 0.95 | 1.05 | 0.06281 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2016-111 | 0.98965 | 0.91698 | -0.072669 |  | 0.95 | 1.05 | 0.045309 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2016-111 | 0.98965 | 0.91698 | -0.072669 |  | 0.95 | 1.05 | 0.035805 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2016-111 | 0.98965 | 0.91698 | -0.072669 |  | 0.95 | 1.05 | 0.032364 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEN-2016-111 | 0.98965 | 0.91698 | -0.072669 |  | 0.95 | 1.05 | 0.031815 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2016-111 | 0.98965 | 0.91698 | -0.072669 |  | 0.95 | 1.05 | 0.033886 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2016-111 | 0.98965 | 0.91698 | -0.072669 |  | 0.95 | 1.05 | 0.035554 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2016-111 | 0.9739 | 0.87179 | -0.10212 |  | 0.95 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GEN-2016-111 | 0.9739 | 0.87179 | -0.10212 |  | 0.95 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2016-111 | 0.9739 | 0.87179 | -0.10212 |  | 0.95 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2016-111 | 0.9739 | 0.87179 | -0.10212 |  | 0.95 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2016-111 | 0.9739 | 0.87179 | -0.10212 |  | 0.95 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | GEN-2016-111 | 0.9739 | 0.87179 | -0.10212 |  | 0.95 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2016-111 | 0.9739 | 0.87179 | -0.10212 |  | 0.95 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | GEN-2016-111 | 0.9739 | 0.87179 | -0.10212 |  | 0.95 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2016-111 | 0.9739 | 0.87179 | -0.10212 |  | 0.95 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | GEN-2016-111 | 0.9739 | 0.87179 | -0.10212 |  | 0.95 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2016-111 | 0.9739 | 0.87179 | -0.10212 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2016-111 | 0.9739 | 0.87179 | -0.10212 |  | 0.95 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2016-111 | 0.9739 | 0.87179 | -0.10212 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2016-111 | 0.9739 | 0.87179 | -0.10212 |  | 0.95 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2016-111 | 0.9739 | 0.87179 | -0.10212 |  | 0.95 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GEN-2016-111 | 0.9739 | 0.87179 | -0.10212 |  | 0.95 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2016-111 | 0.9739 | 0.87179 | -0.10212 |  | 0.95 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | GEN-2016-111 | 0.9739 | 0.87179 | -0.10212 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | GEN-2016-111 | 0.9739 | 0.87179 | -0.10212 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2016-111 | 0.9739 | 0.87179 | -0.10212 |  | 0.95 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2016-111 | 0.9739 | 0.87179 | -0.10212 |  | 0.95 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2016-111 | 0.9739 | 0.87179 | -0.10212 |  | 0.95 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEN-2016-111 | 0.9739 | 0.87179 | -0.10212 |  | 0.95 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2016-111 | 0.9739 | 0.87179 | -0.10212 |  | 0.95 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2016-111 | 0.9739 | 0.87179 | -0.10212 |  | 0.95 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2017-022 | 0.96575 | 0.92862 | -0.037133 |  | 0.93 | 1.05 | 0.091967 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GEN-2017-022 | 0.96575 | 0.92862 | -0.037133 |  | 0.93 | 1.05 | 0.033356 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2017-022 | 0.96575 | 0.92862 | -0.037133 |  | 0.93 | 1.05 | 0.044346 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2017-022 | 0.96575 | 0.92862 | -0.037133 |  | 0.93 | 1.05 | 0.058536 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2017-022 | 0.96575 | 0.92862 | -0.037133 |  | 0.93 | 1.05 | 0.059327 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | GEN-2017-022 | 0.96575 | 0.92862 | -0.037133 |  | 0.93 | 1.05 | 0.041874 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | GEN-2017-022 | 0.96575 | 0.92862 | -0.037133 |  | 0.93 | 1.05 | 0.046192 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2017-022 | 0.96575 | 0.92862 | -0.037133 |  | 0.93 | 1.05 | 0.12754 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | GEN-2017-022 | 0.96575 | 0.92862 | -0.037133 |  | 0.93 | 1.05 | 0.047018 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2017-022 | 0.96575 | 0.92862 | -0.037133 |  | 0.93 | 1.05 | 0.056662 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2017-022 | 0.96575 | 0.92862 | -0.037133 |  | 0.93 | 1.05 | 0.056662 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2017-022 | 0.96575 | 0.92862 | -0.037133 |  | 0.93 | 1.05 | 0.056727 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2017-022 | 0.96575 | 0.92862 | -0.037133 |  | 0.93 | 1.05 | 0.074186 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GEN-2017-022 | 0.96575 | 0.92862 | -0.037133 |  | 0.93 | 1.05 | 0.040839 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2017-022 | 0.96575 | 0.92862 | -0.037133 |  | 0.93 | 1.05 | 0.03863 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | GEN-2017-022 | 0.96575 | 0.92862 | -0.037133 |  | 0.93 | 1.05 | 0.042285 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | GEN-2017-022 | 0.96575 | 0.92862 | -0.037133 |  | 0.93 | 1.05 | 0.042285 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2017-022 | 0.96575 | 0.92862 | -0.037133 |  | 0.93 | 1.05 | 0.050204 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2017-022 | 0.96575 | 0.92862 | -0.037133 |  | 0.93 | 1.05 | 0.058005 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | GEN-2017-022 | 0.96575 | 0.92862 | -0.037133 |  | 0.93 | 1.05 | 0.041735 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2017-022 | 0.96575 | 0.92862 | -0.037133 |  | 0.93 | 1.05 | 0.057076 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEN-2017-022 | 0.96575 | 0.92862 | -0.037133 |  | 0.93 | 1.05 | 0.050111 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2017-022 | 0.96575 | 0.92862 | -0.037133 |  | 0.93 | 1.05 | 0.06491 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2017-022 | 0.96575 | 0.92862 | -0.037133 |  | 0.93 | 1.05 | 0.051051 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | GEN-2017-022 | 0.96575 | 0.92862 | -0.037133 |  | 0.93 | 1.05 | 0.036279 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2017-022 | 0.97153 | 0.92911 | -0.042424 |  | 0.93 | 1.05 | 0.035768 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | GEN-2017-022 | 0.97153 | 0.92911 | -0.042424 |  | 0.93 | 1.05 | 0.088718 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | GEN-2017-022 | 0.97153 | 0.92911 | -0.042424 |  | 0.93 | 1.05 | 0.031473 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | GEN-2017-022 | 0.97153 | 0.92911 | -0.042424 |  | 0.93 | 1.05 | 0.034941 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2017-022 | 0.97153 | 0.92911 | -0.042424 |  | 0.93 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2017-022 | 0.97153 | 0.92911 | -0.042424 |  | 0.93 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2017-022 | 0.97153 | 0.92911 | -0.042424 |  | 0.93 | 1.05 | 0.049224 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2017-022 | 0.97153 | 0.92911 | -0.042424 |  | 0.93 | 1.05 | 0.038981 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2017-022 | 0.97153 | 0.92911 | -0.042424 |  | 0.93 | 1.05 | 0.040399 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | GEN-2017-022 | 0.97153 | 0.92911 | -0.042424 |  | 0.93 | 1.05 | 0.031912 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEN-2017-022 | 0.97153 | 0.92911 | -0.042424 |  | 0.93 | 1.05 | 0.034127 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2017-022 | 0.97153 | 0.92911 | -0.042424 |  | 0.93 | 1.05 | 0.047318 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2017-022 | 0.96198 | 0.91743 | -0.044556 |  | 0.93 | 1.05 | 0.040439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GEN-2017-022 | 0.96198 | 0.91743 | -0.044556 |  | 0.93 | 1.05 | 0.034853 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2017-022 | 0.96198 | 0.91743 | -0.044556 |  | 0.93 | 1.05 | 0.046783 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2017-022 | 0.96198 | 0.91743 | -0.044556 |  | 0.93 | 1.05 | 0.047615 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2017-022 | 0.96198 | 0.91743 | -0.044556 |  | 0.93 | 1.05 | 0.034938 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | GEN-2017-022 | 0.96198 | 0.91743 | -0.044556 |  | 0.93 | 1.05 | 0.037875 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2017-022 | 0.96198 | 0.91743 | -0.044556 |  | 0.93 | 1.05 | 0.044022 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | GEN-2017-022 | 0.96198 | 0.91743 | -0.044556 |  | 0.93 | 1.05 | 0.030552 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2017-022 | 0.96198 | 0.91743 | -0.044556 |  | 0.93 | 1.05 | 0.038531 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2017-022 | 0.96198 | 0.91743 | -0.044556 |  | 0.93 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2017-022 | 0.96198 | 0.91743 | -0.044556 |  | 0.93 | 1.05 | 0.062491 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2017-022 | 0.96198 | 0.91743 | -0.044556 |  | 0.93 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2017-022 | 0.96198 | 0.91743 | -0.044556 |  | 0.93 | 1.05 | 0.038129 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2017-022 | 0.96198 | 0.91743 | -0.044556 |  | 0.93 | 1.05 | 0.038066 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GEN-2017-022 | 0.96198 | 0.91743 | -0.044556 |  | 0.93 | 1.05 | 0.034955 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2017-022 | 0.96198 | 0.91743 | -0.044556 |  | 0.93 | 1.05 | 0.06281 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2017-022 | 0.96198 | 0.91743 | -0.044556 |  | 0.93 | 1.05 | 0.045309 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2017-022 | 0.96198 | 0.91743 | -0.044556 |  | 0.93 | 1.05 | 0.035805 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2017-022 | 0.96198 | 0.91743 | -0.044556 |  | 0.93 | 1.05 | 0.032364 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEN-2017-022 | 0.96198 | 0.91743 | -0.044556 |  | 0.93 | 1.05 | 0.031815 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2017-022 | 0.96198 | 0.91743 | -0.044556 |  | 0.93 | 1.05 | 0.033886 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2017-022 | 0.96198 | 0.91743 | -0.044556 |  | 0.93 | 1.05 | 0.035554 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2017-022 | 0.96705 | 0.9052 | -0.061849 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GEN-2017-022 | 0.96705 | 0.9052 | -0.061849 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2017-022 | 0.96705 | 0.9052 | -0.061849 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2017-022 | 0.96705 | 0.9052 | -0.061849 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2017-022 | 0.96705 | 0.9052 | -0.061849 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | GEN-2017-022 | 0.96705 | 0.9052 | -0.061849 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2017-022 | 0.96705 | 0.9052 | -0.061849 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | GEN-2017-022 | 0.96705 | 0.9052 | -0.061849 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2017-022 | 0.96705 | 0.9052 | -0.061849 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | GEN-2017-022 | 0.96705 | 0.9052 | -0.061849 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2017-022 | 0.96705 | 0.9052 | -0.061849 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2017-022 | 0.96705 | 0.9052 | -0.061849 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2017-022 | 0.96705 | 0.9052 | -0.061849 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2017-022 | 0.96705 | 0.9052 | -0.061849 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2017-022 | 0.96705 | 0.9052 | -0.061849 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GEN-2017-022 | 0.96705 | 0.9052 | -0.061849 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2017-022 | 0.96705 | 0.9052 | -0.061849 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | GEN-2017-022 | 0.96705 | 0.9052 | -0.061849 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | GEN-2017-022 | 0.96705 | 0.9052 | -0.061849 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2017-022 | 0.96705 | 0.9052 | -0.061849 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2017-022 | 0.96705 | 0.9052 | -0.061849 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2017-022 | 0.96705 | 0.9052 | -0.061849 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEN-2017-022 | 0.96705 | 0.9052 | -0.061849 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2017-022 | 0.96705 | 0.9052 | -0.061849 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2017-022 | 0.96705 | 0.9052 | -0.061849 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2017-074 | 0.9406 | 0.91545 | -0.025157 |  | 0.92 | 1.05 | 0.038424 | Single 509752 INOLATP4 138 509790 CATOOSA4 138 1 | Add 57 MVAR switched shunt at GUAVA 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2017-077 | 0.9054 | 0.87785 | -0.027546 |  | 0.92 | 1.05 | 0.038424 | Single 509752 INOLATP4 138 509790 CATOOSA4 138 1 | Add 57 MVAR switched shunt at GUAVA 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2017-077 | 0.91664 | 0.8908 | -0.025842 |  | 0.92 | 1.05 | 0.038424 | Single 509752 INOLATP4 138 510442 GUAVA4 138 1 | Add 57 MVAR switched shunt at GUAVA 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2017-086 | 0.99716 | 0.91989 | -0.077267 |  | 0.95 | 1.05 | 0.091967 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GEN-2017-086 | 0.99716 | 0.91989 | -0.077267 |  | 0.95 | 1.05 | 0.033356 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2017-086 | 0.99716 | 0.91989 | -0.077267 |  | 0.95 | 1.05 | 0.044346 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2017-086 | 0.99716 | 0.91989 | -0.077267 |  | 0.95 | 1.05 | 0.058536 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2017-086 | 0.99716 | 0.91989 | -0.077267 |  | 0.95 | 1.05 | 0.059327 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | GEN-2017-086 | 0.99716 | 0.91989 | -0.077267 |  | 0.95 | 1.05 | 0.041874 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | GEN-2017-086 | 0.99716 | 0.91989 | -0.077267 |  | 0.95 | 1.05 | 0.046192 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2017-086 | 0.99716 | 0.91989 | -0.077267 |  | 0.95 | 1.05 | 0.12754 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | GEN-2017-086 | 0.99716 | 0.91989 | -0.077267 |  | 0.95 | 1.05 | 0.047018 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2017-086 | 0.99716 | 0.91989 | -0.077267 |  | 0.95 | 1.05 | 0.056662 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2017-086 | 0.99716 | 0.91989 | -0.077267 |  | 0.95 | 1.05 | 0.056662 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2017-086 | 0.99716 | 0.91989 | -0.077267 |  | 0.95 | 1.05 | 0.056727 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2017-086 | 0.99716 | 0.91989 | -0.077267 |  | 0.95 | 1.05 | 0.074186 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GEN-2017-086 | 0.99716 | 0.91989 | -0.077267 |  | 0.95 | 1.05 | 0.040839 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2017-086 | 0.99716 | 0.91989 | -0.077267 |  | 0.95 | 1.05 | 0.03863 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | GEN-2017-086 | 0.99716 | 0.91989 | -0.077267 |  | 0.95 | 1.05 | 0.042285 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | GEN-2017-086 | 0.99716 | 0.91989 | -0.077267 |  | 0.95 | 1.05 | 0.042285 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2017-086 | 0.99716 | 0.91989 | -0.077267 |  | 0.95 | 1.05 | 0.050204 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2017-086 | 0.99716 | 0.91989 | -0.077267 |  | 0.95 | 1.05 | 0.058005 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | GEN-2017-086 | 0.99716 | 0.91989 | -0.077267 |  | 0.95 | 1.05 | 0.041735 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2017-086 | 0.99716 | 0.91989 | -0.077267 |  | 0.95 | 1.05 | 0.057076 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEN-2017-086 | 0.99716 | 0.91989 | -0.077267 |  | 0.95 | 1.05 | 0.050111 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2017-086 | 0.99716 | 0.91989 | -0.077267 |  | 0.95 | 1.05 | 0.06491 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2017-086 | 0.99716 | 0.91989 | -0.077267 |  | 0.95 | 1.05 | 0.051051 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | GEN-2017-086 | 0.99716 | 0.91989 | -0.077267 |  | 0.95 | 1.05 | 0.036279 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2017-086 | 0.99977 | 0.94727 | -0.052502 |  | 0.95 | 1.05 | 0.091967 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GEN-2017-086 | 0.99977 | 0.94727 | -0.052502 |  | 0.95 | 1.05 | 0.033356 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2017-086 | 0.99977 | 0.94727 | -0.052502 |  | 0.95 | 1.05 | 0.044346 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2017-086 | 0.99977 | 0.94727 | -0.052502 |  | 0.95 | 1.05 | 0.058536 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2017-086 | 0.99977 | 0.94727 | -0.052502 |  | 0.95 | 1.05 | 0.059327 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | GEN-2017-086 | 0.99977 | 0.94727 | -0.052502 |  | 0.95 | 1.05 | 0.041874 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | GEN-2017-086 | 0.99977 | 0.94727 | -0.052502 |  | 0.95 | 1.05 | 0.046192 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2017-086 | 0.99977 | 0.94727 | -0.052502 |  | 0.95 | 1.05 | 0.12754 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | GEN-2017-086 | 0.99977 | 0.94727 | -0.052502 |  | 0.95 | 1.05 | 0.047018 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2017-086 | 0.99977 | 0.94727 | -0.052502 |  | 0.95 | 1.05 | 0.056662 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2017-086 | 0.99977 | 0.94727 | -0.052502 |  | 0.95 | 1.05 | 0.056662 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2017-086 | 0.99977 | 0.94727 | -0.052502 |  | 0.95 | 1.05 | 0.056727 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2017-086 | 0.99977 | 0.94727 | -0.052502 |  | 0.95 | 1.05 | 0.074186 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GEN-2017-086 | 0.99977 | 0.94727 | -0.052502 |  | 0.95 | 1.05 | 0.040839 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2017-086 | 0.99977 | 0.94727 | -0.052502 |  | 0.95 | 1.05 | 0.03863 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | GEN-2017-086 | 0.99977 | 0.94727 | -0.052502 |  | 0.95 | 1.05 | 0.042285 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | GEN-2017-086 | 0.99977 | 0.94727 | -0.052502 |  | 0.95 | 1.05 | 0.042285 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2017-086 | 0.99977 | 0.94727 | -0.052502 |  | 0.95 | 1.05 | 0.050204 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2017-086 | 0.99977 | 0.94727 | -0.052502 |  | 0.95 | 1.05 | 0.058005 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | GEN-2017-086 | 0.99977 | 0.94727 | -0.052502 |  | 0.95 | 1.05 | 0.041735 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2017-086 | 0.99977 | 0.94727 | -0.052502 |  | 0.95 | 1.05 | 0.057076 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEN-2017-086 | 0.99977 | 0.94727 | -0.052502 |  | 0.95 | 1.05 | 0.050111 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2017-086 | 0.99977 | 0.94727 | -0.052502 |  | 0.95 | 1.05 | 0.06491 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2017-086 | 0.99977 | 0.94727 | -0.052502 |  | 0.95 | 1.05 | 0.051051 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | GEN-2017-086 | 0.99977 | 0.94727 | -0.052502 |  | 0.95 | 1.05 | 0.036279 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2017-086 | 0.99974 | 0.9141 | -0.085635 |  | 0.95 | 1.05 | 0.035768 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | GEN-2017-086 | 0.99974 | 0.9141 | -0.085635 |  | 0.95 | 1.05 | 0.088718 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | GEN-2017-086 | 0.99974 | 0.9141 | -0.085635 |  | 0.95 | 1.05 | 0.031473 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | GEN-2017-086 | 0.99974 | 0.9141 | -0.085635 |  | 0.95 | 1.05 | 0.034941 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2017-086 | 0.99974 | 0.9141 | -0.085635 |  | 0.95 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2017-086 | 0.99974 | 0.9141 | -0.085635 |  | 0.95 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2017-086 | 0.99974 | 0.9141 | -0.085635 |  | 0.95 | 1.05 | 0.049224 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2017-086 | 0.99974 | 0.9141 | -0.085635 |  | 0.95 | 1.05 | 0.038981 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2017-086 | 0.99974 | 0.9141 | -0.085635 |  | 0.95 | 1.05 | 0.040399 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | GEN-2017-086 | 0.99974 | 0.9141 | -0.085635 |  | 0.95 | 1.05 | 0.031912 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEN-2017-086 | 0.99974 | 0.9141 | -0.085635 |  | 0.95 | 1.05 | 0.034127 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2017-086 | 0.99974 | 0.9141 | -0.085635 |  | 0.95 | 1.05 | 0.047318 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2017-086 | 1.0019 | 0.93737 | -0.064549 |  | 0.95 | 1.05 | 0.040439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GEN-2017-086 | 1.0019 | 0.93737 | -0.064549 |  | 0.95 | 1.05 | 0.034853 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2017-086 | 1.0019 | 0.93737 | -0.064549 |  | 0.95 | 1.05 | 0.046783 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2017-086 | 1.0019 | 0.93737 | -0.064549 |  | 0.95 | 1.05 | 0.047615 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2017-086 | 1.0019 | 0.93737 | -0.064549 |  | 0.95 | 1.05 | 0.034938 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | GEN-2017-086 | 1.0019 | 0.93737 | -0.064549 |  | 0.95 | 1.05 | 0.037875 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2017-086 | 1.0019 | 0.93737 | -0.064549 |  | 0.95 | 1.05 | 0.044022 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | GEN-2017-086 | 1.0019 | 0.93737 | -0.064549 |  | 0.95 | 1.05 | 0.030552 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2017-086 | 1.0019 | 0.93737 | -0.064549 |  | 0.95 | 1.05 | 0.038531 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2017-086 | 1.0019 | 0.93737 | -0.064549 |  | 0.95 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2017-086 | 1.0019 | 0.93737 | -0.064549 |  | 0.95 | 1.05 | 0.062491 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2017-086 | 1.0019 | 0.93737 | -0.064549 |  | 0.95 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2017-086 | 1.0019 | 0.93737 | -0.064549 |  | 0.95 | 1.05 | 0.038129 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2017-086 | 1.0019 | 0.93737 | -0.064549 |  | 0.95 | 1.05 | 0.038066 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GEN-2017-086 | 1.0019 | 0.93737 | -0.064549 |  | 0.95 | 1.05 | 0.034955 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2017-086 | 1.0019 | 0.93737 | -0.064549 |  | 0.95 | 1.05 | 0.06281 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2017-086 | 1.0019 | 0.93737 | -0.064549 |  | 0.95 | 1.05 | 0.045309 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2017-086 | 1.0019 | 0.93737 | -0.064549 |  | 0.95 | 1.05 | 0.035805 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2017-086 | 1.0019 | 0.93737 | -0.064549 |  | 0.95 | 1.05 | 0.032364 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEN-2017-086 | 1.0019 | 0.93737 | -0.064549 |  | 0.95 | 1.05 | 0.031815 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2017-086 | 1.0019 | 0.93737 | -0.064549 |  | 0.95 | 1.05 | 0.033886 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2017-086 | 1.0019 | 0.93737 | -0.064549 |  | 0.95 | 1.05 | 0.035554 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2017-086 | 1.0027 | 0.94906 | -0.053599 |  | 0.95 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GEN-2017-086 | 1.0027 | 0.94906 | -0.053599 |  | 0.95 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2017-086 | 1.0027 | 0.94906 | -0.053599 |  | 0.95 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2017-086 | 1.0027 | 0.94906 | -0.053599 |  | 0.95 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2017-086 | 1.0027 | 0.94906 | -0.053599 |  | 0.95 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | GEN-2017-086 | 1.0027 | 0.94906 | -0.053599 |  | 0.95 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2017-086 | 1.0027 | 0.94906 | -0.053599 |  | 0.95 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | GEN-2017-086 | 1.0027 | 0.94906 | -0.053599 |  | 0.95 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2017-086 | 1.0027 | 0.94906 | -0.053599 |  | 0.95 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | GEN-2017-086 | 1.0027 | 0.94906 | -0.053599 |  | 0.95 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2017-086 | 1.0027 | 0.94906 | -0.053599 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2017-086 | 1.0027 | 0.94906 | -0.053599 |  | 0.95 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2017-086 | 1.0027 | 0.94906 | -0.053599 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2017-086 | 1.0027 | 0.94906 | -0.053599 |  | 0.95 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2017-086 | 1.0027 | 0.94906 | -0.053599 |  | 0.95 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GEN-2017-086 | 1.0027 | 0.94906 | -0.053599 |  | 0.95 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2017-086 | 1.0027 | 0.94906 | -0.053599 |  | 0.95 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | GEN-2017-086 | 1.0027 | 0.94906 | -0.053599 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | GEN-2017-086 | 1.0027 | 0.94906 | -0.053599 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2017-086 | 1.0027 | 0.94906 | -0.053599 |  | 0.95 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2017-086 | 1.0027 | 0.94906 | -0.053599 |  | 0.95 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2017-086 | 1.0027 | 0.94906 | -0.053599 |  | 0.95 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEN-2017-086 | 1.0027 | 0.94906 | -0.053599 |  | 0.95 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2017-086 | 1.0027 | 0.94906 | -0.053599 |  | 0.95 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2017-086 | 1.0027 | 0.94906 | -0.053599 |  | 0.95 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2017-108 | 0.99286 | 0.91474 | -0.078112 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GEN-2017-108 | 0.99286 | 0.91474 | -0.078112 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2017-108 | 0.99286 | 0.91474 | -0.078112 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2017-108 | 0.99286 | 0.91474 | -0.078112 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2017-108 | 0.99286 | 0.91474 | -0.078112 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | GEN-2017-108 | 0.99286 | 0.91474 | -0.078112 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2017-108 | 0.99286 | 0.91474 | -0.078112 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | GEN-2017-108 | 0.99286 | 0.91474 | -0.078112 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2017-108 | 0.99286 | 0.91474 | -0.078112 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | GEN-2017-108 | 0.99286 | 0.91474 | -0.078112 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2017-108 | 0.99286 | 0.91474 | -0.078112 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2017-108 | 0.99286 | 0.91474 | -0.078112 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2017-108 | 0.99286 | 0.91474 | -0.078112 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2017-108 | 0.99286 | 0.91474 | -0.078112 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2017-108 | 0.99286 | 0.91474 | -0.078112 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GEN-2017-108 | 0.99286 | 0.91474 | -0.078112 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2017-108 | 0.99286 | 0.91474 | -0.078112 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | GEN-2017-108 | 0.99286 | 0.91474 | -0.078112 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | GEN-2017-108 | 0.99286 | 0.91474 | -0.078112 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2017-108 | 0.99286 | 0.91474 | -0.078112 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2017-108 | 0.99286 | 0.91474 | -0.078112 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2017-108 | 0.99286 | 0.91474 | -0.078112 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEN-2017-108 | 0.99286 | 0.91474 | -0.078112 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2017-108 | 0.99286 | 0.91474 | -0.078112 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2017-108 | 0.99286 | 0.91474 | -0.078112 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2017-195 | 0.9654 | 0.9201 | -0.045301 |  | 0.95 | 1.05 | 0.036307 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2017-195 | 0.9654 | 0.9201 | -0.045301 |  | 0.95 | 1.05 | 0.052743 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2017-195 | 0.9654 | 0.9201 | -0.045301 |  | 0.95 | 1.05 | 0.039345 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2017-195 | 0.9654 | 0.9201 | -0.045301 |  | 0.95 | 1.05 | 0.031366 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2017-195 | 0.9654 | 0.9201 | -0.045301 |  | 0.95 | 1.05 | 0.041888 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2017-195 | 0.9654 | 0.9201 | -0.045301 |  | 0.95 | 1.05 | 0.038797 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2017-195 | 0.9654 | 0.9201 | -0.045301 |  | 0.95 | 1.05 | 0.030557 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2017-195 | 0.9654 | 0.9201 | -0.045301 |  | 0.95 | 1.05 | 0.067346 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2017-195 | 0.9654 | 0.9201 | -0.045301 |  | 0.95 | 1.05 | 0.030557 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2017-195 | 0.9654 | 0.9201 | -0.045301 |  | 0.95 | 1.05 | 0.030851 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2017-195 | 0.9654 | 0.9201 | -0.045301 |  | 0.95 | 1.05 | 0.032161 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2017-195 | 0.9654 | 0.9201 | -0.045301 |  | 0.95 | 1.05 | 0.04067 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2017-195 | 0.9654 | 0.9201 | -0.045301 |  | 0.95 | 1.05 | 0.040569 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2017-195 | 0.9654 | 0.9201 | -0.045301 |  | 0.95 | 1.05 | 0.03086 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2017-195 | 0.9654 | 0.9201 | -0.045301 |  | 0.95 | 1.05 | 0.033223 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2017-195 | 0.9654 | 0.9201 | -0.045301 |  | 0.95 | 1.05 | 0.033733 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2017-195 | 0.95804 | 0.90477 | -0.053273 |  | 0.95 | 1.05 | 0.036307 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2017-195 | 0.95804 | 0.90477 | -0.053273 |  | 0.95 | 1.05 | 0.052743 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2017-195 | 0.95804 | 0.90477 | -0.053273 |  | 0.95 | 1.05 | 0.039345 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2017-195 | 0.95804 | 0.90477 | -0.053273 |  | 0.95 | 1.05 | 0.031366 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2017-195 | 0.95804 | 0.90477 | -0.053273 |  | 0.95 | 1.05 | 0.041888 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2017-195 | 0.95804 | 0.90477 | -0.053273 |  | 0.95 | 1.05 | 0.038797 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2017-195 | 0.95804 | 0.90477 | -0.053273 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2017-195 | 0.95804 | 0.90477 | -0.053273 |  | 0.95 | 1.05 | 0.067346 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2017-195 | 0.95804 | 0.90477 | -0.053273 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2017-195 | 0.95804 | 0.90477 | -0.053273 |  | 0.95 | 1.05 | 0.030851 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2017-195 | 0.95804 | 0.90477 | -0.053273 |  | 0.95 | 1.05 | 0.032161 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2017-195 | 0.95804 | 0.90477 | -0.053273 |  | 0.95 | 1.05 | 0.04067 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2017-195 | 0.95804 | 0.90477 | -0.053273 |  | 0.95 | 1.05 | 0.040569 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2017-195 | 0.95804 | 0.90477 | -0.053273 |  | 0.95 | 1.05 | 0.03086 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2017-195 | 0.95804 | 0.90477 | -0.053273 |  | 0.95 | 1.05 | 0.033223 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2017-195 | 0.95804 | 0.90477 | -0.053273 |  | 0.95 | 1.05 | 0.033733 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2017-195 | 0.97166 | 0.90762 | -0.064042 |  | 0.95 | 1.05 | 0.036307 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2017-195 | 0.97166 | 0.90762 | -0.064042 |  | 0.95 | 1.05 | 0.052743 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2017-195 | 0.97166 | 0.90762 | -0.064042 |  | 0.95 | 1.05 | 0.039345 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2017-195 | 0.97166 | 0.90762 | -0.064042 |  | 0.95 | 1.05 | 0.031366 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2017-195 | 0.97166 | 0.90762 | -0.064042 |  | 0.95 | 1.05 | 0.041888 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2017-195 | 0.97166 | 0.90762 | -0.064042 |  | 0.95 | 1.05 | 0.038797 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2017-195 | 0.97166 | 0.90762 | -0.064042 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2017-195 | 0.97166 | 0.90762 | -0.064042 |  | 0.95 | 1.05 | 0.067346 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2017-195 | 0.97166 | 0.90762 | -0.064042 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2017-195 | 0.97166 | 0.90762 | -0.064042 |  | 0.95 | 1.05 | 0.030851 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2017-195 | 0.97166 | 0.90762 | -0.064042 |  | 0.95 | 1.05 | 0.032161 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2017-195 | 0.97166 | 0.90762 | -0.064042 |  | 0.95 | 1.05 | 0.04067 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2017-195 | 0.97166 | 0.90762 | -0.064042 |  | 0.95 | 1.05 | 0.040569 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2017-195 | 0.97166 | 0.90762 | -0.064042 |  | 0.95 | 1.05 | 0.03086 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2017-195 | 0.97166 | 0.90762 | -0.064042 |  | 0.95 | 1.05 | 0.033223 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2017-195 | 0.97166 | 0.90762 | -0.064042 |  | 0.95 | 1.05 | 0.033733 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2017-195 | 0.97927 | 0.89179 | -0.087477 |  | 0.95 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GEN-2017-195 | 0.97927 | 0.89179 | -0.087477 |  | 0.95 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2017-195 | 0.97927 | 0.89179 | -0.087477 |  | 0.95 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2017-195 | 0.97927 | 0.89179 | -0.087477 |  | 0.95 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2017-195 | 0.97927 | 0.89179 | -0.087477 |  | 0.95 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | GEN-2017-195 | 0.97927 | 0.89179 | -0.087477 |  | 0.95 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2017-195 | 0.97927 | 0.89179 | -0.087477 |  | 0.95 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | GEN-2017-195 | 0.97927 | 0.89179 | -0.087477 |  | 0.95 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2017-195 | 0.97927 | 0.89179 | -0.087477 |  | 0.95 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | GEN-2017-195 | 0.97927 | 0.89179 | -0.087477 |  | 0.95 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2017-195 | 0.97927 | 0.89179 | -0.087477 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2017-195 | 0.97927 | 0.89179 | -0.087477 |  | 0.95 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2017-195 | 0.97927 | 0.89179 | -0.087477 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2017-195 | 0.97927 | 0.89179 | -0.087477 |  | 0.95 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2017-195 | 0.97927 | 0.89179 | -0.087477 |  | 0.95 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GEN-2017-195 | 0.97927 | 0.89179 | -0.087477 |  | 0.95 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2017-195 | 0.97927 | 0.89179 | -0.087477 |  | 0.95 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | GEN-2017-195 | 0.97927 | 0.89179 | -0.087477 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | GEN-2017-195 | 0.97927 | 0.89179 | -0.087477 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2017-195 | 0.97927 | 0.89179 | -0.087477 |  | 0.95 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2017-195 | 0.97927 | 0.89179 | -0.087477 |  | 0.95 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2017-195 | 0.97927 | 0.89179 | -0.087477 |  | 0.95 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEN-2017-195 | 0.97927 | 0.89179 | -0.087477 |  | 0.95 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2017-195 | 0.97927 | 0.89179 | -0.087477 |  | 0.95 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2017-195 | 0.97927 | 0.89179 | -0.087477 |  | 0.95 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2017-195 | 0.96445 | 0.91831 | -0.046147 |  | 0.95 | 1.05 | 0.036307 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2017-195 | 0.96445 | 0.91831 | -0.046147 |  | 0.95 | 1.05 | 0.052743 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2017-195 | 0.96445 | 0.91831 | -0.046147 |  | 0.95 | 1.05 | 0.039345 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2017-195 | 0.96445 | 0.91831 | -0.046147 |  | 0.95 | 1.05 | 0.031366 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2017-195 | 0.96445 | 0.91831 | -0.046147 |  | 0.95 | 1.05 | 0.041888 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2017-195 | 0.96445 | 0.91831 | -0.046147 |  | 0.95 | 1.05 | 0.038797 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2017-195 | 0.96445 | 0.91831 | -0.046147 |  | 0.95 | 1.05 | 0.030557 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2017-195 | 0.96445 | 0.91831 | -0.046147 |  | 0.95 | 1.05 | 0.067346 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2017-195 | 0.96445 | 0.91831 | -0.046147 |  | 0.95 | 1.05 | 0.030557 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2017-195 | 0.96445 | 0.91831 | -0.046147 |  | 0.95 | 1.05 | 0.030851 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2017-195 | 0.96445 | 0.91831 | -0.046147 |  | 0.95 | 1.05 | 0.032161 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2017-195 | 0.96445 | 0.91831 | -0.046147 |  | 0.95 | 1.05 | 0.04067 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2017-195 | 0.96445 | 0.91831 | -0.046147 |  | 0.95 | 1.05 | 0.040569 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2017-195 | 0.96445 | 0.91831 | -0.046147 |  | 0.95 | 1.05 | 0.03086 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2017-195 | 0.96445 | 0.91831 | -0.046147 |  | 0.95 | 1.05 | 0.033223 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2017-195 | 0.96445 | 0.91831 | -0.046147 |  | 0.95 | 1.05 | 0.033733 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | GEN-2017-220 | 0.9928 | 0.93273 | -0.060068 |  | 0.95 | 1.05 | 0.075186 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.02 MVAR switched shunt at BUFFALO7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2017-220 | 0.9928 | 0.93273 | -0.060068 |  | 0.95 | 1.05 | 0.031338 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.02 MVAR switched shunt at BUFFALO7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2017-220 | 0.9928 | 0.93273 | -0.060068 |  | 0.95 | 1.05 | 0.031338 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.02 MVAR switched shunt at BUFFALO7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2017-220 | 0.9928 | 0.93273 | -0.060068 |  | 0.95 | 1.05 | 0.031391 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.02 MVAR switched shunt at BUFFALO7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2017-220 | 0.9928 | 0.93273 | -0.060068 |  | 0.95 | 1.05 | 0.034523 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.02 MVAR switched shunt at BUFFALO7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | GEN-2017-220 | 0.99268 | 0.93158 | -0.0611 |  | 0.95 | 1.05 | 0.075186 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2017-220 | 0.99268 | 0.93158 | -0.0611 |  | 0.95 | 1.05 | 0.031338 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2017-220 | 0.99268 | 0.93158 | -0.0611 |  | 0.95 | 1.05 | 0.031338 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2017-220 | 0.99268 | 0.93158 | -0.0611 |  | 0.95 | 1.05 | 0.031391 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2017-220 | 0.99268 | 0.93158 | -0.0611 |  | 0.95 | 1.05 | 0.034523 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2017-220 | 0.9904 | 0.93158 | -0.058829 |  | 0.95 | 1.05 | 0.035768 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | GEN-2017-220 | 0.9904 | 0.93158 | -0.058829 |  | 0.95 | 1.05 | 0.088718 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | GEN-2017-220 | 0.9904 | 0.93158 | -0.058829 |  | 0.95 | 1.05 | 0.031473 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | GEN-2017-220 | 0.9904 | 0.93158 | -0.058829 |  | 0.95 | 1.05 | 0.034941 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2017-220 | 0.9904 | 0.93158 | -0.058829 |  | 0.95 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2017-220 | 0.9904 | 0.93158 | -0.058829 |  | 0.95 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2017-220 | 0.9904 | 0.93158 | -0.058829 |  | 0.95 | 1.05 | 0.049224 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2017-220 | 0.9904 | 0.93158 | -0.058829 |  | 0.95 | 1.05 | 0.038981 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2017-220 | 0.9904 | 0.93158 | -0.058829 |  | 0.95 | 1.05 | 0.040399 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | GEN-2017-220 | 0.9904 | 0.93158 | -0.058829 |  | 0.95 | 1.05 | 0.031912 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEN-2017-220 | 0.9904 | 0.93158 | -0.058829 |  | 0.95 | 1.05 | 0.034127 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2017-220 | 0.9904 | 0.93158 | -0.058829 |  | 0.95 | 1.05 | 0.047318 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2017-220 | 0.99024 | 0.91802 | -0.072216 |  | 0.95 | 1.05 | 0.040439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GEN-2017-220 | 0.99024 | 0.91802 | -0.072216 |  | 0.95 | 1.05 | 0.034853 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2017-220 | 0.99024 | 0.91802 | -0.072216 |  | 0.95 | 1.05 | 0.046783 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2017-220 | 0.99024 | 0.91802 | -0.072216 |  | 0.95 | 1.05 | 0.047615 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2017-220 | 0.99024 | 0.91802 | -0.072216 |  | 0.95 | 1.05 | 0.034938 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | GEN-2017-220 | 0.99024 | 0.91802 | -0.072216 |  | 0.95 | 1.05 | 0.037875 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2017-220 | 0.99024 | 0.91802 | -0.072216 |  | 0.95 | 1.05 | 0.044022 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | GEN-2017-220 | 0.99024 | 0.91802 | -0.072216 |  | 0.95 | 1.05 | 0.030552 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2017-220 | 0.99024 | 0.91802 | -0.072216 |  | 0.95 | 1.05 | 0.038531 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2017-220 | 0.99024 | 0.91802 | -0.072216 |  | 0.95 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2017-220 | 0.99024 | 0.91802 | -0.072216 |  | 0.95 | 1.05 | 0.062491 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2017-220 | 0.99024 | 0.91802 | -0.072216 |  | 0.95 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2017-220 | 0.99024 | 0.91802 | -0.072216 |  | 0.95 | 1.05 | 0.038129 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2017-220 | 0.99024 | 0.91802 | -0.072216 |  | 0.95 | 1.05 | 0.038066 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GEN-2017-220 | 0.99024 | 0.91802 | -0.072216 |  | 0.95 | 1.05 | 0.034955 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2017-220 | 0.99024 | 0.91802 | -0.072216 |  | 0.95 | 1.05 | 0.06281 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2017-220 | 0.99024 | 0.91802 | -0.072216 |  | 0.95 | 1.05 | 0.045309 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2017-220 | 0.99024 | 0.91802 | -0.072216 |  | 0.95 | 1.05 | 0.035805 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2017-220 | 0.99024 | 0.91802 | -0.072216 |  | 0.95 | 1.05 | 0.032364 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEN-2017-220 | 0.99024 | 0.91802 | -0.072216 |  | 0.95 | 1.05 | 0.031815 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2017-220 | 0.99024 | 0.91802 | -0.072216 |  | 0.95 | 1.05 | 0.033886 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2017-220 | 0.99024 | 0.91802 | -0.072216 |  | 0.95 | 1.05 | 0.035554 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2017-220 | 0.99103 | 0.91955 | -0.071479 |  | 0.95 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GEN-2017-220 | 0.99103 | 0.91955 | -0.071479 |  | 0.95 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2017-220 | 0.99103 | 0.91955 | -0.071479 |  | 0.95 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2017-220 | 0.99103 | 0.91955 | -0.071479 |  | 0.95 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2017-220 | 0.99103 | 0.91955 | -0.071479 |  | 0.95 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | GEN-2017-220 | 0.99103 | 0.91955 | -0.071479 |  | 0.95 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2017-220 | 0.99103 | 0.91955 | -0.071479 |  | 0.95 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | GEN-2017-220 | 0.99103 | 0.91955 | -0.071479 |  | 0.95 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2017-220 | 0.99103 | 0.91955 | -0.071479 |  | 0.95 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | GEN-2017-220 | 0.99103 | 0.91955 | -0.071479 |  | 0.95 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2017-220 | 0.99103 | 0.91955 | -0.071479 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2017-220 | 0.99103 | 0.91955 | -0.071479 |  | 0.95 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2017-220 | 0.99103 | 0.91955 | -0.071479 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2017-220 | 0.99103 | 0.91955 | -0.071479 |  | 0.95 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2017-220 | 0.99103 | 0.91955 | -0.071479 |  | 0.95 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GEN-2017-220 | 0.99103 | 0.91955 | -0.071479 |  | 0.95 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2017-220 | 0.99103 | 0.91955 | -0.071479 |  | 0.95 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | GEN-2017-220 | 0.99103 | 0.91955 | -0.071479 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | GEN-2017-220 | 0.99103 | 0.91955 | -0.071479 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2017-220 | 0.99103 | 0.91955 | -0.071479 |  | 0.95 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2017-220 | 0.99103 | 0.91955 | -0.071479 |  | 0.95 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2017-220 | 0.99103 | 0.91955 | -0.071479 |  | 0.95 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEN-2017-220 | 0.99103 | 0.91955 | -0.071479 |  | 0.95 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2017-220 | 0.99103 | 0.91955 | -0.071479 |  | 0.95 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2017-220 | 0.99103 | 0.91955 | -0.071479 |  | 0.95 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | ASGI-2024-023 | GEN-2018-032 | 1.0039 | 0.94248 | -0.061443 |  | 0.95 | 1.05 | 0.079962 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | GEN-2018-032 | 1.0039 | 0.94248 | -0.061443 |  | 0.95 | 1.05 | 0.065323 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-068 | GEN-2018-032 | 1.0039 | 0.94248 | -0.061443 |  | 0.95 | 1.05 | 0.067422 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-071 | GEN-2018-032 | 1.0039 | 0.94248 | -0.061443 |  | 0.95 | 1.05 | 0.074668 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GEN-2018-032 | 1.0039 | 0.94248 | -0.061443 |  | 0.95 | 1.05 | 0.053027 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-122 | GEN-2018-032 | 1.0039 | 0.94248 | -0.061443 |  | 0.95 | 1.05 | 0.082926 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-177 | GEN-2018-032 | 1.0039 | 0.94248 | -0.061443 |  | 0.95 | 1.05 | 0.084694 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-178 | GEN-2018-032 | 1.0039 | 0.94248 | -0.061443 |  | 0.95 | 1.05 | 0.078867 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | GEN-2018-032 | 1.0039 | 0.94248 | -0.061443 |  | 0.95 | 1.05 | 0.031571 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-220 | GEN-2018-032 | 1.0039 | 0.94248 | -0.061443 |  | 0.95 | 1.05 | 0.075331 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-232 | GEN-2018-032 | 1.0039 | 0.94248 | -0.061443 |  | 0.95 | 1.05 | 0.078906 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | GEN-2018-032 | 1.0039 | 0.94248 | -0.061443 |  | 0.95 | 1.05 | 0.065323 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GEN-2018-032 | 1.0039 | 0.94248 | -0.061443 |  | 0.95 | 1.05 | 0.03431 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | GEN-2018-032 | 1.0039 | 0.94248 | -0.061443 |  | 0.95 | 1.05 | 0.031504 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | GEN-2018-032 | 1.0039 | 0.94248 | -0.061443 |  | 0.95 | 1.05 | 0.031504 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | GEN-2018-032 | 1.0039 | 0.94248 | -0.061443 |  | 0.95 | 1.05 | 0.030663 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | GEN-2018-032 | 1.0039 | 0.94248 | -0.061443 |  | 0.95 | 1.05 | 0.04269 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-376 | GEN-2018-032 | 1.0039 | 0.94248 | -0.061443 |  | 0.95 | 1.05 | 0.082476 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | ASGI-2024-023 | GEN-2018-032 | 1.0048 | 0.94673 | -0.058114 |  | 0.95 | 1.05 | 0.10682 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | GEN-2018-032 | 1.0048 | 0.94673 | -0.058114 |  | 0.95 | 1.05 | 0.084049 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-068 | GEN-2018-032 | 1.0048 | 0.94673 | -0.058114 |  | 0.95 | 1.05 | 0.087538 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-071 | GEN-2018-032 | 1.0048 | 0.94673 | -0.058114 |  | 0.95 | 1.05 | 0.099263 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GEN-2018-032 | 1.0048 | 0.94673 | -0.058114 |  | 0.95 | 1.05 | 0.088785 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-122 | GEN-2018-032 | 1.0048 | 0.94673 | -0.058114 |  | 0.95 | 1.05 | 0.11321 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-177 | GEN-2018-032 | 1.0048 | 0.94673 | -0.058114 |  | 0.95 | 1.05 | 0.11622 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-178 | GEN-2018-032 | 1.0048 | 0.94673 | -0.058114 |  | 0.95 | 1.05 | 0.10702 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | GEN-2018-032 | 1.0048 | 0.94673 | -0.058114 |  | 0.95 | 1.05 | 0.031044 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-220 | GEN-2018-032 | 1.0048 | 0.94673 | -0.058114 |  | 0.95 | 1.05 | 0.10032 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-232 | GEN-2018-032 | 1.0048 | 0.94673 | -0.058114 |  | 0.95 | 1.05 | 0.10939 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | GEN-2018-032 | 1.0048 | 0.94673 | -0.058114 |  | 0.95 | 1.05 | 0.036829 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | GEN-2018-032 | 1.0048 | 0.94673 | -0.058114 |  | 0.95 | 1.05 | 0.084049 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GEN-2018-032 | 1.0048 | 0.94673 | -0.058114 |  | 0.95 | 1.05 | 0.053387 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | GEN-2018-032 | 1.0048 | 0.94673 | -0.058114 |  | 0.95 | 1.05 | 0.042012 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | GEN-2018-032 | 1.0048 | 0.94673 | -0.058114 |  | 0.95 | 1.05 | 0.042012 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | GEN-2018-032 | 1.0048 | 0.94673 | -0.058114 |  | 0.95 | 1.05 | 0.031418 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEN-2018-032 | 1.0048 | 0.94673 | -0.058114 |  | 0.95 | 1.05 | 0.030073 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | GEN-2018-032 | 1.0048 | 0.94673 | -0.058114 |  | 0.95 | 1.05 | 0.047594 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-376 | GEN-2018-032 | 1.0048 | 0.94673 | -0.058114 |  | 0.95 | 1.05 | 0.11583 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2018-032 | 1.0054 | 0.94442 | -0.060928 |  | 0.95 | 1.05 | 0.035768 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | GEN-2018-032 | 1.0054 | 0.94442 | -0.060928 |  | 0.95 | 1.05 | 0.088718 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | GEN-2018-032 | 1.0054 | 0.94442 | -0.060928 |  | 0.95 | 1.05 | 0.031473 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | GEN-2018-032 | 1.0054 | 0.94442 | -0.060928 |  | 0.95 | 1.05 | 0.034941 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2018-032 | 1.0054 | 0.94442 | -0.060928 |  | 0.95 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2018-032 | 1.0054 | 0.94442 | -0.060928 |  | 0.95 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2018-032 | 1.0054 | 0.94442 | -0.060928 |  | 0.95 | 1.05 | 0.049224 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2018-032 | 1.0054 | 0.94442 | -0.060928 |  | 0.95 | 1.05 | 0.038981 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2018-032 | 1.0054 | 0.94442 | -0.060928 |  | 0.95 | 1.05 | 0.040399 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | GEN-2018-032 | 1.0054 | 0.94442 | -0.060928 |  | 0.95 | 1.05 | 0.031912 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEN-2018-032 | 1.0054 | 0.94442 | -0.060928 |  | 0.95 | 1.05 | 0.034127 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2018-032 | 1.0054 | 0.94442 | -0.060928 |  | 0.95 | 1.05 | 0.047318 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2018-032 | 1.0023 | 0.9372 | -0.065062 |  | 0.95 | 1.05 | 0.040439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GEN-2018-032 | 1.0023 | 0.9372 | -0.065062 |  | 0.95 | 1.05 | 0.034853 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2018-032 | 1.0023 | 0.9372 | -0.065062 |  | 0.95 | 1.05 | 0.046783 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2018-032 | 1.0023 | 0.9372 | -0.065062 |  | 0.95 | 1.05 | 0.047615 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2018-032 | 1.0023 | 0.9372 | -0.065062 |  | 0.95 | 1.05 | 0.034938 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | GEN-2018-032 | 1.0023 | 0.9372 | -0.065062 |  | 0.95 | 1.05 | 0.037875 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2018-032 | 1.0023 | 0.9372 | -0.065062 |  | 0.95 | 1.05 | 0.044022 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | GEN-2018-032 | 1.0023 | 0.9372 | -0.065062 |  | 0.95 | 1.05 | 0.030552 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2018-032 | 1.0023 | 0.9372 | -0.065062 |  | 0.95 | 1.05 | 0.038531 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2018-032 | 1.0023 | 0.9372 | -0.065062 |  | 0.95 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2018-032 | 1.0023 | 0.9372 | -0.065062 |  | 0.95 | 1.05 | 0.062491 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2018-032 | 1.0023 | 0.9372 | -0.065062 |  | 0.95 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2018-032 | 1.0023 | 0.9372 | -0.065062 |  | 0.95 | 1.05 | 0.038129 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2018-032 | 1.0023 | 0.9372 | -0.065062 |  | 0.95 | 1.05 | 0.038066 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GEN-2018-032 | 1.0023 | 0.9372 | -0.065062 |  | 0.95 | 1.05 | 0.034955 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2018-032 | 1.0023 | 0.9372 | -0.065062 |  | 0.95 | 1.05 | 0.06281 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2018-032 | 1.0023 | 0.9372 | -0.065062 |  | 0.95 | 1.05 | 0.045309 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2018-032 | 1.0023 | 0.9372 | -0.065062 |  | 0.95 | 1.05 | 0.035805 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2018-032 | 1.0023 | 0.9372 | -0.065062 |  | 0.95 | 1.05 | 0.032364 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEN-2018-032 | 1.0023 | 0.9372 | -0.065062 |  | 0.95 | 1.05 | 0.031815 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2018-032 | 1.0023 | 0.9372 | -0.065062 |  | 0.95 | 1.05 | 0.033886 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2018-032 | 1.0023 | 0.9372 | -0.065062 |  | 0.95 | 1.05 | 0.035554 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2018-032 | 1.0035 | 0.91963 | -0.08388 |  | 0.95 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GEN-2018-032 | 1.0035 | 0.91963 | -0.08388 |  | 0.95 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2018-032 | 1.0035 | 0.91963 | -0.08388 |  | 0.95 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2018-032 | 1.0035 | 0.91963 | -0.08388 |  | 0.95 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2018-032 | 1.0035 | 0.91963 | -0.08388 |  | 0.95 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | GEN-2018-032 | 1.0035 | 0.91963 | -0.08388 |  | 0.95 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2018-032 | 1.0035 | 0.91963 | -0.08388 |  | 0.95 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | GEN-2018-032 | 1.0035 | 0.91963 | -0.08388 |  | 0.95 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2018-032 | 1.0035 | 0.91963 | -0.08388 |  | 0.95 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | GEN-2018-032 | 1.0035 | 0.91963 | -0.08388 |  | 0.95 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2018-032 | 1.0035 | 0.91963 | -0.08388 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2018-032 | 1.0035 | 0.91963 | -0.08388 |  | 0.95 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2018-032 | 1.0035 | 0.91963 | -0.08388 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2018-032 | 1.0035 | 0.91963 | -0.08388 |  | 0.95 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2018-032 | 1.0035 | 0.91963 | -0.08388 |  | 0.95 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GEN-2018-032 | 1.0035 | 0.91963 | -0.08388 |  | 0.95 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2018-032 | 1.0035 | 0.91963 | -0.08388 |  | 0.95 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | GEN-2018-032 | 1.0035 | 0.91963 | -0.08388 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | GEN-2018-032 | 1.0035 | 0.91963 | -0.08388 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2018-032 | 1.0035 | 0.91963 | -0.08388 |  | 0.95 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2018-032 | 1.0035 | 0.91963 | -0.08388 |  | 0.95 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2018-032 | 1.0035 | 0.91963 | -0.08388 |  | 0.95 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEN-2018-032 | 1.0035 | 0.91963 | -0.08388 |  | 0.95 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2018-032 | 1.0035 | 0.91963 | -0.08388 |  | 0.95 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2018-032 | 1.0035 | 0.91963 | -0.08388 |  | 0.95 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2018-128 | 0.97977 | 0.89203 | -0.087738 |  | 0.92 | 1.05 | 0.091967 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GEN-2018-128 | 0.97977 | 0.89203 | -0.087738 |  | 0.92 | 1.05 | 0.033356 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2018-128 | 0.97977 | 0.89203 | -0.087738 |  | 0.92 | 1.05 | 0.044346 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2018-128 | 0.97977 | 0.89203 | -0.087738 |  | 0.92 | 1.05 | 0.058536 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2018-128 | 0.97977 | 0.89203 | -0.087738 |  | 0.92 | 1.05 | 0.059327 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | GEN-2018-128 | 0.97977 | 0.89203 | -0.087738 |  | 0.92 | 1.05 | 0.041874 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | GEN-2018-128 | 0.97977 | 0.89203 | -0.087738 |  | 0.92 | 1.05 | 0.046192 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2018-128 | 0.97977 | 0.89203 | -0.087738 |  | 0.92 | 1.05 | 0.12754 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | GEN-2018-128 | 0.97977 | 0.89203 | -0.087738 |  | 0.92 | 1.05 | 0.047018 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2018-128 | 0.97977 | 0.89203 | -0.087738 |  | 0.92 | 1.05 | 0.056662 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2018-128 | 0.97977 | 0.89203 | -0.087738 |  | 0.92 | 1.05 | 0.056662 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2018-128 | 0.97977 | 0.89203 | -0.087738 |  | 0.92 | 1.05 | 0.056727 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2018-128 | 0.97977 | 0.89203 | -0.087738 |  | 0.92 | 1.05 | 0.074186 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GEN-2018-128 | 0.97977 | 0.89203 | -0.087738 |  | 0.92 | 1.05 | 0.040839 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2018-128 | 0.97977 | 0.89203 | -0.087738 |  | 0.92 | 1.05 | 0.03863 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | GEN-2018-128 | 0.97977 | 0.89203 | -0.087738 |  | 0.92 | 1.05 | 0.042285 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | GEN-2018-128 | 0.97977 | 0.89203 | -0.087738 |  | 0.92 | 1.05 | 0.042285 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2018-128 | 0.97977 | 0.89203 | -0.087738 |  | 0.92 | 1.05 | 0.050204 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2018-128 | 0.97977 | 0.89203 | -0.087738 |  | 0.92 | 1.05 | 0.058005 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | GEN-2018-128 | 0.97977 | 0.89203 | -0.087738 |  | 0.92 | 1.05 | 0.041735 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2018-128 | 0.97977 | 0.89203 | -0.087738 |  | 0.92 | 1.05 | 0.057076 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEN-2018-128 | 0.97977 | 0.89203 | -0.087738 |  | 0.92 | 1.05 | 0.050111 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2018-128 | 0.97977 | 0.89203 | -0.087738 |  | 0.92 | 1.05 | 0.06491 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2018-128 | 0.97977 | 0.89203 | -0.087738 |  | 0.92 | 1.05 | 0.051051 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | GEN-2018-128 | 0.97977 | 0.89203 | -0.087738 |  | 0.92 | 1.05 | 0.036279 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2018-128 | 0.98593 | 0.91978 | -0.066154 |  | 0.92 | 1.05 | 0.091967 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GEN-2018-128 | 0.98593 | 0.91978 | -0.066154 |  | 0.92 | 1.05 | 0.033356 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2018-128 | 0.98593 | 0.91978 | -0.066154 |  | 0.92 | 1.05 | 0.044346 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2018-128 | 0.98593 | 0.91978 | -0.066154 |  | 0.92 | 1.05 | 0.058536 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2018-128 | 0.98593 | 0.91978 | -0.066154 |  | 0.92 | 1.05 | 0.059327 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | GEN-2018-128 | 0.98593 | 0.91978 | -0.066154 |  | 0.92 | 1.05 | 0.041874 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | GEN-2018-128 | 0.98593 | 0.91978 | -0.066154 |  | 0.92 | 1.05 | 0.046192 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2018-128 | 0.98593 | 0.91978 | -0.066154 |  | 0.92 | 1.05 | 0.12754 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | GEN-2018-128 | 0.98593 | 0.91978 | -0.066154 |  | 0.92 | 1.05 | 0.047018 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2018-128 | 0.98593 | 0.91978 | -0.066154 |  | 0.92 | 1.05 | 0.056662 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2018-128 | 0.98593 | 0.91978 | -0.066154 |  | 0.92 | 1.05 | 0.056662 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2018-128 | 0.98593 | 0.91978 | -0.066154 |  | 0.92 | 1.05 | 0.056727 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2018-128 | 0.98593 | 0.91978 | -0.066154 |  | 0.92 | 1.05 | 0.074186 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GEN-2018-128 | 0.98593 | 0.91978 | -0.066154 |  | 0.92 | 1.05 | 0.040839 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2018-128 | 0.98593 | 0.91978 | -0.066154 |  | 0.92 | 1.05 | 0.03863 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | GEN-2018-128 | 0.98593 | 0.91978 | -0.066154 |  | 0.92 | 1.05 | 0.042285 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | GEN-2018-128 | 0.98593 | 0.91978 | -0.066154 |  | 0.92 | 1.05 | 0.042285 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2018-128 | 0.98593 | 0.91978 | -0.066154 |  | 0.92 | 1.05 | 0.050204 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2018-128 | 0.98593 | 0.91978 | -0.066154 |  | 0.92 | 1.05 | 0.058005 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | GEN-2018-128 | 0.98593 | 0.91978 | -0.066154 |  | 0.92 | 1.05 | 0.041735 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2018-128 | 0.98593 | 0.91978 | -0.066154 |  | 0.92 | 1.05 | 0.057076 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEN-2018-128 | 0.98593 | 0.91978 | -0.066154 |  | 0.92 | 1.05 | 0.050111 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2018-128 | 0.98593 | 0.91978 | -0.066154 |  | 0.92 | 1.05 | 0.06491 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2018-128 | 0.98593 | 0.91978 | -0.066154 |  | 0.92 | 1.05 | 0.051051 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | GEN-2018-128 | 0.98593 | 0.91978 | -0.066154 |  | 0.92 | 1.05 | 0.036279 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2018-128 | 0.98639 | 0.88759 | -0.098806 |  | 0.92 | 1.05 | 0.035768 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | GEN-2018-128 | 0.98639 | 0.88759 | -0.098806 |  | 0.92 | 1.05 | 0.088718 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | GEN-2018-128 | 0.98639 | 0.88759 | -0.098806 |  | 0.92 | 1.05 | 0.031473 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | GEN-2018-128 | 0.98639 | 0.88759 | -0.098806 |  | 0.92 | 1.05 | 0.034941 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2018-128 | 0.98639 | 0.88759 | -0.098806 |  | 0.92 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2018-128 | 0.98639 | 0.88759 | -0.098806 |  | 0.92 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2018-128 | 0.98639 | 0.88759 | -0.098806 |  | 0.92 | 1.05 | 0.049224 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2018-128 | 0.98639 | 0.88759 | -0.098806 |  | 0.92 | 1.05 | 0.038981 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2018-128 | 0.98639 | 0.88759 | -0.098806 |  | 0.92 | 1.05 | 0.040399 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | GEN-2018-128 | 0.98639 | 0.88759 | -0.098806 |  | 0.92 | 1.05 | 0.031912 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEN-2018-128 | 0.98639 | 0.88759 | -0.098806 |  | 0.92 | 1.05 | 0.034127 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2018-128 | 0.98639 | 0.88759 | -0.098806 |  | 0.92 | 1.05 | 0.047318 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2018-128 | 0.99552 | 0.91954 | -0.075975 |  | 0.92 | 1.05 | 0.040439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GEN-2018-128 | 0.99552 | 0.91954 | -0.075975 |  | 0.92 | 1.05 | 0.034853 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2018-128 | 0.99552 | 0.91954 | -0.075975 |  | 0.92 | 1.05 | 0.046783 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2018-128 | 0.99552 | 0.91954 | -0.075975 |  | 0.92 | 1.05 | 0.047615 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2018-128 | 0.99552 | 0.91954 | -0.075975 |  | 0.92 | 1.05 | 0.034938 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | GEN-2018-128 | 0.99552 | 0.91954 | -0.075975 |  | 0.92 | 1.05 | 0.037875 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2018-128 | 0.99552 | 0.91954 | -0.075975 |  | 0.92 | 1.05 | 0.044022 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | GEN-2018-128 | 0.99552 | 0.91954 | -0.075975 |  | 0.92 | 1.05 | 0.030552 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2018-128 | 0.99552 | 0.91954 | -0.075975 |  | 0.92 | 1.05 | 0.038531 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2018-128 | 0.99552 | 0.91954 | -0.075975 |  | 0.92 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2018-128 | 0.99552 | 0.91954 | -0.075975 |  | 0.92 | 1.05 | 0.062491 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2018-128 | 0.99552 | 0.91954 | -0.075975 |  | 0.92 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2018-128 | 0.99552 | 0.91954 | -0.075975 |  | 0.92 | 1.05 | 0.038129 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2018-128 | 0.99552 | 0.91954 | -0.075975 |  | 0.92 | 1.05 | 0.038066 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GEN-2018-128 | 0.99552 | 0.91954 | -0.075975 |  | 0.92 | 1.05 | 0.034955 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2018-128 | 0.99552 | 0.91954 | -0.075975 |  | 0.92 | 1.05 | 0.06281 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2018-128 | 0.99552 | 0.91954 | -0.075975 |  | 0.92 | 1.05 | 0.045309 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2018-128 | 0.99552 | 0.91954 | -0.075975 |  | 0.92 | 1.05 | 0.035805 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2018-128 | 0.99552 | 0.91954 | -0.075975 |  | 0.92 | 1.05 | 0.032364 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEN-2018-128 | 0.99552 | 0.91954 | -0.075975 |  | 0.92 | 1.05 | 0.031815 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2018-128 | 0.99552 | 0.91954 | -0.075975 |  | 0.92 | 1.05 | 0.033886 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2018-128 | 0.99552 | 0.91954 | -0.075975 |  | 0.92 | 1.05 | 0.035554 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | ASGI-2024-023 | GEN-2019-016 | 0.98439 | 0.92294 | -0.06145 |  | 0.925 | 1.05 | 0.079962 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | GEN-2019-016 | 0.98439 | 0.92294 | -0.06145 |  | 0.925 | 1.05 | 0.065323 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-068 | GEN-2019-016 | 0.98439 | 0.92294 | -0.06145 |  | 0.925 | 1.05 | 0.067422 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-071 | GEN-2019-016 | 0.98439 | 0.92294 | -0.06145 |  | 0.925 | 1.05 | 0.074668 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GEN-2019-016 | 0.98439 | 0.92294 | -0.06145 |  | 0.925 | 1.05 | 0.053027 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-122 | GEN-2019-016 | 0.98439 | 0.92294 | -0.06145 |  | 0.925 | 1.05 | 0.082926 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-177 | GEN-2019-016 | 0.98439 | 0.92294 | -0.06145 |  | 0.925 | 1.05 | 0.084694 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-178 | GEN-2019-016 | 0.98439 | 0.92294 | -0.06145 |  | 0.925 | 1.05 | 0.078867 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | GEN-2019-016 | 0.98439 | 0.92294 | -0.06145 |  | 0.925 | 1.05 | 0.031571 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-220 | GEN-2019-016 | 0.98439 | 0.92294 | -0.06145 |  | 0.925 | 1.05 | 0.075331 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-232 | GEN-2019-016 | 0.98439 | 0.92294 | -0.06145 |  | 0.925 | 1.05 | 0.078906 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | GEN-2019-016 | 0.98439 | 0.92294 | -0.06145 |  | 0.925 | 1.05 | 0.065323 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GEN-2019-016 | 0.98439 | 0.92294 | -0.06145 |  | 0.925 | 1.05 | 0.03431 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | GEN-2019-016 | 0.98439 | 0.92294 | -0.06145 |  | 0.925 | 1.05 | 0.031504 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | GEN-2019-016 | 0.98439 | 0.92294 | -0.06145 |  | 0.925 | 1.05 | 0.031504 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | GEN-2019-016 | 0.98439 | 0.92294 | -0.06145 |  | 0.925 | 1.05 | 0.030663 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | GEN-2019-016 | 0.98439 | 0.92294 | -0.06145 |  | 0.925 | 1.05 | 0.04269 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-376 | GEN-2019-016 | 0.98439 | 0.92294 | -0.06145 |  | 0.925 | 1.05 | 0.082476 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2019-016 | 0.98623 | 0.91525 | -0.07098 |  | 0.925 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GEN-2019-016 | 0.98623 | 0.91525 | -0.07098 |  | 0.925 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2019-016 | 0.98623 | 0.91525 | -0.07098 |  | 0.925 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2019-016 | 0.98623 | 0.91525 | -0.07098 |  | 0.925 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2019-016 | 0.98623 | 0.91525 | -0.07098 |  | 0.925 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | GEN-2019-016 | 0.98623 | 0.91525 | -0.07098 |  | 0.925 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2019-016 | 0.98623 | 0.91525 | -0.07098 |  | 0.925 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | GEN-2019-016 | 0.98623 | 0.91525 | -0.07098 |  | 0.925 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2019-016 | 0.98623 | 0.91525 | -0.07098 |  | 0.925 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | GEN-2019-016 | 0.98623 | 0.91525 | -0.07098 |  | 0.925 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2019-016 | 0.98623 | 0.91525 | -0.07098 |  | 0.925 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2019-016 | 0.98623 | 0.91525 | -0.07098 |  | 0.925 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2019-016 | 0.98623 | 0.91525 | -0.07098 |  | 0.925 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2019-016 | 0.98623 | 0.91525 | -0.07098 |  | 0.925 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2019-016 | 0.98623 | 0.91525 | -0.07098 |  | 0.925 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GEN-2019-016 | 0.98623 | 0.91525 | -0.07098 |  | 0.925 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2019-016 | 0.98623 | 0.91525 | -0.07098 |  | 0.925 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | GEN-2019-016 | 0.98623 | 0.91525 | -0.07098 |  | 0.925 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | GEN-2019-016 | 0.98623 | 0.91525 | -0.07098 |  | 0.925 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2019-016 | 0.98623 | 0.91525 | -0.07098 |  | 0.925 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2019-016 | 0.98623 | 0.91525 | -0.07098 |  | 0.925 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2019-016 | 0.98623 | 0.91525 | -0.07098 |  | 0.925 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEN-2019-016 | 0.98623 | 0.91525 | -0.07098 |  | 0.925 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2019-016 | 0.98623 | 0.91525 | -0.07098 |  | 0.925 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2019-016 | 0.98623 | 0.91525 | -0.07098 |  | 0.925 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | GEN-2020-007 | 0.99483 | 0.93043 | -0.064397 |  | 0.95 | 1.05 | 0.03053 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2020-007 | 0.99483 | 0.93043 | -0.064397 |  | 0.95 | 1.05 | 0.044933 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GEN-2020-007 | 0.99483 | 0.93043 | -0.064397 |  | 0.95 | 1.05 | 0.047811 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2020-007 | 0.99483 | 0.93043 | -0.064397 |  | 0.95 | 1.05 | 0.09719 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2020-007 | 0.99483 | 0.93043 | -0.064397 |  | 0.95 | 1.05 | 0.069376 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2020-007 | 0.99483 | 0.93043 | -0.064397 |  | 0.95 | 1.05 | 0.04277 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2020-007 | 0.99483 | 0.93043 | -0.064397 |  | 0.95 | 1.05 | 0.071112 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | GEN-2020-007 | 0.99483 | 0.93043 | -0.064397 |  | 0.95 | 1.05 | 0.039357 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | GEN-2020-007 | 0.99483 | 0.93043 | -0.064397 |  | 0.95 | 1.05 | 0.04035 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2020-007 | 0.99483 | 0.93043 | -0.064397 |  | 0.95 | 1.05 | 0.052332 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | GEN-2020-007 | 0.99483 | 0.93043 | -0.064397 |  | 0.95 | 1.05 | 0.045944 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2020-007 | 0.99483 | 0.93043 | -0.064397 |  | 0.95 | 1.05 | 0.038178 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2020-007 | 0.99483 | 0.93043 | -0.064397 |  | 0.95 | 1.05 | 0.13469 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | GEN-2020-007 | 0.99483 | 0.93043 | -0.064397 |  | 0.95 | 1.05 | 0.03053 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2020-007 | 0.99483 | 0.93043 | -0.064397 |  | 0.95 | 1.05 | 0.038178 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2020-007 | 0.99483 | 0.93043 | -0.064397 |  | 0.95 | 1.05 | 0.037309 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2020-007 | 0.99483 | 0.93043 | -0.064397 |  | 0.95 | 1.05 | 0.040075 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GEN-2020-007 | 0.99483 | 0.93043 | -0.064397 |  | 0.95 | 1.05 | 0.053764 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2020-007 | 0.99483 | 0.93043 | -0.064397 |  | 0.95 | 1.05 | 0.071762 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | GEN-2020-007 | 0.99483 | 0.93043 | -0.064397 |  | 0.95 | 1.05 | 0.047827 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | GEN-2020-007 | 0.99483 | 0.93043 | -0.064397 |  | 0.95 | 1.05 | 0.047827 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2020-007 | 0.99483 | 0.93043 | -0.064397 |  | 0.95 | 1.05 | 0.070303 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2020-007 | 0.99483 | 0.93043 | -0.064397 |  | 0.95 | 1.05 | 0.040614 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | GEN-2020-007 | 0.99483 | 0.93043 | -0.064397 |  | 0.95 | 1.05 | 0.039729 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2020-007 | 0.99483 | 0.93043 | -0.064397 |  | 0.95 | 1.05 | 0.049662 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEN-2020-007 | 0.99483 | 0.93043 | -0.064397 |  | 0.95 | 1.05 | 0.042332 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2020-007 | 0.99483 | 0.93043 | -0.064397 |  | 0.95 | 1.05 | 0.048722 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2020-007 | 0.99483 | 0.93043 | -0.064397 |  | 0.95 | 1.05 | 0.038156 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | GEN-2020-007 | 0.99483 | 0.93043 | -0.064397 |  | 0.95 | 1.05 | 0.036794 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2020-007 | 1.0051 | 0.93496 | -0.070136 |  | 0.95 | 1.05 | 0.036307 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2020-007 | 1.0051 | 0.93496 | -0.070136 |  | 0.95 | 1.05 | 0.052743 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2020-007 | 1.0051 | 0.93496 | -0.070136 |  | 0.95 | 1.05 | 0.039345 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2020-007 | 1.0051 | 0.93496 | -0.070136 |  | 0.95 | 1.05 | 0.031366 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2020-007 | 1.0051 | 0.93496 | -0.070136 |  | 0.95 | 1.05 | 0.041888 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2020-007 | 1.0051 | 0.93496 | -0.070136 |  | 0.95 | 1.05 | 0.038797 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2020-007 | 1.0051 | 0.93496 | -0.070136 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2020-007 | 1.0051 | 0.93496 | -0.070136 |  | 0.95 | 1.05 | 0.067346 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2020-007 | 1.0051 | 0.93496 | -0.070136 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2020-007 | 1.0051 | 0.93496 | -0.070136 |  | 0.95 | 1.05 | 0.030851 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2020-007 | 1.0051 | 0.93496 | -0.070136 |  | 0.95 | 1.05 | 0.032161 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2020-007 | 1.0051 | 0.93496 | -0.070136 |  | 0.95 | 1.05 | 0.04067 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2020-007 | 1.0051 | 0.93496 | -0.070136 |  | 0.95 | 1.05 | 0.040569 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2020-007 | 1.0051 | 0.93496 | -0.070136 |  | 0.95 | 1.05 | 0.03086 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2020-007 | 1.0051 | 0.93496 | -0.070136 |  | 0.95 | 1.05 | 0.033223 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2020-007 | 1.0051 | 0.93496 | -0.070136 |  | 0.95 | 1.05 | 0.033733 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2020-007 | 1.0026 | 0.8826 | -0.12001 |  | 0.95 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GEN-2020-007 | 1.0026 | 0.8826 | -0.12001 |  | 0.95 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2020-007 | 1.0026 | 0.8826 | -0.12001 |  | 0.95 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2020-007 | 1.0026 | 0.8826 | -0.12001 |  | 0.95 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2020-007 | 1.0026 | 0.8826 | -0.12001 |  | 0.95 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | GEN-2020-007 | 1.0026 | 0.8826 | -0.12001 |  | 0.95 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2020-007 | 1.0026 | 0.8826 | -0.12001 |  | 0.95 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | GEN-2020-007 | 1.0026 | 0.8826 | -0.12001 |  | 0.95 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2020-007 | 1.0026 | 0.8826 | -0.12001 |  | 0.95 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | GEN-2020-007 | 1.0026 | 0.8826 | -0.12001 |  | 0.95 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2020-007 | 1.0026 | 0.8826 | -0.12001 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2020-007 | 1.0026 | 0.8826 | -0.12001 |  | 0.95 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2020-007 | 1.0026 | 0.8826 | -0.12001 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2020-007 | 1.0026 | 0.8826 | -0.12001 |  | 0.95 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2020-007 | 1.0026 | 0.8826 | -0.12001 |  | 0.95 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GEN-2020-007 | 1.0026 | 0.8826 | -0.12001 |  | 0.95 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2020-007 | 1.0026 | 0.8826 | -0.12001 |  | 0.95 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | GEN-2020-007 | 1.0026 | 0.8826 | -0.12001 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | GEN-2020-007 | 1.0026 | 0.8826 | -0.12001 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2020-007 | 1.0026 | 0.8826 | -0.12001 |  | 0.95 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2020-007 | 1.0026 | 0.8826 | -0.12001 |  | 0.95 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2020-007 | 1.0026 | 0.8826 | -0.12001 |  | 0.95 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEN-2020-007 | 1.0026 | 0.8826 | -0.12001 |  | 0.95 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2020-007 | 1.0026 | 0.8826 | -0.12001 |  | 0.95 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2020-007 | 1.0026 | 0.8826 | -0.12001 |  | 0.95 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2020-057 | 0.96854 | 0.92771 | -0.040829 |  | 0.95 | 1.05 | 0.036307 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2020-057 | 0.96854 | 0.92771 | -0.040829 |  | 0.95 | 1.05 | 0.052743 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2020-057 | 0.96854 | 0.92771 | -0.040829 |  | 0.95 | 1.05 | 0.039345 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2020-057 | 0.96854 | 0.92771 | -0.040829 |  | 0.95 | 1.05 | 0.031366 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2020-057 | 0.96854 | 0.92771 | -0.040829 |  | 0.95 | 1.05 | 0.041888 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2020-057 | 0.96854 | 0.92771 | -0.040829 |  | 0.95 | 1.05 | 0.038797 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2020-057 | 0.96854 | 0.92771 | -0.040829 |  | 0.95 | 1.05 | 0.030557 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2020-057 | 0.96854 | 0.92771 | -0.040829 |  | 0.95 | 1.05 | 0.067346 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2020-057 | 0.96854 | 0.92771 | -0.040829 |  | 0.95 | 1.05 | 0.030557 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2020-057 | 0.96854 | 0.92771 | -0.040829 |  | 0.95 | 1.05 | 0.030851 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2020-057 | 0.96854 | 0.92771 | -0.040829 |  | 0.95 | 1.05 | 0.032161 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2020-057 | 0.96854 | 0.92771 | -0.040829 |  | 0.95 | 1.05 | 0.04067 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2020-057 | 0.96854 | 0.92771 | -0.040829 |  | 0.95 | 1.05 | 0.040569 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2020-057 | 0.96854 | 0.92771 | -0.040829 |  | 0.95 | 1.05 | 0.03086 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2020-057 | 0.96854 | 0.92771 | -0.040829 |  | 0.95 | 1.05 | 0.033223 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2020-057 | 0.96854 | 0.92771 | -0.040829 |  | 0.95 | 1.05 | 0.033733 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2020-057 | 0.96195 | 0.9139 | -0.048048 |  | 0.95 | 1.05 | 0.036307 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2020-057 | 0.96195 | 0.9139 | -0.048048 |  | 0.95 | 1.05 | 0.052743 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2020-057 | 0.96195 | 0.9139 | -0.048048 |  | 0.95 | 1.05 | 0.039345 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2020-057 | 0.96195 | 0.9139 | -0.048048 |  | 0.95 | 1.05 | 0.031366 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2020-057 | 0.96195 | 0.9139 | -0.048048 |  | 0.95 | 1.05 | 0.041888 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2020-057 | 0.96195 | 0.9139 | -0.048048 |  | 0.95 | 1.05 | 0.038797 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2020-057 | 0.96195 | 0.9139 | -0.048048 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2020-057 | 0.96195 | 0.9139 | -0.048048 |  | 0.95 | 1.05 | 0.067346 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2020-057 | 0.96195 | 0.9139 | -0.048048 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2020-057 | 0.96195 | 0.9139 | -0.048048 |  | 0.95 | 1.05 | 0.030851 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2020-057 | 0.96195 | 0.9139 | -0.048048 |  | 0.95 | 1.05 | 0.032161 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2020-057 | 0.96195 | 0.9139 | -0.048048 |  | 0.95 | 1.05 | 0.04067 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2020-057 | 0.96195 | 0.9139 | -0.048048 |  | 0.95 | 1.05 | 0.040569 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2020-057 | 0.96195 | 0.9139 | -0.048048 |  | 0.95 | 1.05 | 0.03086 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2020-057 | 0.96195 | 0.9139 | -0.048048 |  | 0.95 | 1.05 | 0.033223 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2020-057 | 0.96195 | 0.9139 | -0.048048 |  | 0.95 | 1.05 | 0.033733 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2020-057 | 0.97394 | 0.9177 | -0.056236 |  | 0.95 | 1.05 | 0.036307 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2020-057 | 0.97394 | 0.9177 | -0.056236 |  | 0.95 | 1.05 | 0.052743 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2020-057 | 0.97394 | 0.9177 | -0.056236 |  | 0.95 | 1.05 | 0.039345 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2020-057 | 0.97394 | 0.9177 | -0.056236 |  | 0.95 | 1.05 | 0.031366 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2020-057 | 0.97394 | 0.9177 | -0.056236 |  | 0.95 | 1.05 | 0.041888 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2020-057 | 0.97394 | 0.9177 | -0.056236 |  | 0.95 | 1.05 | 0.038797 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2020-057 | 0.97394 | 0.9177 | -0.056236 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2020-057 | 0.97394 | 0.9177 | -0.056236 |  | 0.95 | 1.05 | 0.067346 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2020-057 | 0.97394 | 0.9177 | -0.056236 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2020-057 | 0.97394 | 0.9177 | -0.056236 |  | 0.95 | 1.05 | 0.030851 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2020-057 | 0.97394 | 0.9177 | -0.056236 |  | 0.95 | 1.05 | 0.032161 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2020-057 | 0.97394 | 0.9177 | -0.056236 |  | 0.95 | 1.05 | 0.04067 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2020-057 | 0.97394 | 0.9177 | -0.056236 |  | 0.95 | 1.05 | 0.040569 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2020-057 | 0.97394 | 0.9177 | -0.056236 |  | 0.95 | 1.05 | 0.03086 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2020-057 | 0.97394 | 0.9177 | -0.056236 |  | 0.95 | 1.05 | 0.033223 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2020-057 | 0.97394 | 0.9177 | -0.056236 |  | 0.95 | 1.05 | 0.033733 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2020-057 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GEN-2020-057 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2020-057 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2020-057 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2020-057 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | GEN-2020-057 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2020-057 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | GEN-2020-057 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2020-057 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | GEN-2020-057 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2020-057 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2020-057 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2020-057 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2020-057 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2020-057 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GEN-2020-057 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2020-057 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | GEN-2020-057 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | GEN-2020-057 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2020-057 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2020-057 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2020-057 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEN-2020-057 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2020-057 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2020-057 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2020-057 | 0.96773 | 0.92612 | -0.041612 |  | 0.95 | 1.05 | 0.036307 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2020-057 | 0.96773 | 0.92612 | -0.041612 |  | 0.95 | 1.05 | 0.052743 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2020-057 | 0.96773 | 0.92612 | -0.041612 |  | 0.95 | 1.05 | 0.039345 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2020-057 | 0.96773 | 0.92612 | -0.041612 |  | 0.95 | 1.05 | 0.031366 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2020-057 | 0.96773 | 0.92612 | -0.041612 |  | 0.95 | 1.05 | 0.041888 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2020-057 | 0.96773 | 0.92612 | -0.041612 |  | 0.95 | 1.05 | 0.038797 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2020-057 | 0.96773 | 0.92612 | -0.041612 |  | 0.95 | 1.05 | 0.030557 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2020-057 | 0.96773 | 0.92612 | -0.041612 |  | 0.95 | 1.05 | 0.067346 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2020-057 | 0.96773 | 0.92612 | -0.041612 |  | 0.95 | 1.05 | 0.030557 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2020-057 | 0.96773 | 0.92612 | -0.041612 |  | 0.95 | 1.05 | 0.030851 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2020-057 | 0.96773 | 0.92612 | -0.041612 |  | 0.95 | 1.05 | 0.032161 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2020-057 | 0.96773 | 0.92612 | -0.041612 |  | 0.95 | 1.05 | 0.04067 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2020-057 | 0.96773 | 0.92612 | -0.041612 |  | 0.95 | 1.05 | 0.040569 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2020-057 | 0.96773 | 0.92612 | -0.041612 |  | 0.95 | 1.05 | 0.03086 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2020-057 | 0.96773 | 0.92612 | -0.041612 |  | 0.95 | 1.05 | 0.033223 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2020-057 | 0.96773 | 0.92612 | -0.041612 |  | 0.95 | 1.05 | 0.033733 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2020-058 | 0.96854 | 0.92771 | -0.040829 |  | 0.95 | 1.05 | 0.036307 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2020-058 | 0.96854 | 0.92771 | -0.040829 |  | 0.95 | 1.05 | 0.052743 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2020-058 | 0.96854 | 0.92771 | -0.040829 |  | 0.95 | 1.05 | 0.039345 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2020-058 | 0.96854 | 0.92771 | -0.040829 |  | 0.95 | 1.05 | 0.031366 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2020-058 | 0.96854 | 0.92771 | -0.040829 |  | 0.95 | 1.05 | 0.041888 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2020-058 | 0.96854 | 0.92771 | -0.040829 |  | 0.95 | 1.05 | 0.038797 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2020-058 | 0.96854 | 0.92771 | -0.040829 |  | 0.95 | 1.05 | 0.030557 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2020-058 | 0.96854 | 0.92771 | -0.040829 |  | 0.95 | 1.05 | 0.067346 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2020-058 | 0.96854 | 0.92771 | -0.040829 |  | 0.95 | 1.05 | 0.030557 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2020-058 | 0.96854 | 0.92771 | -0.040829 |  | 0.95 | 1.05 | 0.030851 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2020-058 | 0.96854 | 0.92771 | -0.040829 |  | 0.95 | 1.05 | 0.032161 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2020-058 | 0.96854 | 0.92771 | -0.040829 |  | 0.95 | 1.05 | 0.04067 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2020-058 | 0.96854 | 0.92771 | -0.040829 |  | 0.95 | 1.05 | 0.040569 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2020-058 | 0.96854 | 0.92771 | -0.040829 |  | 0.95 | 1.05 | 0.03086 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2020-058 | 0.96854 | 0.92771 | -0.040829 |  | 0.95 | 1.05 | 0.033223 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2020-058 | 0.96854 | 0.92771 | -0.040829 |  | 0.95 | 1.05 | 0.033733 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2020-058 | 0.96195 | 0.9139 | -0.048048 |  | 0.95 | 1.05 | 0.036307 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2020-058 | 0.96195 | 0.9139 | -0.048048 |  | 0.95 | 1.05 | 0.052743 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2020-058 | 0.96195 | 0.9139 | -0.048048 |  | 0.95 | 1.05 | 0.039345 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2020-058 | 0.96195 | 0.9139 | -0.048048 |  | 0.95 | 1.05 | 0.031366 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2020-058 | 0.96195 | 0.9139 | -0.048048 |  | 0.95 | 1.05 | 0.041888 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2020-058 | 0.96195 | 0.9139 | -0.048048 |  | 0.95 | 1.05 | 0.038797 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2020-058 | 0.96195 | 0.9139 | -0.048048 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2020-058 | 0.96195 | 0.9139 | -0.048048 |  | 0.95 | 1.05 | 0.067346 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2020-058 | 0.96195 | 0.9139 | -0.048048 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2020-058 | 0.96195 | 0.9139 | -0.048048 |  | 0.95 | 1.05 | 0.030851 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2020-058 | 0.96195 | 0.9139 | -0.048048 |  | 0.95 | 1.05 | 0.032161 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2020-058 | 0.96195 | 0.9139 | -0.048048 |  | 0.95 | 1.05 | 0.04067 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2020-058 | 0.96195 | 0.9139 | -0.048048 |  | 0.95 | 1.05 | 0.040569 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2020-058 | 0.96195 | 0.9139 | -0.048048 |  | 0.95 | 1.05 | 0.03086 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2020-058 | 0.96195 | 0.9139 | -0.048048 |  | 0.95 | 1.05 | 0.033223 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2020-058 | 0.96195 | 0.9139 | -0.048048 |  | 0.95 | 1.05 | 0.033733 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2020-058 | 0.97394 | 0.9177 | -0.056236 |  | 0.95 | 1.05 | 0.036307 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2020-058 | 0.97394 | 0.9177 | -0.056236 |  | 0.95 | 1.05 | 0.052743 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2020-058 | 0.97394 | 0.9177 | -0.056236 |  | 0.95 | 1.05 | 0.039345 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2020-058 | 0.97394 | 0.9177 | -0.056236 |  | 0.95 | 1.05 | 0.031366 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2020-058 | 0.97394 | 0.9177 | -0.056236 |  | 0.95 | 1.05 | 0.041888 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2020-058 | 0.97394 | 0.9177 | -0.056236 |  | 0.95 | 1.05 | 0.038797 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2020-058 | 0.97394 | 0.9177 | -0.056236 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2020-058 | 0.97394 | 0.9177 | -0.056236 |  | 0.95 | 1.05 | 0.067346 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2020-058 | 0.97394 | 0.9177 | -0.056236 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2020-058 | 0.97394 | 0.9177 | -0.056236 |  | 0.95 | 1.05 | 0.030851 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2020-058 | 0.97394 | 0.9177 | -0.056236 |  | 0.95 | 1.05 | 0.032161 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2020-058 | 0.97394 | 0.9177 | -0.056236 |  | 0.95 | 1.05 | 0.04067 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2020-058 | 0.97394 | 0.9177 | -0.056236 |  | 0.95 | 1.05 | 0.040569 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2020-058 | 0.97394 | 0.9177 | -0.056236 |  | 0.95 | 1.05 | 0.03086 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2020-058 | 0.97394 | 0.9177 | -0.056236 |  | 0.95 | 1.05 | 0.033223 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2020-058 | 0.97394 | 0.9177 | -0.056236 |  | 0.95 | 1.05 | 0.033733 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2020-058 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GEN-2020-058 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2020-058 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2020-058 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2020-058 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | GEN-2020-058 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2020-058 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | GEN-2020-058 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2020-058 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | GEN-2020-058 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2020-058 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2020-058 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2020-058 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2020-058 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2020-058 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GEN-2020-058 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2020-058 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | GEN-2020-058 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | GEN-2020-058 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2020-058 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2020-058 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2020-058 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEN-2020-058 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2020-058 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2020-058 | 0.98076 | 0.90497 | -0.075793 |  | 0.95 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2020-058 | 0.96773 | 0.92612 | -0.041612 |  | 0.95 | 1.05 | 0.036307 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2020-058 | 0.96773 | 0.92612 | -0.041612 |  | 0.95 | 1.05 | 0.052743 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2020-058 | 0.96773 | 0.92612 | -0.041612 |  | 0.95 | 1.05 | 0.039345 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2020-058 | 0.96773 | 0.92612 | -0.041612 |  | 0.95 | 1.05 | 0.031366 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2020-058 | 0.96773 | 0.92612 | -0.041612 |  | 0.95 | 1.05 | 0.041888 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2020-058 | 0.96773 | 0.92612 | -0.041612 |  | 0.95 | 1.05 | 0.038797 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2020-058 | 0.96773 | 0.92612 | -0.041612 |  | 0.95 | 1.05 | 0.030557 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2020-058 | 0.96773 | 0.92612 | -0.041612 |  | 0.95 | 1.05 | 0.067346 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2020-058 | 0.96773 | 0.92612 | -0.041612 |  | 0.95 | 1.05 | 0.030557 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2020-058 | 0.96773 | 0.92612 | -0.041612 |  | 0.95 | 1.05 | 0.030851 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2020-058 | 0.96773 | 0.92612 | -0.041612 |  | 0.95 | 1.05 | 0.032161 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2020-058 | 0.96773 | 0.92612 | -0.041612 |  | 0.95 | 1.05 | 0.04067 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2020-058 | 0.96773 | 0.92612 | -0.041612 |  | 0.95 | 1.05 | 0.040569 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2020-058 | 0.96773 | 0.92612 | -0.041612 |  | 0.95 | 1.05 | 0.03086 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2020-058 | 0.96773 | 0.92612 | -0.041612 |  | 0.95 | 1.05 | 0.033223 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2020-058 | 0.96773 | 0.92612 | -0.041612 |  | 0.95 | 1.05 | 0.033733 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2020-072 | 0.99362 | 0.92593 | -0.067687 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GEN-2020-072 | 0.99362 | 0.92593 | -0.067687 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2020-072 | 0.99362 | 0.92593 | -0.067687 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2020-072 | 0.99362 | 0.92593 | -0.067687 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2020-072 | 0.99362 | 0.92593 | -0.067687 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | GEN-2020-072 | 0.99362 | 0.92593 | -0.067687 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2020-072 | 0.99362 | 0.92593 | -0.067687 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | GEN-2020-072 | 0.99362 | 0.92593 | -0.067687 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2020-072 | 0.99362 | 0.92593 | -0.067687 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | GEN-2020-072 | 0.99362 | 0.92593 | -0.067687 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2020-072 | 0.99362 | 0.92593 | -0.067687 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2020-072 | 0.99362 | 0.92593 | -0.067687 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2020-072 | 0.99362 | 0.92593 | -0.067687 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2020-072 | 0.99362 | 0.92593 | -0.067687 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2020-072 | 0.99362 | 0.92593 | -0.067687 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GEN-2020-072 | 0.99362 | 0.92593 | -0.067687 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2020-072 | 0.99362 | 0.92593 | -0.067687 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | GEN-2020-072 | 0.99362 | 0.92593 | -0.067687 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | GEN-2020-072 | 0.99362 | 0.92593 | -0.067687 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2020-072 | 0.99362 | 0.92593 | -0.067687 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2020-072 | 0.99362 | 0.92593 | -0.067687 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2020-072 | 0.99362 | 0.92593 | -0.067687 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEN-2020-072 | 0.99362 | 0.92593 | -0.067687 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2020-072 | 0.99362 | 0.92593 | -0.067687 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2020-072 | 0.99362 | 0.92593 | -0.067687 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2020-073 | 1.0074 | 0.91747 | -0.089885 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GEN-2020-073 | 1.0074 | 0.91747 | -0.089885 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2020-073 | 1.0074 | 0.91747 | -0.089885 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2020-073 | 1.0074 | 0.91747 | -0.089885 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2020-073 | 1.0074 | 0.91747 | -0.089885 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | GEN-2020-073 | 1.0074 | 0.91747 | -0.089885 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2020-073 | 1.0074 | 0.91747 | -0.089885 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | GEN-2020-073 | 1.0074 | 0.91747 | -0.089885 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2020-073 | 1.0074 | 0.91747 | -0.089885 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | GEN-2020-073 | 1.0074 | 0.91747 | -0.089885 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2020-073 | 1.0074 | 0.91747 | -0.089885 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2020-073 | 1.0074 | 0.91747 | -0.089885 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2020-073 | 1.0074 | 0.91747 | -0.089885 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2020-073 | 1.0074 | 0.91747 | -0.089885 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2020-073 | 1.0074 | 0.91747 | -0.089885 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GEN-2020-073 | 1.0074 | 0.91747 | -0.089885 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2020-073 | 1.0074 | 0.91747 | -0.089885 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | GEN-2020-073 | 1.0074 | 0.91747 | -0.089885 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | GEN-2020-073 | 1.0074 | 0.91747 | -0.089885 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2020-073 | 1.0074 | 0.91747 | -0.089885 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2020-073 | 1.0074 | 0.91747 | -0.089885 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2020-073 | 1.0074 | 0.91747 | -0.089885 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEN-2020-073 | 1.0074 | 0.91747 | -0.089885 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2020-073 | 1.0074 | 0.91747 | -0.089885 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2020-073 | 1.0074 | 0.91747 | -0.089885 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2020-092 | 0.93719 | 0.91176 | -0.025429 |  | 0.92 | 1.05 | 0.038424 | Single 509752 INOLATP4 138 509790 CATOOSA4 138 1 | Add 57 MVAR switched shunt at GUAVA 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | ASGI-2024-023 | GEN-2021-006 | 1.0037 | 0.94228 | -0.06143 |  | 0.95 | 1.05 | 0.079962 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | GEN-2021-006 | 1.0037 | 0.94228 | -0.06143 |  | 0.95 | 1.05 | 0.065323 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-068 | GEN-2021-006 | 1.0037 | 0.94228 | -0.06143 |  | 0.95 | 1.05 | 0.067422 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-071 | GEN-2021-006 | 1.0037 | 0.94228 | -0.06143 |  | 0.95 | 1.05 | 0.074668 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GEN-2021-006 | 1.0037 | 0.94228 | -0.06143 |  | 0.95 | 1.05 | 0.053027 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-122 | GEN-2021-006 | 1.0037 | 0.94228 | -0.06143 |  | 0.95 | 1.05 | 0.082926 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-177 | GEN-2021-006 | 1.0037 | 0.94228 | -0.06143 |  | 0.95 | 1.05 | 0.084694 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-178 | GEN-2021-006 | 1.0037 | 0.94228 | -0.06143 |  | 0.95 | 1.05 | 0.078867 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | GEN-2021-006 | 1.0037 | 0.94228 | -0.06143 |  | 0.95 | 1.05 | 0.031571 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-220 | GEN-2021-006 | 1.0037 | 0.94228 | -0.06143 |  | 0.95 | 1.05 | 0.075331 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-232 | GEN-2021-006 | 1.0037 | 0.94228 | -0.06143 |  | 0.95 | 1.05 | 0.078906 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | GEN-2021-006 | 1.0037 | 0.94228 | -0.06143 |  | 0.95 | 1.05 | 0.065323 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GEN-2021-006 | 1.0037 | 0.94228 | -0.06143 |  | 0.95 | 1.05 | 0.03431 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | GEN-2021-006 | 1.0037 | 0.94228 | -0.06143 |  | 0.95 | 1.05 | 0.031504 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | GEN-2021-006 | 1.0037 | 0.94228 | -0.06143 |  | 0.95 | 1.05 | 0.031504 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | GEN-2021-006 | 1.0037 | 0.94228 | -0.06143 |  | 0.95 | 1.05 | 0.030663 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | GEN-2021-006 | 1.0037 | 0.94228 | -0.06143 |  | 0.95 | 1.05 | 0.04269 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-376 | GEN-2021-006 | 1.0037 | 0.94228 | -0.06143 |  | 0.95 | 1.05 | 0.082476 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | ASGI-2024-023 | GEN-2021-006 | 1.0046 | 0.94653 | -0.058102 |  | 0.95 | 1.05 | 0.10682 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | GEN-2021-006 | 1.0046 | 0.94653 | -0.058102 |  | 0.95 | 1.05 | 0.084049 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-068 | GEN-2021-006 | 1.0046 | 0.94653 | -0.058102 |  | 0.95 | 1.05 | 0.087538 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-071 | GEN-2021-006 | 1.0046 | 0.94653 | -0.058102 |  | 0.95 | 1.05 | 0.099263 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GEN-2021-006 | 1.0046 | 0.94653 | -0.058102 |  | 0.95 | 1.05 | 0.088785 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-122 | GEN-2021-006 | 1.0046 | 0.94653 | -0.058102 |  | 0.95 | 1.05 | 0.11321 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-177 | GEN-2021-006 | 1.0046 | 0.94653 | -0.058102 |  | 0.95 | 1.05 | 0.11622 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-178 | GEN-2021-006 | 1.0046 | 0.94653 | -0.058102 |  | 0.95 | 1.05 | 0.10702 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | GEN-2021-006 | 1.0046 | 0.94653 | -0.058102 |  | 0.95 | 1.05 | 0.031044 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-220 | GEN-2021-006 | 1.0046 | 0.94653 | -0.058102 |  | 0.95 | 1.05 | 0.10032 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-232 | GEN-2021-006 | 1.0046 | 0.94653 | -0.058102 |  | 0.95 | 1.05 | 0.10939 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | GEN-2021-006 | 1.0046 | 0.94653 | -0.058102 |  | 0.95 | 1.05 | 0.036829 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | GEN-2021-006 | 1.0046 | 0.94653 | -0.058102 |  | 0.95 | 1.05 | 0.084049 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GEN-2021-006 | 1.0046 | 0.94653 | -0.058102 |  | 0.95 | 1.05 | 0.053387 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | GEN-2021-006 | 1.0046 | 0.94653 | -0.058102 |  | 0.95 | 1.05 | 0.042012 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | GEN-2021-006 | 1.0046 | 0.94653 | -0.058102 |  | 0.95 | 1.05 | 0.042012 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | GEN-2021-006 | 1.0046 | 0.94653 | -0.058102 |  | 0.95 | 1.05 | 0.031418 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEN-2021-006 | 1.0046 | 0.94653 | -0.058102 |  | 0.95 | 1.05 | 0.030073 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | GEN-2021-006 | 1.0046 | 0.94653 | -0.058102 |  | 0.95 | 1.05 | 0.047594 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-376 | GEN-2021-006 | 1.0046 | 0.94653 | -0.058102 |  | 0.95 | 1.05 | 0.11583 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2021-006 | 1.0051 | 0.94422 | -0.060915 |  | 0.95 | 1.05 | 0.035768 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | GEN-2021-006 | 1.0051 | 0.94422 | -0.060915 |  | 0.95 | 1.05 | 0.088718 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | GEN-2021-006 | 1.0051 | 0.94422 | -0.060915 |  | 0.95 | 1.05 | 0.031473 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | GEN-2021-006 | 1.0051 | 0.94422 | -0.060915 |  | 0.95 | 1.05 | 0.034941 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2021-006 | 1.0051 | 0.94422 | -0.060915 |  | 0.95 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2021-006 | 1.0051 | 0.94422 | -0.060915 |  | 0.95 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2021-006 | 1.0051 | 0.94422 | -0.060915 |  | 0.95 | 1.05 | 0.049224 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2021-006 | 1.0051 | 0.94422 | -0.060915 |  | 0.95 | 1.05 | 0.038981 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2021-006 | 1.0051 | 0.94422 | -0.060915 |  | 0.95 | 1.05 | 0.040399 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | GEN-2021-006 | 1.0051 | 0.94422 | -0.060915 |  | 0.95 | 1.05 | 0.031912 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEN-2021-006 | 1.0051 | 0.94422 | -0.060915 |  | 0.95 | 1.05 | 0.034127 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2021-006 | 1.0051 | 0.94422 | -0.060915 |  | 0.95 | 1.05 | 0.047318 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2021-006 | 1.002 | 0.937 | -0.065049 |  | 0.95 | 1.05 | 0.040439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GEN-2021-006 | 1.002 | 0.937 | -0.065049 |  | 0.95 | 1.05 | 0.034853 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2021-006 | 1.002 | 0.937 | -0.065049 |  | 0.95 | 1.05 | 0.046783 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2021-006 | 1.002 | 0.937 | -0.065049 |  | 0.95 | 1.05 | 0.047615 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2021-006 | 1.002 | 0.937 | -0.065049 |  | 0.95 | 1.05 | 0.034938 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | GEN-2021-006 | 1.002 | 0.937 | -0.065049 |  | 0.95 | 1.05 | 0.037875 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2021-006 | 1.002 | 0.937 | -0.065049 |  | 0.95 | 1.05 | 0.044022 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | GEN-2021-006 | 1.002 | 0.937 | -0.065049 |  | 0.95 | 1.05 | 0.030552 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2021-006 | 1.002 | 0.937 | -0.065049 |  | 0.95 | 1.05 | 0.038531 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2021-006 | 1.002 | 0.937 | -0.065049 |  | 0.95 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2021-006 | 1.002 | 0.937 | -0.065049 |  | 0.95 | 1.05 | 0.062491 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2021-006 | 1.002 | 0.937 | -0.065049 |  | 0.95 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2021-006 | 1.002 | 0.937 | -0.065049 |  | 0.95 | 1.05 | 0.038129 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2021-006 | 1.002 | 0.937 | -0.065049 |  | 0.95 | 1.05 | 0.038066 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GEN-2021-006 | 1.002 | 0.937 | -0.065049 |  | 0.95 | 1.05 | 0.034955 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2021-006 | 1.002 | 0.937 | -0.065049 |  | 0.95 | 1.05 | 0.06281 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2021-006 | 1.002 | 0.937 | -0.065049 |  | 0.95 | 1.05 | 0.045309 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2021-006 | 1.002 | 0.937 | -0.065049 |  | 0.95 | 1.05 | 0.035805 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2021-006 | 1.002 | 0.937 | -0.065049 |  | 0.95 | 1.05 | 0.032364 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEN-2021-006 | 1.002 | 0.937 | -0.065049 |  | 0.95 | 1.05 | 0.031815 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2021-006 | 1.002 | 0.937 | -0.065049 |  | 0.95 | 1.05 | 0.033886 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2021-006 | 1.002 | 0.937 | -0.065049 |  | 0.95 | 1.05 | 0.035554 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2021-006 | 1.0033 | 0.91944 | -0.083863 |  | 0.95 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GEN-2021-006 | 1.0033 | 0.91944 | -0.083863 |  | 0.95 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2021-006 | 1.0033 | 0.91944 | -0.083863 |  | 0.95 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2021-006 | 1.0033 | 0.91944 | -0.083863 |  | 0.95 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2021-006 | 1.0033 | 0.91944 | -0.083863 |  | 0.95 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | GEN-2021-006 | 1.0033 | 0.91944 | -0.083863 |  | 0.95 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2021-006 | 1.0033 | 0.91944 | -0.083863 |  | 0.95 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | GEN-2021-006 | 1.0033 | 0.91944 | -0.083863 |  | 0.95 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2021-006 | 1.0033 | 0.91944 | -0.083863 |  | 0.95 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | GEN-2021-006 | 1.0033 | 0.91944 | -0.083863 |  | 0.95 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2021-006 | 1.0033 | 0.91944 | -0.083863 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2021-006 | 1.0033 | 0.91944 | -0.083863 |  | 0.95 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2021-006 | 1.0033 | 0.91944 | -0.083863 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2021-006 | 1.0033 | 0.91944 | -0.083863 |  | 0.95 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2021-006 | 1.0033 | 0.91944 | -0.083863 |  | 0.95 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GEN-2021-006 | 1.0033 | 0.91944 | -0.083863 |  | 0.95 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2021-006 | 1.0033 | 0.91944 | -0.083863 |  | 0.95 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | GEN-2021-006 | 1.0033 | 0.91944 | -0.083863 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | GEN-2021-006 | 1.0033 | 0.91944 | -0.083863 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2021-006 | 1.0033 | 0.91944 | -0.083863 |  | 0.95 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2021-006 | 1.0033 | 0.91944 | -0.083863 |  | 0.95 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2021-006 | 1.0033 | 0.91944 | -0.083863 |  | 0.95 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEN-2021-006 | 1.0033 | 0.91944 | -0.083863 |  | 0.95 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2021-006 | 1.0033 | 0.91944 | -0.083863 |  | 0.95 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2021-006 | 1.0033 | 0.91944 | -0.083863 |  | 0.95 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | GEN-2021-029 | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.03053 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2021-029 | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.044933 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GEN-2021-029 | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.047811 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2021-029 | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.09719 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2021-029 | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.069376 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2021-029 | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.04277 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2021-029 | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.071112 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | GEN-2021-029 | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.039357 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | GEN-2021-029 | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.04035 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2021-029 | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.052332 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | GEN-2021-029 | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.045944 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2021-029 | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.038178 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2021-029 | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.13469 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | GEN-2021-029 | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.03053 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2021-029 | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.038178 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2021-029 | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.037309 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2021-029 | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.040075 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GEN-2021-029 | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.053764 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2021-029 | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.071762 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | GEN-2021-029 | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.047827 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | GEN-2021-029 | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.047827 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2021-029 | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.070303 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2021-029 | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.040614 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | GEN-2021-029 | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.039729 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2021-029 | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.049662 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEN-2021-029 | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.042332 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2021-029 | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.048722 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2021-029 | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.038156 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | GEN-2021-029 | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.036794 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2021-029 | 0.96836 | 0.92888 | -0.039481 |  | 0.95 | 1.05 | 0.036307 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2021-029 | 0.96836 | 0.92888 | -0.039481 |  | 0.95 | 1.05 | 0.052743 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2021-029 | 0.96836 | 0.92888 | -0.039481 |  | 0.95 | 1.05 | 0.039345 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2021-029 | 0.96836 | 0.92888 | -0.039481 |  | 0.95 | 1.05 | 0.031366 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2021-029 | 0.96836 | 0.92888 | -0.039481 |  | 0.95 | 1.05 | 0.041888 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2021-029 | 0.96836 | 0.92888 | -0.039481 |  | 0.95 | 1.05 | 0.038797 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2021-029 | 0.96836 | 0.92888 | -0.039481 |  | 0.95 | 1.05 | 0.030557 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2021-029 | 0.96836 | 0.92888 | -0.039481 |  | 0.95 | 1.05 | 0.067346 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2021-029 | 0.96836 | 0.92888 | -0.039481 |  | 0.95 | 1.05 | 0.030557 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2021-029 | 0.96836 | 0.92888 | -0.039481 |  | 0.95 | 1.05 | 0.030851 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2021-029 | 0.96836 | 0.92888 | -0.039481 |  | 0.95 | 1.05 | 0.032161 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2021-029 | 0.96836 | 0.92888 | -0.039481 |  | 0.95 | 1.05 | 0.04067 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2021-029 | 0.96836 | 0.92888 | -0.039481 |  | 0.95 | 1.05 | 0.040569 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2021-029 | 0.96836 | 0.92888 | -0.039481 |  | 0.95 | 1.05 | 0.03086 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2021-029 | 0.96836 | 0.92888 | -0.039481 |  | 0.95 | 1.05 | 0.033223 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2021-029 | 0.96836 | 0.92888 | -0.039481 |  | 0.95 | 1.05 | 0.033733 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2021-029 | 0.97297 | 0.91992 | -0.053049 |  | 0.95 | 1.05 | 0.036307 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2021-029 | 0.97297 | 0.91992 | -0.053049 |  | 0.95 | 1.05 | 0.052743 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2021-029 | 0.97297 | 0.91992 | -0.053049 |  | 0.95 | 1.05 | 0.039345 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2021-029 | 0.97297 | 0.91992 | -0.053049 |  | 0.95 | 1.05 | 0.031366 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2021-029 | 0.97297 | 0.91992 | -0.053049 |  | 0.95 | 1.05 | 0.041888 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2021-029 | 0.97297 | 0.91992 | -0.053049 |  | 0.95 | 1.05 | 0.038797 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2021-029 | 0.97297 | 0.91992 | -0.053049 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2021-029 | 0.97297 | 0.91992 | -0.053049 |  | 0.95 | 1.05 | 0.067346 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2021-029 | 0.97297 | 0.91992 | -0.053049 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2021-029 | 0.97297 | 0.91992 | -0.053049 |  | 0.95 | 1.05 | 0.030851 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2021-029 | 0.97297 | 0.91992 | -0.053049 |  | 0.95 | 1.05 | 0.032161 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2021-029 | 0.97297 | 0.91992 | -0.053049 |  | 0.95 | 1.05 | 0.04067 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2021-029 | 0.97297 | 0.91992 | -0.053049 |  | 0.95 | 1.05 | 0.040569 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2021-029 | 0.97297 | 0.91992 | -0.053049 |  | 0.95 | 1.05 | 0.03086 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2021-029 | 0.97297 | 0.91992 | -0.053049 |  | 0.95 | 1.05 | 0.033223 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2021-029 | 0.97297 | 0.91992 | -0.053049 |  | 0.95 | 1.05 | 0.033733 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2021-029 | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GEN-2021-029 | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2021-029 | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2021-029 | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2021-029 | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | GEN-2021-029 | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2021-029 | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | GEN-2021-029 | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2021-029 | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | GEN-2021-029 | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2021-029 | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2021-029 | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2021-029 | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2021-029 | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2021-029 | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GEN-2021-029 | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2021-029 | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | GEN-2021-029 | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | GEN-2021-029 | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2021-029 | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2021-029 | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2021-029 | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEN-2021-029 | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2021-029 | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2021-029 | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | GEN-2021-030 | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.03053 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2021-030 | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.044933 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GEN-2021-030 | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.047811 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2021-030 | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.09719 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2021-030 | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.069376 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2021-030 | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.04277 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2021-030 | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.071112 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | GEN-2021-030 | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.039357 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | GEN-2021-030 | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.04035 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2021-030 | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.052332 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | GEN-2021-030 | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.045944 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2021-030 | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.038178 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2021-030 | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.13469 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | GEN-2021-030 | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.03053 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2021-030 | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.038178 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2021-030 | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.037309 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2021-030 | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.040075 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GEN-2021-030 | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.053764 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2021-030 | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.071762 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | GEN-2021-030 | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.047827 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | GEN-2021-030 | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.047827 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2021-030 | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.070303 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2021-030 | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.040614 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | GEN-2021-030 | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.039729 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2021-030 | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.049662 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEN-2021-030 | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.042332 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2021-030 | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.048722 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2021-030 | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.038156 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | GEN-2021-030 | 0.99372 | 0.93026 | -0.063452 |  | 0.95 | 1.05 | 0.036794 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2021-030 | 0.96836 | 0.92888 | -0.039481 |  | 0.95 | 1.05 | 0.036307 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2021-030 | 0.96836 | 0.92888 | -0.039481 |  | 0.95 | 1.05 | 0.052743 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2021-030 | 0.96836 | 0.92888 | -0.039481 |  | 0.95 | 1.05 | 0.039345 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2021-030 | 0.96836 | 0.92888 | -0.039481 |  | 0.95 | 1.05 | 0.031366 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2021-030 | 0.96836 | 0.92888 | -0.039481 |  | 0.95 | 1.05 | 0.041888 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2021-030 | 0.96836 | 0.92888 | -0.039481 |  | 0.95 | 1.05 | 0.038797 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2021-030 | 0.96836 | 0.92888 | -0.039481 |  | 0.95 | 1.05 | 0.030557 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2021-030 | 0.96836 | 0.92888 | -0.039481 |  | 0.95 | 1.05 | 0.067346 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2021-030 | 0.96836 | 0.92888 | -0.039481 |  | 0.95 | 1.05 | 0.030557 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2021-030 | 0.96836 | 0.92888 | -0.039481 |  | 0.95 | 1.05 | 0.030851 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2021-030 | 0.96836 | 0.92888 | -0.039481 |  | 0.95 | 1.05 | 0.032161 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2021-030 | 0.96836 | 0.92888 | -0.039481 |  | 0.95 | 1.05 | 0.04067 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2021-030 | 0.96836 | 0.92888 | -0.039481 |  | 0.95 | 1.05 | 0.040569 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2021-030 | 0.96836 | 0.92888 | -0.039481 |  | 0.95 | 1.05 | 0.03086 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2021-030 | 0.96836 | 0.92888 | -0.039481 |  | 0.95 | 1.05 | 0.033223 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2021-030 | 0.96836 | 0.92888 | -0.039481 |  | 0.95 | 1.05 | 0.033733 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2021-030 | 0.97297 | 0.91992 | -0.053049 |  | 0.95 | 1.05 | 0.036307 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2021-030 | 0.97297 | 0.91992 | -0.053049 |  | 0.95 | 1.05 | 0.052743 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2021-030 | 0.97297 | 0.91992 | -0.053049 |  | 0.95 | 1.05 | 0.039345 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2021-030 | 0.97297 | 0.91992 | -0.053049 |  | 0.95 | 1.05 | 0.031366 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2021-030 | 0.97297 | 0.91992 | -0.053049 |  | 0.95 | 1.05 | 0.041888 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2021-030 | 0.97297 | 0.91992 | -0.053049 |  | 0.95 | 1.05 | 0.038797 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2021-030 | 0.97297 | 0.91992 | -0.053049 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2021-030 | 0.97297 | 0.91992 | -0.053049 |  | 0.95 | 1.05 | 0.067346 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2021-030 | 0.97297 | 0.91992 | -0.053049 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2021-030 | 0.97297 | 0.91992 | -0.053049 |  | 0.95 | 1.05 | 0.030851 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2021-030 | 0.97297 | 0.91992 | -0.053049 |  | 0.95 | 1.05 | 0.032161 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2021-030 | 0.97297 | 0.91992 | -0.053049 |  | 0.95 | 1.05 | 0.04067 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2021-030 | 0.97297 | 0.91992 | -0.053049 |  | 0.95 | 1.05 | 0.040569 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2021-030 | 0.97297 | 0.91992 | -0.053049 |  | 0.95 | 1.05 | 0.03086 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2021-030 | 0.97297 | 0.91992 | -0.053049 |  | 0.95 | 1.05 | 0.033223 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2021-030 | 0.97297 | 0.91992 | -0.053049 |  | 0.95 | 1.05 | 0.033733 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2021-030 | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GEN-2021-030 | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2021-030 | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2021-030 | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2021-030 | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | GEN-2021-030 | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2021-030 | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | GEN-2021-030 | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2021-030 | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | GEN-2021-030 | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2021-030 | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2021-030 | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2021-030 | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2021-030 | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2021-030 | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GEN-2021-030 | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2021-030 | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | GEN-2021-030 | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | GEN-2021-030 | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2021-030 | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2021-030 | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2021-030 | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEN-2021-030 | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2021-030 | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2021-030 | 1.0002 | 0.88054 | -0.11968 |  | 0.95 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2021-096 | 0.99739 | 0.92248 | -0.074906 |  | 0.95 | 1.05 | 0.040439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GEN-2021-096 | 0.99739 | 0.92248 | -0.074906 |  | 0.95 | 1.05 | 0.034853 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2021-096 | 0.99739 | 0.92248 | -0.074906 |  | 0.95 | 1.05 | 0.046783 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2021-096 | 0.99739 | 0.92248 | -0.074906 |  | 0.95 | 1.05 | 0.047615 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2021-096 | 0.99739 | 0.92248 | -0.074906 |  | 0.95 | 1.05 | 0.034938 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | GEN-2021-096 | 0.99739 | 0.92248 | -0.074906 |  | 0.95 | 1.05 | 0.037875 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2021-096 | 0.99739 | 0.92248 | -0.074906 |  | 0.95 | 1.05 | 0.044022 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | GEN-2021-096 | 0.99739 | 0.92248 | -0.074906 |  | 0.95 | 1.05 | 0.030552 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2021-096 | 0.99739 | 0.92248 | -0.074906 |  | 0.95 | 1.05 | 0.038531 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2021-096 | 0.99739 | 0.92248 | -0.074906 |  | 0.95 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2021-096 | 0.99739 | 0.92248 | -0.074906 |  | 0.95 | 1.05 | 0.062491 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2021-096 | 0.99739 | 0.92248 | -0.074906 |  | 0.95 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2021-096 | 0.99739 | 0.92248 | -0.074906 |  | 0.95 | 1.05 | 0.038129 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2021-096 | 0.99739 | 0.92248 | -0.074906 |  | 0.95 | 1.05 | 0.038066 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GEN-2021-096 | 0.99739 | 0.92248 | -0.074906 |  | 0.95 | 1.05 | 0.034955 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2021-096 | 0.99739 | 0.92248 | -0.074906 |  | 0.95 | 1.05 | 0.06281 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2021-096 | 0.99739 | 0.92248 | -0.074906 |  | 0.95 | 1.05 | 0.045309 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2021-096 | 0.99739 | 0.92248 | -0.074906 |  | 0.95 | 1.05 | 0.035805 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2021-096 | 0.99739 | 0.92248 | -0.074906 |  | 0.95 | 1.05 | 0.032364 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEN-2021-096 | 0.99739 | 0.92248 | -0.074906 |  | 0.95 | 1.05 | 0.031815 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2021-096 | 0.99739 | 0.92248 | -0.074906 |  | 0.95 | 1.05 | 0.033886 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2021-096 | 0.99739 | 0.92248 | -0.074906 |  | 0.95 | 1.05 | 0.035554 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2021-103 | 0.96792 | 0.92353 | -0.044392 |  | 0.93 | 1.05 | 0.036307 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2021-103 | 0.96792 | 0.92353 | -0.044392 |  | 0.93 | 1.05 | 0.052743 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2021-103 | 0.96792 | 0.92353 | -0.044392 |  | 0.93 | 1.05 | 0.039345 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2021-103 | 0.96792 | 0.92353 | -0.044392 |  | 0.93 | 1.05 | 0.031366 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2021-103 | 0.96792 | 0.92353 | -0.044392 |  | 0.93 | 1.05 | 0.041888 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2021-103 | 0.96792 | 0.92353 | -0.044392 |  | 0.93 | 1.05 | 0.038797 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2021-103 | 0.96792 | 0.92353 | -0.044392 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2021-103 | 0.96792 | 0.92353 | -0.044392 |  | 0.93 | 1.05 | 0.067346 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2021-103 | 0.96792 | 0.92353 | -0.044392 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2021-103 | 0.96792 | 0.92353 | -0.044392 |  | 0.93 | 1.05 | 0.030851 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2021-103 | 0.96792 | 0.92353 | -0.044392 |  | 0.93 | 1.05 | 0.032161 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2021-103 | 0.96792 | 0.92353 | -0.044392 |  | 0.93 | 1.05 | 0.04067 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2021-103 | 0.96792 | 0.92353 | -0.044392 |  | 0.93 | 1.05 | 0.040569 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2021-103 | 0.96792 | 0.92353 | -0.044392 |  | 0.93 | 1.05 | 0.03086 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2021-103 | 0.96792 | 0.92353 | -0.044392 |  | 0.93 | 1.05 | 0.033223 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2021-103 | 0.96792 | 0.92353 | -0.044392 |  | 0.93 | 1.05 | 0.033733 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2021-103 | 0.97806 | 0.92688 | -0.051176 |  | 0.93 | 1.05 | 0.036307 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2021-103 | 0.97806 | 0.92688 | -0.051176 |  | 0.93 | 1.05 | 0.052743 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2021-103 | 0.97806 | 0.92688 | -0.051176 |  | 0.93 | 1.05 | 0.039345 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2021-103 | 0.97806 | 0.92688 | -0.051176 |  | 0.93 | 1.05 | 0.031366 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2021-103 | 0.97806 | 0.92688 | -0.051176 |  | 0.93 | 1.05 | 0.041888 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2021-103 | 0.97806 | 0.92688 | -0.051176 |  | 0.93 | 1.05 | 0.038797 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2021-103 | 0.97806 | 0.92688 | -0.051176 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2021-103 | 0.97806 | 0.92688 | -0.051176 |  | 0.93 | 1.05 | 0.067346 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2021-103 | 0.97806 | 0.92688 | -0.051176 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2021-103 | 0.97806 | 0.92688 | -0.051176 |  | 0.93 | 1.05 | 0.030851 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2021-103 | 0.97806 | 0.92688 | -0.051176 |  | 0.93 | 1.05 | 0.032161 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2021-103 | 0.97806 | 0.92688 | -0.051176 |  | 0.93 | 1.05 | 0.04067 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2021-103 | 0.97806 | 0.92688 | -0.051176 |  | 0.93 | 1.05 | 0.040569 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2021-103 | 0.97806 | 0.92688 | -0.051176 |  | 0.93 | 1.05 | 0.03086 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2021-103 | 0.97806 | 0.92688 | -0.051176 |  | 0.93 | 1.05 | 0.033223 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2021-103 | 0.97806 | 0.92688 | -0.051176 |  | 0.93 | 1.05 | 0.033733 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2021-103 | 0.98485 | 0.91679 | -0.06806 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GEN-2021-103 | 0.98485 | 0.91679 | -0.06806 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2021-103 | 0.98485 | 0.91679 | -0.06806 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2021-103 | 0.98485 | 0.91679 | -0.06806 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2021-103 | 0.98485 | 0.91679 | -0.06806 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | GEN-2021-103 | 0.98485 | 0.91679 | -0.06806 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2021-103 | 0.98485 | 0.91679 | -0.06806 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | GEN-2021-103 | 0.98485 | 0.91679 | -0.06806 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2021-103 | 0.98485 | 0.91679 | -0.06806 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | GEN-2021-103 | 0.98485 | 0.91679 | -0.06806 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2021-103 | 0.98485 | 0.91679 | -0.06806 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2021-103 | 0.98485 | 0.91679 | -0.06806 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2021-103 | 0.98485 | 0.91679 | -0.06806 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2021-103 | 0.98485 | 0.91679 | -0.06806 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2021-103 | 0.98485 | 0.91679 | -0.06806 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GEN-2021-103 | 0.98485 | 0.91679 | -0.06806 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2021-103 | 0.98485 | 0.91679 | -0.06806 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | GEN-2021-103 | 0.98485 | 0.91679 | -0.06806 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | GEN-2021-103 | 0.98485 | 0.91679 | -0.06806 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2021-103 | 0.98485 | 0.91679 | -0.06806 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2021-103 | 0.98485 | 0.91679 | -0.06806 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2021-103 | 0.98485 | 0.91679 | -0.06806 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEN-2021-103 | 0.98485 | 0.91679 | -0.06806 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2021-103 | 0.98485 | 0.91679 | -0.06806 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2021-103 | 0.98485 | 0.91679 | -0.06806 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2022-006 | 0.99576 | 0.92254 | -0.073219 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GEN-2022-006 | 0.99576 | 0.92254 | -0.073219 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2022-006 | 0.99576 | 0.92254 | -0.073219 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2022-006 | 0.99576 | 0.92254 | -0.073219 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2022-006 | 0.99576 | 0.92254 | -0.073219 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | GEN-2022-006 | 0.99576 | 0.92254 | -0.073219 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2022-006 | 0.99576 | 0.92254 | -0.073219 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | GEN-2022-006 | 0.99576 | 0.92254 | -0.073219 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2022-006 | 0.99576 | 0.92254 | -0.073219 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | GEN-2022-006 | 0.99576 | 0.92254 | -0.073219 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2022-006 | 0.99576 | 0.92254 | -0.073219 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2022-006 | 0.99576 | 0.92254 | -0.073219 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2022-006 | 0.99576 | 0.92254 | -0.073219 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2022-006 | 0.99576 | 0.92254 | -0.073219 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2022-006 | 0.99576 | 0.92254 | -0.073219 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GEN-2022-006 | 0.99576 | 0.92254 | -0.073219 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2022-006 | 0.99576 | 0.92254 | -0.073219 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | GEN-2022-006 | 0.99576 | 0.92254 | -0.073219 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | GEN-2022-006 | 0.99576 | 0.92254 | -0.073219 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2022-006 | 0.99576 | 0.92254 | -0.073219 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2022-006 | 0.99576 | 0.92254 | -0.073219 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2022-006 | 0.99576 | 0.92254 | -0.073219 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEN-2022-006 | 0.99576 | 0.92254 | -0.073219 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2022-006 | 0.99576 | 0.92254 | -0.073219 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2022-006 | 0.99576 | 0.92254 | -0.073219 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2022-007 | 0.96384 | 0.86895 | -0.094885 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GEN-2022-007 | 0.96384 | 0.86895 | -0.094885 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2022-007 | 0.96384 | 0.86895 | -0.094885 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2022-007 | 0.96384 | 0.86895 | -0.094885 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2022-007 | 0.96384 | 0.86895 | -0.094885 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | GEN-2022-007 | 0.96384 | 0.86895 | -0.094885 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2022-007 | 0.96384 | 0.86895 | -0.094885 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | GEN-2022-007 | 0.96384 | 0.86895 | -0.094885 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2022-007 | 0.96384 | 0.86895 | -0.094885 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | GEN-2022-007 | 0.96384 | 0.86895 | -0.094885 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2022-007 | 0.96384 | 0.86895 | -0.094885 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2022-007 | 0.96384 | 0.86895 | -0.094885 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2022-007 | 0.96384 | 0.86895 | -0.094885 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2022-007 | 0.96384 | 0.86895 | -0.094885 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2022-007 | 0.96384 | 0.86895 | -0.094885 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GEN-2022-007 | 0.96384 | 0.86895 | -0.094885 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2022-007 | 0.96384 | 0.86895 | -0.094885 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | GEN-2022-007 | 0.96384 | 0.86895 | -0.094885 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | GEN-2022-007 | 0.96384 | 0.86895 | -0.094885 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2022-007 | 0.96384 | 0.86895 | -0.094885 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2022-007 | 0.96384 | 0.86895 | -0.094885 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2022-007 | 0.96384 | 0.86895 | -0.094885 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEN-2022-007 | 0.96384 | 0.86895 | -0.094885 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2022-007 | 0.96384 | 0.86895 | -0.094885 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2022-007 | 0.96384 | 0.86895 | -0.094885 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | ASGI-2024-023 | GEN-2022-013 | 1.0053 | 0.94276 | -0.062556 |  | 0.95 | 1.05 | 0.079962 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | GEN-2022-013 | 1.0053 | 0.94276 | -0.062556 |  | 0.95 | 1.05 | 0.065323 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-068 | GEN-2022-013 | 1.0053 | 0.94276 | -0.062556 |  | 0.95 | 1.05 | 0.067422 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-071 | GEN-2022-013 | 1.0053 | 0.94276 | -0.062556 |  | 0.95 | 1.05 | 0.074668 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GEN-2022-013 | 1.0053 | 0.94276 | -0.062556 |  | 0.95 | 1.05 | 0.053027 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-122 | GEN-2022-013 | 1.0053 | 0.94276 | -0.062556 |  | 0.95 | 1.05 | 0.082926 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-177 | GEN-2022-013 | 1.0053 | 0.94276 | -0.062556 |  | 0.95 | 1.05 | 0.084694 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-178 | GEN-2022-013 | 1.0053 | 0.94276 | -0.062556 |  | 0.95 | 1.05 | 0.078867 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | GEN-2022-013 | 1.0053 | 0.94276 | -0.062556 |  | 0.95 | 1.05 | 0.031571 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-220 | GEN-2022-013 | 1.0053 | 0.94276 | -0.062556 |  | 0.95 | 1.05 | 0.075331 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-232 | GEN-2022-013 | 1.0053 | 0.94276 | -0.062556 |  | 0.95 | 1.05 | 0.078906 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | GEN-2022-013 | 1.0053 | 0.94276 | -0.062556 |  | 0.95 | 1.05 | 0.065323 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GEN-2022-013 | 1.0053 | 0.94276 | -0.062556 |  | 0.95 | 1.05 | 0.03431 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | GEN-2022-013 | 1.0053 | 0.94276 | -0.062556 |  | 0.95 | 1.05 | 0.031504 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | GEN-2022-013 | 1.0053 | 0.94276 | -0.062556 |  | 0.95 | 1.05 | 0.031504 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | GEN-2022-013 | 1.0053 | 0.94276 | -0.062556 |  | 0.95 | 1.05 | 0.030663 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | GEN-2022-013 | 1.0053 | 0.94276 | -0.062556 |  | 0.95 | 1.05 | 0.04269 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-376 | GEN-2022-013 | 1.0053 | 0.94276 | -0.062556 |  | 0.95 | 1.05 | 0.082476 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2022-013 | 1.0014 | 0.94262 | -0.05878 |  | 0.95 | 1.05 | 0.040439 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2022-013 | 1.0014 | 0.94262 | -0.05878 |  | 0.95 | 1.05 | 0.034938 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | GEN-2022-013 | 1.0014 | 0.94262 | -0.05878 |  | 0.95 | 1.05 | 0.037875 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | GEN-2022-013 | 1.0014 | 0.94262 | -0.05878 |  | 0.95 | 1.05 | 0.030552 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2022-013 | 1.0014 | 0.94262 | -0.05878 |  | 0.95 | 1.05 | 0.038531 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2022-013 | 1.0014 | 0.94262 | -0.05878 |  | 0.95 | 1.05 | 0.037118 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2022-013 | 1.0014 | 0.94262 | -0.05878 |  | 0.95 | 1.05 | 0.037118 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2022-013 | 1.0014 | 0.94262 | -0.05878 |  | 0.95 | 1.05 | 0.038129 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2022-013 | 1.0014 | 0.94262 | -0.05878 |  | 0.95 | 1.05 | 0.038066 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2022-013 | 1.0014 | 0.94262 | -0.05878 |  | 0.95 | 1.05 | 0.035805 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2022-013 | 1.0014 | 0.94262 | -0.05878 |  | 0.95 | 1.05 | 0.032364 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEN-2022-013 | 1.0014 | 0.94262 | -0.05878 |  | 0.95 | 1.05 | 0.031815 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2022-013 | 1.0014 | 0.94262 | -0.05878 |  | 0.95 | 1.05 | 0.033886 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2022-013 | 1.0014 | 0.94262 | -0.05878 |  | 0.95 | 1.05 | 0.035554 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2022-013 | 1.0013 | 0.9454 | -0.055938 |  | 0.95 | 1.05 | 0.039728 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2022-013 | 1.0013 | 0.9454 | -0.055938 |  | 0.95 | 1.05 | 0.034227 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | GEN-2022-013 | 1.0013 | 0.9454 | -0.055938 |  | 0.95 | 1.05 | 0.037164 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2022-013 | 1.0013 | 0.9454 | -0.055938 |  | 0.95 | 1.05 | 0.03782 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2022-013 | 1.0013 | 0.9454 | -0.055938 |  | 0.95 | 1.05 | 0.036407 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2022-013 | 1.0013 | 0.9454 | -0.055938 |  | 0.95 | 1.05 | 0.036407 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2022-013 | 1.0013 | 0.9454 | -0.055938 |  | 0.95 | 1.05 | 0.037418 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2022-013 | 1.0013 | 0.9454 | -0.055938 |  | 0.95 | 1.05 | 0.037355 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2022-013 | 1.0013 | 0.9454 | -0.055938 |  | 0.95 | 1.05 | 0.035094 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2022-013 | 1.0013 | 0.9454 | -0.055938 |  | 0.95 | 1.05 | 0.031652 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEN-2022-013 | 1.0013 | 0.9454 | -0.055938 |  | 0.95 | 1.05 | 0.031104 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2022-013 | 1.0013 | 0.9454 | -0.055938 |  | 0.95 | 1.05 | 0.033175 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2022-013 | 1.0013 | 0.9454 | -0.055938 |  | 0.95 | 1.05 | 0.034843 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2022-013 | 1.0015 | 0.94147 | -0.060015 |  | 0.95 | 1.05 | 0.040439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GEN-2022-013 | 1.0015 | 0.94147 | -0.060015 |  | 0.95 | 1.05 | 0.034853 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2022-013 | 1.0015 | 0.94147 | -0.060015 |  | 0.95 | 1.05 | 0.046783 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2022-013 | 1.0015 | 0.94147 | -0.060015 |  | 0.95 | 1.05 | 0.047615 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2022-013 | 1.0015 | 0.94147 | -0.060015 |  | 0.95 | 1.05 | 0.034938 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | GEN-2022-013 | 1.0015 | 0.94147 | -0.060015 |  | 0.95 | 1.05 | 0.037875 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2022-013 | 1.0015 | 0.94147 | -0.060015 |  | 0.95 | 1.05 | 0.044022 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | GEN-2022-013 | 1.0015 | 0.94147 | -0.060015 |  | 0.95 | 1.05 | 0.030552 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2022-013 | 1.0015 | 0.94147 | -0.060015 |  | 0.95 | 1.05 | 0.038531 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2022-013 | 1.0015 | 0.94147 | -0.060015 |  | 0.95 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2022-013 | 1.0015 | 0.94147 | -0.060015 |  | 0.95 | 1.05 | 0.062491 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2022-013 | 1.0015 | 0.94147 | -0.060015 |  | 0.95 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2022-013 | 1.0015 | 0.94147 | -0.060015 |  | 0.95 | 1.05 | 0.038129 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2022-013 | 1.0015 | 0.94147 | -0.060015 |  | 0.95 | 1.05 | 0.038066 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GEN-2022-013 | 1.0015 | 0.94147 | -0.060015 |  | 0.95 | 1.05 | 0.034955 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2022-013 | 1.0015 | 0.94147 | -0.060015 |  | 0.95 | 1.05 | 0.06281 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2022-013 | 1.0015 | 0.94147 | -0.060015 |  | 0.95 | 1.05 | 0.045309 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2022-013 | 1.0015 | 0.94147 | -0.060015 |  | 0.95 | 1.05 | 0.035805 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2022-013 | 1.0015 | 0.94147 | -0.060015 |  | 0.95 | 1.05 | 0.032364 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEN-2022-013 | 1.0015 | 0.94147 | -0.060015 |  | 0.95 | 1.05 | 0.031815 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2022-013 | 1.0015 | 0.94147 | -0.060015 |  | 0.95 | 1.05 | 0.033886 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2022-013 | 1.0015 | 0.94147 | -0.060015 |  | 0.95 | 1.05 | 0.035554 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2022-013 | 1.0022 | 0.88966 | -0.11254 |  | 0.95 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GEN-2022-013 | 1.0022 | 0.88966 | -0.11254 |  | 0.95 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2022-013 | 1.0022 | 0.88966 | -0.11254 |  | 0.95 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2022-013 | 1.0022 | 0.88966 | -0.11254 |  | 0.95 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2022-013 | 1.0022 | 0.88966 | -0.11254 |  | 0.95 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | GEN-2022-013 | 1.0022 | 0.88966 | -0.11254 |  | 0.95 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2022-013 | 1.0022 | 0.88966 | -0.11254 |  | 0.95 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | GEN-2022-013 | 1.0022 | 0.88966 | -0.11254 |  | 0.95 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2022-013 | 1.0022 | 0.88966 | -0.11254 |  | 0.95 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | GEN-2022-013 | 1.0022 | 0.88966 | -0.11254 |  | 0.95 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2022-013 | 1.0022 | 0.88966 | -0.11254 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2022-013 | 1.0022 | 0.88966 | -0.11254 |  | 0.95 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2022-013 | 1.0022 | 0.88966 | -0.11254 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2022-013 | 1.0022 | 0.88966 | -0.11254 |  | 0.95 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2022-013 | 1.0022 | 0.88966 | -0.11254 |  | 0.95 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GEN-2022-013 | 1.0022 | 0.88966 | -0.11254 |  | 0.95 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2022-013 | 1.0022 | 0.88966 | -0.11254 |  | 0.95 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | GEN-2022-013 | 1.0022 | 0.88966 | -0.11254 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | GEN-2022-013 | 1.0022 | 0.88966 | -0.11254 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2022-013 | 1.0022 | 0.88966 | -0.11254 |  | 0.95 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2022-013 | 1.0022 | 0.88966 | -0.11254 |  | 0.95 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2022-013 | 1.0022 | 0.88966 | -0.11254 |  | 0.95 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEN-2022-013 | 1.0022 | 0.88966 | -0.11254 |  | 0.95 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2022-013 | 1.0022 | 0.88966 | -0.11254 |  | 0.95 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2022-013 | 1.0022 | 0.88966 | -0.11254 |  | 0.95 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2023-220 | 0.99132 | 0.92973 | -0.061586 |  | 0.95 | 1.05 | 0.039728 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2023-220 | 0.99132 | 0.92973 | -0.061586 |  | 0.95 | 1.05 | 0.040762 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2023-220 | 0.99132 | 0.92973 | -0.061586 |  | 0.95 | 1.05 | 0.030778 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2023-220 | 0.99132 | 0.92973 | -0.061586 |  | 0.95 | 1.05 | 0.034227 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | GEN-2023-220 | 0.99132 | 0.92973 | -0.061586 |  | 0.95 | 1.05 | 0.037164 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2023-220 | 0.99132 | 0.92973 | -0.061586 |  | 0.95 | 1.05 | 0.031937 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2023-220 | 0.99132 | 0.92973 | -0.061586 |  | 0.95 | 1.05 | 0.03782 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2023-220 | 0.99132 | 0.92973 | -0.061586 |  | 0.95 | 1.05 | 0.036407 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2023-220 | 0.99132 | 0.92973 | -0.061586 |  | 0.95 | 1.05 | 0.053181 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2023-220 | 0.99132 | 0.92973 | -0.061586 |  | 0.95 | 1.05 | 0.036407 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2023-220 | 0.99132 | 0.92973 | -0.061586 |  | 0.95 | 1.05 | 0.037418 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2023-220 | 0.99132 | 0.92973 | -0.061586 |  | 0.95 | 1.05 | 0.037355 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2023-220 | 0.99132 | 0.92973 | -0.061586 |  | 0.95 | 1.05 | 0.032533 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2023-220 | 0.99132 | 0.92973 | -0.061586 |  | 0.95 | 1.05 | 0.031326 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2023-220 | 0.99132 | 0.92973 | -0.061586 |  | 0.95 | 1.05 | 0.035094 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2023-220 | 0.99132 | 0.92973 | -0.061586 |  | 0.95 | 1.05 | 0.031652 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEN-2023-220 | 0.99132 | 0.92973 | -0.061586 |  | 0.95 | 1.05 | 0.031104 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2023-220 | 0.99132 | 0.92973 | -0.061586 |  | 0.95 | 1.05 | 0.033175 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2023-220 | 0.99132 | 0.92973 | -0.061586 |  | 0.95 | 1.05 | 0.034843 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | GEN-2023-220 | 0.99498 | 0.93081 | -0.064164 |  | 0.95 | 1.05 | 0.03053 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2023-220 | 0.99498 | 0.93081 | -0.064164 |  | 0.95 | 1.05 | 0.044933 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GEN-2023-220 | 0.99498 | 0.93081 | -0.064164 |  | 0.95 | 1.05 | 0.047811 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2023-220 | 0.99498 | 0.93081 | -0.064164 |  | 0.95 | 1.05 | 0.09719 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2023-220 | 0.99498 | 0.93081 | -0.064164 |  | 0.95 | 1.05 | 0.069376 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2023-220 | 0.99498 | 0.93081 | -0.064164 |  | 0.95 | 1.05 | 0.04277 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2023-220 | 0.99498 | 0.93081 | -0.064164 |  | 0.95 | 1.05 | 0.071112 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | GEN-2023-220 | 0.99498 | 0.93081 | -0.064164 |  | 0.95 | 1.05 | 0.039357 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | GEN-2023-220 | 0.99498 | 0.93081 | -0.064164 |  | 0.95 | 1.05 | 0.04035 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2023-220 | 0.99498 | 0.93081 | -0.064164 |  | 0.95 | 1.05 | 0.052332 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | GEN-2023-220 | 0.99498 | 0.93081 | -0.064164 |  | 0.95 | 1.05 | 0.045944 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2023-220 | 0.99498 | 0.93081 | -0.064164 |  | 0.95 | 1.05 | 0.038178 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2023-220 | 0.99498 | 0.93081 | -0.064164 |  | 0.95 | 1.05 | 0.13469 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | GEN-2023-220 | 0.99498 | 0.93081 | -0.064164 |  | 0.95 | 1.05 | 0.03053 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2023-220 | 0.99498 | 0.93081 | -0.064164 |  | 0.95 | 1.05 | 0.038178 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2023-220 | 0.99498 | 0.93081 | -0.064164 |  | 0.95 | 1.05 | 0.037309 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2023-220 | 0.99498 | 0.93081 | -0.064164 |  | 0.95 | 1.05 | 0.040075 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GEN-2023-220 | 0.99498 | 0.93081 | -0.064164 |  | 0.95 | 1.05 | 0.053764 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2023-220 | 0.99498 | 0.93081 | -0.064164 |  | 0.95 | 1.05 | 0.071762 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | GEN-2023-220 | 0.99498 | 0.93081 | -0.064164 |  | 0.95 | 1.05 | 0.047827 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | GEN-2023-220 | 0.99498 | 0.93081 | -0.064164 |  | 0.95 | 1.05 | 0.047827 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2023-220 | 0.99498 | 0.93081 | -0.064164 |  | 0.95 | 1.05 | 0.070303 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2023-220 | 0.99498 | 0.93081 | -0.064164 |  | 0.95 | 1.05 | 0.040614 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | GEN-2023-220 | 0.99498 | 0.93081 | -0.064164 |  | 0.95 | 1.05 | 0.039729 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2023-220 | 0.99498 | 0.93081 | -0.064164 |  | 0.95 | 1.05 | 0.049662 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEN-2023-220 | 0.99498 | 0.93081 | -0.064164 |  | 0.95 | 1.05 | 0.042332 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2023-220 | 0.99498 | 0.93081 | -0.064164 |  | 0.95 | 1.05 | 0.048722 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2023-220 | 0.99498 | 0.93081 | -0.064164 |  | 0.95 | 1.05 | 0.038156 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | GEN-2023-220 | 0.99498 | 0.93081 | -0.064164 |  | 0.95 | 1.05 | 0.036794 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2023-220 | 0.99126 | 0.9358 | -0.055463 |  | 0.95 | 1.05 | 0.036307 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2023-220 | 0.99126 | 0.9358 | -0.055463 |  | 0.95 | 1.05 | 0.052743 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2023-220 | 0.99126 | 0.9358 | -0.055463 |  | 0.95 | 1.05 | 0.039345 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2023-220 | 0.99126 | 0.9358 | -0.055463 |  | 0.95 | 1.05 | 0.031366 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2023-220 | 0.99126 | 0.9358 | -0.055463 |  | 0.95 | 1.05 | 0.041888 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2023-220 | 0.99126 | 0.9358 | -0.055463 |  | 0.95 | 1.05 | 0.038797 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2023-220 | 0.99126 | 0.9358 | -0.055463 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2023-220 | 0.99126 | 0.9358 | -0.055463 |  | 0.95 | 1.05 | 0.067346 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2023-220 | 0.99126 | 0.9358 | -0.055463 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2023-220 | 0.99126 | 0.9358 | -0.055463 |  | 0.95 | 1.05 | 0.030851 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2023-220 | 0.99126 | 0.9358 | -0.055463 |  | 0.95 | 1.05 | 0.032161 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2023-220 | 0.99126 | 0.9358 | -0.055463 |  | 0.95 | 1.05 | 0.04067 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2023-220 | 0.99126 | 0.9358 | -0.055463 |  | 0.95 | 1.05 | 0.040569 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2023-220 | 0.99126 | 0.9358 | -0.055463 |  | 0.95 | 1.05 | 0.03086 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2023-220 | 0.99126 | 0.9358 | -0.055463 |  | 0.95 | 1.05 | 0.033223 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2023-220 | 0.99126 | 0.9358 | -0.055463 |  | 0.95 | 1.05 | 0.033733 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2023-220 | 0.99303 | 0.92766 | -0.065366 |  | 0.95 | 1.05 | 0.036307 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2023-220 | 0.99303 | 0.92766 | -0.065366 |  | 0.95 | 1.05 | 0.052743 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2023-220 | 0.99303 | 0.92766 | -0.065366 |  | 0.95 | 1.05 | 0.039345 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2023-220 | 0.99303 | 0.92766 | -0.065366 |  | 0.95 | 1.05 | 0.031366 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2023-220 | 0.99303 | 0.92766 | -0.065366 |  | 0.95 | 1.05 | 0.041888 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2023-220 | 0.99303 | 0.92766 | -0.065366 |  | 0.95 | 1.05 | 0.038797 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2023-220 | 0.99303 | 0.92766 | -0.065366 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2023-220 | 0.99303 | 0.92766 | -0.065366 |  | 0.95 | 1.05 | 0.067346 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2023-220 | 0.99303 | 0.92766 | -0.065366 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2023-220 | 0.99303 | 0.92766 | -0.065366 |  | 0.95 | 1.05 | 0.030851 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2023-220 | 0.99303 | 0.92766 | -0.065366 |  | 0.95 | 1.05 | 0.032161 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2023-220 | 0.99303 | 0.92766 | -0.065366 |  | 0.95 | 1.05 | 0.04067 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2023-220 | 0.99303 | 0.92766 | -0.065366 |  | 0.95 | 1.05 | 0.040569 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2023-220 | 0.99303 | 0.92766 | -0.065366 |  | 0.95 | 1.05 | 0.03086 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2023-220 | 0.99303 | 0.92766 | -0.065366 |  | 0.95 | 1.05 | 0.033223 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2023-220 | 0.99303 | 0.92766 | -0.065366 |  | 0.95 | 1.05 | 0.033733 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2023-220 | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GEN-2023-220 | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2023-220 | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2023-220 | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2023-220 | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | GEN-2023-220 | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2023-220 | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | GEN-2023-220 | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2023-220 | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | GEN-2023-220 | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2023-220 | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2023-220 | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2023-220 | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2023-220 | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2023-220 | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GEN-2023-220 | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2023-220 | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | GEN-2023-220 | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | GEN-2023-220 | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2023-220 | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2023-220 | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2023-220 | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEN-2023-220 | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2023-220 | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2023-220 | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2023-221 | 0.99221 | 0.93069 | -0.061519 |  | 0.95 | 1.05 | 0.039728 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2023-221 | 0.99221 | 0.93069 | -0.061519 |  | 0.95 | 1.05 | 0.040762 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2023-221 | 0.99221 | 0.93069 | -0.061519 |  | 0.95 | 1.05 | 0.030778 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2023-221 | 0.99221 | 0.93069 | -0.061519 |  | 0.95 | 1.05 | 0.034227 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | GEN-2023-221 | 0.99221 | 0.93069 | -0.061519 |  | 0.95 | 1.05 | 0.037164 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2023-221 | 0.99221 | 0.93069 | -0.061519 |  | 0.95 | 1.05 | 0.031937 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2023-221 | 0.99221 | 0.93069 | -0.061519 |  | 0.95 | 1.05 | 0.03782 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2023-221 | 0.99221 | 0.93069 | -0.061519 |  | 0.95 | 1.05 | 0.036407 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2023-221 | 0.99221 | 0.93069 | -0.061519 |  | 0.95 | 1.05 | 0.053181 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2023-221 | 0.99221 | 0.93069 | -0.061519 |  | 0.95 | 1.05 | 0.036407 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2023-221 | 0.99221 | 0.93069 | -0.061519 |  | 0.95 | 1.05 | 0.037418 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2023-221 | 0.99221 | 0.93069 | -0.061519 |  | 0.95 | 1.05 | 0.037355 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2023-221 | 0.99221 | 0.93069 | -0.061519 |  | 0.95 | 1.05 | 0.032533 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2023-221 | 0.99221 | 0.93069 | -0.061519 |  | 0.95 | 1.05 | 0.031326 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2023-221 | 0.99221 | 0.93069 | -0.061519 |  | 0.95 | 1.05 | 0.035094 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2023-221 | 0.99221 | 0.93069 | -0.061519 |  | 0.95 | 1.05 | 0.031652 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEN-2023-221 | 0.99221 | 0.93069 | -0.061519 |  | 0.95 | 1.05 | 0.031104 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2023-221 | 0.99221 | 0.93069 | -0.061519 |  | 0.95 | 1.05 | 0.033175 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2023-221 | 0.99221 | 0.93069 | -0.061519 |  | 0.95 | 1.05 | 0.034843 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | GEN-2023-221 | 0.99565 | 0.93146 | -0.064187 |  | 0.95 | 1.05 | 0.03053 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2023-221 | 0.99565 | 0.93146 | -0.064187 |  | 0.95 | 1.05 | 0.044933 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GEN-2023-221 | 0.99565 | 0.93146 | -0.064187 |  | 0.95 | 1.05 | 0.047811 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2023-221 | 0.99565 | 0.93146 | -0.064187 |  | 0.95 | 1.05 | 0.09719 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2023-221 | 0.99565 | 0.93146 | -0.064187 |  | 0.95 | 1.05 | 0.069376 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2023-221 | 0.99565 | 0.93146 | -0.064187 |  | 0.95 | 1.05 | 0.04277 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2023-221 | 0.99565 | 0.93146 | -0.064187 |  | 0.95 | 1.05 | 0.071112 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | GEN-2023-221 | 0.99565 | 0.93146 | -0.064187 |  | 0.95 | 1.05 | 0.039357 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | GEN-2023-221 | 0.99565 | 0.93146 | -0.064187 |  | 0.95 | 1.05 | 0.04035 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2023-221 | 0.99565 | 0.93146 | -0.064187 |  | 0.95 | 1.05 | 0.052332 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | GEN-2023-221 | 0.99565 | 0.93146 | -0.064187 |  | 0.95 | 1.05 | 0.045944 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2023-221 | 0.99565 | 0.93146 | -0.064187 |  | 0.95 | 1.05 | 0.038178 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2023-221 | 0.99565 | 0.93146 | -0.064187 |  | 0.95 | 1.05 | 0.13469 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | GEN-2023-221 | 0.99565 | 0.93146 | -0.064187 |  | 0.95 | 1.05 | 0.03053 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2023-221 | 0.99565 | 0.93146 | -0.064187 |  | 0.95 | 1.05 | 0.038178 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2023-221 | 0.99565 | 0.93146 | -0.064187 |  | 0.95 | 1.05 | 0.037309 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2023-221 | 0.99565 | 0.93146 | -0.064187 |  | 0.95 | 1.05 | 0.040075 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GEN-2023-221 | 0.99565 | 0.93146 | -0.064187 |  | 0.95 | 1.05 | 0.053764 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2023-221 | 0.99565 | 0.93146 | -0.064187 |  | 0.95 | 1.05 | 0.071762 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | GEN-2023-221 | 0.99565 | 0.93146 | -0.064187 |  | 0.95 | 1.05 | 0.047827 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | GEN-2023-221 | 0.99565 | 0.93146 | -0.064187 |  | 0.95 | 1.05 | 0.047827 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2023-221 | 0.99565 | 0.93146 | -0.064187 |  | 0.95 | 1.05 | 0.070303 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2023-221 | 0.99565 | 0.93146 | -0.064187 |  | 0.95 | 1.05 | 0.040614 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | GEN-2023-221 | 0.99565 | 0.93146 | -0.064187 |  | 0.95 | 1.05 | 0.039729 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2023-221 | 0.99565 | 0.93146 | -0.064187 |  | 0.95 | 1.05 | 0.049662 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEN-2023-221 | 0.99565 | 0.93146 | -0.064187 |  | 0.95 | 1.05 | 0.042332 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2023-221 | 0.99565 | 0.93146 | -0.064187 |  | 0.95 | 1.05 | 0.048722 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2023-221 | 0.99565 | 0.93146 | -0.064187 |  | 0.95 | 1.05 | 0.038156 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | GEN-2023-221 | 0.99565 | 0.93146 | -0.064187 |  | 0.95 | 1.05 | 0.036794 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2023-221 | 0.99222 | 0.93695 | -0.05527 |  | 0.95 | 1.05 | 0.036307 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2023-221 | 0.99222 | 0.93695 | -0.05527 |  | 0.95 | 1.05 | 0.052743 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2023-221 | 0.99222 | 0.93695 | -0.05527 |  | 0.95 | 1.05 | 0.039345 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2023-221 | 0.99222 | 0.93695 | -0.05527 |  | 0.95 | 1.05 | 0.031366 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2023-221 | 0.99222 | 0.93695 | -0.05527 |  | 0.95 | 1.05 | 0.041888 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2023-221 | 0.99222 | 0.93695 | -0.05527 |  | 0.95 | 1.05 | 0.038797 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2023-221 | 0.99222 | 0.93695 | -0.05527 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2023-221 | 0.99222 | 0.93695 | -0.05527 |  | 0.95 | 1.05 | 0.067346 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2023-221 | 0.99222 | 0.93695 | -0.05527 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2023-221 | 0.99222 | 0.93695 | -0.05527 |  | 0.95 | 1.05 | 0.030851 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2023-221 | 0.99222 | 0.93695 | -0.05527 |  | 0.95 | 1.05 | 0.032161 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2023-221 | 0.99222 | 0.93695 | -0.05527 |  | 0.95 | 1.05 | 0.04067 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2023-221 | 0.99222 | 0.93695 | -0.05527 |  | 0.95 | 1.05 | 0.040569 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2023-221 | 0.99222 | 0.93695 | -0.05527 |  | 0.95 | 1.05 | 0.03086 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2023-221 | 0.99222 | 0.93695 | -0.05527 |  | 0.95 | 1.05 | 0.033223 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2023-221 | 0.99222 | 0.93695 | -0.05527 |  | 0.95 | 1.05 | 0.033733 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2023-221 | 0.99384 | 0.92866 | -0.065176 |  | 0.95 | 1.05 | 0.036307 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2023-221 | 0.99384 | 0.92866 | -0.065176 |  | 0.95 | 1.05 | 0.052743 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2023-221 | 0.99384 | 0.92866 | -0.065176 |  | 0.95 | 1.05 | 0.039345 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2023-221 | 0.99384 | 0.92866 | -0.065176 |  | 0.95 | 1.05 | 0.031366 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2023-221 | 0.99384 | 0.92866 | -0.065176 |  | 0.95 | 1.05 | 0.041888 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2023-221 | 0.99384 | 0.92866 | -0.065176 |  | 0.95 | 1.05 | 0.038797 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2023-221 | 0.99384 | 0.92866 | -0.065176 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2023-221 | 0.99384 | 0.92866 | -0.065176 |  | 0.95 | 1.05 | 0.067346 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2023-221 | 0.99384 | 0.92866 | -0.065176 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2023-221 | 0.99384 | 0.92866 | -0.065176 |  | 0.95 | 1.05 | 0.030851 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2023-221 | 0.99384 | 0.92866 | -0.065176 |  | 0.95 | 1.05 | 0.032161 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2023-221 | 0.99384 | 0.92866 | -0.065176 |  | 0.95 | 1.05 | 0.04067 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2023-221 | 0.99384 | 0.92866 | -0.065176 |  | 0.95 | 1.05 | 0.040569 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2023-221 | 0.99384 | 0.92866 | -0.065176 |  | 0.95 | 1.05 | 0.03086 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2023-221 | 0.99384 | 0.92866 | -0.065176 |  | 0.95 | 1.05 | 0.033223 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2023-221 | 0.99384 | 0.92866 | -0.065176 |  | 0.95 | 1.05 | 0.033733 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2023-221 | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GEN-2023-221 | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2023-221 | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2023-221 | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2023-221 | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | GEN-2023-221 | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2023-221 | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | GEN-2023-221 | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2023-221 | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | GEN-2023-221 | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2023-221 | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2023-221 | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2023-221 | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2023-221 | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2023-221 | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GEN-2023-221 | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2023-221 | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | GEN-2023-221 | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | GEN-2023-221 | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2023-221 | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2023-221 | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2023-221 | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEN-2023-221 | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2023-221 | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2023-221 | 0.98593 | 0.91876 | -0.067163 |  | 0.95 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | ASGI-2024-023 | GEN-2024-076 | 1.0056 | 0.94502 | -0.06055 |  | 0.95 | 1.05 | 0.079962 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | GEN-2024-076 | 1.0056 | 0.94502 | -0.06055 |  | 0.95 | 1.05 | 0.065323 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-068 | GEN-2024-076 | 1.0056 | 0.94502 | -0.06055 |  | 0.95 | 1.05 | 0.067422 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-071 | GEN-2024-076 | 1.0056 | 0.94502 | -0.06055 |  | 0.95 | 1.05 | 0.074668 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GEN-2024-076 | 1.0056 | 0.94502 | -0.06055 |  | 0.95 | 1.05 | 0.053027 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-122 | GEN-2024-076 | 1.0056 | 0.94502 | -0.06055 |  | 0.95 | 1.05 | 0.082926 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-177 | GEN-2024-076 | 1.0056 | 0.94502 | -0.06055 |  | 0.95 | 1.05 | 0.084694 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-178 | GEN-2024-076 | 1.0056 | 0.94502 | -0.06055 |  | 0.95 | 1.05 | 0.078867 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | GEN-2024-076 | 1.0056 | 0.94502 | -0.06055 |  | 0.95 | 1.05 | 0.031571 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-220 | GEN-2024-076 | 1.0056 | 0.94502 | -0.06055 |  | 0.95 | 1.05 | 0.075331 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-232 | GEN-2024-076 | 1.0056 | 0.94502 | -0.06055 |  | 0.95 | 1.05 | 0.078906 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | GEN-2024-076 | 1.0056 | 0.94502 | -0.06055 |  | 0.95 | 1.05 | 0.065323 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GEN-2024-076 | 1.0056 | 0.94502 | -0.06055 |  | 0.95 | 1.05 | 0.03431 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | GEN-2024-076 | 1.0056 | 0.94502 | -0.06055 |  | 0.95 | 1.05 | 0.031504 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | GEN-2024-076 | 1.0056 | 0.94502 | -0.06055 |  | 0.95 | 1.05 | 0.031504 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | GEN-2024-076 | 1.0056 | 0.94502 | -0.06055 |  | 0.95 | 1.05 | 0.030663 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | GEN-2024-076 | 1.0056 | 0.94502 | -0.06055 |  | 0.95 | 1.05 | 0.04269 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-376 | GEN-2024-076 | 1.0056 | 0.94502 | -0.06055 |  | 0.95 | 1.05 | 0.082476 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2024-076 | 1.0017 | 0.94474 | -0.056933 |  | 0.95 | 1.05 | 0.040439 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2024-076 | 1.0017 | 0.94474 | -0.056933 |  | 0.95 | 1.05 | 0.034938 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | GEN-2024-076 | 1.0017 | 0.94474 | -0.056933 |  | 0.95 | 1.05 | 0.037875 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | GEN-2024-076 | 1.0017 | 0.94474 | -0.056933 |  | 0.95 | 1.05 | 0.030552 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2024-076 | 1.0017 | 0.94474 | -0.056933 |  | 0.95 | 1.05 | 0.038531 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2024-076 | 1.0017 | 0.94474 | -0.056933 |  | 0.95 | 1.05 | 0.037118 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2024-076 | 1.0017 | 0.94474 | -0.056933 |  | 0.95 | 1.05 | 0.037118 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2024-076 | 1.0017 | 0.94474 | -0.056933 |  | 0.95 | 1.05 | 0.038129 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2024-076 | 1.0017 | 0.94474 | -0.056933 |  | 0.95 | 1.05 | 0.038066 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2024-076 | 1.0017 | 0.94474 | -0.056933 |  | 0.95 | 1.05 | 0.035805 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2024-076 | 1.0017 | 0.94474 | -0.056933 |  | 0.95 | 1.05 | 0.032364 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEN-2024-076 | 1.0017 | 0.94474 | -0.056933 |  | 0.95 | 1.05 | 0.031815 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2024-076 | 1.0017 | 0.94474 | -0.056933 |  | 0.95 | 1.05 | 0.033886 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2024-076 | 1.0017 | 0.94474 | -0.056933 |  | 0.95 | 1.05 | 0.035554 | P23:345:WERE:WAVS-BKRS:EHV: | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2024-076 | 1.0016 | 0.94746 | -0.054151 |  | 0.95 | 1.05 | 0.039728 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2024-076 | 1.0016 | 0.94746 | -0.054151 |  | 0.95 | 1.05 | 0.034227 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | GEN-2024-076 | 1.0016 | 0.94746 | -0.054151 |  | 0.95 | 1.05 | 0.037164 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2024-076 | 1.0016 | 0.94746 | -0.054151 |  | 0.95 | 1.05 | 0.03782 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2024-076 | 1.0016 | 0.94746 | -0.054151 |  | 0.95 | 1.05 | 0.036407 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2024-076 | 1.0016 | 0.94746 | -0.054151 |  | 0.95 | 1.05 | 0.036407 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2024-076 | 1.0016 | 0.94746 | -0.054151 |  | 0.95 | 1.05 | 0.037418 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2024-076 | 1.0016 | 0.94746 | -0.054151 |  | 0.95 | 1.05 | 0.037355 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2024-076 | 1.0016 | 0.94746 | -0.054151 |  | 0.95 | 1.05 | 0.035094 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2024-076 | 1.0016 | 0.94746 | -0.054151 |  | 0.95 | 1.05 | 0.031652 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEN-2024-076 | 1.0016 | 0.94746 | -0.054151 |  | 0.95 | 1.05 | 0.031104 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2024-076 | 1.0016 | 0.94746 | -0.054151 |  | 0.95 | 1.05 | 0.033175 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2024-076 | 1.0016 | 0.94746 | -0.054151 |  | 0.95 | 1.05 | 0.034843 | Single 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Add 0.02 MVAR switched shunt at G22-013-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2024-076 | 1.0017 | 0.94311 | -0.058616 |  | 0.95 | 1.05 | 0.040439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GEN-2024-076 | 1.0017 | 0.94311 | -0.058616 |  | 0.95 | 1.05 | 0.034853 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2024-076 | 1.0017 | 0.94311 | -0.058616 |  | 0.95 | 1.05 | 0.046783 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2024-076 | 1.0017 | 0.94311 | -0.058616 |  | 0.95 | 1.05 | 0.047615 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2024-076 | 1.0017 | 0.94311 | -0.058616 |  | 0.95 | 1.05 | 0.034938 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | GEN-2024-076 | 1.0017 | 0.94311 | -0.058616 |  | 0.95 | 1.05 | 0.037875 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2024-076 | 1.0017 | 0.94311 | -0.058616 |  | 0.95 | 1.05 | 0.044022 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | GEN-2024-076 | 1.0017 | 0.94311 | -0.058616 |  | 0.95 | 1.05 | 0.030552 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2024-076 | 1.0017 | 0.94311 | -0.058616 |  | 0.95 | 1.05 | 0.038531 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2024-076 | 1.0017 | 0.94311 | -0.058616 |  | 0.95 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2024-076 | 1.0017 | 0.94311 | -0.058616 |  | 0.95 | 1.05 | 0.062491 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2024-076 | 1.0017 | 0.94311 | -0.058616 |  | 0.95 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2024-076 | 1.0017 | 0.94311 | -0.058616 |  | 0.95 | 1.05 | 0.038129 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2024-076 | 1.0017 | 0.94311 | -0.058616 |  | 0.95 | 1.05 | 0.038066 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GEN-2024-076 | 1.0017 | 0.94311 | -0.058616 |  | 0.95 | 1.05 | 0.034955 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2024-076 | 1.0017 | 0.94311 | -0.058616 |  | 0.95 | 1.05 | 0.06281 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2024-076 | 1.0017 | 0.94311 | -0.058616 |  | 0.95 | 1.05 | 0.045309 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2024-076 | 1.0017 | 0.94311 | -0.058616 |  | 0.95 | 1.05 | 0.035805 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2024-076 | 1.0017 | 0.94311 | -0.058616 |  | 0.95 | 1.05 | 0.032364 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEN-2024-076 | 1.0017 | 0.94311 | -0.058616 |  | 0.95 | 1.05 | 0.031815 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2024-076 | 1.0017 | 0.94311 | -0.058616 |  | 0.95 | 1.05 | 0.033886 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2024-076 | 1.0017 | 0.94311 | -0.058616 |  | 0.95 | 1.05 | 0.035554 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2024-076 | 1.0025 | 0.89328 | -0.10922 |  | 0.95 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GEN-2024-076 | 1.0025 | 0.89328 | -0.10922 |  | 0.95 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2024-076 | 1.0025 | 0.89328 | -0.10922 |  | 0.95 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2024-076 | 1.0025 | 0.89328 | -0.10922 |  | 0.95 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2024-076 | 1.0025 | 0.89328 | -0.10922 |  | 0.95 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | GEN-2024-076 | 1.0025 | 0.89328 | -0.10922 |  | 0.95 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2024-076 | 1.0025 | 0.89328 | -0.10922 |  | 0.95 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | GEN-2024-076 | 1.0025 | 0.89328 | -0.10922 |  | 0.95 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2024-076 | 1.0025 | 0.89328 | -0.10922 |  | 0.95 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | GEN-2024-076 | 1.0025 | 0.89328 | -0.10922 |  | 0.95 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2024-076 | 1.0025 | 0.89328 | -0.10922 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2024-076 | 1.0025 | 0.89328 | -0.10922 |  | 0.95 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2024-076 | 1.0025 | 0.89328 | -0.10922 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2024-076 | 1.0025 | 0.89328 | -0.10922 |  | 0.95 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2024-076 | 1.0025 | 0.89328 | -0.10922 |  | 0.95 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GEN-2024-076 | 1.0025 | 0.89328 | -0.10922 |  | 0.95 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2024-076 | 1.0025 | 0.89328 | -0.10922 |  | 0.95 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | GEN-2024-076 | 1.0025 | 0.89328 | -0.10922 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | GEN-2024-076 | 1.0025 | 0.89328 | -0.10922 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2024-076 | 1.0025 | 0.89328 | -0.10922 |  | 0.95 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2024-076 | 1.0025 | 0.89328 | -0.10922 |  | 0.95 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2024-076 | 1.0025 | 0.89328 | -0.10922 |  | 0.95 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEN-2024-076 | 1.0025 | 0.89328 | -0.10922 |  | 0.95 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2024-076 | 1.0025 | 0.89328 | -0.10922 |  | 0.95 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2024-076 | 1.0025 | 0.89328 | -0.10922 |  | 0.95 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2024-125 | 0.9898 | 0.94306 | -0.046743 |  | 0.95 | 1.05 | 0.040439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GEN-2024-125 | 0.9898 | 0.94306 | -0.046743 |  | 0.95 | 1.05 | 0.034853 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2024-125 | 0.9898 | 0.94306 | -0.046743 |  | 0.95 | 1.05 | 0.046783 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2024-125 | 0.9898 | 0.94306 | -0.046743 |  | 0.95 | 1.05 | 0.047615 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2024-125 | 0.9898 | 0.94306 | -0.046743 |  | 0.95 | 1.05 | 0.034938 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | GEN-2024-125 | 0.9898 | 0.94306 | -0.046743 |  | 0.95 | 1.05 | 0.037875 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2024-125 | 0.9898 | 0.94306 | -0.046743 |  | 0.95 | 1.05 | 0.044022 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | GEN-2024-125 | 0.9898 | 0.94306 | -0.046743 |  | 0.95 | 1.05 | 0.030552 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2024-125 | 0.9898 | 0.94306 | -0.046743 |  | 0.95 | 1.05 | 0.038531 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2024-125 | 0.9898 | 0.94306 | -0.046743 |  | 0.95 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2024-125 | 0.9898 | 0.94306 | -0.046743 |  | 0.95 | 1.05 | 0.062491 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2024-125 | 0.9898 | 0.94306 | -0.046743 |  | 0.95 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2024-125 | 0.9898 | 0.94306 | -0.046743 |  | 0.95 | 1.05 | 0.038129 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2024-125 | 0.9898 | 0.94306 | -0.046743 |  | 0.95 | 1.05 | 0.038066 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GEN-2024-125 | 0.9898 | 0.94306 | -0.046743 |  | 0.95 | 1.05 | 0.034955 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2024-125 | 0.9898 | 0.94306 | -0.046743 |  | 0.95 | 1.05 | 0.06281 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2024-125 | 0.9898 | 0.94306 | -0.046743 |  | 0.95 | 1.05 | 0.045309 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2024-125 | 0.9898 | 0.94306 | -0.046743 |  | 0.95 | 1.05 | 0.035805 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2024-125 | 0.9898 | 0.94306 | -0.046743 |  | 0.95 | 1.05 | 0.032364 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEN-2024-125 | 0.9898 | 0.94306 | -0.046743 |  | 0.95 | 1.05 | 0.031815 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2024-125 | 0.9898 | 0.94306 | -0.046743 |  | 0.95 | 1.05 | 0.033886 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2024-125 | 0.9898 | 0.94306 | -0.046743 |  | 0.95 | 1.05 | 0.035554 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2024-125 | 0.99752 | 0.94725 | -0.050272 |  | 0.95 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GEN-2024-125 | 0.99752 | 0.94725 | -0.050272 |  | 0.95 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2024-125 | 0.99752 | 0.94725 | -0.050272 |  | 0.95 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2024-125 | 0.99752 | 0.94725 | -0.050272 |  | 0.95 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2024-125 | 0.99752 | 0.94725 | -0.050272 |  | 0.95 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | GEN-2024-125 | 0.99752 | 0.94725 | -0.050272 |  | 0.95 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2024-125 | 0.99752 | 0.94725 | -0.050272 |  | 0.95 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | GEN-2024-125 | 0.99752 | 0.94725 | -0.050272 |  | 0.95 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2024-125 | 0.99752 | 0.94725 | -0.050272 |  | 0.95 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | GEN-2024-125 | 0.99752 | 0.94725 | -0.050272 |  | 0.95 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2024-125 | 0.99752 | 0.94725 | -0.050272 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2024-125 | 0.99752 | 0.94725 | -0.050272 |  | 0.95 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2024-125 | 0.99752 | 0.94725 | -0.050272 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2024-125 | 0.99752 | 0.94725 | -0.050272 |  | 0.95 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2024-125 | 0.99752 | 0.94725 | -0.050272 |  | 0.95 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GEN-2024-125 | 0.99752 | 0.94725 | -0.050272 |  | 0.95 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2024-125 | 0.99752 | 0.94725 | -0.050272 |  | 0.95 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | GEN-2024-125 | 0.99752 | 0.94725 | -0.050272 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | GEN-2024-125 | 0.99752 | 0.94725 | -0.050272 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2024-125 | 0.99752 | 0.94725 | -0.050272 |  | 0.95 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2024-125 | 0.99752 | 0.94725 | -0.050272 |  | 0.95 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2024-125 | 0.99752 | 0.94725 | -0.050272 |  | 0.95 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEN-2024-125 | 0.99752 | 0.94725 | -0.050272 |  | 0.95 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2024-125 | 0.99752 | 0.94725 | -0.050272 |  | 0.95 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2024-125 | 0.99752 | 0.94725 | -0.050272 |  | 0.95 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2024-129 | 0.99922 | 0.94262 | -0.056605 |  | 0.95 | 1.05 | 0.040439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GEN-2024-129 | 0.99922 | 0.94262 | -0.056605 |  | 0.95 | 1.05 | 0.034853 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2024-129 | 0.99922 | 0.94262 | -0.056605 |  | 0.95 | 1.05 | 0.046783 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2024-129 | 0.99922 | 0.94262 | -0.056605 |  | 0.95 | 1.05 | 0.047615 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2024-129 | 0.99922 | 0.94262 | -0.056605 |  | 0.95 | 1.05 | 0.034938 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | GEN-2024-129 | 0.99922 | 0.94262 | -0.056605 |  | 0.95 | 1.05 | 0.037875 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2024-129 | 0.99922 | 0.94262 | -0.056605 |  | 0.95 | 1.05 | 0.044022 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | GEN-2024-129 | 0.99922 | 0.94262 | -0.056605 |  | 0.95 | 1.05 | 0.030552 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2024-129 | 0.99922 | 0.94262 | -0.056605 |  | 0.95 | 1.05 | 0.038531 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2024-129 | 0.99922 | 0.94262 | -0.056605 |  | 0.95 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2024-129 | 0.99922 | 0.94262 | -0.056605 |  | 0.95 | 1.05 | 0.062491 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2024-129 | 0.99922 | 0.94262 | -0.056605 |  | 0.95 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2024-129 | 0.99922 | 0.94262 | -0.056605 |  | 0.95 | 1.05 | 0.038129 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2024-129 | 0.99922 | 0.94262 | -0.056605 |  | 0.95 | 1.05 | 0.038066 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GEN-2024-129 | 0.99922 | 0.94262 | -0.056605 |  | 0.95 | 1.05 | 0.034955 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2024-129 | 0.99922 | 0.94262 | -0.056605 |  | 0.95 | 1.05 | 0.06281 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2024-129 | 0.99922 | 0.94262 | -0.056605 |  | 0.95 | 1.05 | 0.045309 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2024-129 | 0.99922 | 0.94262 | -0.056605 |  | 0.95 | 1.05 | 0.035805 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2024-129 | 0.99922 | 0.94262 | -0.056605 |  | 0.95 | 1.05 | 0.032364 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEN-2024-129 | 0.99922 | 0.94262 | -0.056605 |  | 0.95 | 1.05 | 0.031815 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2024-129 | 0.99922 | 0.94262 | -0.056605 |  | 0.95 | 1.05 | 0.033886 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2024-129 | 0.99922 | 0.94262 | -0.056605 |  | 0.95 | 1.05 | 0.035554 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2024-129 | 1.0037 | 0.93575 | -0.067967 |  | 0.95 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GEN-2024-129 | 1.0037 | 0.93575 | -0.067967 |  | 0.95 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2024-129 | 1.0037 | 0.93575 | -0.067967 |  | 0.95 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2024-129 | 1.0037 | 0.93575 | -0.067967 |  | 0.95 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2024-129 | 1.0037 | 0.93575 | -0.067967 |  | 0.95 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | GEN-2024-129 | 1.0037 | 0.93575 | -0.067967 |  | 0.95 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2024-129 | 1.0037 | 0.93575 | -0.067967 |  | 0.95 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | GEN-2024-129 | 1.0037 | 0.93575 | -0.067967 |  | 0.95 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2024-129 | 1.0037 | 0.93575 | -0.067967 |  | 0.95 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | GEN-2024-129 | 1.0037 | 0.93575 | -0.067967 |  | 0.95 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2024-129 | 1.0037 | 0.93575 | -0.067967 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2024-129 | 1.0037 | 0.93575 | -0.067967 |  | 0.95 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2024-129 | 1.0037 | 0.93575 | -0.067967 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2024-129 | 1.0037 | 0.93575 | -0.067967 |  | 0.95 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2024-129 | 1.0037 | 0.93575 | -0.067967 |  | 0.95 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GEN-2024-129 | 1.0037 | 0.93575 | -0.067967 |  | 0.95 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2024-129 | 1.0037 | 0.93575 | -0.067967 |  | 0.95 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | GEN-2024-129 | 1.0037 | 0.93575 | -0.067967 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | GEN-2024-129 | 1.0037 | 0.93575 | -0.067967 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2024-129 | 1.0037 | 0.93575 | -0.067967 |  | 0.95 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2024-129 | 1.0037 | 0.93575 | -0.067967 |  | 0.95 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2024-129 | 1.0037 | 0.93575 | -0.067967 |  | 0.95 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEN-2024-129 | 1.0037 | 0.93575 | -0.067967 |  | 0.95 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2024-129 | 1.0037 | 0.93575 | -0.067967 |  | 0.95 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2024-129 | 1.0037 | 0.93575 | -0.067967 |  | 0.95 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | ASGI-2024-023 | GEN-2024-170 | 0.9764 | 0.94661 | -0.02979 |  | 0.95 | 1.05 | 0.042651 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1 | Add 0.02 MVAR switched shunt at PHILL 7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | GEN-2024-170 | 0.9764 | 0.94661 | -0.02979 |  | 0.95 | 1.05 | 0.037101 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1 | Add 0.02 MVAR switched shunt at PHILL 7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-068 | GEN-2024-170 | 0.9764 | 0.94661 | -0.02979 |  | 0.95 | 1.05 | 0.03842 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1 | Add 0.02 MVAR switched shunt at PHILL 7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-071 | GEN-2024-170 | 0.9764 | 0.94661 | -0.02979 |  | 0.95 | 1.05 | 0.042496 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1 | Add 0.02 MVAR switched shunt at PHILL 7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-122 | GEN-2024-170 | 0.9764 | 0.94661 | -0.02979 |  | 0.95 | 1.05 | 0.047877 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1 | Add 0.02 MVAR switched shunt at PHILL 7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-177 | GEN-2024-170 | 0.9764 | 0.94661 | -0.02979 |  | 0.95 | 1.05 | 0.049112 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1 | Add 0.02 MVAR switched shunt at PHILL 7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-178 | GEN-2024-170 | 0.9764 | 0.94661 | -0.02979 |  | 0.95 | 1.05 | 0.04656 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1 | Add 0.02 MVAR switched shunt at PHILL 7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-220 | GEN-2024-170 | 0.9764 | 0.94661 | -0.02979 |  | 0.95 | 1.05 | 0.04282 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1 | Add 0.02 MVAR switched shunt at PHILL 7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-232 | GEN-2024-170 | 0.9764 | 0.94661 | -0.02979 |  | 0.95 | 1.05 | 0.051563 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1 | Add 0.02 MVAR switched shunt at PHILL 7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2024-170 | 0.9764 | 0.94661 | -0.02979 |  | 0.95 | 1.05 | 0.033373 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1 | Add 0.02 MVAR switched shunt at PHILL 7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | GEN-2024-170 | 0.9764 | 0.94661 | -0.02979 |  | 0.95 | 1.05 | 0.037101 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1 | Add 0.02 MVAR switched shunt at PHILL 7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-376 | GEN-2024-170 | 0.9764 | 0.94661 | -0.02979 |  | 0.95 | 1.05 | 0.054826 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1 | Add 0.02 MVAR switched shunt at PHILL 7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2024-170 | 0.97531 | 0.94169 | -0.033622 |  | 0.95 | 1.05 | 0.040762 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2024-170 | 0.97531 | 0.94169 | -0.033622 |  | 0.95 | 1.05 | 0.030778 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2024-170 | 0.97531 | 0.94169 | -0.033622 |  | 0.95 | 1.05 | 0.031937 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2024-170 | 0.97531 | 0.94169 | -0.033622 |  | 0.95 | 1.05 | 0.053181 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2024-170 | 0.97531 | 0.94169 | -0.033622 |  | 0.95 | 1.05 | 0.032533 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2024-170 | 0.97531 | 0.94169 | -0.033622 |  | 0.95 | 1.05 | 0.031326 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2024-170 | 0.98131 | 0.94167 | -0.03964 |  | 0.95 | 1.05 | 0.036307 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2024-170 | 0.98131 | 0.94167 | -0.03964 |  | 0.95 | 1.05 | 0.052743 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2024-170 | 0.98131 | 0.94167 | -0.03964 |  | 0.95 | 1.05 | 0.039345 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2024-170 | 0.98131 | 0.94167 | -0.03964 |  | 0.95 | 1.05 | 0.031366 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2024-170 | 0.98131 | 0.94167 | -0.03964 |  | 0.95 | 1.05 | 0.041888 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2024-170 | 0.98131 | 0.94167 | -0.03964 |  | 0.95 | 1.05 | 0.038797 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2024-170 | 0.98131 | 0.94167 | -0.03964 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2024-170 | 0.98131 | 0.94167 | -0.03964 |  | 0.95 | 1.05 | 0.067346 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2024-170 | 0.98131 | 0.94167 | -0.03964 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2024-170 | 0.98131 | 0.94167 | -0.03964 |  | 0.95 | 1.05 | 0.030851 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2024-170 | 0.98131 | 0.94167 | -0.03964 |  | 0.95 | 1.05 | 0.032161 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2024-170 | 0.98131 | 0.94167 | -0.03964 |  | 0.95 | 1.05 | 0.04067 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2024-170 | 0.98131 | 0.94167 | -0.03964 |  | 0.95 | 1.05 | 0.040569 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2024-170 | 0.98131 | 0.94167 | -0.03964 |  | 0.95 | 1.05 | 0.03086 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2024-170 | 0.98131 | 0.94167 | -0.03964 |  | 0.95 | 1.05 | 0.033223 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2024-170 | 0.98131 | 0.94167 | -0.03964 |  | 0.95 | 1.05 | 0.033733 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2024-170 | 0.98187 | 0.91187 | -0.070003 |  | 0.95 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GEN-2024-170 | 0.98187 | 0.91187 | -0.070003 |  | 0.95 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2024-170 | 0.98187 | 0.91187 | -0.070003 |  | 0.95 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2024-170 | 0.98187 | 0.91187 | -0.070003 |  | 0.95 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2024-170 | 0.98187 | 0.91187 | -0.070003 |  | 0.95 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | GEN-2024-170 | 0.98187 | 0.91187 | -0.070003 |  | 0.95 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2024-170 | 0.98187 | 0.91187 | -0.070003 |  | 0.95 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | GEN-2024-170 | 0.98187 | 0.91187 | -0.070003 |  | 0.95 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2024-170 | 0.98187 | 0.91187 | -0.070003 |  | 0.95 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | GEN-2024-170 | 0.98187 | 0.91187 | -0.070003 |  | 0.95 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2024-170 | 0.98187 | 0.91187 | -0.070003 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2024-170 | 0.98187 | 0.91187 | -0.070003 |  | 0.95 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2024-170 | 0.98187 | 0.91187 | -0.070003 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2024-170 | 0.98187 | 0.91187 | -0.070003 |  | 0.95 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2024-170 | 0.98187 | 0.91187 | -0.070003 |  | 0.95 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GEN-2024-170 | 0.98187 | 0.91187 | -0.070003 |  | 0.95 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2024-170 | 0.98187 | 0.91187 | -0.070003 |  | 0.95 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | GEN-2024-170 | 0.98187 | 0.91187 | -0.070003 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | GEN-2024-170 | 0.98187 | 0.91187 | -0.070003 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2024-170 | 0.98187 | 0.91187 | -0.070003 |  | 0.95 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2024-170 | 0.98187 | 0.91187 | -0.070003 |  | 0.95 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2024-170 | 0.98187 | 0.91187 | -0.070003 |  | 0.95 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEN-2024-170 | 0.98187 | 0.91187 | -0.070003 |  | 0.95 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2024-170 | 0.98187 | 0.91187 | -0.070003 |  | 0.95 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2024-170 | 0.98187 | 0.91187 | -0.070003 |  | 0.95 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2024-170 | 0.97773 | 0.94664 | -0.031093 |  | 0.95 | 1.05 | 0.036307 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2024-170 | 0.97773 | 0.94664 | -0.031093 |  | 0.95 | 1.05 | 0.052743 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2024-170 | 0.97773 | 0.94664 | -0.031093 |  | 0.95 | 1.05 | 0.039345 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2024-170 | 0.97773 | 0.94664 | -0.031093 |  | 0.95 | 1.05 | 0.031366 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2024-170 | 0.97773 | 0.94664 | -0.031093 |  | 0.95 | 1.05 | 0.041888 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2024-170 | 0.97773 | 0.94664 | -0.031093 |  | 0.95 | 1.05 | 0.038797 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2024-170 | 0.97773 | 0.94664 | -0.031093 |  | 0.95 | 1.05 | 0.030557 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2024-170 | 0.97773 | 0.94664 | -0.031093 |  | 0.95 | 1.05 | 0.067346 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2024-170 | 0.97773 | 0.94664 | -0.031093 |  | 0.95 | 1.05 | 0.030557 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2024-170 | 0.97773 | 0.94664 | -0.031093 |  | 0.95 | 1.05 | 0.030851 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2024-170 | 0.97773 | 0.94664 | -0.031093 |  | 0.95 | 1.05 | 0.032161 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2024-170 | 0.97773 | 0.94664 | -0.031093 |  | 0.95 | 1.05 | 0.04067 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2024-170 | 0.97773 | 0.94664 | -0.031093 |  | 0.95 | 1.05 | 0.040569 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2024-170 | 0.97773 | 0.94664 | -0.031093 |  | 0.95 | 1.05 | 0.03086 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2024-170 | 0.97773 | 0.94664 | -0.031093 |  | 0.95 | 1.05 | 0.033223 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2024-170 | 0.97773 | 0.94664 | -0.031093 |  | 0.95 | 1.05 | 0.033733 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2024-276 | 0.97122 | 0.93553 | -0.035693 |  | 0.95 | 1.05 | 0.039728 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2024-276 | 0.97122 | 0.93553 | -0.035693 |  | 0.95 | 1.05 | 0.040762 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2024-276 | 0.97122 | 0.93553 | -0.035693 |  | 0.95 | 1.05 | 0.030778 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2024-276 | 0.97122 | 0.93553 | -0.035693 |  | 0.95 | 1.05 | 0.034227 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | GEN-2024-276 | 0.97122 | 0.93553 | -0.035693 |  | 0.95 | 1.05 | 0.037164 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2024-276 | 0.97122 | 0.93553 | -0.035693 |  | 0.95 | 1.05 | 0.031937 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2024-276 | 0.97122 | 0.93553 | -0.035693 |  | 0.95 | 1.05 | 0.03782 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2024-276 | 0.97122 | 0.93553 | -0.035693 |  | 0.95 | 1.05 | 0.036407 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2024-276 | 0.97122 | 0.93553 | -0.035693 |  | 0.95 | 1.05 | 0.053181 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2024-276 | 0.97122 | 0.93553 | -0.035693 |  | 0.95 | 1.05 | 0.036407 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2024-276 | 0.97122 | 0.93553 | -0.035693 |  | 0.95 | 1.05 | 0.037418 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2024-276 | 0.97122 | 0.93553 | -0.035693 |  | 0.95 | 1.05 | 0.037355 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2024-276 | 0.97122 | 0.93553 | -0.035693 |  | 0.95 | 1.05 | 0.032533 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2024-276 | 0.97122 | 0.93553 | -0.035693 |  | 0.95 | 1.05 | 0.031326 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2024-276 | 0.97122 | 0.93553 | -0.035693 |  | 0.95 | 1.05 | 0.035094 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2024-276 | 0.97122 | 0.93553 | -0.035693 |  | 0.95 | 1.05 | 0.031652 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEN-2024-276 | 0.97122 | 0.93553 | -0.035693 |  | 0.95 | 1.05 | 0.031104 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2024-276 | 0.97122 | 0.93553 | -0.035693 |  | 0.95 | 1.05 | 0.033175 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2024-276 | 0.97122 | 0.93553 | -0.035693 |  | 0.95 | 1.05 | 0.034843 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2024-276 | 0.96789 | 0.9308 | -0.037085 |  | 0.95 | 1.05 | 0.036307 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2024-276 | 0.96789 | 0.9308 | -0.037085 |  | 0.95 | 1.05 | 0.052743 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2024-276 | 0.96789 | 0.9308 | -0.037085 |  | 0.95 | 1.05 | 0.039345 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2024-276 | 0.96789 | 0.9308 | -0.037085 |  | 0.95 | 1.05 | 0.031366 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2024-276 | 0.96789 | 0.9308 | -0.037085 |  | 0.95 | 1.05 | 0.041888 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2024-276 | 0.96789 | 0.9308 | -0.037085 |  | 0.95 | 1.05 | 0.038797 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2024-276 | 0.96789 | 0.9308 | -0.037085 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2024-276 | 0.96789 | 0.9308 | -0.037085 |  | 0.95 | 1.05 | 0.067346 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2024-276 | 0.96789 | 0.9308 | -0.037085 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2024-276 | 0.96789 | 0.9308 | -0.037085 |  | 0.95 | 1.05 | 0.030851 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2024-276 | 0.96789 | 0.9308 | -0.037085 |  | 0.95 | 1.05 | 0.032161 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2024-276 | 0.96789 | 0.9308 | -0.037085 |  | 0.95 | 1.05 | 0.04067 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2024-276 | 0.96789 | 0.9308 | -0.037085 |  | 0.95 | 1.05 | 0.040569 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2024-276 | 0.96789 | 0.9308 | -0.037085 |  | 0.95 | 1.05 | 0.03086 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2024-276 | 0.96789 | 0.9308 | -0.037085 |  | 0.95 | 1.05 | 0.033223 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2024-276 | 0.96789 | 0.9308 | -0.037085 |  | 0.95 | 1.05 | 0.033733 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2024-276 | 0.97267 | 0.92981 | -0.042861 |  | 0.95 | 1.05 | 0.036307 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2024-276 | 0.97267 | 0.92981 | -0.042861 |  | 0.95 | 1.05 | 0.052743 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2024-276 | 0.97267 | 0.92981 | -0.042861 |  | 0.95 | 1.05 | 0.039345 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2024-276 | 0.97267 | 0.92981 | -0.042861 |  | 0.95 | 1.05 | 0.031366 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2024-276 | 0.97267 | 0.92981 | -0.042861 |  | 0.95 | 1.05 | 0.041888 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2024-276 | 0.97267 | 0.92981 | -0.042861 |  | 0.95 | 1.05 | 0.038797 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2024-276 | 0.97267 | 0.92981 | -0.042861 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2024-276 | 0.97267 | 0.92981 | -0.042861 |  | 0.95 | 1.05 | 0.067346 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2024-276 | 0.97267 | 0.92981 | -0.042861 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2024-276 | 0.97267 | 0.92981 | -0.042861 |  | 0.95 | 1.05 | 0.030851 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2024-276 | 0.97267 | 0.92981 | -0.042861 |  | 0.95 | 1.05 | 0.032161 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2024-276 | 0.97267 | 0.92981 | -0.042861 |  | 0.95 | 1.05 | 0.04067 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2024-276 | 0.97267 | 0.92981 | -0.042861 |  | 0.95 | 1.05 | 0.040569 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2024-276 | 0.97267 | 0.92981 | -0.042861 |  | 0.95 | 1.05 | 0.03086 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2024-276 | 0.97267 | 0.92981 | -0.042861 |  | 0.95 | 1.05 | 0.033223 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2024-276 | 0.97267 | 0.92981 | -0.042861 |  | 0.95 | 1.05 | 0.033733 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2024-276 | 0.97739 | 0.93354 | -0.043851 |  | 0.95 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GEN-2024-276 | 0.97739 | 0.93354 | -0.043851 |  | 0.95 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2024-276 | 0.97739 | 0.93354 | -0.043851 |  | 0.95 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2024-276 | 0.97739 | 0.93354 | -0.043851 |  | 0.95 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2024-276 | 0.97739 | 0.93354 | -0.043851 |  | 0.95 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | GEN-2024-276 | 0.97739 | 0.93354 | -0.043851 |  | 0.95 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2024-276 | 0.97739 | 0.93354 | -0.043851 |  | 0.95 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | GEN-2024-276 | 0.97739 | 0.93354 | -0.043851 |  | 0.95 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2024-276 | 0.97739 | 0.93354 | -0.043851 |  | 0.95 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | GEN-2024-276 | 0.97739 | 0.93354 | -0.043851 |  | 0.95 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2024-276 | 0.97739 | 0.93354 | -0.043851 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2024-276 | 0.97739 | 0.93354 | -0.043851 |  | 0.95 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2024-276 | 0.97739 | 0.93354 | -0.043851 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2024-276 | 0.97739 | 0.93354 | -0.043851 |  | 0.95 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2024-276 | 0.97739 | 0.93354 | -0.043851 |  | 0.95 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GEN-2024-276 | 0.97739 | 0.93354 | -0.043851 |  | 0.95 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2024-276 | 0.97739 | 0.93354 | -0.043851 |  | 0.95 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | GEN-2024-276 | 0.97739 | 0.93354 | -0.043851 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | GEN-2024-276 | 0.97739 | 0.93354 | -0.043851 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2024-276 | 0.97739 | 0.93354 | -0.043851 |  | 0.95 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2024-276 | 0.97739 | 0.93354 | -0.043851 |  | 0.95 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2024-276 | 0.97739 | 0.93354 | -0.043851 |  | 0.95 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEN-2024-276 | 0.97739 | 0.93354 | -0.043851 |  | 0.95 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2024-276 | 0.97739 | 0.93354 | -0.043851 |  | 0.95 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2024-276 | 0.97739 | 0.93354 | -0.043851 |  | 0.95 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2024-276 | 0.97003 | 0.93836 | -0.031667 |  | 0.95 | 1.05 | 0.036307 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2024-276 | 0.97003 | 0.93836 | -0.031667 |  | 0.95 | 1.05 | 0.052743 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2024-276 | 0.97003 | 0.93836 | -0.031667 |  | 0.95 | 1.05 | 0.039345 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2024-276 | 0.97003 | 0.93836 | -0.031667 |  | 0.95 | 1.05 | 0.031366 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2024-276 | 0.97003 | 0.93836 | -0.031667 |  | 0.95 | 1.05 | 0.041888 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2024-276 | 0.97003 | 0.93836 | -0.031667 |  | 0.95 | 1.05 | 0.038797 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2024-276 | 0.97003 | 0.93836 | -0.031667 |  | 0.95 | 1.05 | 0.030557 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2024-276 | 0.97003 | 0.93836 | -0.031667 |  | 0.95 | 1.05 | 0.067346 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2024-276 | 0.97003 | 0.93836 | -0.031667 |  | 0.95 | 1.05 | 0.030557 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2024-276 | 0.97003 | 0.93836 | -0.031667 |  | 0.95 | 1.05 | 0.030851 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2024-276 | 0.97003 | 0.93836 | -0.031667 |  | 0.95 | 1.05 | 0.032161 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2024-276 | 0.97003 | 0.93836 | -0.031667 |  | 0.95 | 1.05 | 0.04067 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2024-276 | 0.97003 | 0.93836 | -0.031667 |  | 0.95 | 1.05 | 0.040569 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2024-276 | 0.97003 | 0.93836 | -0.031667 |  | 0.95 | 1.05 | 0.03086 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2024-276 | 0.97003 | 0.93836 | -0.031667 |  | 0.95 | 1.05 | 0.033223 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2024-276 | 0.97003 | 0.93836 | -0.031667 |  | 0.95 | 1.05 | 0.033733 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GEN-2024-352 | 0.99164 | 0.94146 | -0.050175 |  | 0.95 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GEN-2024-352 | 0.99164 | 0.94146 | -0.050175 |  | 0.95 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GEN-2024-352 | 0.99164 | 0.94146 | -0.050175 |  | 0.95 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GEN-2024-352 | 0.99164 | 0.94146 | -0.050175 |  | 0.95 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GEN-2024-352 | 0.99164 | 0.94146 | -0.050175 |  | 0.95 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | GEN-2024-352 | 0.99164 | 0.94146 | -0.050175 |  | 0.95 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GEN-2024-352 | 0.99164 | 0.94146 | -0.050175 |  | 0.95 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | GEN-2024-352 | 0.99164 | 0.94146 | -0.050175 |  | 0.95 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GEN-2024-352 | 0.99164 | 0.94146 | -0.050175 |  | 0.95 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | GEN-2024-352 | 0.99164 | 0.94146 | -0.050175 |  | 0.95 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GEN-2024-352 | 0.99164 | 0.94146 | -0.050175 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GEN-2024-352 | 0.99164 | 0.94146 | -0.050175 |  | 0.95 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GEN-2024-352 | 0.99164 | 0.94146 | -0.050175 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GEN-2024-352 | 0.99164 | 0.94146 | -0.050175 |  | 0.95 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GEN-2024-352 | 0.99164 | 0.94146 | -0.050175 |  | 0.95 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GEN-2024-352 | 0.99164 | 0.94146 | -0.050175 |  | 0.95 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GEN-2024-352 | 0.99164 | 0.94146 | -0.050175 |  | 0.95 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | GEN-2024-352 | 0.99164 | 0.94146 | -0.050175 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | GEN-2024-352 | 0.99164 | 0.94146 | -0.050175 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GEN-2024-352 | 0.99164 | 0.94146 | -0.050175 |  | 0.95 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GEN-2024-352 | 0.99164 | 0.94146 | -0.050175 |  | 0.95 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GEN-2024-352 | 0.99164 | 0.94146 | -0.050175 |  | 0.95 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GEN-2024-352 | 0.99164 | 0.94146 | -0.050175 |  | 0.95 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GEN-2024-352 | 0.99164 | 0.94146 | -0.050175 |  | 0.95 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GEN-2024-352 | 0.99164 | 0.94146 | -0.050175 |  | 0.95 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GRDVWE 5 | 0.99264 | 0.92385 | -0.06879 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GRDVWE 5 | 0.99264 | 0.92385 | -0.06879 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GRDVWE 5 | 0.99264 | 0.92385 | -0.06879 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GRDVWE 5 | 0.99264 | 0.92385 | -0.06879 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | GRDVWE 5 | 0.99264 | 0.92385 | -0.06879 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | GRDVWE 5 | 0.99264 | 0.92385 | -0.06879 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GRDVWE 5 | 0.99264 | 0.92385 | -0.06879 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | GRDVWE 5 | 0.99264 | 0.92385 | -0.06879 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GRDVWE 5 | 0.99264 | 0.92385 | -0.06879 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | GRDVWE 5 | 0.99264 | 0.92385 | -0.06879 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | GRDVWE 5 | 0.99264 | 0.92385 | -0.06879 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GRDVWE 5 | 0.99264 | 0.92385 | -0.06879 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | GRDVWE 5 | 0.99264 | 0.92385 | -0.06879 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | GRDVWE 5 | 0.99264 | 0.92385 | -0.06879 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | GRDVWE 5 | 0.99264 | 0.92385 | -0.06879 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GRDVWE 5 | 0.99264 | 0.92385 | -0.06879 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GRDVWE 5 | 0.99264 | 0.92385 | -0.06879 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | GRDVWE 5 | 0.99264 | 0.92385 | -0.06879 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | GRDVWE 5 | 0.99264 | 0.92385 | -0.06879 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GRDVWE 5 | 0.99264 | 0.92385 | -0.06879 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | GRDVWE 5 | 0.99264 | 0.92385 | -0.06879 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GRDVWE 5 | 0.99264 | 0.92385 | -0.06879 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | GRDVWE 5 | 0.99264 | 0.92385 | -0.06879 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GRDVWE 5 | 0.99264 | 0.92385 | -0.06879 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | GRDVWE 5 | 0.99264 | 0.92385 | -0.06879 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GROVE 4 | 0.96144 | 0.89843 | -0.063009 |  | 0.92 | 1.05 | 0.033596 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GROVE 4 | 0.96144 | 0.89843 | -0.063009 |  | 0.92 | 1.05 | 0.040193 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GROVE 4 | 0.96144 | 0.89843 | -0.063009 |  | 0.92 | 1.05 | 0.088122 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GROVE 4 | 0.96144 | 0.89843 | -0.063009 |  | 0.92 | 1.05 | 0.074664 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GROVE 4 | 0.96144 | 0.89843 | -0.063009 |  | 0.92 | 1.05 | 0.068051 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GROVE 4 | 0.96144 | 0.89843 | -0.063009 |  | 0.92 | 1.05 | 0.035565 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | GROVE 4 | 0.96144 | 0.89843 | -0.063009 |  | 0.92 | 1.05 | 0.033904 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GROVE 4 | 0.96144 | 0.89843 | -0.063009 |  | 0.92 | 1.05 | 0.16366 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GROVE 4 | 0.96144 | 0.89843 | -0.063009 |  | 0.92 | 1.05 | 0.045569 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GROVE 4 | 0.96144 | 0.89843 | -0.063009 |  | 0.92 | 1.05 | 0.13458 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | GROVE 4 | 0.96144 | 0.89843 | -0.063009 |  | 0.92 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | GROVE 4 | 0.96144 | 0.89843 | -0.063009 |  | 0.92 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GROVE 4 | 0.96144 | 0.89843 | -0.063009 |  | 0.92 | 1.05 | 0.068426 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GROVE 4 | 0.96144 | 0.89843 | -0.063009 |  | 0.92 | 1.05 | 0.035223 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GROVE 4 | 0.96144 | 0.89843 | -0.063009 |  | 0.92 | 1.05 | 0.034504 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GROVE 4 | 0.96156 | 0.89918 | -0.062382 |  | 0.92 | 1.05 | 0.040193 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GROVE 4 | 0.96156 | 0.89918 | -0.062382 |  | 0.92 | 1.05 | 0.088122 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GROVE 4 | 0.96156 | 0.89918 | -0.062382 |  | 0.92 | 1.05 | 0.074664 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GROVE 4 | 0.96156 | 0.89918 | -0.062382 |  | 0.92 | 1.05 | 0.068051 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GROVE 4 | 0.96156 | 0.89918 | -0.062382 |  | 0.92 | 1.05 | 0.034774 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | GROVE 4 | 0.96156 | 0.89918 | -0.062382 |  | 0.92 | 1.05 | 0.033904 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GROVE 4 | 0.96156 | 0.89918 | -0.062382 |  | 0.92 | 1.05 | 0.16366 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GROVE 4 | 0.96156 | 0.89918 | -0.062382 |  | 0.92 | 1.05 | 0.045569 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GROVE 4 | 0.96156 | 0.89918 | -0.062382 |  | 0.92 | 1.05 | 0.13458 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | GROVE 4 | 0.96156 | 0.89918 | -0.062382 |  | 0.92 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | GROVE 4 | 0.96156 | 0.89918 | -0.062382 |  | 0.92 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GROVE 4 | 0.96156 | 0.89918 | -0.062382 |  | 0.92 | 1.05 | 0.068426 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GROVE 4 | 0.96156 | 0.89918 | -0.062382 |  | 0.92 | 1.05 | 0.035223 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GROVE 4 | 0.96156 | 0.89918 | -0.062382 |  | 0.92 | 1.05 | 0.034504 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GROVE 4 | 0.96154 | 0.90278 | -0.058761 |  | 0.92 | 1.05 | 0.033596 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GROVE 4 | 0.96154 | 0.90278 | -0.058761 |  | 0.92 | 1.05 | 0.040193 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GROVE 4 | 0.96154 | 0.90278 | -0.058761 |  | 0.92 | 1.05 | 0.056051 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GROVE 4 | 0.96154 | 0.90278 | -0.058761 |  | 0.92 | 1.05 | 0.074664 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GROVE 4 | 0.96154 | 0.90278 | -0.058761 |  | 0.92 | 1.05 | 0.068051 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GROVE 4 | 0.96154 | 0.90278 | -0.058761 |  | 0.92 | 1.05 | 0.035565 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | GROVE 4 | 0.96154 | 0.90278 | -0.058761 |  | 0.92 | 1.05 | 0.033904 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GROVE 4 | 0.96154 | 0.90278 | -0.058761 |  | 0.92 | 1.05 | 0.082596 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GROVE 4 | 0.96154 | 0.90278 | -0.058761 |  | 0.92 | 1.05 | 0.045569 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GROVE 4 | 0.96154 | 0.90278 | -0.058761 |  | 0.92 | 1.05 | 0.13458 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | GROVE 4 | 0.96154 | 0.90278 | -0.058761 |  | 0.92 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | GROVE 4 | 0.96154 | 0.90278 | -0.058761 |  | 0.92 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GROVE 4 | 0.96154 | 0.90278 | -0.058761 |  | 0.92 | 1.05 | 0.068426 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GROVE 4 | 0.96154 | 0.90278 | -0.058761 |  | 0.92 | 1.05 | 0.035223 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GROVE 4 | 0.96154 | 0.90278 | -0.058761 |  | 0.92 | 1.05 | 0.034504 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GROVE 4 | 0.96251 | 0.90834 | -0.054168 |  | 0.92 | 1.05 | 0.035932 | P23:345:GRDA:TONNECE CB9580:::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GROVE 4 | 0.96251 | 0.90834 | -0.054168 |  | 0.92 | 1.05 | 0.057432 | P23:345:GRDA:TONNECE CB9580:::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GROVE 4 | 0.96251 | 0.90834 | -0.054168 |  | 0.92 | 1.05 | 0.068475 | P23:345:GRDA:TONNECE CB9580:::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GROVE 4 | 0.96251 | 0.90834 | -0.054168 |  | 0.92 | 1.05 | 0.035744 | P23:345:GRDA:TONNECE CB9580:::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GROVE 4 | 0.96251 | 0.90834 | -0.054168 |  | 0.92 | 1.05 | 0.1501 | P23:345:GRDA:TONNECE CB9580:::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GROVE 4 | 0.96251 | 0.90834 | -0.054168 |  | 0.92 | 1.05 | 0.058419 | P23:345:GRDA:TONNECE CB9580:::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | ASGI-2024-023 | GROVE 4 | 0.96653 | 0.90941 | -0.057112 |  | 0.92 | 1.05 | 0.079962 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | GROVE 4 | 0.96653 | 0.90941 | -0.057112 |  | 0.92 | 1.05 | 0.065323 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-068 | GROVE 4 | 0.96653 | 0.90941 | -0.057112 |  | 0.92 | 1.05 | 0.067422 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-071 | GROVE 4 | 0.96653 | 0.90941 | -0.057112 |  | 0.92 | 1.05 | 0.074668 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GROVE 4 | 0.96653 | 0.90941 | -0.057112 |  | 0.92 | 1.05 | 0.053027 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-122 | GROVE 4 | 0.96653 | 0.90941 | -0.057112 |  | 0.92 | 1.05 | 0.082926 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-177 | GROVE 4 | 0.96653 | 0.90941 | -0.057112 |  | 0.92 | 1.05 | 0.084694 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-178 | GROVE 4 | 0.96653 | 0.90941 | -0.057112 |  | 0.92 | 1.05 | 0.078867 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | GROVE 4 | 0.96653 | 0.90941 | -0.057112 |  | 0.92 | 1.05 | 0.031571 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-220 | GROVE 4 | 0.96653 | 0.90941 | -0.057112 |  | 0.92 | 1.05 | 0.075331 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-232 | GROVE 4 | 0.96653 | 0.90941 | -0.057112 |  | 0.92 | 1.05 | 0.078906 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | GROVE 4 | 0.96653 | 0.90941 | -0.057112 |  | 0.92 | 1.05 | 0.065323 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GROVE 4 | 0.96653 | 0.90941 | -0.057112 |  | 0.92 | 1.05 | 0.03431 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | GROVE 4 | 0.96653 | 0.90941 | -0.057112 |  | 0.92 | 1.05 | 0.031504 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | GROVE 4 | 0.96653 | 0.90941 | -0.057112 |  | 0.92 | 1.05 | 0.031504 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | GROVE 4 | 0.96653 | 0.90941 | -0.057112 |  | 0.92 | 1.05 | 0.030663 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | GROVE 4 | 0.96653 | 0.90941 | -0.057112 |  | 0.92 | 1.05 | 0.04269 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-376 | GROVE 4 | 0.96653 | 0.90941 | -0.057112 |  | 0.92 | 1.05 | 0.082476 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GROVE 5 | 0.96961 | 0.90541 | -0.064205 |  | 0.92 | 1.05 | 0.033596 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GROVE 5 | 0.96961 | 0.90541 | -0.064205 |  | 0.92 | 1.05 | 0.040193 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GROVE 5 | 0.96961 | 0.90541 | -0.064205 |  | 0.92 | 1.05 | 0.088122 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GROVE 5 | 0.96961 | 0.90541 | -0.064205 |  | 0.92 | 1.05 | 0.074664 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GROVE 5 | 0.96961 | 0.90541 | -0.064205 |  | 0.92 | 1.05 | 0.068051 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GROVE 5 | 0.96961 | 0.90541 | -0.064205 |  | 0.92 | 1.05 | 0.035565 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | GROVE 5 | 0.96961 | 0.90541 | -0.064205 |  | 0.92 | 1.05 | 0.033904 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GROVE 5 | 0.96961 | 0.90541 | -0.064205 |  | 0.92 | 1.05 | 0.16366 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GROVE 5 | 0.96961 | 0.90541 | -0.064205 |  | 0.92 | 1.05 | 0.045569 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GROVE 5 | 0.96961 | 0.90541 | -0.064205 |  | 0.92 | 1.05 | 0.13458 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | GROVE 5 | 0.96961 | 0.90541 | -0.064205 |  | 0.92 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | GROVE 5 | 0.96961 | 0.90541 | -0.064205 |  | 0.92 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GROVE 5 | 0.96961 | 0.90541 | -0.064205 |  | 0.92 | 1.05 | 0.068426 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GROVE 5 | 0.96961 | 0.90541 | -0.064205 |  | 0.92 | 1.05 | 0.035223 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GROVE 5 | 0.96961 | 0.90541 | -0.064205 |  | 0.92 | 1.05 | 0.034504 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GROVE 5 | 0.96975 | 0.90626 | -0.063494 |  | 0.92 | 1.05 | 0.040193 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GROVE 5 | 0.96975 | 0.90626 | -0.063494 |  | 0.92 | 1.05 | 0.088122 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GROVE 5 | 0.96975 | 0.90626 | -0.063494 |  | 0.92 | 1.05 | 0.074664 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GROVE 5 | 0.96975 | 0.90626 | -0.063494 |  | 0.92 | 1.05 | 0.068051 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GROVE 5 | 0.96975 | 0.90626 | -0.063494 |  | 0.92 | 1.05 | 0.034774 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | GROVE 5 | 0.96975 | 0.90626 | -0.063494 |  | 0.92 | 1.05 | 0.033904 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GROVE 5 | 0.96975 | 0.90626 | -0.063494 |  | 0.92 | 1.05 | 0.16366 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GROVE 5 | 0.96975 | 0.90626 | -0.063494 |  | 0.92 | 1.05 | 0.045569 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GROVE 5 | 0.96975 | 0.90626 | -0.063494 |  | 0.92 | 1.05 | 0.13458 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | GROVE 5 | 0.96975 | 0.90626 | -0.063494 |  | 0.92 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | GROVE 5 | 0.96975 | 0.90626 | -0.063494 |  | 0.92 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GROVE 5 | 0.96975 | 0.90626 | -0.063494 |  | 0.92 | 1.05 | 0.068426 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GROVE 5 | 0.96975 | 0.90626 | -0.063494 |  | 0.92 | 1.05 | 0.035223 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GROVE 5 | 0.96975 | 0.90626 | -0.063494 |  | 0.92 | 1.05 | 0.034504 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GROVE 5 | 0.96971 | 0.91031 | -0.059403 |  | 0.92 | 1.05 | 0.033596 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GROVE 5 | 0.96971 | 0.91031 | -0.059403 |  | 0.92 | 1.05 | 0.040193 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GROVE 5 | 0.96971 | 0.91031 | -0.059403 |  | 0.92 | 1.05 | 0.056051 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GROVE 5 | 0.96971 | 0.91031 | -0.059403 |  | 0.92 | 1.05 | 0.074664 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GROVE 5 | 0.96971 | 0.91031 | -0.059403 |  | 0.92 | 1.05 | 0.068051 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GROVE 5 | 0.96971 | 0.91031 | -0.059403 |  | 0.92 | 1.05 | 0.035565 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | GROVE 5 | 0.96971 | 0.91031 | -0.059403 |  | 0.92 | 1.05 | 0.033904 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GROVE 5 | 0.96971 | 0.91031 | -0.059403 |  | 0.92 | 1.05 | 0.082596 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GROVE 5 | 0.96971 | 0.91031 | -0.059403 |  | 0.92 | 1.05 | 0.045569 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GROVE 5 | 0.96971 | 0.91031 | -0.059403 |  | 0.92 | 1.05 | 0.13458 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | GROVE 5 | 0.96971 | 0.91031 | -0.059403 |  | 0.92 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | GROVE 5 | 0.96971 | 0.91031 | -0.059403 |  | 0.92 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GROVE 5 | 0.96971 | 0.91031 | -0.059403 |  | 0.92 | 1.05 | 0.068426 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | GROVE 5 | 0.96971 | 0.91031 | -0.059403 |  | 0.92 | 1.05 | 0.035223 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | GROVE 5 | 0.96971 | 0.91031 | -0.059403 |  | 0.92 | 1.05 | 0.034504 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | ASGI-2024-023 | GROVE 5 | 0.97472 | 0.91725 | -0.057469 |  | 0.92 | 1.05 | 0.079962 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | GROVE 5 | 0.97472 | 0.91725 | -0.057469 |  | 0.92 | 1.05 | 0.065323 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-068 | GROVE 5 | 0.97472 | 0.91725 | -0.057469 |  | 0.92 | 1.05 | 0.067422 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-071 | GROVE 5 | 0.97472 | 0.91725 | -0.057469 |  | 0.92 | 1.05 | 0.074668 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | GROVE 5 | 0.97472 | 0.91725 | -0.057469 |  | 0.92 | 1.05 | 0.053027 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-122 | GROVE 5 | 0.97472 | 0.91725 | -0.057469 |  | 0.92 | 1.05 | 0.082926 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-177 | GROVE 5 | 0.97472 | 0.91725 | -0.057469 |  | 0.92 | 1.05 | 0.084694 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-178 | GROVE 5 | 0.97472 | 0.91725 | -0.057469 |  | 0.92 | 1.05 | 0.078867 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | GROVE 5 | 0.97472 | 0.91725 | -0.057469 |  | 0.92 | 1.05 | 0.031571 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-220 | GROVE 5 | 0.97472 | 0.91725 | -0.057469 |  | 0.92 | 1.05 | 0.075331 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-232 | GROVE 5 | 0.97472 | 0.91725 | -0.057469 |  | 0.92 | 1.05 | 0.078906 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | GROVE 5 | 0.97472 | 0.91725 | -0.057469 |  | 0.92 | 1.05 | 0.065323 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | GROVE 5 | 0.97472 | 0.91725 | -0.057469 |  | 0.92 | 1.05 | 0.03431 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | GROVE 5 | 0.97472 | 0.91725 | -0.057469 |  | 0.92 | 1.05 | 0.031504 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | GROVE 5 | 0.97472 | 0.91725 | -0.057469 |  | 0.92 | 1.05 | 0.031504 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | GROVE 5 | 0.97472 | 0.91725 | -0.057469 |  | 0.92 | 1.05 | 0.030663 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | GROVE 5 | 0.97472 | 0.91725 | -0.057469 |  | 0.92 | 1.05 | 0.04269 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-376 | GROVE 5 | 0.97472 | 0.91725 | -0.057469 |  | 0.92 | 1.05 | 0.082476 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | GROVE 5 | 0.97269 | 0.91694 | -0.055745 |  | 0.92 | 1.05 | 0.033596 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.2 MVAR switched shunt at GROVE 5 161 kV; Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | GROVE 5 | 0.97269 | 0.91694 | -0.055745 |  | 0.92 | 1.05 | 0.088122 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.2 MVAR switched shunt at GROVE 5 161 kV; Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GROVE 5 | 0.97269 | 0.91694 | -0.055745 |  | 0.92 | 1.05 | 0.030897 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.2 MVAR switched shunt at GROVE 5 161 kV; Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | GROVE 5 | 0.97269 | 0.91694 | -0.055745 |  | 0.92 | 1.05 | 0.038719 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.2 MVAR switched shunt at GROVE 5 161 kV; Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | GROVE 5 | 0.97269 | 0.91694 | -0.055745 |  | 0.92 | 1.05 | 0.035565 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.2 MVAR switched shunt at GROVE 5 161 kV; Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | GROVE 5 | 0.97269 | 0.91694 | -0.055745 |  | 0.92 | 1.05 | 0.16366 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.2 MVAR switched shunt at GROVE 5 161 kV; Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | GROVE 5 | 0.97269 | 0.91694 | -0.055745 |  | 0.92 | 1.05 | 0.038589 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.2 MVAR switched shunt at GROVE 5 161 kV; Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | GROVE 5 | 0.97269 | 0.91694 | -0.055745 |  | 0.92 | 1.05 | 0.034208 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.2 MVAR switched shunt at GROVE 5 161 kV; Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GUAVA 4 | 0.82982 | 0.79862 | -0.031199 |  | 0.92 | 1.05 | 0.038424 | Single 509752 INOLATP4 138 509790 CATOOSA4 138 1 | Add 57 MVAR switched shunt at GUAVA 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | GUAVA 4 | 0.84695 | 0.81817 | -0.028777 |  | 0.92 | 1.05 | 0.038424 | Single 509752 INOLATP4 138 510442 GUAVA4 138 1 | Add 57 MVAR switched shunt at GUAVA 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | HALSTD 4 | 0.95459 | 0.90198 | -0.052609 |  | 0.93 | 1.05 | 0.044747 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | HALSTD 4 | 0.95459 | 0.90198 | -0.052609 |  | 0.93 | 1.05 | 0.063323 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | HALSTD 4 | 0.95459 | 0.90198 | -0.052609 |  | 0.93 | 1.05 | 0.043143 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | HALSTD 4 | 0.95459 | 0.90198 | -0.052609 |  | 0.93 | 1.05 | 0.038771 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | HALSTD 4 | 0.95459 | 0.90198 | -0.052609 |  | 0.93 | 1.05 | 0.038438 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | HALSTD 4 | 0.95459 | 0.90198 | -0.052609 |  | 0.93 | 1.05 | 0.04552 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | HALSTD 4 | 0.95459 | 0.90198 | -0.052609 |  | 0.93 | 1.05 | 0.03158 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | HALSTD 4 | 0.95459 | 0.90198 | -0.052609 |  | 0.93 | 1.05 | 0.034131 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | HALSTD 4 | 0.95459 | 0.90198 | -0.052609 |  | 0.93 | 1.05 | 0.042547 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | HALSTD 4 | 0.95459 | 0.90198 | -0.052609 |  | 0.93 | 1.05 | 0.032964 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | HALSTD 4 | 0.95459 | 0.90198 | -0.052609 |  | 0.93 | 1.05 | 0.041072 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | HALSTD 4 | 0.95459 | 0.90198 | -0.052609 |  | 0.93 | 1.05 | 0.069811 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | HALSTD 4 | 0.95459 | 0.90198 | -0.052609 |  | 0.93 | 1.05 | 0.041072 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | HALSTD 4 | 0.95459 | 0.90198 | -0.052609 |  | 0.93 | 1.05 | 0.042352 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | HALSTD 4 | 0.95459 | 0.90198 | -0.052609 |  | 0.93 | 1.05 | 0.041773 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | HALSTD 4 | 0.95459 | 0.90198 | -0.052609 |  | 0.93 | 1.05 | 0.048747 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | HALSTD 4 | 0.95459 | 0.90198 | -0.052609 |  | 0.93 | 1.05 | 0.044283 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | HALSTD 4 | 0.95459 | 0.90198 | -0.052609 |  | 0.93 | 1.05 | 0.039667 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | HALSTD 4 | 0.95459 | 0.90198 | -0.052609 |  | 0.93 | 1.05 | 0.031705 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | HALSTD 4 | 0.95459 | 0.90198 | -0.052609 |  | 0.93 | 1.05 | 0.036041 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | HALSTD 4 | 0.95459 | 0.90198 | -0.052609 |  | 0.93 | 1.05 | 0.035457 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | HALSTD 4 | 0.95459 | 0.90198 | -0.052609 |  | 0.93 | 1.05 | 0.0376 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | HALSTD 4 | 0.95459 | 0.90198 | -0.052609 |  | 0.93 | 1.05 | 0.039043 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | HALSTD 4 | 0.95495 | 0.903 | -0.051953 |  | 0.93 | 1.05 | 0.044747 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | HALSTD 4 | 0.95495 | 0.903 | -0.051953 |  | 0.93 | 1.05 | 0.038771 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | HALSTD 4 | 0.95495 | 0.903 | -0.051953 |  | 0.93 | 1.05 | 0.038438 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | HALSTD 4 | 0.95495 | 0.903 | -0.051953 |  | 0.93 | 1.05 | 0.030968 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | HALSTD 4 | 0.95495 | 0.903 | -0.051953 |  | 0.93 | 1.05 | 0.03158 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | HALSTD 4 | 0.95495 | 0.903 | -0.051953 |  | 0.93 | 1.05 | 0.034131 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | HALSTD 4 | 0.95495 | 0.903 | -0.051953 |  | 0.93 | 1.05 | 0.040933 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | HALSTD 4 | 0.95495 | 0.903 | -0.051953 |  | 0.93 | 1.05 | 0.032964 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | HALSTD 4 | 0.95495 | 0.903 | -0.051953 |  | 0.93 | 1.05 | 0.041072 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | HALSTD 4 | 0.95495 | 0.903 | -0.051953 |  | 0.93 | 1.05 | 0.041072 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | HALSTD 4 | 0.95495 | 0.903 | -0.051953 |  | 0.93 | 1.05 | 0.042352 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | HALSTD 4 | 0.95495 | 0.903 | -0.051953 |  | 0.93 | 1.05 | 0.041773 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | HALSTD 4 | 0.95495 | 0.903 | -0.051953 |  | 0.93 | 1.05 | 0.039667 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | HALSTD 4 | 0.95495 | 0.903 | -0.051953 |  | 0.93 | 1.05 | 0.031705 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | HALSTD 4 | 0.95495 | 0.903 | -0.051953 |  | 0.93 | 1.05 | 0.036041 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | HALSTD 4 | 0.95495 | 0.903 | -0.051953 |  | 0.93 | 1.05 | 0.035457 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | HALSTD 4 | 0.95495 | 0.903 | -0.051953 |  | 0.93 | 1.05 | 0.0376 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | HALSTD 4 | 0.95495 | 0.903 | -0.051953 |  | 0.93 | 1.05 | 0.039043 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | HALSTD 4 | 0.97763 | 0.91924 | -0.058389 |  | 0.93 | 1.05 | 0.040439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | HALSTD 4 | 0.97763 | 0.91924 | -0.058389 |  | 0.93 | 1.05 | 0.034853 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | HALSTD 4 | 0.97763 | 0.91924 | -0.058389 |  | 0.93 | 1.05 | 0.046783 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | HALSTD 4 | 0.97763 | 0.91924 | -0.058389 |  | 0.93 | 1.05 | 0.047615 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | HALSTD 4 | 0.97763 | 0.91924 | -0.058389 |  | 0.93 | 1.05 | 0.034938 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | HALSTD 4 | 0.97763 | 0.91924 | -0.058389 |  | 0.93 | 1.05 | 0.037875 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | HALSTD 4 | 0.97763 | 0.91924 | -0.058389 |  | 0.93 | 1.05 | 0.044022 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | HALSTD 4 | 0.97763 | 0.91924 | -0.058389 |  | 0.93 | 1.05 | 0.030552 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | HALSTD 4 | 0.97763 | 0.91924 | -0.058389 |  | 0.93 | 1.05 | 0.038531 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | HALSTD 4 | 0.97763 | 0.91924 | -0.058389 |  | 0.93 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | HALSTD 4 | 0.97763 | 0.91924 | -0.058389 |  | 0.93 | 1.05 | 0.062491 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | HALSTD 4 | 0.97763 | 0.91924 | -0.058389 |  | 0.93 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | HALSTD 4 | 0.97763 | 0.91924 | -0.058389 |  | 0.93 | 1.05 | 0.038129 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | HALSTD 4 | 0.97763 | 0.91924 | -0.058389 |  | 0.93 | 1.05 | 0.038066 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | HALSTD 4 | 0.97763 | 0.91924 | -0.058389 |  | 0.93 | 1.05 | 0.034955 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | HALSTD 4 | 0.97763 | 0.91924 | -0.058389 |  | 0.93 | 1.05 | 0.06281 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | HALSTD 4 | 0.97763 | 0.91924 | -0.058389 |  | 0.93 | 1.05 | 0.045309 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | HALSTD 4 | 0.97763 | 0.91924 | -0.058389 |  | 0.93 | 1.05 | 0.035805 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | HALSTD 4 | 0.97763 | 0.91924 | -0.058389 |  | 0.93 | 1.05 | 0.032364 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | HALSTD 4 | 0.97763 | 0.91924 | -0.058389 |  | 0.93 | 1.05 | 0.031815 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | HALSTD 4 | 0.97763 | 0.91924 | -0.058389 |  | 0.93 | 1.05 | 0.033886 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | HALSTD 4 | 0.97763 | 0.91924 | -0.058389 |  | 0.93 | 1.05 | 0.035554 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | HALSTD 4 | 0.96594 | 0.88581 | -0.080128 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | HALSTD 4 | 0.96594 | 0.88581 | -0.080128 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | HALSTD 4 | 0.96594 | 0.88581 | -0.080128 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | HALSTD 4 | 0.96594 | 0.88581 | -0.080128 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | HALSTD 4 | 0.96594 | 0.88581 | -0.080128 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | HALSTD 4 | 0.96594 | 0.88581 | -0.080128 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | HALSTD 4 | 0.96594 | 0.88581 | -0.080128 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | HALSTD 4 | 0.96594 | 0.88581 | -0.080128 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | HALSTD 4 | 0.96594 | 0.88581 | -0.080128 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | HALSTD 4 | 0.96594 | 0.88581 | -0.080128 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | HALSTD 4 | 0.96594 | 0.88581 | -0.080128 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | HALSTD 4 | 0.96594 | 0.88581 | -0.080128 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | HALSTD 4 | 0.96594 | 0.88581 | -0.080128 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | HALSTD 4 | 0.96594 | 0.88581 | -0.080128 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | HALSTD 4 | 0.96594 | 0.88581 | -0.080128 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | HALSTD 4 | 0.96594 | 0.88581 | -0.080128 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | HALSTD 4 | 0.96594 | 0.88581 | -0.080128 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | HALSTD 4 | 0.96594 | 0.88581 | -0.080128 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | HALSTD 4 | 0.96594 | 0.88581 | -0.080128 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | HALSTD 4 | 0.96594 | 0.88581 | -0.080128 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | HALSTD 4 | 0.96594 | 0.88581 | -0.080128 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | HALSTD 4 | 0.96594 | 0.88581 | -0.080128 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | HALSTD 4 | 0.96594 | 0.88581 | -0.080128 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | HALSTD 4 | 0.96594 | 0.88581 | -0.080128 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | HALSTD 4 | 0.96594 | 0.88581 | -0.080128 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | HALSTED2 | 1.0006 | 0.92877 | -0.071782 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | HALSTED2 | 1.0006 | 0.92877 | -0.071782 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | HALSTED2 | 1.0006 | 0.92877 | -0.071782 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | HALSTED2 | 1.0006 | 0.92877 | -0.071782 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | HALSTED2 | 1.0006 | 0.92877 | -0.071782 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | HALSTED2 | 1.0006 | 0.92877 | -0.071782 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | HALSTED2 | 1.0006 | 0.92877 | -0.071782 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | HALSTED2 | 1.0006 | 0.92877 | -0.071782 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | HALSTED2 | 1.0006 | 0.92877 | -0.071782 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | HALSTED2 | 1.0006 | 0.92877 | -0.071782 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | HALSTED2 | 1.0006 | 0.92877 | -0.071782 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | HALSTED2 | 1.0006 | 0.92877 | -0.071782 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | HALSTED2 | 1.0006 | 0.92877 | -0.071782 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | HALSTED2 | 1.0006 | 0.92877 | -0.071782 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | HALSTED2 | 1.0006 | 0.92877 | -0.071782 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | HALSTED2 | 1.0006 | 0.92877 | -0.071782 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | HALSTED2 | 1.0006 | 0.92877 | -0.071782 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | HALSTED2 | 1.0006 | 0.92877 | -0.071782 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | HALSTED2 | 1.0006 | 0.92877 | -0.071782 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | HALSTED2 | 1.0006 | 0.92877 | -0.071782 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | HALSTED2 | 1.0006 | 0.92877 | -0.071782 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | HALSTED2 | 1.0006 | 0.92877 | -0.071782 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | HALSTED2 | 1.0006 | 0.92877 | -0.071782 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | HALSTED2 | 1.0006 | 0.92877 | -0.071782 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | HALSTED2 | 1.0006 | 0.92877 | -0.071782 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | HAWTH 7 | 0.99129 | 0.94933 | -0.041959 |  | 0.95 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | HAWTH 7 | 0.99129 | 0.94933 | -0.041959 |  | 0.95 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | HAWTH 7 | 0.99129 | 0.94933 | -0.041959 |  | 0.95 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | HAWTH 7 | 0.99129 | 0.94933 | -0.041959 |  | 0.95 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | HAWTH 7 | 0.99129 | 0.94933 | -0.041959 |  | 0.95 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | HAWTH 7 | 0.99129 | 0.94933 | -0.041959 |  | 0.95 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | HAWTH 7 | 0.99129 | 0.94933 | -0.041959 |  | 0.95 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | HAWTH 7 | 0.99129 | 0.94933 | -0.041959 |  | 0.95 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | HAWTH 7 | 0.99129 | 0.94933 | -0.041959 |  | 0.95 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | HAWTH 7 | 0.99129 | 0.94933 | -0.041959 |  | 0.95 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | HAWTH 7 | 0.99129 | 0.94933 | -0.041959 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | HAWTH 7 | 0.99129 | 0.94933 | -0.041959 |  | 0.95 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | HAWTH 7 | 0.99129 | 0.94933 | -0.041959 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | HAWTH 7 | 0.99129 | 0.94933 | -0.041959 |  | 0.95 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | HAWTH 7 | 0.99129 | 0.94933 | -0.041959 |  | 0.95 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | HAWTH 7 | 0.99129 | 0.94933 | -0.041959 |  | 0.95 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | HAWTH 7 | 0.99129 | 0.94933 | -0.041959 |  | 0.95 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | HAWTH 7 | 0.99129 | 0.94933 | -0.041959 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | HAWTH 7 | 0.99129 | 0.94933 | -0.041959 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | HAWTH 7 | 0.99129 | 0.94933 | -0.041959 |  | 0.95 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | HAWTH 7 | 0.99129 | 0.94933 | -0.041959 |  | 0.95 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | HAWTH 7 | 0.99129 | 0.94933 | -0.041959 |  | 0.95 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | HAWTH 7 | 0.99129 | 0.94933 | -0.041959 |  | 0.95 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | HAWTH 7 | 0.99129 | 0.94933 | -0.041959 |  | 0.95 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | HAWTH 7 | 0.99129 | 0.94933 | -0.041959 |  | 0.95 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | HESSTON2 | 0.98548 | 0.92223 | -0.06325 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | HESSTON2 | 0.98548 | 0.92223 | -0.06325 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | HESSTON2 | 0.98548 | 0.92223 | -0.06325 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | HESSTON2 | 0.98548 | 0.92223 | -0.06325 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | HESSTON2 | 0.98548 | 0.92223 | -0.06325 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | HESSTON2 | 0.98548 | 0.92223 | -0.06325 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | HESSTON2 | 0.98548 | 0.92223 | -0.06325 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | HESSTON2 | 0.98548 | 0.92223 | -0.06325 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | HESSTON2 | 0.98548 | 0.92223 | -0.06325 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | HESSTON2 | 0.98548 | 0.92223 | -0.06325 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | HESSTON2 | 0.98548 | 0.92223 | -0.06325 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | HESSTON2 | 0.98548 | 0.92223 | -0.06325 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | HESSTON2 | 0.98548 | 0.92223 | -0.06325 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | HESSTON2 | 0.98548 | 0.92223 | -0.06325 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | HESSTON2 | 0.98548 | 0.92223 | -0.06325 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | HESSTON2 | 0.98548 | 0.92223 | -0.06325 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | HESSTON2 | 0.98548 | 0.92223 | -0.06325 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | HESSTON2 | 0.98548 | 0.92223 | -0.06325 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | HESSTON2 | 0.98548 | 0.92223 | -0.06325 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | HESSTON2 | 0.98548 | 0.92223 | -0.06325 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | HESSTON2 | 0.98548 | 0.92223 | -0.06325 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | HESSTON2 | 0.98548 | 0.92223 | -0.06325 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | HESSTON2 | 0.98548 | 0.92223 | -0.06325 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | HESSTON2 | 0.98548 | 0.92223 | -0.06325 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | HESSTON2 | 0.98548 | 0.92223 | -0.06325 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | HICKMAN5 | 0.98763 | 0.91537 | -0.07226 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | HICKMAN5 | 0.98763 | 0.91537 | -0.07226 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | HICKMAN5 | 0.98763 | 0.91537 | -0.07226 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | HICKMAN5 | 0.98763 | 0.91537 | -0.07226 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | HICKMAN5 | 0.98763 | 0.91537 | -0.07226 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | HICKMAN5 | 0.98763 | 0.91537 | -0.07226 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | HICKMAN5 | 0.98763 | 0.91537 | -0.07226 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | HICKMAN5 | 0.98763 | 0.91537 | -0.07226 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | HICKMAN5 | 0.98763 | 0.91537 | -0.07226 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | HICKMAN5 | 0.98763 | 0.91537 | -0.07226 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | HICKMAN5 | 0.98763 | 0.91537 | -0.07226 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | HICKMAN5 | 0.98763 | 0.91537 | -0.07226 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | HICKMAN5 | 0.98763 | 0.91537 | -0.07226 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | HICKMAN5 | 0.98763 | 0.91537 | -0.07226 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | HICKMAN5 | 0.98763 | 0.91537 | -0.07226 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | HICKMAN5 | 0.98763 | 0.91537 | -0.07226 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | HICKMAN5 | 0.98763 | 0.91537 | -0.07226 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | HICKMAN5 | 0.98763 | 0.91537 | -0.07226 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | HICKMAN5 | 0.98763 | 0.91537 | -0.07226 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | HICKMAN5 | 0.98763 | 0.91537 | -0.07226 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | HICKMAN5 | 0.98763 | 0.91537 | -0.07226 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | HICKMAN5 | 0.98763 | 0.91537 | -0.07226 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | HICKMAN5 | 0.98763 | 0.91537 | -0.07226 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | HICKMAN5 | 0.98763 | 0.91537 | -0.07226 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | HICKMAN5 | 0.98763 | 0.91537 | -0.07226 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | HONEYWL5 | 0.99083 | 0.91664 | -0.074184 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | HONEYWL5 | 0.99083 | 0.91664 | -0.074184 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | HONEYWL5 | 0.99083 | 0.91664 | -0.074184 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | HONEYWL5 | 0.99083 | 0.91664 | -0.074184 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | HONEYWL5 | 0.99083 | 0.91664 | -0.074184 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | HONEYWL5 | 0.99083 | 0.91664 | -0.074184 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | HONEYWL5 | 0.99083 | 0.91664 | -0.074184 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | HONEYWL5 | 0.99083 | 0.91664 | -0.074184 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | HONEYWL5 | 0.99083 | 0.91664 | -0.074184 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | HONEYWL5 | 0.99083 | 0.91664 | -0.074184 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | HONEYWL5 | 0.99083 | 0.91664 | -0.074184 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | HONEYWL5 | 0.99083 | 0.91664 | -0.074184 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | HONEYWL5 | 0.99083 | 0.91664 | -0.074184 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | HONEYWL5 | 0.99083 | 0.91664 | -0.074184 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | HONEYWL5 | 0.99083 | 0.91664 | -0.074184 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | HONEYWL5 | 0.99083 | 0.91664 | -0.074184 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | HONEYWL5 | 0.99083 | 0.91664 | -0.074184 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | HONEYWL5 | 0.99083 | 0.91664 | -0.074184 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | HONEYWL5 | 0.99083 | 0.91664 | -0.074184 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | HONEYWL5 | 0.99083 | 0.91664 | -0.074184 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | HONEYWL5 | 0.99083 | 0.91664 | -0.074184 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | HONEYWL5 | 0.99083 | 0.91664 | -0.074184 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | HONEYWL5 | 0.99083 | 0.91664 | -0.074184 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | HONEYWL5 | 0.99083 | 0.91664 | -0.074184 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | HONEYWL5 | 0.99083 | 0.91664 | -0.074184 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | HOOVER 4 | 0.99012 | 0.92721 | -0.062903 |  | 0.93 | 1.05 | 0.040439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | HOOVER 4 | 0.99012 | 0.92721 | -0.062903 |  | 0.93 | 1.05 | 0.034853 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | HOOVER 4 | 0.99012 | 0.92721 | -0.062903 |  | 0.93 | 1.05 | 0.046783 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | HOOVER 4 | 0.99012 | 0.92721 | -0.062903 |  | 0.93 | 1.05 | 0.047615 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | HOOVER 4 | 0.99012 | 0.92721 | -0.062903 |  | 0.93 | 1.05 | 0.034938 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | HOOVER 4 | 0.99012 | 0.92721 | -0.062903 |  | 0.93 | 1.05 | 0.037875 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | HOOVER 4 | 0.99012 | 0.92721 | -0.062903 |  | 0.93 | 1.05 | 0.044022 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | HOOVER 4 | 0.99012 | 0.92721 | -0.062903 |  | 0.93 | 1.05 | 0.030552 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | HOOVER 4 | 0.99012 | 0.92721 | -0.062903 |  | 0.93 | 1.05 | 0.038531 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | HOOVER 4 | 0.99012 | 0.92721 | -0.062903 |  | 0.93 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | HOOVER 4 | 0.99012 | 0.92721 | -0.062903 |  | 0.93 | 1.05 | 0.062491 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | HOOVER 4 | 0.99012 | 0.92721 | -0.062903 |  | 0.93 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | HOOVER 4 | 0.99012 | 0.92721 | -0.062903 |  | 0.93 | 1.05 | 0.038129 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | HOOVER 4 | 0.99012 | 0.92721 | -0.062903 |  | 0.93 | 1.05 | 0.038066 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | HOOVER 4 | 0.99012 | 0.92721 | -0.062903 |  | 0.93 | 1.05 | 0.034955 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | HOOVER 4 | 0.99012 | 0.92721 | -0.062903 |  | 0.93 | 1.05 | 0.06281 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | HOOVER 4 | 0.99012 | 0.92721 | -0.062903 |  | 0.93 | 1.05 | 0.045309 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | HOOVER 4 | 0.99012 | 0.92721 | -0.062903 |  | 0.93 | 1.05 | 0.035805 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | HOOVER 4 | 0.99012 | 0.92721 | -0.062903 |  | 0.93 | 1.05 | 0.032364 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | HOOVER 4 | 0.99012 | 0.92721 | -0.062903 |  | 0.93 | 1.05 | 0.031815 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | HOOVER 4 | 0.99012 | 0.92721 | -0.062903 |  | 0.93 | 1.05 | 0.033886 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | HOOVER 4 | 0.99012 | 0.92721 | -0.062903 |  | 0.93 | 1.05 | 0.035554 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | HOOVER 4 | 0.99196 | 0.92568 | -0.066284 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | HOOVER 4 | 0.99196 | 0.92568 | -0.066284 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | HOOVER 4 | 0.99196 | 0.92568 | -0.066284 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | HOOVER 4 | 0.99196 | 0.92568 | -0.066284 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | HOOVER 4 | 0.99196 | 0.92568 | -0.066284 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | HOOVER 4 | 0.99196 | 0.92568 | -0.066284 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | HOOVER 4 | 0.99196 | 0.92568 | -0.066284 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | HOOVER 4 | 0.99196 | 0.92568 | -0.066284 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | HOOVER 4 | 0.99196 | 0.92568 | -0.066284 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | HOOVER 4 | 0.99196 | 0.92568 | -0.066284 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | HOOVER 4 | 0.99196 | 0.92568 | -0.066284 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | HOOVER 4 | 0.99196 | 0.92568 | -0.066284 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | HOOVER 4 | 0.99196 | 0.92568 | -0.066284 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | HOOVER 4 | 0.99196 | 0.92568 | -0.066284 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | HOOVER 4 | 0.99196 | 0.92568 | -0.066284 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | HOOVER 4 | 0.99196 | 0.92568 | -0.066284 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | HOOVER 4 | 0.99196 | 0.92568 | -0.066284 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | HOOVER 4 | 0.99196 | 0.92568 | -0.066284 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | HOOVER 4 | 0.99196 | 0.92568 | -0.066284 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | HOOVER 4 | 0.99196 | 0.92568 | -0.066284 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | HOOVER 4 | 0.99196 | 0.92568 | -0.066284 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | HOOVER 4 | 0.99196 | 0.92568 | -0.066284 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | HOOVER 4 | 0.99196 | 0.92568 | -0.066284 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | HOOVER 4 | 0.99196 | 0.92568 | -0.066284 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | HOOVER 4 | 0.99196 | 0.92568 | -0.066284 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | HOYT 7 | 0.98529 | 0.94737 | -0.037921 |  | 0.95 | 1.05 | 0.036307 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | HOYT 7 | 0.98529 | 0.94737 | -0.037921 |  | 0.95 | 1.05 | 0.052743 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | HOYT 7 | 0.98529 | 0.94737 | -0.037921 |  | 0.95 | 1.05 | 0.039345 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | HOYT 7 | 0.98529 | 0.94737 | -0.037921 |  | 0.95 | 1.05 | 0.031366 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | HOYT 7 | 0.98529 | 0.94737 | -0.037921 |  | 0.95 | 1.05 | 0.041888 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | HOYT 7 | 0.98529 | 0.94737 | -0.037921 |  | 0.95 | 1.05 | 0.038797 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | HOYT 7 | 0.98529 | 0.94737 | -0.037921 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | HOYT 7 | 0.98529 | 0.94737 | -0.037921 |  | 0.95 | 1.05 | 0.067346 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | HOYT 7 | 0.98529 | 0.94737 | -0.037921 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | HOYT 7 | 0.98529 | 0.94737 | -0.037921 |  | 0.95 | 1.05 | 0.030851 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | HOYT 7 | 0.98529 | 0.94737 | -0.037921 |  | 0.95 | 1.05 | 0.032161 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | HOYT 7 | 0.98529 | 0.94737 | -0.037921 |  | 0.95 | 1.05 | 0.04067 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | HOYT 7 | 0.98529 | 0.94737 | -0.037921 |  | 0.95 | 1.05 | 0.040569 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | HOYT 7 | 0.98529 | 0.94737 | -0.037921 |  | 0.95 | 1.05 | 0.03086 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | HOYT 7 | 0.98529 | 0.94737 | -0.037921 |  | 0.95 | 1.05 | 0.033223 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | HOYT 7 | 0.98529 | 0.94737 | -0.037921 |  | 0.95 | 1.05 | 0.033733 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | HOYT 7 | 0.98867 | 0.9466 | -0.042072 |  | 0.95 | 1.05 | 0.036307 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | HOYT 7 | 0.98867 | 0.9466 | -0.042072 |  | 0.95 | 1.05 | 0.052743 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | HOYT 7 | 0.98867 | 0.9466 | -0.042072 |  | 0.95 | 1.05 | 0.039345 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | HOYT 7 | 0.98867 | 0.9466 | -0.042072 |  | 0.95 | 1.05 | 0.031366 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | HOYT 7 | 0.98867 | 0.9466 | -0.042072 |  | 0.95 | 1.05 | 0.041888 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | HOYT 7 | 0.98867 | 0.9466 | -0.042072 |  | 0.95 | 1.05 | 0.038797 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | HOYT 7 | 0.98867 | 0.9466 | -0.042072 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | HOYT 7 | 0.98867 | 0.9466 | -0.042072 |  | 0.95 | 1.05 | 0.067346 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | HOYT 7 | 0.98867 | 0.9466 | -0.042072 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | HOYT 7 | 0.98867 | 0.9466 | -0.042072 |  | 0.95 | 1.05 | 0.030851 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | HOYT 7 | 0.98867 | 0.9466 | -0.042072 |  | 0.95 | 1.05 | 0.032161 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | HOYT 7 | 0.98867 | 0.9466 | -0.042072 |  | 0.95 | 1.05 | 0.04067 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | HOYT 7 | 0.98867 | 0.9466 | -0.042072 |  | 0.95 | 1.05 | 0.040569 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | HOYT 7 | 0.98867 | 0.9466 | -0.042072 |  | 0.95 | 1.05 | 0.03086 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | HOYT 7 | 0.98867 | 0.9466 | -0.042072 |  | 0.95 | 1.05 | 0.033223 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | HOYT 7 | 0.98867 | 0.9466 | -0.042072 |  | 0.95 | 1.05 | 0.033733 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | ASGI-2024-023 | INDEPCO5 | 0.9703 | 0.91914 | -0.051166 |  | 0.92 | 1.05 | 0.079962 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 40 MVAR switched shunt at INDEPCO5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | INDEPCO5 | 0.9703 | 0.91914 | -0.051166 |  | 0.92 | 1.05 | 0.065323 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 40 MVAR switched shunt at INDEPCO5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-068 | INDEPCO5 | 0.9703 | 0.91914 | -0.051166 |  | 0.92 | 1.05 | 0.067422 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 40 MVAR switched shunt at INDEPCO5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-071 | INDEPCO5 | 0.9703 | 0.91914 | -0.051166 |  | 0.92 | 1.05 | 0.074668 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 40 MVAR switched shunt at INDEPCO5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | INDEPCO5 | 0.9703 | 0.91914 | -0.051166 |  | 0.92 | 1.05 | 0.053027 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 40 MVAR switched shunt at INDEPCO5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-122 | INDEPCO5 | 0.9703 | 0.91914 | -0.051166 |  | 0.92 | 1.05 | 0.082926 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 40 MVAR switched shunt at INDEPCO5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-177 | INDEPCO5 | 0.9703 | 0.91914 | -0.051166 |  | 0.92 | 1.05 | 0.084694 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 40 MVAR switched shunt at INDEPCO5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-178 | INDEPCO5 | 0.9703 | 0.91914 | -0.051166 |  | 0.92 | 1.05 | 0.078867 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 40 MVAR switched shunt at INDEPCO5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | INDEPCO5 | 0.9703 | 0.91914 | -0.051166 |  | 0.92 | 1.05 | 0.031571 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 40 MVAR switched shunt at INDEPCO5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-220 | INDEPCO5 | 0.9703 | 0.91914 | -0.051166 |  | 0.92 | 1.05 | 0.075331 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 40 MVAR switched shunt at INDEPCO5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-232 | INDEPCO5 | 0.9703 | 0.91914 | -0.051166 |  | 0.92 | 1.05 | 0.078906 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 40 MVAR switched shunt at INDEPCO5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | INDEPCO5 | 0.9703 | 0.91914 | -0.051166 |  | 0.92 | 1.05 | 0.065323 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 40 MVAR switched shunt at INDEPCO5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | INDEPCO5 | 0.9703 | 0.91914 | -0.051166 |  | 0.92 | 1.05 | 0.03431 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 40 MVAR switched shunt at INDEPCO5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | INDEPCO5 | 0.9703 | 0.91914 | -0.051166 |  | 0.92 | 1.05 | 0.031504 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 40 MVAR switched shunt at INDEPCO5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | INDEPCO5 | 0.9703 | 0.91914 | -0.051166 |  | 0.92 | 1.05 | 0.031504 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 40 MVAR switched shunt at INDEPCO5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | INDEPCO5 | 0.9703 | 0.91914 | -0.051166 |  | 0.92 | 1.05 | 0.030663 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 40 MVAR switched shunt at INDEPCO5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | INDEPCO5 | 0.9703 | 0.91914 | -0.051166 |  | 0.92 | 1.05 | 0.04269 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 40 MVAR switched shunt at INDEPCO5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-376 | INDEPCO5 | 0.9703 | 0.91914 | -0.051166 |  | 0.92 | 1.05 | 0.082476 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 40 MVAR switched shunt at INDEPCO5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | INDIAN_CK_5 | 0.98049 | 0.91456 | -0.065929 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | INDIAN_CK_5 | 0.98049 | 0.91456 | -0.065929 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | INDIAN_CK_5 | 0.98049 | 0.91456 | -0.065929 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | INDIAN_CK_5 | 0.98049 | 0.91456 | -0.065929 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | INDIAN_CK_5 | 0.98049 | 0.91456 | -0.065929 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | INDIAN_CK_5 | 0.98049 | 0.91456 | -0.065929 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | INDIAN_CK_5 | 0.98049 | 0.91456 | -0.065929 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | INDIAN_CK_5 | 0.98049 | 0.91456 | -0.065929 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | INDIAN_CK_5 | 0.98049 | 0.91456 | -0.065929 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | INDIAN_CK_5 | 0.98049 | 0.91456 | -0.065929 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | INDIAN_CK_5 | 0.98049 | 0.91456 | -0.065929 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | INDIAN_CK_5 | 0.98049 | 0.91456 | -0.065929 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | INDIAN_CK_5 | 0.98049 | 0.91456 | -0.065929 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | INDIAN_CK_5 | 0.98049 | 0.91456 | -0.065929 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | INDIAN_CK_5 | 0.98049 | 0.91456 | -0.065929 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | INDIAN_CK_5 | 0.98049 | 0.91456 | -0.065929 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | INDIAN_CK_5 | 0.98049 | 0.91456 | -0.065929 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | INDIAN_CK_5 | 0.98049 | 0.91456 | -0.065929 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | INDIAN_CK_5 | 0.98049 | 0.91456 | -0.065929 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | INDIAN_CK_5 | 0.98049 | 0.91456 | -0.065929 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | INDIAN_CK_5 | 0.98049 | 0.91456 | -0.065929 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | INDIAN_CK_5 | 0.98049 | 0.91456 | -0.065929 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | INDIAN_CK_5 | 0.98049 | 0.91456 | -0.065929 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | INDIAN_CK_5 | 0.98049 | 0.91456 | -0.065929 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | INDIAN_CK_5 | 0.98049 | 0.91456 | -0.065929 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | INOLA 4 | 0.82925 | 0.79802 | -0.031224 |  | 0.92 | 1.05 | 0.038424 | Single 509752 INOLATP4 138 509790 CATOOSA4 138 1 | Add 57 MVAR switched shunt at GUAVA 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | INOLATP4 | 0.82959 | 0.79838 | -0.03121 |  | 0.92 | 1.05 | 0.038424 | Single 509752 INOLATP4 138 509790 CATOOSA4 138 1 | Add 57 MVAR switched shunt at GUAVA 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | JADE 3 | 0.96934 | 0.89206 | -0.077282 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | JADE 3 | 0.96934 | 0.89206 | -0.077282 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | JADE 3 | 0.96934 | 0.89206 | -0.077282 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | JADE 3 | 0.96934 | 0.89206 | -0.077282 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | JADE 3 | 0.96934 | 0.89206 | -0.077282 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | JADE 3 | 0.96934 | 0.89206 | -0.077282 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | JADE 3 | 0.96934 | 0.89206 | -0.077282 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | JADE 3 | 0.96934 | 0.89206 | -0.077282 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | JADE 3 | 0.96934 | 0.89206 | -0.077282 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | JADE 3 | 0.96934 | 0.89206 | -0.077282 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | JADE 3 | 0.96934 | 0.89206 | -0.077282 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | JADE 3 | 0.96934 | 0.89206 | -0.077282 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | JADE 3 | 0.96934 | 0.89206 | -0.077282 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | JADE 3 | 0.96934 | 0.89206 | -0.077282 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | JADE 3 | 0.96934 | 0.89206 | -0.077282 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | JADE 3 | 0.96934 | 0.89206 | -0.077282 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | JADE 3 | 0.96934 | 0.89206 | -0.077282 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | JADE 3 | 0.96934 | 0.89206 | -0.077282 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | JADE 3 | 0.96934 | 0.89206 | -0.077282 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | JADE 3 | 0.96934 | 0.89206 | -0.077282 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | JADE 3 | 0.96934 | 0.89206 | -0.077282 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | JADE 3 | 0.96934 | 0.89206 | -0.077282 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | JADE 3 | 0.96934 | 0.89206 | -0.077282 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | JADE 3 | 0.96934 | 0.89206 | -0.077282 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | JADE 3 | 0.96934 | 0.89206 | -0.077282 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | JAY 4 | 0.96442 | 0.90661 | -0.057813 |  | 0.92 | 1.05 | 0.033596 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | JAY 4 | 0.96442 | 0.90661 | -0.057813 |  | 0.92 | 1.05 | 0.040193 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | JAY 4 | 0.96442 | 0.90661 | -0.057813 |  | 0.92 | 1.05 | 0.088122 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | JAY 4 | 0.96442 | 0.90661 | -0.057813 |  | 0.92 | 1.05 | 0.074664 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | JAY 4 | 0.96442 | 0.90661 | -0.057813 |  | 0.92 | 1.05 | 0.068051 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | JAY 4 | 0.96442 | 0.90661 | -0.057813 |  | 0.92 | 1.05 | 0.035565 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | JAY 4 | 0.96442 | 0.90661 | -0.057813 |  | 0.92 | 1.05 | 0.033904 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | JAY 4 | 0.96442 | 0.90661 | -0.057813 |  | 0.92 | 1.05 | 0.16366 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | JAY 4 | 0.96442 | 0.90661 | -0.057813 |  | 0.92 | 1.05 | 0.045569 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | JAY 4 | 0.96442 | 0.90661 | -0.057813 |  | 0.92 | 1.05 | 0.13458 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | JAY 4 | 0.96442 | 0.90661 | -0.057813 |  | 0.92 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | JAY 4 | 0.96442 | 0.90661 | -0.057813 |  | 0.92 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | JAY 4 | 0.96442 | 0.90661 | -0.057813 |  | 0.92 | 1.05 | 0.068426 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | JAY 4 | 0.96442 | 0.90661 | -0.057813 |  | 0.92 | 1.05 | 0.035223 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | JAY 4 | 0.96442 | 0.90661 | -0.057813 |  | 0.92 | 1.05 | 0.034504 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | JAY 4 | 0.96452 | 0.90724 | -0.057278 |  | 0.92 | 1.05 | 0.040193 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | JAY 4 | 0.96452 | 0.90724 | -0.057278 |  | 0.92 | 1.05 | 0.088122 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | JAY 4 | 0.96452 | 0.90724 | -0.057278 |  | 0.92 | 1.05 | 0.074664 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | JAY 4 | 0.96452 | 0.90724 | -0.057278 |  | 0.92 | 1.05 | 0.068051 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | JAY 4 | 0.96452 | 0.90724 | -0.057278 |  | 0.92 | 1.05 | 0.034774 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | JAY 4 | 0.96452 | 0.90724 | -0.057278 |  | 0.92 | 1.05 | 0.033904 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | JAY 4 | 0.96452 | 0.90724 | -0.057278 |  | 0.92 | 1.05 | 0.16366 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | JAY 4 | 0.96452 | 0.90724 | -0.057278 |  | 0.92 | 1.05 | 0.045569 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | JAY 4 | 0.96452 | 0.90724 | -0.057278 |  | 0.92 | 1.05 | 0.13458 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | JAY 4 | 0.96452 | 0.90724 | -0.057278 |  | 0.92 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | JAY 4 | 0.96452 | 0.90724 | -0.057278 |  | 0.92 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | JAY 4 | 0.96452 | 0.90724 | -0.057278 |  | 0.92 | 1.05 | 0.068426 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | JAY 4 | 0.96452 | 0.90724 | -0.057278 |  | 0.92 | 1.05 | 0.035223 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | JAY 4 | 0.96452 | 0.90724 | -0.057278 |  | 0.92 | 1.05 | 0.034504 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | JAY 4 | 0.96454 | 0.91035 | -0.054193 |  | 0.92 | 1.05 | 0.033596 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | JAY 4 | 0.96454 | 0.91035 | -0.054193 |  | 0.92 | 1.05 | 0.040193 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | JAY 4 | 0.96454 | 0.91035 | -0.054193 |  | 0.92 | 1.05 | 0.056051 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | JAY 4 | 0.96454 | 0.91035 | -0.054193 |  | 0.92 | 1.05 | 0.074664 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | JAY 4 | 0.96454 | 0.91035 | -0.054193 |  | 0.92 | 1.05 | 0.068051 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | JAY 4 | 0.96454 | 0.91035 | -0.054193 |  | 0.92 | 1.05 | 0.035565 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | JAY 4 | 0.96454 | 0.91035 | -0.054193 |  | 0.92 | 1.05 | 0.033904 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | JAY 4 | 0.96454 | 0.91035 | -0.054193 |  | 0.92 | 1.05 | 0.082596 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | JAY 4 | 0.96454 | 0.91035 | -0.054193 |  | 0.92 | 1.05 | 0.045569 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | JAY 4 | 0.96454 | 0.91035 | -0.054193 |  | 0.92 | 1.05 | 0.13458 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | JAY 4 | 0.96454 | 0.91035 | -0.054193 |  | 0.92 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | JAY 4 | 0.96454 | 0.91035 | -0.054193 |  | 0.92 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | JAY 4 | 0.96454 | 0.91035 | -0.054193 |  | 0.92 | 1.05 | 0.068426 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | JAY 4 | 0.96454 | 0.91035 | -0.054193 |  | 0.92 | 1.05 | 0.035223 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | JAY 4 | 0.96454 | 0.91035 | -0.054193 |  | 0.92 | 1.05 | 0.034504 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | JAY 4 | 0.96349 | 0.91152 | -0.051972 |  | 0.92 | 1.05 | 0.035932 | P23:345:GRDA:TONNECE CB9580:::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | JAY 4 | 0.96349 | 0.91152 | -0.051972 |  | 0.92 | 1.05 | 0.057432 | P23:345:GRDA:TONNECE CB9580:::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | JAY 4 | 0.96349 | 0.91152 | -0.051972 |  | 0.92 | 1.05 | 0.068475 | P23:345:GRDA:TONNECE CB9580:::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | JAY 4 | 0.96349 | 0.91152 | -0.051972 |  | 0.92 | 1.05 | 0.035744 | P23:345:GRDA:TONNECE CB9580:::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | JAY 4 | 0.96349 | 0.91152 | -0.051972 |  | 0.92 | 1.05 | 0.1501 | P23:345:GRDA:TONNECE CB9580:::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | JAY 4 | 0.96349 | 0.91152 | -0.051972 |  | 0.92 | 1.05 | 0.058419 | P23:345:GRDA:TONNECE CB9580:::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | JAY 4 | 0.96425 | 0.91378 | -0.050474 |  | 0.92 | 1.05 | 0.035932 | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: | Add 0.02 MVAR switched shunt at JAY 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | JAY 4 | 0.96425 | 0.91378 | -0.050474 |  | 0.92 | 1.05 | 0.054461 | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: | Add 0.02 MVAR switched shunt at JAY 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | JAY 4 | 0.96425 | 0.91378 | -0.050474 |  | 0.92 | 1.05 | 0.068475 | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: | Add 0.02 MVAR switched shunt at JAY 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | JAY 4 | 0.96425 | 0.91378 | -0.050474 |  | 0.92 | 1.05 | 0.034821 | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: | Add 0.02 MVAR switched shunt at JAY 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | JAY 4 | 0.96425 | 0.91378 | -0.050474 |  | 0.92 | 1.05 | 0.1501 | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: | Add 0.02 MVAR switched shunt at JAY 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | JAY 4 | 0.96425 | 0.91378 | -0.050474 |  | 0.92 | 1.05 | 0.057116 | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: | Add 0.02 MVAR switched shunt at JAY 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | JOP391 5 | 0.97586 | 0.92395 | -0.051914 |  | 0.925 | 1.05 | 0.033596 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | JOP391 5 | 0.97586 | 0.92395 | -0.051914 |  | 0.925 | 1.05 | 0.040193 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | JOP391 5 | 0.97586 | 0.92395 | -0.051914 |  | 0.925 | 1.05 | 0.088122 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | JOP391 5 | 0.97586 | 0.92395 | -0.051914 |  | 0.925 | 1.05 | 0.074664 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | JOP391 5 | 0.97586 | 0.92395 | -0.051914 |  | 0.925 | 1.05 | 0.068051 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | JOP391 5 | 0.97586 | 0.92395 | -0.051914 |  | 0.925 | 1.05 | 0.035565 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | JOP391 5 | 0.97586 | 0.92395 | -0.051914 |  | 0.925 | 1.05 | 0.033904 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | JOP391 5 | 0.97586 | 0.92395 | -0.051914 |  | 0.925 | 1.05 | 0.16366 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | JOP391 5 | 0.97586 | 0.92395 | -0.051914 |  | 0.925 | 1.05 | 0.045569 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | JOP391 5 | 0.97586 | 0.92395 | -0.051914 |  | 0.925 | 1.05 | 0.13458 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | JOP391 5 | 0.97586 | 0.92395 | -0.051914 |  | 0.925 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | JOP391 5 | 0.97586 | 0.92395 | -0.051914 |  | 0.925 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | JOP391 5 | 0.97586 | 0.92395 | -0.051914 |  | 0.925 | 1.05 | 0.068426 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | JOP391 5 | 0.97586 | 0.92395 | -0.051914 |  | 0.925 | 1.05 | 0.035223 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | JOP391 5 | 0.97586 | 0.92395 | -0.051914 |  | 0.925 | 1.05 | 0.034504 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | KNLWRTH5 | 0.97884 | 0.91368 | -0.065153 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | KNLWRTH5 | 0.97884 | 0.91368 | -0.065153 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | KNLWRTH5 | 0.97884 | 0.91368 | -0.065153 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | KNLWRTH5 | 0.97884 | 0.91368 | -0.065153 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | KNLWRTH5 | 0.97884 | 0.91368 | -0.065153 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | KNLWRTH5 | 0.97884 | 0.91368 | -0.065153 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | KNLWRTH5 | 0.97884 | 0.91368 | -0.065153 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | KNLWRTH5 | 0.97884 | 0.91368 | -0.065153 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | KNLWRTH5 | 0.97884 | 0.91368 | -0.065153 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | KNLWRTH5 | 0.97884 | 0.91368 | -0.065153 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | KNLWRTH5 | 0.97884 | 0.91368 | -0.065153 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | KNLWRTH5 | 0.97884 | 0.91368 | -0.065153 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | KNLWRTH5 | 0.97884 | 0.91368 | -0.065153 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | KNLWRTH5 | 0.97884 | 0.91368 | -0.065153 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | KNLWRTH5 | 0.97884 | 0.91368 | -0.065153 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | KNLWRTH5 | 0.97884 | 0.91368 | -0.065153 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | KNLWRTH5 | 0.97884 | 0.91368 | -0.065153 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | KNLWRTH5 | 0.97884 | 0.91368 | -0.065153 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | KNLWRTH5 | 0.97884 | 0.91368 | -0.065153 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | KNLWRTH5 | 0.97884 | 0.91368 | -0.065153 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | KNLWRTH5 | 0.97884 | 0.91368 | -0.065153 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | KNLWRTH5 | 0.97884 | 0.91368 | -0.065153 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | KNLWRTH5 | 0.97884 | 0.91368 | -0.065153 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | KNLWRTH5 | 0.97884 | 0.91368 | -0.065153 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | KNLWRTH5 | 0.97884 | 0.91368 | -0.065153 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | ASGI-2024-023 | LABETTE2 | 0.95774 | 0.9085 | -0.049234 |  | 0.93 | 1.05 | 0.079962 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | LABETTE2 | 0.95774 | 0.9085 | -0.049234 |  | 0.93 | 1.05 | 0.065323 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-068 | LABETTE2 | 0.95774 | 0.9085 | -0.049234 |  | 0.93 | 1.05 | 0.067422 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-071 | LABETTE2 | 0.95774 | 0.9085 | -0.049234 |  | 0.93 | 1.05 | 0.074668 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | LABETTE2 | 0.95774 | 0.9085 | -0.049234 |  | 0.93 | 1.05 | 0.053027 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-122 | LABETTE2 | 0.95774 | 0.9085 | -0.049234 |  | 0.93 | 1.05 | 0.082926 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-177 | LABETTE2 | 0.95774 | 0.9085 | -0.049234 |  | 0.93 | 1.05 | 0.084694 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-178 | LABETTE2 | 0.95774 | 0.9085 | -0.049234 |  | 0.93 | 1.05 | 0.078867 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | LABETTE2 | 0.95774 | 0.9085 | -0.049234 |  | 0.93 | 1.05 | 0.031571 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-220 | LABETTE2 | 0.95774 | 0.9085 | -0.049234 |  | 0.93 | 1.05 | 0.075331 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-232 | LABETTE2 | 0.95774 | 0.9085 | -0.049234 |  | 0.93 | 1.05 | 0.078906 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | LABETTE2 | 0.95774 | 0.9085 | -0.049234 |  | 0.93 | 1.05 | 0.065323 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | LABETTE2 | 0.95774 | 0.9085 | -0.049234 |  | 0.93 | 1.05 | 0.03431 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | LABETTE2 | 0.95774 | 0.9085 | -0.049234 |  | 0.93 | 1.05 | 0.031504 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | LABETTE2 | 0.95774 | 0.9085 | -0.049234 |  | 0.93 | 1.05 | 0.031504 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | LABETTE2 | 0.95774 | 0.9085 | -0.049234 |  | 0.93 | 1.05 | 0.030663 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | LABETTE2 | 0.95774 | 0.9085 | -0.049234 |  | 0.93 | 1.05 | 0.04269 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-376 | LABETTE2 | 0.95774 | 0.9085 | -0.049234 |  | 0.93 | 1.05 | 0.082476 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | ASGI-2024-023 | LABETTE2 | 0.95856 | 0.91174 | -0.046819 |  | 0.93 | 1.05 | 0.10682 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | LABETTE2 | 0.95856 | 0.91174 | -0.046819 |  | 0.93 | 1.05 | 0.084049 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-068 | LABETTE2 | 0.95856 | 0.91174 | -0.046819 |  | 0.93 | 1.05 | 0.087538 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-071 | LABETTE2 | 0.95856 | 0.91174 | -0.046819 |  | 0.93 | 1.05 | 0.099263 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | LABETTE2 | 0.95856 | 0.91174 | -0.046819 |  | 0.93 | 1.05 | 0.088785 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-122 | LABETTE2 | 0.95856 | 0.91174 | -0.046819 |  | 0.93 | 1.05 | 0.11321 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-177 | LABETTE2 | 0.95856 | 0.91174 | -0.046819 |  | 0.93 | 1.05 | 0.11622 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-178 | LABETTE2 | 0.95856 | 0.91174 | -0.046819 |  | 0.93 | 1.05 | 0.10702 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | LABETTE2 | 0.95856 | 0.91174 | -0.046819 |  | 0.93 | 1.05 | 0.031044 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-220 | LABETTE2 | 0.95856 | 0.91174 | -0.046819 |  | 0.93 | 1.05 | 0.10032 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-232 | LABETTE2 | 0.95856 | 0.91174 | -0.046819 |  | 0.93 | 1.05 | 0.10939 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | LABETTE2 | 0.95856 | 0.91174 | -0.046819 |  | 0.93 | 1.05 | 0.036829 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | LABETTE2 | 0.95856 | 0.91174 | -0.046819 |  | 0.93 | 1.05 | 0.084049 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | LABETTE2 | 0.95856 | 0.91174 | -0.046819 |  | 0.93 | 1.05 | 0.053387 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | LABETTE2 | 0.95856 | 0.91174 | -0.046819 |  | 0.93 | 1.05 | 0.042012 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | LABETTE2 | 0.95856 | 0.91174 | -0.046819 |  | 0.93 | 1.05 | 0.042012 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | LABETTE2 | 0.95856 | 0.91174 | -0.046819 |  | 0.93 | 1.05 | 0.031418 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | LABETTE2 | 0.95856 | 0.91174 | -0.046819 |  | 0.93 | 1.05 | 0.030073 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | LABETTE2 | 0.95856 | 0.91174 | -0.046819 |  | 0.93 | 1.05 | 0.047594 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-376 | LABETTE2 | 0.95856 | 0.91174 | -0.046819 |  | 0.93 | 1.05 | 0.11583 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | LABETTE2 | 0.95915 | 0.91083 | -0.048321 |  | 0.93 | 1.05 | 0.035768 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | LABETTE2 | 0.95915 | 0.91083 | -0.048321 |  | 0.93 | 1.05 | 0.088718 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | LABETTE2 | 0.95915 | 0.91083 | -0.048321 |  | 0.93 | 1.05 | 0.031473 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | LABETTE2 | 0.95915 | 0.91083 | -0.048321 |  | 0.93 | 1.05 | 0.034941 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | LABETTE2 | 0.95915 | 0.91083 | -0.048321 |  | 0.93 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | LABETTE2 | 0.95915 | 0.91083 | -0.048321 |  | 0.93 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | LABETTE2 | 0.95915 | 0.91083 | -0.048321 |  | 0.93 | 1.05 | 0.049224 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | LABETTE2 | 0.95915 | 0.91083 | -0.048321 |  | 0.93 | 1.05 | 0.038981 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | LABETTE2 | 0.95915 | 0.91083 | -0.048321 |  | 0.93 | 1.05 | 0.040399 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | LABETTE2 | 0.95915 | 0.91083 | -0.048321 |  | 0.93 | 1.05 | 0.031912 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | LABETTE2 | 0.95915 | 0.91083 | -0.048321 |  | 0.93 | 1.05 | 0.034127 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | LABETTE2 | 0.95915 | 0.91083 | -0.048321 |  | 0.93 | 1.05 | 0.047318 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | LABETTE2 | 0.95614 | 0.90462 | -0.051522 |  | 0.93 | 1.05 | 0.040439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | LABETTE2 | 0.95614 | 0.90462 | -0.051522 |  | 0.93 | 1.05 | 0.034853 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | LABETTE2 | 0.95614 | 0.90462 | -0.051522 |  | 0.93 | 1.05 | 0.046783 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | LABETTE2 | 0.95614 | 0.90462 | -0.051522 |  | 0.93 | 1.05 | 0.047615 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | LABETTE2 | 0.95614 | 0.90462 | -0.051522 |  | 0.93 | 1.05 | 0.034938 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | LABETTE2 | 0.95614 | 0.90462 | -0.051522 |  | 0.93 | 1.05 | 0.037875 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | LABETTE2 | 0.95614 | 0.90462 | -0.051522 |  | 0.93 | 1.05 | 0.044022 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | LABETTE2 | 0.95614 | 0.90462 | -0.051522 |  | 0.93 | 1.05 | 0.030552 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | LABETTE2 | 0.95614 | 0.90462 | -0.051522 |  | 0.93 | 1.05 | 0.038531 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | LABETTE2 | 0.95614 | 0.90462 | -0.051522 |  | 0.93 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | LABETTE2 | 0.95614 | 0.90462 | -0.051522 |  | 0.93 | 1.05 | 0.062491 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | LABETTE2 | 0.95614 | 0.90462 | -0.051522 |  | 0.93 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | LABETTE2 | 0.95614 | 0.90462 | -0.051522 |  | 0.93 | 1.05 | 0.038129 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | LABETTE2 | 0.95614 | 0.90462 | -0.051522 |  | 0.93 | 1.05 | 0.038066 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | LABETTE2 | 0.95614 | 0.90462 | -0.051522 |  | 0.93 | 1.05 | 0.034955 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | LABETTE2 | 0.95614 | 0.90462 | -0.051522 |  | 0.93 | 1.05 | 0.06281 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | LABETTE2 | 0.95614 | 0.90462 | -0.051522 |  | 0.93 | 1.05 | 0.045309 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | LABETTE2 | 0.95614 | 0.90462 | -0.051522 |  | 0.93 | 1.05 | 0.035805 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | LABETTE2 | 0.95614 | 0.90462 | -0.051522 |  | 0.93 | 1.05 | 0.032364 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | LABETTE2 | 0.95614 | 0.90462 | -0.051522 |  | 0.93 | 1.05 | 0.031815 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | LABETTE2 | 0.95614 | 0.90462 | -0.051522 |  | 0.93 | 1.05 | 0.033886 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | LABETTE2 | 0.95614 | 0.90462 | -0.051522 |  | 0.93 | 1.05 | 0.035554 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | LABETTE2 | 0.95753 | 0.891 | -0.066526 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | LABETTE2 | 0.95753 | 0.891 | -0.066526 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | LABETTE2 | 0.95753 | 0.891 | -0.066526 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | LABETTE2 | 0.95753 | 0.891 | -0.066526 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | LABETTE2 | 0.95753 | 0.891 | -0.066526 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | LABETTE2 | 0.95753 | 0.891 | -0.066526 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | LABETTE2 | 0.95753 | 0.891 | -0.066526 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | LABETTE2 | 0.95753 | 0.891 | -0.066526 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | LABETTE2 | 0.95753 | 0.891 | -0.066526 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | LABETTE2 | 0.95753 | 0.891 | -0.066526 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | LABETTE2 | 0.95753 | 0.891 | -0.066526 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | LABETTE2 | 0.95753 | 0.891 | -0.066526 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | LABETTE2 | 0.95753 | 0.891 | -0.066526 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | LABETTE2 | 0.95753 | 0.891 | -0.066526 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | LABETTE2 | 0.95753 | 0.891 | -0.066526 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | LABETTE2 | 0.95753 | 0.891 | -0.066526 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | LABETTE2 | 0.95753 | 0.891 | -0.066526 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | LABETTE2 | 0.95753 | 0.891 | -0.066526 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | LABETTE2 | 0.95753 | 0.891 | -0.066526 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | LABETTE2 | 0.95753 | 0.891 | -0.066526 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | LABETTE2 | 0.95753 | 0.891 | -0.066526 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | LABETTE2 | 0.95753 | 0.891 | -0.066526 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | LABETTE2 | 0.95753 | 0.891 | -0.066526 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | LABETTE2 | 0.95753 | 0.891 | -0.066526 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | LABETTE2 | 0.95753 | 0.891 | -0.066526 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | ASGI-2024-023 | LABETTS2 | 0.95966 | 0.91053 | -0.049125 |  | 0.93 | 1.05 | 0.079962 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | LABETTS2 | 0.95966 | 0.91053 | -0.049125 |  | 0.93 | 1.05 | 0.065323 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-068 | LABETTS2 | 0.95966 | 0.91053 | -0.049125 |  | 0.93 | 1.05 | 0.067422 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-071 | LABETTS2 | 0.95966 | 0.91053 | -0.049125 |  | 0.93 | 1.05 | 0.074668 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | LABETTS2 | 0.95966 | 0.91053 | -0.049125 |  | 0.93 | 1.05 | 0.053027 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-122 | LABETTS2 | 0.95966 | 0.91053 | -0.049125 |  | 0.93 | 1.05 | 0.082926 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-177 | LABETTS2 | 0.95966 | 0.91053 | -0.049125 |  | 0.93 | 1.05 | 0.084694 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-178 | LABETTS2 | 0.95966 | 0.91053 | -0.049125 |  | 0.93 | 1.05 | 0.078867 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | LABETTS2 | 0.95966 | 0.91053 | -0.049125 |  | 0.93 | 1.05 | 0.031571 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-220 | LABETTS2 | 0.95966 | 0.91053 | -0.049125 |  | 0.93 | 1.05 | 0.075331 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-232 | LABETTS2 | 0.95966 | 0.91053 | -0.049125 |  | 0.93 | 1.05 | 0.078906 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | LABETTS2 | 0.95966 | 0.91053 | -0.049125 |  | 0.93 | 1.05 | 0.065323 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | LABETTS2 | 0.95966 | 0.91053 | -0.049125 |  | 0.93 | 1.05 | 0.03431 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | LABETTS2 | 0.95966 | 0.91053 | -0.049125 |  | 0.93 | 1.05 | 0.031504 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | LABETTS2 | 0.95966 | 0.91053 | -0.049125 |  | 0.93 | 1.05 | 0.031504 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | LABETTS2 | 0.95966 | 0.91053 | -0.049125 |  | 0.93 | 1.05 | 0.030663 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | LABETTS2 | 0.95966 | 0.91053 | -0.049125 |  | 0.93 | 1.05 | 0.04269 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-376 | LABETTS2 | 0.95966 | 0.91053 | -0.049125 |  | 0.93 | 1.05 | 0.082476 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | ASGI-2024-023 | LABETTS2 | 0.96048 | 0.91377 | -0.046716 |  | 0.93 | 1.05 | 0.10682 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | LABETTS2 | 0.96048 | 0.91377 | -0.046716 |  | 0.93 | 1.05 | 0.084049 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-068 | LABETTS2 | 0.96048 | 0.91377 | -0.046716 |  | 0.93 | 1.05 | 0.087538 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-071 | LABETTS2 | 0.96048 | 0.91377 | -0.046716 |  | 0.93 | 1.05 | 0.099263 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | LABETTS2 | 0.96048 | 0.91377 | -0.046716 |  | 0.93 | 1.05 | 0.088785 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-122 | LABETTS2 | 0.96048 | 0.91377 | -0.046716 |  | 0.93 | 1.05 | 0.11321 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-177 | LABETTS2 | 0.96048 | 0.91377 | -0.046716 |  | 0.93 | 1.05 | 0.11622 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-178 | LABETTS2 | 0.96048 | 0.91377 | -0.046716 |  | 0.93 | 1.05 | 0.10702 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | LABETTS2 | 0.96048 | 0.91377 | -0.046716 |  | 0.93 | 1.05 | 0.031044 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-220 | LABETTS2 | 0.96048 | 0.91377 | -0.046716 |  | 0.93 | 1.05 | 0.10032 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-232 | LABETTS2 | 0.96048 | 0.91377 | -0.046716 |  | 0.93 | 1.05 | 0.10939 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | LABETTS2 | 0.96048 | 0.91377 | -0.046716 |  | 0.93 | 1.05 | 0.036829 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | LABETTS2 | 0.96048 | 0.91377 | -0.046716 |  | 0.93 | 1.05 | 0.084049 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | LABETTS2 | 0.96048 | 0.91377 | -0.046716 |  | 0.93 | 1.05 | 0.053387 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | LABETTS2 | 0.96048 | 0.91377 | -0.046716 |  | 0.93 | 1.05 | 0.042012 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | LABETTS2 | 0.96048 | 0.91377 | -0.046716 |  | 0.93 | 1.05 | 0.042012 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | LABETTS2 | 0.96048 | 0.91377 | -0.046716 |  | 0.93 | 1.05 | 0.031418 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | LABETTS2 | 0.96048 | 0.91377 | -0.046716 |  | 0.93 | 1.05 | 0.030073 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | LABETTS2 | 0.96048 | 0.91377 | -0.046716 |  | 0.93 | 1.05 | 0.047594 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-376 | LABETTS2 | 0.96048 | 0.91377 | -0.046716 |  | 0.93 | 1.05 | 0.11583 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | LABETTS2 | 0.96107 | 0.91286 | -0.048215 |  | 0.93 | 1.05 | 0.035768 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | LABETTS2 | 0.96107 | 0.91286 | -0.048215 |  | 0.93 | 1.05 | 0.088718 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | LABETTS2 | 0.96107 | 0.91286 | -0.048215 |  | 0.93 | 1.05 | 0.031473 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | LABETTS2 | 0.96107 | 0.91286 | -0.048215 |  | 0.93 | 1.05 | 0.034941 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | LABETTS2 | 0.96107 | 0.91286 | -0.048215 |  | 0.93 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | LABETTS2 | 0.96107 | 0.91286 | -0.048215 |  | 0.93 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | LABETTS2 | 0.96107 | 0.91286 | -0.048215 |  | 0.93 | 1.05 | 0.049224 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | LABETTS2 | 0.96107 | 0.91286 | -0.048215 |  | 0.93 | 1.05 | 0.038981 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | LABETTS2 | 0.96107 | 0.91286 | -0.048215 |  | 0.93 | 1.05 | 0.040399 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | LABETTS2 | 0.96107 | 0.91286 | -0.048215 |  | 0.93 | 1.05 | 0.031912 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | LABETTS2 | 0.96107 | 0.91286 | -0.048215 |  | 0.93 | 1.05 | 0.034127 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | LABETTS2 | 0.96107 | 0.91286 | -0.048215 |  | 0.93 | 1.05 | 0.047318 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | LABETTS2 | 0.95807 | 0.90666 | -0.051407 |  | 0.93 | 1.05 | 0.040439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | LABETTS2 | 0.95807 | 0.90666 | -0.051407 |  | 0.93 | 1.05 | 0.034853 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | LABETTS2 | 0.95807 | 0.90666 | -0.051407 |  | 0.93 | 1.05 | 0.046783 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | LABETTS2 | 0.95807 | 0.90666 | -0.051407 |  | 0.93 | 1.05 | 0.047615 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | LABETTS2 | 0.95807 | 0.90666 | -0.051407 |  | 0.93 | 1.05 | 0.034938 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | LABETTS2 | 0.95807 | 0.90666 | -0.051407 |  | 0.93 | 1.05 | 0.037875 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | LABETTS2 | 0.95807 | 0.90666 | -0.051407 |  | 0.93 | 1.05 | 0.044022 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | LABETTS2 | 0.95807 | 0.90666 | -0.051407 |  | 0.93 | 1.05 | 0.030552 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | LABETTS2 | 0.95807 | 0.90666 | -0.051407 |  | 0.93 | 1.05 | 0.038531 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | LABETTS2 | 0.95807 | 0.90666 | -0.051407 |  | 0.93 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | LABETTS2 | 0.95807 | 0.90666 | -0.051407 |  | 0.93 | 1.05 | 0.062491 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | LABETTS2 | 0.95807 | 0.90666 | -0.051407 |  | 0.93 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | LABETTS2 | 0.95807 | 0.90666 | -0.051407 |  | 0.93 | 1.05 | 0.038129 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | LABETTS2 | 0.95807 | 0.90666 | -0.051407 |  | 0.93 | 1.05 | 0.038066 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | LABETTS2 | 0.95807 | 0.90666 | -0.051407 |  | 0.93 | 1.05 | 0.034955 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | LABETTS2 | 0.95807 | 0.90666 | -0.051407 |  | 0.93 | 1.05 | 0.06281 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | LABETTS2 | 0.95807 | 0.90666 | -0.051407 |  | 0.93 | 1.05 | 0.045309 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | LABETTS2 | 0.95807 | 0.90666 | -0.051407 |  | 0.93 | 1.05 | 0.035805 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | LABETTS2 | 0.95807 | 0.90666 | -0.051407 |  | 0.93 | 1.05 | 0.032364 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | LABETTS2 | 0.95807 | 0.90666 | -0.051407 |  | 0.93 | 1.05 | 0.031815 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | LABETTS2 | 0.95807 | 0.90666 | -0.051407 |  | 0.93 | 1.05 | 0.033886 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | LABETTS2 | 0.95807 | 0.90666 | -0.051407 |  | 0.93 | 1.05 | 0.035554 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | LABETTS2 | 0.95945 | 0.89308 | -0.066376 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | LABETTS2 | 0.95945 | 0.89308 | -0.066376 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | LABETTS2 | 0.95945 | 0.89308 | -0.066376 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | LABETTS2 | 0.95945 | 0.89308 | -0.066376 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | LABETTS2 | 0.95945 | 0.89308 | -0.066376 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | LABETTS2 | 0.95945 | 0.89308 | -0.066376 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | LABETTS2 | 0.95945 | 0.89308 | -0.066376 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | LABETTS2 | 0.95945 | 0.89308 | -0.066376 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | LABETTS2 | 0.95945 | 0.89308 | -0.066376 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | LABETTS2 | 0.95945 | 0.89308 | -0.066376 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | LABETTS2 | 0.95945 | 0.89308 | -0.066376 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | LABETTS2 | 0.95945 | 0.89308 | -0.066376 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | LABETTS2 | 0.95945 | 0.89308 | -0.066376 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | LABETTS2 | 0.95945 | 0.89308 | -0.066376 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | LABETTS2 | 0.95945 | 0.89308 | -0.066376 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | LABETTS2 | 0.95945 | 0.89308 | -0.066376 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | LABETTS2 | 0.95945 | 0.89308 | -0.066376 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | LABETTS2 | 0.95945 | 0.89308 | -0.066376 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | LABETTS2 | 0.95945 | 0.89308 | -0.066376 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | LABETTS2 | 0.95945 | 0.89308 | -0.066376 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | LABETTS2 | 0.95945 | 0.89308 | -0.066376 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | LABETTS2 | 0.95945 | 0.89308 | -0.066376 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | LABETTS2 | 0.95945 | 0.89308 | -0.066376 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | LABETTS2 | 0.95945 | 0.89308 | -0.066376 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | LABETTS2 | 0.95945 | 0.89308 | -0.066376 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | LACKMAN5 | 0.99071 | 0.90938 | -0.08133 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | LACKMAN5 | 0.99071 | 0.90938 | -0.08133 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | LACKMAN5 | 0.99071 | 0.90938 | -0.08133 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | LACKMAN5 | 0.99071 | 0.90938 | -0.08133 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | LACKMAN5 | 0.99071 | 0.90938 | -0.08133 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | LACKMAN5 | 0.99071 | 0.90938 | -0.08133 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | LACKMAN5 | 0.99071 | 0.90938 | -0.08133 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | LACKMAN5 | 0.99071 | 0.90938 | -0.08133 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | LACKMAN5 | 0.99071 | 0.90938 | -0.08133 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | LACKMAN5 | 0.99071 | 0.90938 | -0.08133 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | LACKMAN5 | 0.99071 | 0.90938 | -0.08133 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | LACKMAN5 | 0.99071 | 0.90938 | -0.08133 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | LACKMAN5 | 0.99071 | 0.90938 | -0.08133 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | LACKMAN5 | 0.99071 | 0.90938 | -0.08133 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | LACKMAN5 | 0.99071 | 0.90938 | -0.08133 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | LACKMAN5 | 0.99071 | 0.90938 | -0.08133 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | LACKMAN5 | 0.99071 | 0.90938 | -0.08133 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | LACKMAN5 | 0.99071 | 0.90938 | -0.08133 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | LACKMAN5 | 0.99071 | 0.90938 | -0.08133 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | LACKMAN5 | 0.99071 | 0.90938 | -0.08133 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | LACKMAN5 | 0.99071 | 0.90938 | -0.08133 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | LACKMAN5 | 0.99071 | 0.90938 | -0.08133 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | LACKMAN5 | 0.99071 | 0.90938 | -0.08133 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | LACKMAN5 | 0.99071 | 0.90938 | -0.08133 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | LACKMAN5 | 0.99071 | 0.90938 | -0.08133 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | LACYGNE11_7 | 0.99489 | 0.93087 | -0.064024 |  | 0.95 | 1.05 | 0.03053 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | LACYGNE11_7 | 0.99489 | 0.93087 | -0.064024 |  | 0.95 | 1.05 | 0.044933 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | LACYGNE11_7 | 0.99489 | 0.93087 | -0.064024 |  | 0.95 | 1.05 | 0.047811 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | LACYGNE11_7 | 0.99489 | 0.93087 | -0.064024 |  | 0.95 | 1.05 | 0.09719 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | LACYGNE11_7 | 0.99489 | 0.93087 | -0.064024 |  | 0.95 | 1.05 | 0.069376 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | LACYGNE11_7 | 0.99489 | 0.93087 | -0.064024 |  | 0.95 | 1.05 | 0.04277 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | LACYGNE11_7 | 0.99489 | 0.93087 | -0.064024 |  | 0.95 | 1.05 | 0.071112 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | LACYGNE11_7 | 0.99489 | 0.93087 | -0.064024 |  | 0.95 | 1.05 | 0.039357 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | LACYGNE11_7 | 0.99489 | 0.93087 | -0.064024 |  | 0.95 | 1.05 | 0.04035 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | LACYGNE11_7 | 0.99489 | 0.93087 | -0.064024 |  | 0.95 | 1.05 | 0.052332 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | LACYGNE11_7 | 0.99489 | 0.93087 | -0.064024 |  | 0.95 | 1.05 | 0.045944 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | LACYGNE11_7 | 0.99489 | 0.93087 | -0.064024 |  | 0.95 | 1.05 | 0.038178 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | LACYGNE11_7 | 0.99489 | 0.93087 | -0.064024 |  | 0.95 | 1.05 | 0.13469 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | LACYGNE11_7 | 0.99489 | 0.93087 | -0.064024 |  | 0.95 | 1.05 | 0.03053 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | LACYGNE11_7 | 0.99489 | 0.93087 | -0.064024 |  | 0.95 | 1.05 | 0.038178 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | LACYGNE11_7 | 0.99489 | 0.93087 | -0.064024 |  | 0.95 | 1.05 | 0.037309 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | LACYGNE11_7 | 0.99489 | 0.93087 | -0.064024 |  | 0.95 | 1.05 | 0.040075 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | LACYGNE11_7 | 0.99489 | 0.93087 | -0.064024 |  | 0.95 | 1.05 | 0.053764 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | LACYGNE11_7 | 0.99489 | 0.93087 | -0.064024 |  | 0.95 | 1.05 | 0.071762 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | LACYGNE11_7 | 0.99489 | 0.93087 | -0.064024 |  | 0.95 | 1.05 | 0.047827 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | LACYGNE11_7 | 0.99489 | 0.93087 | -0.064024 |  | 0.95 | 1.05 | 0.047827 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | LACYGNE11_7 | 0.99489 | 0.93087 | -0.064024 |  | 0.95 | 1.05 | 0.070303 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | LACYGNE11_7 | 0.99489 | 0.93087 | -0.064024 |  | 0.95 | 1.05 | 0.040614 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | LACYGNE11_7 | 0.99489 | 0.93087 | -0.064024 |  | 0.95 | 1.05 | 0.039729 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | LACYGNE11_7 | 0.99489 | 0.93087 | -0.064024 |  | 0.95 | 1.05 | 0.049662 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | LACYGNE11_7 | 0.99489 | 0.93087 | -0.064024 |  | 0.95 | 1.05 | 0.042332 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | LACYGNE11_7 | 0.99489 | 0.93087 | -0.064024 |  | 0.95 | 1.05 | 0.048722 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | LACYGNE11_7 | 0.99489 | 0.93087 | -0.064024 |  | 0.95 | 1.05 | 0.038156 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | LACYGNE11_7 | 0.99489 | 0.93087 | -0.064024 |  | 0.95 | 1.05 | 0.036794 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | LACYGNE11_7 | 1.005 | 0.93449 | -0.070471 |  | 0.95 | 1.05 | 0.036307 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | LACYGNE11_7 | 1.005 | 0.93449 | -0.070471 |  | 0.95 | 1.05 | 0.052743 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | LACYGNE11_7 | 1.005 | 0.93449 | -0.070471 |  | 0.95 | 1.05 | 0.039345 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | LACYGNE11_7 | 1.005 | 0.93449 | -0.070471 |  | 0.95 | 1.05 | 0.031366 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | LACYGNE11_7 | 1.005 | 0.93449 | -0.070471 |  | 0.95 | 1.05 | 0.041888 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | LACYGNE11_7 | 1.005 | 0.93449 | -0.070471 |  | 0.95 | 1.05 | 0.038797 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | LACYGNE11_7 | 1.005 | 0.93449 | -0.070471 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | LACYGNE11_7 | 1.005 | 0.93449 | -0.070471 |  | 0.95 | 1.05 | 0.067346 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | LACYGNE11_7 | 1.005 | 0.93449 | -0.070471 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | LACYGNE11_7 | 1.005 | 0.93449 | -0.070471 |  | 0.95 | 1.05 | 0.030851 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | LACYGNE11_7 | 1.005 | 0.93449 | -0.070471 |  | 0.95 | 1.05 | 0.032161 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | LACYGNE11_7 | 1.005 | 0.93449 | -0.070471 |  | 0.95 | 1.05 | 0.04067 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | LACYGNE11_7 | 1.005 | 0.93449 | -0.070471 |  | 0.95 | 1.05 | 0.040569 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | LACYGNE11_7 | 1.005 | 0.93449 | -0.070471 |  | 0.95 | 1.05 | 0.03086 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | LACYGNE11_7 | 1.005 | 0.93449 | -0.070471 |  | 0.95 | 1.05 | 0.033223 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | LACYGNE11_7 | 1.005 | 0.93449 | -0.070471 |  | 0.95 | 1.05 | 0.033733 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | LACYGNE11_7 | 1.0028 | 0.88286 | -0.11992 |  | 0.95 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | LACYGNE11_7 | 1.0028 | 0.88286 | -0.11992 |  | 0.95 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | LACYGNE11_7 | 1.0028 | 0.88286 | -0.11992 |  | 0.95 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | LACYGNE11_7 | 1.0028 | 0.88286 | -0.11992 |  | 0.95 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | LACYGNE11_7 | 1.0028 | 0.88286 | -0.11992 |  | 0.95 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | LACYGNE11_7 | 1.0028 | 0.88286 | -0.11992 |  | 0.95 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | LACYGNE11_7 | 1.0028 | 0.88286 | -0.11992 |  | 0.95 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | LACYGNE11_7 | 1.0028 | 0.88286 | -0.11992 |  | 0.95 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | LACYGNE11_7 | 1.0028 | 0.88286 | -0.11992 |  | 0.95 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | LACYGNE11_7 | 1.0028 | 0.88286 | -0.11992 |  | 0.95 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | LACYGNE11_7 | 1.0028 | 0.88286 | -0.11992 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | LACYGNE11_7 | 1.0028 | 0.88286 | -0.11992 |  | 0.95 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | LACYGNE11_7 | 1.0028 | 0.88286 | -0.11992 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | LACYGNE11_7 | 1.0028 | 0.88286 | -0.11992 |  | 0.95 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | LACYGNE11_7 | 1.0028 | 0.88286 | -0.11992 |  | 0.95 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | LACYGNE11_7 | 1.0028 | 0.88286 | -0.11992 |  | 0.95 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | LACYGNE11_7 | 1.0028 | 0.88286 | -0.11992 |  | 0.95 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | LACYGNE11_7 | 1.0028 | 0.88286 | -0.11992 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | LACYGNE11_7 | 1.0028 | 0.88286 | -0.11992 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | LACYGNE11_7 | 1.0028 | 0.88286 | -0.11992 |  | 0.95 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | LACYGNE11_7 | 1.0028 | 0.88286 | -0.11992 |  | 0.95 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | LACYGNE11_7 | 1.0028 | 0.88286 | -0.11992 |  | 0.95 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | LACYGNE11_7 | 1.0028 | 0.88286 | -0.11992 |  | 0.95 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | LACYGNE11_7 | 1.0028 | 0.88286 | -0.11992 |  | 0.95 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | LACYGNE11_7 | 1.0028 | 0.88286 | -0.11992 |  | 0.95 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | LACYGNE2 | 0.98423 | 0.91931 | -0.064919 |  | 0.93 | 1.05 | 0.03053 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | LACYGNE2 | 0.98423 | 0.91931 | -0.064919 |  | 0.93 | 1.05 | 0.044933 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | LACYGNE2 | 0.98423 | 0.91931 | -0.064919 |  | 0.93 | 1.05 | 0.047811 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | LACYGNE2 | 0.98423 | 0.91931 | -0.064919 |  | 0.93 | 1.05 | 0.09719 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | LACYGNE2 | 0.98423 | 0.91931 | -0.064919 |  | 0.93 | 1.05 | 0.069376 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | LACYGNE2 | 0.98423 | 0.91931 | -0.064919 |  | 0.93 | 1.05 | 0.04277 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | LACYGNE2 | 0.98423 | 0.91931 | -0.064919 |  | 0.93 | 1.05 | 0.071112 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | LACYGNE2 | 0.98423 | 0.91931 | -0.064919 |  | 0.93 | 1.05 | 0.039357 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | LACYGNE2 | 0.98423 | 0.91931 | -0.064919 |  | 0.93 | 1.05 | 0.04035 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | LACYGNE2 | 0.98423 | 0.91931 | -0.064919 |  | 0.93 | 1.05 | 0.052332 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | LACYGNE2 | 0.98423 | 0.91931 | -0.064919 |  | 0.93 | 1.05 | 0.045944 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | LACYGNE2 | 0.98423 | 0.91931 | -0.064919 |  | 0.93 | 1.05 | 0.038178 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | LACYGNE2 | 0.98423 | 0.91931 | -0.064919 |  | 0.93 | 1.05 | 0.13469 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | LACYGNE2 | 0.98423 | 0.91931 | -0.064919 |  | 0.93 | 1.05 | 0.03053 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | LACYGNE2 | 0.98423 | 0.91931 | -0.064919 |  | 0.93 | 1.05 | 0.038178 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | LACYGNE2 | 0.98423 | 0.91931 | -0.064919 |  | 0.93 | 1.05 | 0.037309 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | LACYGNE2 | 0.98423 | 0.91931 | -0.064919 |  | 0.93 | 1.05 | 0.040075 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | LACYGNE2 | 0.98423 | 0.91931 | -0.064919 |  | 0.93 | 1.05 | 0.053764 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | LACYGNE2 | 0.98423 | 0.91931 | -0.064919 |  | 0.93 | 1.05 | 0.071762 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | LACYGNE2 | 0.98423 | 0.91931 | -0.064919 |  | 0.93 | 1.05 | 0.047827 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | LACYGNE2 | 0.98423 | 0.91931 | -0.064919 |  | 0.93 | 1.05 | 0.047827 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | LACYGNE2 | 0.98423 | 0.91931 | -0.064919 |  | 0.93 | 1.05 | 0.070303 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | LACYGNE2 | 0.98423 | 0.91931 | -0.064919 |  | 0.93 | 1.05 | 0.040614 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | LACYGNE2 | 0.98423 | 0.91931 | -0.064919 |  | 0.93 | 1.05 | 0.039729 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | LACYGNE2 | 0.98423 | 0.91931 | -0.064919 |  | 0.93 | 1.05 | 0.049662 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | LACYGNE2 | 0.98423 | 0.91931 | -0.064919 |  | 0.93 | 1.05 | 0.042332 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | LACYGNE2 | 0.98423 | 0.91931 | -0.064919 |  | 0.93 | 1.05 | 0.048722 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | LACYGNE2 | 0.98423 | 0.91931 | -0.064919 |  | 0.93 | 1.05 | 0.038156 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | LACYGNE2 | 0.98423 | 0.91931 | -0.064919 |  | 0.93 | 1.05 | 0.036794 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | LACYGNE2 | 0.99442 | 0.92298 | -0.07144 |  | 0.93 | 1.05 | 0.036307 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | LACYGNE2 | 0.99442 | 0.92298 | -0.07144 |  | 0.93 | 1.05 | 0.052743 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | LACYGNE2 | 0.99442 | 0.92298 | -0.07144 |  | 0.93 | 1.05 | 0.039345 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | LACYGNE2 | 0.99442 | 0.92298 | -0.07144 |  | 0.93 | 1.05 | 0.031366 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | LACYGNE2 | 0.99442 | 0.92298 | -0.07144 |  | 0.93 | 1.05 | 0.041888 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | LACYGNE2 | 0.99442 | 0.92298 | -0.07144 |  | 0.93 | 1.05 | 0.038797 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | LACYGNE2 | 0.99442 | 0.92298 | -0.07144 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | LACYGNE2 | 0.99442 | 0.92298 | -0.07144 |  | 0.93 | 1.05 | 0.067346 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | LACYGNE2 | 0.99442 | 0.92298 | -0.07144 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | LACYGNE2 | 0.99442 | 0.92298 | -0.07144 |  | 0.93 | 1.05 | 0.030851 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | LACYGNE2 | 0.99442 | 0.92298 | -0.07144 |  | 0.93 | 1.05 | 0.032161 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | LACYGNE2 | 0.99442 | 0.92298 | -0.07144 |  | 0.93 | 1.05 | 0.04067 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | LACYGNE2 | 0.99442 | 0.92298 | -0.07144 |  | 0.93 | 1.05 | 0.040569 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | LACYGNE2 | 0.99442 | 0.92298 | -0.07144 |  | 0.93 | 1.05 | 0.03086 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | LACYGNE2 | 0.99442 | 0.92298 | -0.07144 |  | 0.93 | 1.05 | 0.033223 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | LACYGNE2 | 0.99442 | 0.92298 | -0.07144 |  | 0.93 | 1.05 | 0.033733 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | LACYGNE2 | 0.99221 | 0.87052 | -0.12169 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | LACYGNE2 | 0.99221 | 0.87052 | -0.12169 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | LACYGNE2 | 0.99221 | 0.87052 | -0.12169 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | LACYGNE2 | 0.99221 | 0.87052 | -0.12169 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | LACYGNE2 | 0.99221 | 0.87052 | -0.12169 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | LACYGNE2 | 0.99221 | 0.87052 | -0.12169 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | LACYGNE2 | 0.99221 | 0.87052 | -0.12169 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | LACYGNE2 | 0.99221 | 0.87052 | -0.12169 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | LACYGNE2 | 0.99221 | 0.87052 | -0.12169 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | LACYGNE2 | 0.99221 | 0.87052 | -0.12169 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | LACYGNE2 | 0.99221 | 0.87052 | -0.12169 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | LACYGNE2 | 0.99221 | 0.87052 | -0.12169 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | LACYGNE2 | 0.99221 | 0.87052 | -0.12169 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | LACYGNE2 | 0.99221 | 0.87052 | -0.12169 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | LACYGNE2 | 0.99221 | 0.87052 | -0.12169 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | LACYGNE2 | 0.99221 | 0.87052 | -0.12169 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | LACYGNE2 | 0.99221 | 0.87052 | -0.12169 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | LACYGNE2 | 0.99221 | 0.87052 | -0.12169 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | LACYGNE2 | 0.99221 | 0.87052 | -0.12169 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | LACYGNE2 | 0.99221 | 0.87052 | -0.12169 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | LACYGNE2 | 0.99221 | 0.87052 | -0.12169 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | LACYGNE2 | 0.99221 | 0.87052 | -0.12169 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | LACYGNE2 | 0.99221 | 0.87052 | -0.12169 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | LACYGNE2 | 0.99221 | 0.87052 | -0.12169 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | LACYGNE2 | 0.99221 | 0.87052 | -0.12169 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | LACYGNE22_7 | 0.9949 | 0.93088 | -0.064023 |  | 0.95 | 1.05 | 0.03053 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | LACYGNE22_7 | 0.9949 | 0.93088 | -0.064023 |  | 0.95 | 1.05 | 0.044933 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | LACYGNE22_7 | 0.9949 | 0.93088 | -0.064023 |  | 0.95 | 1.05 | 0.047811 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | LACYGNE22_7 | 0.9949 | 0.93088 | -0.064023 |  | 0.95 | 1.05 | 0.09719 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | LACYGNE22_7 | 0.9949 | 0.93088 | -0.064023 |  | 0.95 | 1.05 | 0.069376 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | LACYGNE22_7 | 0.9949 | 0.93088 | -0.064023 |  | 0.95 | 1.05 | 0.04277 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | LACYGNE22_7 | 0.9949 | 0.93088 | -0.064023 |  | 0.95 | 1.05 | 0.071112 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | LACYGNE22_7 | 0.9949 | 0.93088 | -0.064023 |  | 0.95 | 1.05 | 0.039357 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | LACYGNE22_7 | 0.9949 | 0.93088 | -0.064023 |  | 0.95 | 1.05 | 0.04035 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | LACYGNE22_7 | 0.9949 | 0.93088 | -0.064023 |  | 0.95 | 1.05 | 0.052332 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | LACYGNE22_7 | 0.9949 | 0.93088 | -0.064023 |  | 0.95 | 1.05 | 0.045944 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | LACYGNE22_7 | 0.9949 | 0.93088 | -0.064023 |  | 0.95 | 1.05 | 0.038178 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | LACYGNE22_7 | 0.9949 | 0.93088 | -0.064023 |  | 0.95 | 1.05 | 0.13469 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | LACYGNE22_7 | 0.9949 | 0.93088 | -0.064023 |  | 0.95 | 1.05 | 0.03053 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | LACYGNE22_7 | 0.9949 | 0.93088 | -0.064023 |  | 0.95 | 1.05 | 0.038178 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | LACYGNE22_7 | 0.9949 | 0.93088 | -0.064023 |  | 0.95 | 1.05 | 0.037309 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | LACYGNE22_7 | 0.9949 | 0.93088 | -0.064023 |  | 0.95 | 1.05 | 0.040075 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | LACYGNE22_7 | 0.9949 | 0.93088 | -0.064023 |  | 0.95 | 1.05 | 0.053764 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | LACYGNE22_7 | 0.9949 | 0.93088 | -0.064023 |  | 0.95 | 1.05 | 0.071762 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | LACYGNE22_7 | 0.9949 | 0.93088 | -0.064023 |  | 0.95 | 1.05 | 0.047827 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | LACYGNE22_7 | 0.9949 | 0.93088 | -0.064023 |  | 0.95 | 1.05 | 0.047827 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | LACYGNE22_7 | 0.9949 | 0.93088 | -0.064023 |  | 0.95 | 1.05 | 0.070303 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | LACYGNE22_7 | 0.9949 | 0.93088 | -0.064023 |  | 0.95 | 1.05 | 0.040614 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | LACYGNE22_7 | 0.9949 | 0.93088 | -0.064023 |  | 0.95 | 1.05 | 0.039729 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | LACYGNE22_7 | 0.9949 | 0.93088 | -0.064023 |  | 0.95 | 1.05 | 0.049662 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | LACYGNE22_7 | 0.9949 | 0.93088 | -0.064023 |  | 0.95 | 1.05 | 0.042332 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | LACYGNE22_7 | 0.9949 | 0.93088 | -0.064023 |  | 0.95 | 1.05 | 0.048722 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | LACYGNE22_7 | 0.9949 | 0.93088 | -0.064023 |  | 0.95 | 1.05 | 0.038156 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | LACYGNE22_7 | 0.9949 | 0.93088 | -0.064023 |  | 0.95 | 1.05 | 0.036794 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | LACYGNE22_7 | 1.005 | 0.93449 | -0.070471 |  | 0.95 | 1.05 | 0.036307 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | LACYGNE22_7 | 1.005 | 0.93449 | -0.070471 |  | 0.95 | 1.05 | 0.052743 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | LACYGNE22_7 | 1.005 | 0.93449 | -0.070471 |  | 0.95 | 1.05 | 0.039345 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | LACYGNE22_7 | 1.005 | 0.93449 | -0.070471 |  | 0.95 | 1.05 | 0.031366 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | LACYGNE22_7 | 1.005 | 0.93449 | -0.070471 |  | 0.95 | 1.05 | 0.041888 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | LACYGNE22_7 | 1.005 | 0.93449 | -0.070471 |  | 0.95 | 1.05 | 0.038797 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | LACYGNE22_7 | 1.005 | 0.93449 | -0.070471 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | LACYGNE22_7 | 1.005 | 0.93449 | -0.070471 |  | 0.95 | 1.05 | 0.067346 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | LACYGNE22_7 | 1.005 | 0.93449 | -0.070471 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | LACYGNE22_7 | 1.005 | 0.93449 | -0.070471 |  | 0.95 | 1.05 | 0.030851 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | LACYGNE22_7 | 1.005 | 0.93449 | -0.070471 |  | 0.95 | 1.05 | 0.032161 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | LACYGNE22_7 | 1.005 | 0.93449 | -0.070471 |  | 0.95 | 1.05 | 0.04067 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | LACYGNE22_7 | 1.005 | 0.93449 | -0.070471 |  | 0.95 | 1.05 | 0.040569 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | LACYGNE22_7 | 1.005 | 0.93449 | -0.070471 |  | 0.95 | 1.05 | 0.03086 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | LACYGNE22_7 | 1.005 | 0.93449 | -0.070471 |  | 0.95 | 1.05 | 0.033223 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | LACYGNE22_7 | 1.005 | 0.93449 | -0.070471 |  | 0.95 | 1.05 | 0.033733 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | LACYGNE22_7 | 1.0028 | 0.88286 | -0.11992 |  | 0.95 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | LACYGNE22_7 | 1.0028 | 0.88286 | -0.11992 |  | 0.95 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | LACYGNE22_7 | 1.0028 | 0.88286 | -0.11992 |  | 0.95 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | LACYGNE22_7 | 1.0028 | 0.88286 | -0.11992 |  | 0.95 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | LACYGNE22_7 | 1.0028 | 0.88286 | -0.11992 |  | 0.95 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | LACYGNE22_7 | 1.0028 | 0.88286 | -0.11992 |  | 0.95 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | LACYGNE22_7 | 1.0028 | 0.88286 | -0.11992 |  | 0.95 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | LACYGNE22_7 | 1.0028 | 0.88286 | -0.11992 |  | 0.95 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | LACYGNE22_7 | 1.0028 | 0.88286 | -0.11992 |  | 0.95 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | LACYGNE22_7 | 1.0028 | 0.88286 | -0.11992 |  | 0.95 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | LACYGNE22_7 | 1.0028 | 0.88286 | -0.11992 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | LACYGNE22_7 | 1.0028 | 0.88286 | -0.11992 |  | 0.95 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | LACYGNE22_7 | 1.0028 | 0.88286 | -0.11992 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | LACYGNE22_7 | 1.0028 | 0.88286 | -0.11992 |  | 0.95 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | LACYGNE22_7 | 1.0028 | 0.88286 | -0.11992 |  | 0.95 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | LACYGNE22_7 | 1.0028 | 0.88286 | -0.11992 |  | 0.95 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | LACYGNE22_7 | 1.0028 | 0.88286 | -0.11992 |  | 0.95 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | LACYGNE22_7 | 1.0028 | 0.88286 | -0.11992 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | LACYGNE22_7 | 1.0028 | 0.88286 | -0.11992 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | LACYGNE22_7 | 1.0028 | 0.88286 | -0.11992 |  | 0.95 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | LACYGNE22_7 | 1.0028 | 0.88286 | -0.11992 |  | 0.95 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | LACYGNE22_7 | 1.0028 | 0.88286 | -0.11992 |  | 0.95 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | LACYGNE22_7 | 1.0028 | 0.88286 | -0.11992 |  | 0.95 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | LACYGNE22_7 | 1.0028 | 0.88286 | -0.11992 |  | 0.95 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | LACYGNE22_7 | 1.0028 | 0.88286 | -0.11992 |  | 0.95 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | LACYGNE_LK2 | 0.98308 | 0.91807 | -0.065001 |  | 0.93 | 1.05 | 0.03053 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | LACYGNE_LK2 | 0.98308 | 0.91807 | -0.065001 |  | 0.93 | 1.05 | 0.044933 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | LACYGNE_LK2 | 0.98308 | 0.91807 | -0.065001 |  | 0.93 | 1.05 | 0.047811 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | LACYGNE_LK2 | 0.98308 | 0.91807 | -0.065001 |  | 0.93 | 1.05 | 0.09719 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | LACYGNE_LK2 | 0.98308 | 0.91807 | -0.065001 |  | 0.93 | 1.05 | 0.069376 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | LACYGNE_LK2 | 0.98308 | 0.91807 | -0.065001 |  | 0.93 | 1.05 | 0.04277 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | LACYGNE_LK2 | 0.98308 | 0.91807 | -0.065001 |  | 0.93 | 1.05 | 0.071112 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | LACYGNE_LK2 | 0.98308 | 0.91807 | -0.065001 |  | 0.93 | 1.05 | 0.039357 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | LACYGNE_LK2 | 0.98308 | 0.91807 | -0.065001 |  | 0.93 | 1.05 | 0.04035 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | LACYGNE_LK2 | 0.98308 | 0.91807 | -0.065001 |  | 0.93 | 1.05 | 0.052332 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | LACYGNE_LK2 | 0.98308 | 0.91807 | -0.065001 |  | 0.93 | 1.05 | 0.045944 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | LACYGNE_LK2 | 0.98308 | 0.91807 | -0.065001 |  | 0.93 | 1.05 | 0.038178 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | LACYGNE_LK2 | 0.98308 | 0.91807 | -0.065001 |  | 0.93 | 1.05 | 0.13469 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | LACYGNE_LK2 | 0.98308 | 0.91807 | -0.065001 |  | 0.93 | 1.05 | 0.03053 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | LACYGNE_LK2 | 0.98308 | 0.91807 | -0.065001 |  | 0.93 | 1.05 | 0.038178 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | LACYGNE_LK2 | 0.98308 | 0.91807 | -0.065001 |  | 0.93 | 1.05 | 0.037309 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | LACYGNE_LK2 | 0.98308 | 0.91807 | -0.065001 |  | 0.93 | 1.05 | 0.040075 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | LACYGNE_LK2 | 0.98308 | 0.91807 | -0.065001 |  | 0.93 | 1.05 | 0.053764 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | LACYGNE_LK2 | 0.98308 | 0.91807 | -0.065001 |  | 0.93 | 1.05 | 0.071762 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | LACYGNE_LK2 | 0.98308 | 0.91807 | -0.065001 |  | 0.93 | 1.05 | 0.047827 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | LACYGNE_LK2 | 0.98308 | 0.91807 | -0.065001 |  | 0.93 | 1.05 | 0.047827 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | LACYGNE_LK2 | 0.98308 | 0.91807 | -0.065001 |  | 0.93 | 1.05 | 0.070303 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | LACYGNE_LK2 | 0.98308 | 0.91807 | -0.065001 |  | 0.93 | 1.05 | 0.040614 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | LACYGNE_LK2 | 0.98308 | 0.91807 | -0.065001 |  | 0.93 | 1.05 | 0.039729 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | LACYGNE_LK2 | 0.98308 | 0.91807 | -0.065001 |  | 0.93 | 1.05 | 0.049662 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | LACYGNE_LK2 | 0.98308 | 0.91807 | -0.065001 |  | 0.93 | 1.05 | 0.042332 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | LACYGNE_LK2 | 0.98308 | 0.91807 | -0.065001 |  | 0.93 | 1.05 | 0.048722 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | LACYGNE_LK2 | 0.98308 | 0.91807 | -0.065001 |  | 0.93 | 1.05 | 0.038156 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | LACYGNE_LK2 | 0.98308 | 0.91807 | -0.065001 |  | 0.93 | 1.05 | 0.036794 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | LACYGNE_LK2 | 0.99328 | 0.92175 | -0.071529 |  | 0.93 | 1.05 | 0.036307 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | LACYGNE_LK2 | 0.99328 | 0.92175 | -0.071529 |  | 0.93 | 1.05 | 0.052743 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | LACYGNE_LK2 | 0.99328 | 0.92175 | -0.071529 |  | 0.93 | 1.05 | 0.039345 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | LACYGNE_LK2 | 0.99328 | 0.92175 | -0.071529 |  | 0.93 | 1.05 | 0.031366 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | LACYGNE_LK2 | 0.99328 | 0.92175 | -0.071529 |  | 0.93 | 1.05 | 0.041888 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | LACYGNE_LK2 | 0.99328 | 0.92175 | -0.071529 |  | 0.93 | 1.05 | 0.038797 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | LACYGNE_LK2 | 0.99328 | 0.92175 | -0.071529 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | LACYGNE_LK2 | 0.99328 | 0.92175 | -0.071529 |  | 0.93 | 1.05 | 0.067346 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | LACYGNE_LK2 | 0.99328 | 0.92175 | -0.071529 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | LACYGNE_LK2 | 0.99328 | 0.92175 | -0.071529 |  | 0.93 | 1.05 | 0.030851 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | LACYGNE_LK2 | 0.99328 | 0.92175 | -0.071529 |  | 0.93 | 1.05 | 0.032161 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | LACYGNE_LK2 | 0.99328 | 0.92175 | -0.071529 |  | 0.93 | 1.05 | 0.04067 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | LACYGNE_LK2 | 0.99328 | 0.92175 | -0.071529 |  | 0.93 | 1.05 | 0.040569 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | LACYGNE_LK2 | 0.99328 | 0.92175 | -0.071529 |  | 0.93 | 1.05 | 0.03086 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | LACYGNE_LK2 | 0.99328 | 0.92175 | -0.071529 |  | 0.93 | 1.05 | 0.033223 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | LACYGNE_LK2 | 0.99328 | 0.92175 | -0.071529 |  | 0.93 | 1.05 | 0.033733 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | LACYGNE_LK2 | 0.99106 | 0.86921 | -0.12186 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | LACYGNE_LK2 | 0.99106 | 0.86921 | -0.12186 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | LACYGNE_LK2 | 0.99106 | 0.86921 | -0.12186 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | LACYGNE_LK2 | 0.99106 | 0.86921 | -0.12186 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | LACYGNE_LK2 | 0.99106 | 0.86921 | -0.12186 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | LACYGNE_LK2 | 0.99106 | 0.86921 | -0.12186 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | LACYGNE_LK2 | 0.99106 | 0.86921 | -0.12186 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | LACYGNE_LK2 | 0.99106 | 0.86921 | -0.12186 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | LACYGNE_LK2 | 0.99106 | 0.86921 | -0.12186 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | LACYGNE_LK2 | 0.99106 | 0.86921 | -0.12186 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | LACYGNE_LK2 | 0.99106 | 0.86921 | -0.12186 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | LACYGNE_LK2 | 0.99106 | 0.86921 | -0.12186 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | LACYGNE_LK2 | 0.99106 | 0.86921 | -0.12186 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | LACYGNE_LK2 | 0.99106 | 0.86921 | -0.12186 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | LACYGNE_LK2 | 0.99106 | 0.86921 | -0.12186 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | LACYGNE_LK2 | 0.99106 | 0.86921 | -0.12186 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | LACYGNE_LK2 | 0.99106 | 0.86921 | -0.12186 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | LACYGNE_LK2 | 0.99106 | 0.86921 | -0.12186 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | LACYGNE_LK2 | 0.99106 | 0.86921 | -0.12186 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | LACYGNE_LK2 | 0.99106 | 0.86921 | -0.12186 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | LACYGNE_LK2 | 0.99106 | 0.86921 | -0.12186 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | LACYGNE_LK2 | 0.99106 | 0.86921 | -0.12186 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | LACYGNE_LK2 | 0.99106 | 0.86921 | -0.12186 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | LACYGNE_LK2 | 0.99106 | 0.86921 | -0.12186 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | LACYGNE_LK2 | 0.99106 | 0.86921 | -0.12186 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | LANG 3 | 0.96367 | 0.86847 | -0.095203 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | LANG 3 | 0.96367 | 0.86847 | -0.095203 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | LANG 3 | 0.96367 | 0.86847 | -0.095203 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | LANG 3 | 0.96367 | 0.86847 | -0.095203 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | LANG 3 | 0.96367 | 0.86847 | -0.095203 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | LANG 3 | 0.96367 | 0.86847 | -0.095203 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | LANG 3 | 0.96367 | 0.86847 | -0.095203 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | LANG 3 | 0.96367 | 0.86847 | -0.095203 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | LANG 3 | 0.96367 | 0.86847 | -0.095203 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | LANG 3 | 0.96367 | 0.86847 | -0.095203 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | LANG 3 | 0.96367 | 0.86847 | -0.095203 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | LANG 3 | 0.96367 | 0.86847 | -0.095203 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | LANG 3 | 0.96367 | 0.86847 | -0.095203 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | LANG 3 | 0.96367 | 0.86847 | -0.095203 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | LANG 3 | 0.96367 | 0.86847 | -0.095203 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | LANG 3 | 0.96367 | 0.86847 | -0.095203 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | LANG 3 | 0.96367 | 0.86847 | -0.095203 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | LANG 3 | 0.96367 | 0.86847 | -0.095203 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | LANG 3 | 0.96367 | 0.86847 | -0.095203 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | LANG 3 | 0.96367 | 0.86847 | -0.095203 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | LANG 3 | 0.96367 | 0.86847 | -0.095203 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | LANG 3 | 0.96367 | 0.86847 | -0.095203 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | LANG 3 | 0.96367 | 0.86847 | -0.095203 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | LANG 3 | 0.96367 | 0.86847 | -0.095203 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | LANG 3 | 0.96367 | 0.86847 | -0.095203 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | LANG 7 | 1.005 | 0.94212 | -0.062843 |  | 0.95 | 1.05 | 0.03053 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | LANG 7 | 1.005 | 0.94212 | -0.062843 |  | 0.95 | 1.05 | 0.044933 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | LANG 7 | 1.005 | 0.94212 | -0.062843 |  | 0.95 | 1.05 | 0.047811 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | LANG 7 | 1.005 | 0.94212 | -0.062843 |  | 0.95 | 1.05 | 0.09719 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | LANG 7 | 1.005 | 0.94212 | -0.062843 |  | 0.95 | 1.05 | 0.069376 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | LANG 7 | 1.005 | 0.94212 | -0.062843 |  | 0.95 | 1.05 | 0.04277 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | LANG 7 | 1.005 | 0.94212 | -0.062843 |  | 0.95 | 1.05 | 0.071112 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | LANG 7 | 1.005 | 0.94212 | -0.062843 |  | 0.95 | 1.05 | 0.039357 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | LANG 7 | 1.005 | 0.94212 | -0.062843 |  | 0.95 | 1.05 | 0.04035 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | LANG 7 | 1.005 | 0.94212 | -0.062843 |  | 0.95 | 1.05 | 0.052332 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | LANG 7 | 1.005 | 0.94212 | -0.062843 |  | 0.95 | 1.05 | 0.045944 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | LANG 7 | 1.005 | 0.94212 | -0.062843 |  | 0.95 | 1.05 | 0.038178 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | LANG 7 | 1.005 | 0.94212 | -0.062843 |  | 0.95 | 1.05 | 0.13469 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | LANG 7 | 1.005 | 0.94212 | -0.062843 |  | 0.95 | 1.05 | 0.03053 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | LANG 7 | 1.005 | 0.94212 | -0.062843 |  | 0.95 | 1.05 | 0.038178 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | LANG 7 | 1.005 | 0.94212 | -0.062843 |  | 0.95 | 1.05 | 0.037309 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | LANG 7 | 1.005 | 0.94212 | -0.062843 |  | 0.95 | 1.05 | 0.040075 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | LANG 7 | 1.005 | 0.94212 | -0.062843 |  | 0.95 | 1.05 | 0.053764 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | LANG 7 | 1.005 | 0.94212 | -0.062843 |  | 0.95 | 1.05 | 0.071762 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | LANG 7 | 1.005 | 0.94212 | -0.062843 |  | 0.95 | 1.05 | 0.047827 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | LANG 7 | 1.005 | 0.94212 | -0.062843 |  | 0.95 | 1.05 | 0.047827 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | LANG 7 | 1.005 | 0.94212 | -0.062843 |  | 0.95 | 1.05 | 0.070303 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | LANG 7 | 1.005 | 0.94212 | -0.062843 |  | 0.95 | 1.05 | 0.040614 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | LANG 7 | 1.005 | 0.94212 | -0.062843 |  | 0.95 | 1.05 | 0.039729 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | LANG 7 | 1.005 | 0.94212 | -0.062843 |  | 0.95 | 1.05 | 0.049662 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | LANG 7 | 1.005 | 0.94212 | -0.062843 |  | 0.95 | 1.05 | 0.042332 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | LANG 7 | 1.005 | 0.94212 | -0.062843 |  | 0.95 | 1.05 | 0.048722 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | LANG 7 | 1.005 | 0.94212 | -0.062843 |  | 0.95 | 1.05 | 0.038156 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | LANG 7 | 1.005 | 0.94212 | -0.062843 |  | 0.95 | 1.05 | 0.036794 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | LANG 7 | 1.0048 | 0.94627 | -0.058544 |  | 0.95 | 1.05 | 0.039728 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | LANG 7 | 1.0048 | 0.94627 | -0.058544 |  | 0.95 | 1.05 | 0.040762 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | LANG 7 | 1.0048 | 0.94627 | -0.058544 |  | 0.95 | 1.05 | 0.030778 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | LANG 7 | 1.0048 | 0.94627 | -0.058544 |  | 0.95 | 1.05 | 0.034227 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | LANG 7 | 1.0048 | 0.94627 | -0.058544 |  | 0.95 | 1.05 | 0.037164 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | LANG 7 | 1.0048 | 0.94627 | -0.058544 |  | 0.95 | 1.05 | 0.031937 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | LANG 7 | 1.0048 | 0.94627 | -0.058544 |  | 0.95 | 1.05 | 0.03782 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | LANG 7 | 1.0048 | 0.94627 | -0.058544 |  | 0.95 | 1.05 | 0.036407 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | LANG 7 | 1.0048 | 0.94627 | -0.058544 |  | 0.95 | 1.05 | 0.053181 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | LANG 7 | 1.0048 | 0.94627 | -0.058544 |  | 0.95 | 1.05 | 0.036407 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | LANG 7 | 1.0048 | 0.94627 | -0.058544 |  | 0.95 | 1.05 | 0.037418 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | LANG 7 | 1.0048 | 0.94627 | -0.058544 |  | 0.95 | 1.05 | 0.037355 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | LANG 7 | 1.0048 | 0.94627 | -0.058544 |  | 0.95 | 1.05 | 0.032533 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | LANG 7 | 1.0048 | 0.94627 | -0.058544 |  | 0.95 | 1.05 | 0.031326 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | LANG 7 | 1.0048 | 0.94627 | -0.058544 |  | 0.95 | 1.05 | 0.035094 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | LANG 7 | 1.0048 | 0.94627 | -0.058544 |  | 0.95 | 1.05 | 0.031652 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | LANG 7 | 1.0048 | 0.94627 | -0.058544 |  | 0.95 | 1.05 | 0.031104 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | LANG 7 | 1.0048 | 0.94627 | -0.058544 |  | 0.95 | 1.05 | 0.033175 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | LANG 7 | 1.0048 | 0.94627 | -0.058544 |  | 0.95 | 1.05 | 0.034843 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | LANG 7 | 1.005 | 0.94363 | -0.061325 |  | 0.95 | 1.05 | 0.036307 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | LANG 7 | 1.005 | 0.94363 | -0.061325 |  | 0.95 | 1.05 | 0.052743 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | LANG 7 | 1.005 | 0.94363 | -0.061325 |  | 0.95 | 1.05 | 0.039345 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | LANG 7 | 1.005 | 0.94363 | -0.061325 |  | 0.95 | 1.05 | 0.031366 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | LANG 7 | 1.005 | 0.94363 | -0.061325 |  | 0.95 | 1.05 | 0.041888 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | LANG 7 | 1.005 | 0.94363 | -0.061325 |  | 0.95 | 1.05 | 0.038797 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | LANG 7 | 1.005 | 0.94363 | -0.061325 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | LANG 7 | 1.005 | 0.94363 | -0.061325 |  | 0.95 | 1.05 | 0.067346 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | LANG 7 | 1.005 | 0.94363 | -0.061325 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | LANG 7 | 1.005 | 0.94363 | -0.061325 |  | 0.95 | 1.05 | 0.030851 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | LANG 7 | 1.005 | 0.94363 | -0.061325 |  | 0.95 | 1.05 | 0.032161 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | LANG 7 | 1.005 | 0.94363 | -0.061325 |  | 0.95 | 1.05 | 0.04067 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | LANG 7 | 1.005 | 0.94363 | -0.061325 |  | 0.95 | 1.05 | 0.040569 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | LANG 7 | 1.005 | 0.94363 | -0.061325 |  | 0.95 | 1.05 | 0.03086 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | LANG 7 | 1.005 | 0.94363 | -0.061325 |  | 0.95 | 1.05 | 0.033223 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | LANG 7 | 1.005 | 0.94363 | -0.061325 |  | 0.95 | 1.05 | 0.033733 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | LANG 7 | 1.005 | 0.94487 | -0.060098 |  | 0.95 | 1.05 | 0.040439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | LANG 7 | 1.005 | 0.94487 | -0.060098 |  | 0.95 | 1.05 | 0.034853 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | LANG 7 | 1.005 | 0.94487 | -0.060098 |  | 0.95 | 1.05 | 0.046783 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | LANG 7 | 1.005 | 0.94487 | -0.060098 |  | 0.95 | 1.05 | 0.047615 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | LANG 7 | 1.005 | 0.94487 | -0.060098 |  | 0.95 | 1.05 | 0.034938 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | LANG 7 | 1.005 | 0.94487 | -0.060098 |  | 0.95 | 1.05 | 0.037875 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | LANG 7 | 1.005 | 0.94487 | -0.060098 |  | 0.95 | 1.05 | 0.044022 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | LANG 7 | 1.005 | 0.94487 | -0.060098 |  | 0.95 | 1.05 | 0.030552 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | LANG 7 | 1.005 | 0.94487 | -0.060098 |  | 0.95 | 1.05 | 0.038531 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | LANG 7 | 1.005 | 0.94487 | -0.060098 |  | 0.95 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | LANG 7 | 1.005 | 0.94487 | -0.060098 |  | 0.95 | 1.05 | 0.062491 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | LANG 7 | 1.005 | 0.94487 | -0.060098 |  | 0.95 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | LANG 7 | 1.005 | 0.94487 | -0.060098 |  | 0.95 | 1.05 | 0.038129 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | LANG 7 | 1.005 | 0.94487 | -0.060098 |  | 0.95 | 1.05 | 0.038066 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | LANG 7 | 1.005 | 0.94487 | -0.060098 |  | 0.95 | 1.05 | 0.034955 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | LANG 7 | 1.005 | 0.94487 | -0.060098 |  | 0.95 | 1.05 | 0.06281 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | LANG 7 | 1.005 | 0.94487 | -0.060098 |  | 0.95 | 1.05 | 0.045309 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | LANG 7 | 1.005 | 0.94487 | -0.060098 |  | 0.95 | 1.05 | 0.035805 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | LANG 7 | 1.005 | 0.94487 | -0.060098 |  | 0.95 | 1.05 | 0.032364 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | LANG 7 | 1.005 | 0.94487 | -0.060098 |  | 0.95 | 1.05 | 0.031815 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | LANG 7 | 1.005 | 0.94487 | -0.060098 |  | 0.95 | 1.05 | 0.033886 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | LANG 7 | 1.005 | 0.94487 | -0.060098 |  | 0.95 | 1.05 | 0.035554 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | LANG 7 | 0.87604 | 0.7895 | -0.086546 |  | 0.95 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | LANG 7 | 0.87604 | 0.7895 | -0.086546 |  | 0.95 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | LANG 7 | 0.87604 | 0.7895 | -0.086546 |  | 0.95 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | LANG 7 | 0.87604 | 0.7895 | -0.086546 |  | 0.95 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | LANG 7 | 0.87604 | 0.7895 | -0.086546 |  | 0.95 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | LANG 7 | 0.87604 | 0.7895 | -0.086546 |  | 0.95 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | LANG 7 | 0.87604 | 0.7895 | -0.086546 |  | 0.95 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | LANG 7 | 0.87604 | 0.7895 | -0.086546 |  | 0.95 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | LANG 7 | 0.87604 | 0.7895 | -0.086546 |  | 0.95 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | LANG 7 | 0.87604 | 0.7895 | -0.086546 |  | 0.95 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | LANG 7 | 0.87604 | 0.7895 | -0.086546 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | LANG 7 | 0.87604 | 0.7895 | -0.086546 |  | 0.95 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | LANG 7 | 0.87604 | 0.7895 | -0.086546 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | LANG 7 | 0.87604 | 0.7895 | -0.086546 |  | 0.95 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | LANG 7 | 0.87604 | 0.7895 | -0.086546 |  | 0.95 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | LANG 7 | 0.87604 | 0.7895 | -0.086546 |  | 0.95 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | LANG 7 | 0.87604 | 0.7895 | -0.086546 |  | 0.95 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | LANG 7 | 0.87604 | 0.7895 | -0.086546 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | LANG 7 | 0.87604 | 0.7895 | -0.086546 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | LANG 7 | 0.87604 | 0.7895 | -0.086546 |  | 0.95 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | LANG 7 | 0.87604 | 0.7895 | -0.086546 |  | 0.95 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | LANG 7 | 0.87604 | 0.7895 | -0.086546 |  | 0.95 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | LANG 7 | 0.87604 | 0.7895 | -0.086546 |  | 0.95 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | LANG 7 | 0.87604 | 0.7895 | -0.086546 |  | 0.95 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | LANG 7 | 0.87604 | 0.7895 | -0.086546 |  | 0.95 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | LENEXA 5 | 0.98522 | 0.92236 | -0.062857 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | LENEXA 5 | 0.98522 | 0.92236 | -0.062857 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | LENEXA 5 | 0.98522 | 0.92236 | -0.062857 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | LENEXA 5 | 0.98522 | 0.92236 | -0.062857 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | LENEXA 5 | 0.98522 | 0.92236 | -0.062857 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | LENEXA 5 | 0.98522 | 0.92236 | -0.062857 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | LENEXA 5 | 0.98522 | 0.92236 | -0.062857 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | LENEXA 5 | 0.98522 | 0.92236 | -0.062857 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | LENEXA 5 | 0.98522 | 0.92236 | -0.062857 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | LENEXA 5 | 0.98522 | 0.92236 | -0.062857 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | LENEXA 5 | 0.98522 | 0.92236 | -0.062857 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | LENEXA 5 | 0.98522 | 0.92236 | -0.062857 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | LENEXA 5 | 0.98522 | 0.92236 | -0.062857 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | LENEXA 5 | 0.98522 | 0.92236 | -0.062857 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | LENEXA 5 | 0.98522 | 0.92236 | -0.062857 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | LENEXA 5 | 0.98522 | 0.92236 | -0.062857 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | LENEXA 5 | 0.98522 | 0.92236 | -0.062857 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | LENEXA 5 | 0.98522 | 0.92236 | -0.062857 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | LENEXA 5 | 0.98522 | 0.92236 | -0.062857 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | LENEXA 5 | 0.98522 | 0.92236 | -0.062857 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | LENEXA 5 | 0.98522 | 0.92236 | -0.062857 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | LENEXA 5 | 0.98522 | 0.92236 | -0.062857 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | LENEXA 5 | 0.98522 | 0.92236 | -0.062857 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | LENEXA 5 | 0.98522 | 0.92236 | -0.062857 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | LENEXA 5 | 0.98522 | 0.92236 | -0.062857 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | LIBERTY4 | 0.9598 | 0.9143 | -0.045504 |  | 0.93 | 1.05 | 0.091967 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | LIBERTY4 | 0.9598 | 0.9143 | -0.045504 |  | 0.93 | 1.05 | 0.033356 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | LIBERTY4 | 0.9598 | 0.9143 | -0.045504 |  | 0.93 | 1.05 | 0.044346 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | LIBERTY4 | 0.9598 | 0.9143 | -0.045504 |  | 0.93 | 1.05 | 0.058536 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | LIBERTY4 | 0.9598 | 0.9143 | -0.045504 |  | 0.93 | 1.05 | 0.059327 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | LIBERTY4 | 0.9598 | 0.9143 | -0.045504 |  | 0.93 | 1.05 | 0.041874 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | LIBERTY4 | 0.9598 | 0.9143 | -0.045504 |  | 0.93 | 1.05 | 0.046192 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | LIBERTY4 | 0.9598 | 0.9143 | -0.045504 |  | 0.93 | 1.05 | 0.12754 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | LIBERTY4 | 0.9598 | 0.9143 | -0.045504 |  | 0.93 | 1.05 | 0.047018 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | LIBERTY4 | 0.9598 | 0.9143 | -0.045504 |  | 0.93 | 1.05 | 0.056662 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | LIBERTY4 | 0.9598 | 0.9143 | -0.045504 |  | 0.93 | 1.05 | 0.056662 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | LIBERTY4 | 0.9598 | 0.9143 | -0.045504 |  | 0.93 | 1.05 | 0.056727 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | LIBERTY4 | 0.9598 | 0.9143 | -0.045504 |  | 0.93 | 1.05 | 0.074186 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | LIBERTY4 | 0.9598 | 0.9143 | -0.045504 |  | 0.93 | 1.05 | 0.040839 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | LIBERTY4 | 0.9598 | 0.9143 | -0.045504 |  | 0.93 | 1.05 | 0.03863 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | LIBERTY4 | 0.9598 | 0.9143 | -0.045504 |  | 0.93 | 1.05 | 0.042285 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | LIBERTY4 | 0.9598 | 0.9143 | -0.045504 |  | 0.93 | 1.05 | 0.042285 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | LIBERTY4 | 0.9598 | 0.9143 | -0.045504 |  | 0.93 | 1.05 | 0.050204 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | LIBERTY4 | 0.9598 | 0.9143 | -0.045504 |  | 0.93 | 1.05 | 0.058005 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | LIBERTY4 | 0.9598 | 0.9143 | -0.045504 |  | 0.93 | 1.05 | 0.041735 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | LIBERTY4 | 0.9598 | 0.9143 | -0.045504 |  | 0.93 | 1.05 | 0.057076 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | LIBERTY4 | 0.9598 | 0.9143 | -0.045504 |  | 0.93 | 1.05 | 0.050111 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | LIBERTY4 | 0.9598 | 0.9143 | -0.045504 |  | 0.93 | 1.05 | 0.06491 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | LIBERTY4 | 0.9598 | 0.9143 | -0.045504 |  | 0.93 | 1.05 | 0.051051 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | LIBERTY4 | 0.9598 | 0.9143 | -0.045504 |  | 0.93 | 1.05 | 0.036279 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | LIBERTY4 | 0.96613 | 0.92063 | -0.045495 |  | 0.93 | 1.05 | 0.049206 | P23:345:WERE:N345-345-20:EHV: | Add 20 MVAR switched shunt at LIBERTY4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | LIBERTY4 | 0.96613 | 0.92063 | -0.045495 |  | 0.93 | 1.05 | 0.056808 | P23:345:WERE:N345-345-20:EHV: | Add 20 MVAR switched shunt at LIBERTY4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | LIBERTY4 | 0.96613 | 0.92063 | -0.045495 |  | 0.93 | 1.05 | 0.079992 | P23:345:WERE:N345-345-20:EHV: | Add 20 MVAR switched shunt at LIBERTY4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | LIBERTY4 | 0.96613 | 0.92063 | -0.045495 |  | 0.93 | 1.05 | 0.085896 | P23:345:WERE:N345-345-20:EHV: | Add 20 MVAR switched shunt at LIBERTY4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | LIBERTY4 | 0.96613 | 0.92063 | -0.045495 |  | 0.93 | 1.05 | 0.049659 | P23:345:WERE:N345-345-20:EHV: | Add 20 MVAR switched shunt at LIBERTY4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | LIBERTY4 | 0.96613 | 0.92063 | -0.045495 |  | 0.93 | 1.05 | 0.11417 | P23:345:WERE:N345-345-20:EHV: | Add 20 MVAR switched shunt at LIBERTY4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | LIBERTY4 | 0.96613 | 0.92063 | -0.045495 |  | 0.93 | 1.05 | 0.043555 | P23:345:WERE:N345-345-20:EHV: | Add 20 MVAR switched shunt at LIBERTY4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | LIBERTY4 | 0.96613 | 0.92063 | -0.045495 |  | 0.93 | 1.05 | 0.045351 | P23:345:WERE:N345-345-20:EHV: | Add 20 MVAR switched shunt at LIBERTY4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | LIBERTY4 | 0.96613 | 0.92063 | -0.045495 |  | 0.93 | 1.05 | 0.067102 | P23:345:WERE:N345-345-20:EHV: | Add 20 MVAR switched shunt at LIBERTY4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | LIBERTY4 | 0.96613 | 0.92063 | -0.045495 |  | 0.93 | 1.05 | 0.05564 | P23:345:WERE:N345-345-20:EHV: | Add 20 MVAR switched shunt at LIBERTY4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | LIBERTY4 | 0.96613 | 0.92063 | -0.045495 |  | 0.93 | 1.05 | 0.040761 | P23:345:WERE:N345-345-20:EHV: | Add 20 MVAR switched shunt at LIBERTY4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | LIBERTY4 | 0.96613 | 0.92063 | -0.045495 |  | 0.93 | 1.05 | 0.4666 | P23:345:WERE:N345-345-20:EHV: | Add 20 MVAR switched shunt at LIBERTY4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | LIBERTY4 | 0.96613 | 0.92063 | -0.045495 |  | 0.93 | 1.05 | 0.040761 | P23:345:WERE:N345-345-20:EHV: | Add 20 MVAR switched shunt at LIBERTY4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | LIBERTY4 | 0.96613 | 0.92063 | -0.045495 |  | 0.93 | 1.05 | 0.038981 | P23:345:WERE:N345-345-20:EHV: | Add 20 MVAR switched shunt at LIBERTY4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | LIBERTY4 | 0.96613 | 0.92063 | -0.045495 |  | 0.93 | 1.05 | 0.043527 | P23:345:WERE:N345-345-20:EHV: | Add 20 MVAR switched shunt at LIBERTY4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | LIBERTY4 | 0.96613 | 0.92063 | -0.045495 |  | 0.93 | 1.05 | 0.070027 | P23:345:WERE:N345-345-20:EHV: | Add 20 MVAR switched shunt at LIBERTY4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | LIBERTY4 | 0.96613 | 0.92063 | -0.045495 |  | 0.93 | 1.05 | 0.06871 | P23:345:WERE:N345-345-20:EHV: | Add 20 MVAR switched shunt at LIBERTY4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | LIBERTY4 | 0.96613 | 0.92063 | -0.045495 |  | 0.93 | 1.05 | 0.059117 | P23:345:WERE:N345-345-20:EHV: | Add 20 MVAR switched shunt at LIBERTY4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | LIBERTY4 | 0.96613 | 0.92063 | -0.045495 |  | 0.93 | 1.05 | 0.059117 | P23:345:WERE:N345-345-20:EHV: | Add 20 MVAR switched shunt at LIBERTY4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | LIBERTY4 | 0.96613 | 0.92063 | -0.045495 |  | 0.93 | 1.05 | 0.094447 | P23:345:WERE:N345-345-20:EHV: | Add 20 MVAR switched shunt at LIBERTY4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | LIBERTY4 | 0.96613 | 0.92063 | -0.045495 |  | 0.93 | 1.05 | 0.045445 | P23:345:WERE:N345-345-20:EHV: | Add 20 MVAR switched shunt at LIBERTY4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | LIBERTY4 | 0.96613 | 0.92063 | -0.045495 |  | 0.93 | 1.05 | 0.044374 | P23:345:WERE:N345-345-20:EHV: | Add 20 MVAR switched shunt at LIBERTY4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | LIBERTY4 | 0.96613 | 0.92063 | -0.045495 |  | 0.93 | 1.05 | 0.06597 | P23:345:WERE:N345-345-20:EHV: | Add 20 MVAR switched shunt at LIBERTY4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | LIBERTY4 | 0.96613 | 0.92063 | -0.045495 |  | 0.93 | 1.05 | 0.048874 | P23:345:WERE:N345-345-20:EHV: | Add 20 MVAR switched shunt at LIBERTY4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | LIBERTY4 | 0.96613 | 0.92063 | -0.045495 |  | 0.93 | 1.05 | 0.060524 | P23:345:WERE:N345-345-20:EHV: | Add 20 MVAR switched shunt at LIBERTY4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | LIBERTY4 | 0.96613 | 0.92063 | -0.045495 |  | 0.93 | 1.05 | 0.04115 | P23:345:WERE:N345-345-20:EHV: | Add 20 MVAR switched shunt at LIBERTY4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | LIBERTY4 | 0.96613 | 0.92063 | -0.045495 |  | 0.93 | 1.05 | 0.038988 | P23:345:WERE:N345-345-20:EHV: | Add 20 MVAR switched shunt at LIBERTY4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | LIBERTY4 | 0.97342 | 0.94885 | -0.024568 |  | 0.95 | 1.05 | 0.14491 | System Intact | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | LIBERTY4 | 0.96821 | 0.92036 | -0.047854 |  | 0.93 | 1.05 | 0.035768 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | LIBERTY4 | 0.96821 | 0.92036 | -0.047854 |  | 0.93 | 1.05 | 0.088718 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | LIBERTY4 | 0.96821 | 0.92036 | -0.047854 |  | 0.93 | 1.05 | 0.031473 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | LIBERTY4 | 0.96821 | 0.92036 | -0.047854 |  | 0.93 | 1.05 | 0.034941 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | LIBERTY4 | 0.96821 | 0.92036 | -0.047854 |  | 0.93 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | LIBERTY4 | 0.96821 | 0.92036 | -0.047854 |  | 0.93 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | LIBERTY4 | 0.96821 | 0.92036 | -0.047854 |  | 0.93 | 1.05 | 0.049224 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | LIBERTY4 | 0.96821 | 0.92036 | -0.047854 |  | 0.93 | 1.05 | 0.038981 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | LIBERTY4 | 0.96821 | 0.92036 | -0.047854 |  | 0.93 | 1.05 | 0.040399 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | LIBERTY4 | 0.96821 | 0.92036 | -0.047854 |  | 0.93 | 1.05 | 0.031912 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | LIBERTY4 | 0.96821 | 0.92036 | -0.047854 |  | 0.93 | 1.05 | 0.034127 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | LIBERTY4 | 0.96821 | 0.92036 | -0.047854 |  | 0.93 | 1.05 | 0.047318 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | LIBERTY4 | 0.96351 | 0.9167 | -0.046806 |  | 0.93 | 1.05 | 0.040439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | LIBERTY4 | 0.96351 | 0.9167 | -0.046806 |  | 0.93 | 1.05 | 0.034853 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | LIBERTY4 | 0.96351 | 0.9167 | -0.046806 |  | 0.93 | 1.05 | 0.046783 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | LIBERTY4 | 0.96351 | 0.9167 | -0.046806 |  | 0.93 | 1.05 | 0.047615 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | LIBERTY4 | 0.96351 | 0.9167 | -0.046806 |  | 0.93 | 1.05 | 0.034938 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | LIBERTY4 | 0.96351 | 0.9167 | -0.046806 |  | 0.93 | 1.05 | 0.037875 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | LIBERTY4 | 0.96351 | 0.9167 | -0.046806 |  | 0.93 | 1.05 | 0.044022 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | LIBERTY4 | 0.96351 | 0.9167 | -0.046806 |  | 0.93 | 1.05 | 0.030552 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | LIBERTY4 | 0.96351 | 0.9167 | -0.046806 |  | 0.93 | 1.05 | 0.038531 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | LIBERTY4 | 0.96351 | 0.9167 | -0.046806 |  | 0.93 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | LIBERTY4 | 0.96351 | 0.9167 | -0.046806 |  | 0.93 | 1.05 | 0.062491 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | LIBERTY4 | 0.96351 | 0.9167 | -0.046806 |  | 0.93 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | LIBERTY4 | 0.96351 | 0.9167 | -0.046806 |  | 0.93 | 1.05 | 0.038129 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | LIBERTY4 | 0.96351 | 0.9167 | -0.046806 |  | 0.93 | 1.05 | 0.038066 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | LIBERTY4 | 0.96351 | 0.9167 | -0.046806 |  | 0.93 | 1.05 | 0.034955 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | LIBERTY4 | 0.96351 | 0.9167 | -0.046806 |  | 0.93 | 1.05 | 0.06281 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | LIBERTY4 | 0.96351 | 0.9167 | -0.046806 |  | 0.93 | 1.05 | 0.045309 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | LIBERTY4 | 0.96351 | 0.9167 | -0.046806 |  | 0.93 | 1.05 | 0.035805 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | LIBERTY4 | 0.96351 | 0.9167 | -0.046806 |  | 0.93 | 1.05 | 0.032364 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | LIBERTY4 | 0.96351 | 0.9167 | -0.046806 |  | 0.93 | 1.05 | 0.031815 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | LIBERTY4 | 0.96351 | 0.9167 | -0.046806 |  | 0.93 | 1.05 | 0.033886 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | LIBERTY4 | 0.96351 | 0.9167 | -0.046806 |  | 0.93 | 1.05 | 0.035554 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | LIBERTY4 | 0.96732 | 0.91024 | -0.057074 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | LIBERTY4 | 0.96732 | 0.91024 | -0.057074 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | LIBERTY4 | 0.96732 | 0.91024 | -0.057074 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | LIBERTY4 | 0.96732 | 0.91024 | -0.057074 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | LIBERTY4 | 0.96732 | 0.91024 | -0.057074 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | LIBERTY4 | 0.96732 | 0.91024 | -0.057074 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | LIBERTY4 | 0.96732 | 0.91024 | -0.057074 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | LIBERTY4 | 0.96732 | 0.91024 | -0.057074 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | LIBERTY4 | 0.96732 | 0.91024 | -0.057074 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | LIBERTY4 | 0.96732 | 0.91024 | -0.057074 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | LIBERTY4 | 0.96732 | 0.91024 | -0.057074 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | LIBERTY4 | 0.96732 | 0.91024 | -0.057074 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | LIBERTY4 | 0.96732 | 0.91024 | -0.057074 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | LIBERTY4 | 0.96732 | 0.91024 | -0.057074 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | LIBERTY4 | 0.96732 | 0.91024 | -0.057074 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | LIBERTY4 | 0.96732 | 0.91024 | -0.057074 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | LIBERTY4 | 0.96732 | 0.91024 | -0.057074 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | LIBERTY4 | 0.96732 | 0.91024 | -0.057074 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | LIBERTY4 | 0.96732 | 0.91024 | -0.057074 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | LIBERTY4 | 0.96732 | 0.91024 | -0.057074 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | LIBERTY4 | 0.96732 | 0.91024 | -0.057074 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | LIBERTY4 | 0.96732 | 0.91024 | -0.057074 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | LIBERTY4 | 0.96732 | 0.91024 | -0.057074 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | LIBERTY4 | 0.96732 | 0.91024 | -0.057074 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | LIBERTY4 | 0.96732 | 0.91024 | -0.057074 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | MARMTNE5 | 0.99222 | 0.92729 | -0.064932 |  | 0.93 | 1.05 | 0.03053 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | MARMTNE5 | 0.99222 | 0.92729 | -0.064932 |  | 0.93 | 1.05 | 0.044933 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | MARMTNE5 | 0.99222 | 0.92729 | -0.064932 |  | 0.93 | 1.05 | 0.047811 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | MARMTNE5 | 0.99222 | 0.92729 | -0.064932 |  | 0.93 | 1.05 | 0.09719 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | MARMTNE5 | 0.99222 | 0.92729 | -0.064932 |  | 0.93 | 1.05 | 0.069376 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | MARMTNE5 | 0.99222 | 0.92729 | -0.064932 |  | 0.93 | 1.05 | 0.04277 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | MARMTNE5 | 0.99222 | 0.92729 | -0.064932 |  | 0.93 | 1.05 | 0.071112 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | MARMTNE5 | 0.99222 | 0.92729 | -0.064932 |  | 0.93 | 1.05 | 0.039357 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | MARMTNE5 | 0.99222 | 0.92729 | -0.064932 |  | 0.93 | 1.05 | 0.04035 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | MARMTNE5 | 0.99222 | 0.92729 | -0.064932 |  | 0.93 | 1.05 | 0.052332 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | MARMTNE5 | 0.99222 | 0.92729 | -0.064932 |  | 0.93 | 1.05 | 0.045944 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | MARMTNE5 | 0.99222 | 0.92729 | -0.064932 |  | 0.93 | 1.05 | 0.038178 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | MARMTNE5 | 0.99222 | 0.92729 | -0.064932 |  | 0.93 | 1.05 | 0.13469 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | MARMTNE5 | 0.99222 | 0.92729 | -0.064932 |  | 0.93 | 1.05 | 0.03053 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | MARMTNE5 | 0.99222 | 0.92729 | -0.064932 |  | 0.93 | 1.05 | 0.038178 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | MARMTNE5 | 0.99222 | 0.92729 | -0.064932 |  | 0.93 | 1.05 | 0.037309 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | MARMTNE5 | 0.99222 | 0.92729 | -0.064932 |  | 0.93 | 1.05 | 0.040075 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | MARMTNE5 | 0.99222 | 0.92729 | -0.064932 |  | 0.93 | 1.05 | 0.053764 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | MARMTNE5 | 0.99222 | 0.92729 | -0.064932 |  | 0.93 | 1.05 | 0.071762 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | MARMTNE5 | 0.99222 | 0.92729 | -0.064932 |  | 0.93 | 1.05 | 0.047827 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | MARMTNE5 | 0.99222 | 0.92729 | -0.064932 |  | 0.93 | 1.05 | 0.047827 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | MARMTNE5 | 0.99222 | 0.92729 | -0.064932 |  | 0.93 | 1.05 | 0.070303 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | MARMTNE5 | 0.99222 | 0.92729 | -0.064932 |  | 0.93 | 1.05 | 0.040614 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | MARMTNE5 | 0.99222 | 0.92729 | -0.064932 |  | 0.93 | 1.05 | 0.039729 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | MARMTNE5 | 0.99222 | 0.92729 | -0.064932 |  | 0.93 | 1.05 | 0.049662 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | MARMTNE5 | 0.99222 | 0.92729 | -0.064932 |  | 0.93 | 1.05 | 0.042332 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | MARMTNE5 | 0.99222 | 0.92729 | -0.064932 |  | 0.93 | 1.05 | 0.048722 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | MARMTNE5 | 0.99222 | 0.92729 | -0.064932 |  | 0.93 | 1.05 | 0.038156 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | MARMTNE5 | 0.99222 | 0.92729 | -0.064932 |  | 0.93 | 1.05 | 0.036794 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | MARMTNE5 | 0.99018 | 0.92951 | -0.060676 |  | 0.93 | 1.05 | 0.036307 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | MARMTNE5 | 0.99018 | 0.92951 | -0.060676 |  | 0.93 | 1.05 | 0.052743 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | MARMTNE5 | 0.99018 | 0.92951 | -0.060676 |  | 0.93 | 1.05 | 0.039345 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | MARMTNE5 | 0.99018 | 0.92951 | -0.060676 |  | 0.93 | 1.05 | 0.031366 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | MARMTNE5 | 0.99018 | 0.92951 | -0.060676 |  | 0.93 | 1.05 | 0.041888 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | MARMTNE5 | 0.99018 | 0.92951 | -0.060676 |  | 0.93 | 1.05 | 0.038797 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | MARMTNE5 | 0.99018 | 0.92951 | -0.060676 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | MARMTNE5 | 0.99018 | 0.92951 | -0.060676 |  | 0.93 | 1.05 | 0.067346 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | MARMTNE5 | 0.99018 | 0.92951 | -0.060676 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | MARMTNE5 | 0.99018 | 0.92951 | -0.060676 |  | 0.93 | 1.05 | 0.030851 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | MARMTNE5 | 0.99018 | 0.92951 | -0.060676 |  | 0.93 | 1.05 | 0.032161 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | MARMTNE5 | 0.99018 | 0.92951 | -0.060676 |  | 0.93 | 1.05 | 0.04067 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | MARMTNE5 | 0.99018 | 0.92951 | -0.060676 |  | 0.93 | 1.05 | 0.040569 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | MARMTNE5 | 0.99018 | 0.92951 | -0.060676 |  | 0.93 | 1.05 | 0.03086 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | MARMTNE5 | 0.99018 | 0.92951 | -0.060676 |  | 0.93 | 1.05 | 0.033223 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | MARMTNE5 | 0.99018 | 0.92951 | -0.060676 |  | 0.93 | 1.05 | 0.033733 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | MARMTNE5 | 0.99051 | 0.92251 | -0.068001 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | MARMTNE5 | 0.99051 | 0.92251 | -0.068001 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | MARMTNE5 | 0.99051 | 0.92251 | -0.068001 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | MARMTNE5 | 0.99051 | 0.92251 | -0.068001 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | MARMTNE5 | 0.99051 | 0.92251 | -0.068001 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | MARMTNE5 | 0.99051 | 0.92251 | -0.068001 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | MARMTNE5 | 0.99051 | 0.92251 | -0.068001 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | MARMTNE5 | 0.99051 | 0.92251 | -0.068001 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | MARMTNE5 | 0.99051 | 0.92251 | -0.068001 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | MARMTNE5 | 0.99051 | 0.92251 | -0.068001 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | MARMTNE5 | 0.99051 | 0.92251 | -0.068001 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | MARMTNE5 | 0.99051 | 0.92251 | -0.068001 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | MARMTNE5 | 0.99051 | 0.92251 | -0.068001 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | MARMTNE5 | 0.99051 | 0.92251 | -0.068001 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | MARMTNE5 | 0.99051 | 0.92251 | -0.068001 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | MARMTNE5 | 0.99051 | 0.92251 | -0.068001 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | MARMTNE5 | 0.99051 | 0.92251 | -0.068001 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | MARMTNE5 | 0.99051 | 0.92251 | -0.068001 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | MARMTNE5 | 0.99051 | 0.92251 | -0.068001 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | MARMTNE5 | 0.99051 | 0.92251 | -0.068001 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | MARMTNE5 | 0.99051 | 0.92251 | -0.068001 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | MARMTNE5 | 0.99051 | 0.92251 | -0.068001 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | MARMTNE5 | 0.99051 | 0.92251 | -0.068001 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | MARMTNE5 | 0.99051 | 0.92251 | -0.068001 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | MARMTNE5 | 0.99051 | 0.92251 | -0.068001 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | MARMTNW5 | 0.99218 | 0.92723 | -0.064943 |  | 0.93 | 1.05 | 0.03053 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | MARMTNW5 | 0.99218 | 0.92723 | -0.064943 |  | 0.93 | 1.05 | 0.044933 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | MARMTNW5 | 0.99218 | 0.92723 | -0.064943 |  | 0.93 | 1.05 | 0.047811 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | MARMTNW5 | 0.99218 | 0.92723 | -0.064943 |  | 0.93 | 1.05 | 0.09719 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | MARMTNW5 | 0.99218 | 0.92723 | -0.064943 |  | 0.93 | 1.05 | 0.069376 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | MARMTNW5 | 0.99218 | 0.92723 | -0.064943 |  | 0.93 | 1.05 | 0.04277 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | MARMTNW5 | 0.99218 | 0.92723 | -0.064943 |  | 0.93 | 1.05 | 0.071112 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | MARMTNW5 | 0.99218 | 0.92723 | -0.064943 |  | 0.93 | 1.05 | 0.039357 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | MARMTNW5 | 0.99218 | 0.92723 | -0.064943 |  | 0.93 | 1.05 | 0.04035 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | MARMTNW5 | 0.99218 | 0.92723 | -0.064943 |  | 0.93 | 1.05 | 0.052332 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | MARMTNW5 | 0.99218 | 0.92723 | -0.064943 |  | 0.93 | 1.05 | 0.045944 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | MARMTNW5 | 0.99218 | 0.92723 | -0.064943 |  | 0.93 | 1.05 | 0.038178 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | MARMTNW5 | 0.99218 | 0.92723 | -0.064943 |  | 0.93 | 1.05 | 0.13469 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | MARMTNW5 | 0.99218 | 0.92723 | -0.064943 |  | 0.93 | 1.05 | 0.03053 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | MARMTNW5 | 0.99218 | 0.92723 | -0.064943 |  | 0.93 | 1.05 | 0.038178 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | MARMTNW5 | 0.99218 | 0.92723 | -0.064943 |  | 0.93 | 1.05 | 0.037309 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | MARMTNW5 | 0.99218 | 0.92723 | -0.064943 |  | 0.93 | 1.05 | 0.040075 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | MARMTNW5 | 0.99218 | 0.92723 | -0.064943 |  | 0.93 | 1.05 | 0.053764 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | MARMTNW5 | 0.99218 | 0.92723 | -0.064943 |  | 0.93 | 1.05 | 0.071762 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | MARMTNW5 | 0.99218 | 0.92723 | -0.064943 |  | 0.93 | 1.05 | 0.047827 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | MARMTNW5 | 0.99218 | 0.92723 | -0.064943 |  | 0.93 | 1.05 | 0.047827 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | MARMTNW5 | 0.99218 | 0.92723 | -0.064943 |  | 0.93 | 1.05 | 0.070303 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | MARMTNW5 | 0.99218 | 0.92723 | -0.064943 |  | 0.93 | 1.05 | 0.040614 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | MARMTNW5 | 0.99218 | 0.92723 | -0.064943 |  | 0.93 | 1.05 | 0.039729 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | MARMTNW5 | 0.99218 | 0.92723 | -0.064943 |  | 0.93 | 1.05 | 0.049662 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | MARMTNW5 | 0.99218 | 0.92723 | -0.064943 |  | 0.93 | 1.05 | 0.042332 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | MARMTNW5 | 0.99218 | 0.92723 | -0.064943 |  | 0.93 | 1.05 | 0.048722 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | MARMTNW5 | 0.99218 | 0.92723 | -0.064943 |  | 0.93 | 1.05 | 0.038156 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | MARMTNW5 | 0.99218 | 0.92723 | -0.064943 |  | 0.93 | 1.05 | 0.036794 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | MARMTNW5 | 0.99014 | 0.92945 | -0.060685 |  | 0.93 | 1.05 | 0.036307 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | MARMTNW5 | 0.99014 | 0.92945 | -0.060685 |  | 0.93 | 1.05 | 0.052743 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | MARMTNW5 | 0.99014 | 0.92945 | -0.060685 |  | 0.93 | 1.05 | 0.039345 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | MARMTNW5 | 0.99014 | 0.92945 | -0.060685 |  | 0.93 | 1.05 | 0.031366 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | MARMTNW5 | 0.99014 | 0.92945 | -0.060685 |  | 0.93 | 1.05 | 0.041888 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | MARMTNW5 | 0.99014 | 0.92945 | -0.060685 |  | 0.93 | 1.05 | 0.038797 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | MARMTNW5 | 0.99014 | 0.92945 | -0.060685 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | MARMTNW5 | 0.99014 | 0.92945 | -0.060685 |  | 0.93 | 1.05 | 0.067346 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | MARMTNW5 | 0.99014 | 0.92945 | -0.060685 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | MARMTNW5 | 0.99014 | 0.92945 | -0.060685 |  | 0.93 | 1.05 | 0.030851 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | MARMTNW5 | 0.99014 | 0.92945 | -0.060685 |  | 0.93 | 1.05 | 0.032161 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | MARMTNW5 | 0.99014 | 0.92945 | -0.060685 |  | 0.93 | 1.05 | 0.04067 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | MARMTNW5 | 0.99014 | 0.92945 | -0.060685 |  | 0.93 | 1.05 | 0.040569 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | MARMTNW5 | 0.99014 | 0.92945 | -0.060685 |  | 0.93 | 1.05 | 0.03086 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | MARMTNW5 | 0.99014 | 0.92945 | -0.060685 |  | 0.93 | 1.05 | 0.033223 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | MARMTNW5 | 0.99014 | 0.92945 | -0.060685 |  | 0.93 | 1.05 | 0.033733 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | MARMTNW5 | 0.99047 | 0.92243 | -0.068033 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | MARMTNW5 | 0.99047 | 0.92243 | -0.068033 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | MARMTNW5 | 0.99047 | 0.92243 | -0.068033 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | MARMTNW5 | 0.99047 | 0.92243 | -0.068033 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | MARMTNW5 | 0.99047 | 0.92243 | -0.068033 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | MARMTNW5 | 0.99047 | 0.92243 | -0.068033 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | MARMTNW5 | 0.99047 | 0.92243 | -0.068033 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | MARMTNW5 | 0.99047 | 0.92243 | -0.068033 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | MARMTNW5 | 0.99047 | 0.92243 | -0.068033 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | MARMTNW5 | 0.99047 | 0.92243 | -0.068033 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | MARMTNW5 | 0.99047 | 0.92243 | -0.068033 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | MARMTNW5 | 0.99047 | 0.92243 | -0.068033 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | MARMTNW5 | 0.99047 | 0.92243 | -0.068033 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | MARMTNW5 | 0.99047 | 0.92243 | -0.068033 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | MARMTNW5 | 0.99047 | 0.92243 | -0.068033 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | MARMTNW5 | 0.99047 | 0.92243 | -0.068033 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | MARMTNW5 | 0.99047 | 0.92243 | -0.068033 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | MARMTNW5 | 0.99047 | 0.92243 | -0.068033 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | MARMTNW5 | 0.99047 | 0.92243 | -0.068033 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | MARMTNW5 | 0.99047 | 0.92243 | -0.068033 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | MARMTNW5 | 0.99047 | 0.92243 | -0.068033 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | MARMTNW5 | 0.99047 | 0.92243 | -0.068033 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | MARMTNW5 | 0.99047 | 0.92243 | -0.068033 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | MARMTNW5 | 0.99047 | 0.92243 | -0.068033 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | MARMTNW5 | 0.99047 | 0.92243 | -0.068033 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | MARTCIT5 | 0.9899 | 0.9138 | -0.076094 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | MARTCIT5 | 0.9899 | 0.9138 | -0.076094 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | MARTCIT5 | 0.9899 | 0.9138 | -0.076094 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | MARTCIT5 | 0.9899 | 0.9138 | -0.076094 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | MARTCIT5 | 0.9899 | 0.9138 | -0.076094 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | MARTCIT5 | 0.9899 | 0.9138 | -0.076094 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | MARTCIT5 | 0.9899 | 0.9138 | -0.076094 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | MARTCIT5 | 0.9899 | 0.9138 | -0.076094 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | MARTCIT5 | 0.9899 | 0.9138 | -0.076094 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | MARTCIT5 | 0.9899 | 0.9138 | -0.076094 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | MARTCIT5 | 0.9899 | 0.9138 | -0.076094 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | MARTCIT5 | 0.9899 | 0.9138 | -0.076094 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | MARTCIT5 | 0.9899 | 0.9138 | -0.076094 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | MARTCIT5 | 0.9899 | 0.9138 | -0.076094 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | MARTCIT5 | 0.9899 | 0.9138 | -0.076094 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | MARTCIT5 | 0.9899 | 0.9138 | -0.076094 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | MARTCIT5 | 0.9899 | 0.9138 | -0.076094 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | MARTCIT5 | 0.9899 | 0.9138 | -0.076094 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | MARTCIT5 | 0.9899 | 0.9138 | -0.076094 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | MARTCIT5 | 0.9899 | 0.9138 | -0.076094 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | MARTCIT5 | 0.9899 | 0.9138 | -0.076094 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | MARTCIT5 | 0.9899 | 0.9138 | -0.076094 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | MARTCIT5 | 0.9899 | 0.9138 | -0.076094 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | MARTCIT5 | 0.9899 | 0.9138 | -0.076094 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | MARTCIT5 | 0.9899 | 0.9138 | -0.076094 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | MARTCTY5 | 0.9902 | 0.91671 | -0.073491 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | MARTCTY5 | 0.9902 | 0.91671 | -0.073491 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | MARTCTY5 | 0.9902 | 0.91671 | -0.073491 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | MARTCTY5 | 0.9902 | 0.91671 | -0.073491 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | MARTCTY5 | 0.9902 | 0.91671 | -0.073491 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | MARTCTY5 | 0.9902 | 0.91671 | -0.073491 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | MARTCTY5 | 0.9902 | 0.91671 | -0.073491 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | MARTCTY5 | 0.9902 | 0.91671 | -0.073491 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | MARTCTY5 | 0.9902 | 0.91671 | -0.073491 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | MARTCTY5 | 0.9902 | 0.91671 | -0.073491 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | MARTCTY5 | 0.9902 | 0.91671 | -0.073491 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | MARTCTY5 | 0.9902 | 0.91671 | -0.073491 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | MARTCTY5 | 0.9902 | 0.91671 | -0.073491 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | MARTCTY5 | 0.9902 | 0.91671 | -0.073491 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | MARTCTY5 | 0.9902 | 0.91671 | -0.073491 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | MARTCTY5 | 0.9902 | 0.91671 | -0.073491 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | MARTCTY5 | 0.9902 | 0.91671 | -0.073491 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | MARTCTY5 | 0.9902 | 0.91671 | -0.073491 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | MARTCTY5 | 0.9902 | 0.91671 | -0.073491 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | MARTCTY5 | 0.9902 | 0.91671 | -0.073491 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | MARTCTY5 | 0.9902 | 0.91671 | -0.073491 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | MARTCTY5 | 0.9902 | 0.91671 | -0.073491 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | MARTCTY5 | 0.9902 | 0.91671 | -0.073491 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | MARTCTY5 | 0.9902 | 0.91671 | -0.073491 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | MARTCTY5 | 0.9902 | 0.91671 | -0.073491 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | MCARBDE4 | 0.92612 | 0.89994 | -0.026183 |  | 0.92 | 1.05 | 0.038424 | Single 509752 INOLATP4 138 509790 CATOOSA4 138 1 | Add 57 MVAR switched shunt at GUAVA 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | MCARBDE4 | 0.93495 | 0.91016 | -0.024783 |  | 0.92 | 1.05 | 0.038424 | Single 509752 INOLATP4 138 510442 GUAVA4 138 1 | Add 57 MVAR switched shunt at GUAVA 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | MERRIAM5 | 0.98475 | 0.92228 | -0.062473 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | MERRIAM5 | 0.98475 | 0.92228 | -0.062473 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | MERRIAM5 | 0.98475 | 0.92228 | -0.062473 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | MERRIAM5 | 0.98475 | 0.92228 | -0.062473 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | MERRIAM5 | 0.98475 | 0.92228 | -0.062473 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | MERRIAM5 | 0.98475 | 0.92228 | -0.062473 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | MERRIAM5 | 0.98475 | 0.92228 | -0.062473 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | MERRIAM5 | 0.98475 | 0.92228 | -0.062473 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | MERRIAM5 | 0.98475 | 0.92228 | -0.062473 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | MERRIAM5 | 0.98475 | 0.92228 | -0.062473 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | MERRIAM5 | 0.98475 | 0.92228 | -0.062473 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | MERRIAM5 | 0.98475 | 0.92228 | -0.062473 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | MERRIAM5 | 0.98475 | 0.92228 | -0.062473 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | MERRIAM5 | 0.98475 | 0.92228 | -0.062473 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | MERRIAM5 | 0.98475 | 0.92228 | -0.062473 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | MERRIAM5 | 0.98475 | 0.92228 | -0.062473 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | MERRIAM5 | 0.98475 | 0.92228 | -0.062473 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | MERRIAM5 | 0.98475 | 0.92228 | -0.062473 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | MERRIAM5 | 0.98475 | 0.92228 | -0.062473 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | MERRIAM5 | 0.98475 | 0.92228 | -0.062473 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | MERRIAM5 | 0.98475 | 0.92228 | -0.062473 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | MERRIAM5 | 0.98475 | 0.92228 | -0.062473 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | MERRIAM5 | 0.98475 | 0.92228 | -0.062473 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | MERRIAM5 | 0.98475 | 0.92228 | -0.062473 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | MERRIAM5 | 0.98475 | 0.92228 | -0.062473 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | MERRIAM_CAP5 | 0.98583 | 0.92329 | -0.062542 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | MERRIAM_CAP5 | 0.98583 | 0.92329 | -0.062542 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | MERRIAM_CAP5 | 0.98583 | 0.92329 | -0.062542 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | MERRIAM_CAP5 | 0.98583 | 0.92329 | -0.062542 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | MERRIAM_CAP5 | 0.98583 | 0.92329 | -0.062542 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | MERRIAM_CAP5 | 0.98583 | 0.92329 | -0.062542 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | MERRIAM_CAP5 | 0.98583 | 0.92329 | -0.062542 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | MERRIAM_CAP5 | 0.98583 | 0.92329 | -0.062542 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | MERRIAM_CAP5 | 0.98583 | 0.92329 | -0.062542 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | MERRIAM_CAP5 | 0.98583 | 0.92329 | -0.062542 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | MERRIAM_CAP5 | 0.98583 | 0.92329 | -0.062542 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | MERRIAM_CAP5 | 0.98583 | 0.92329 | -0.062542 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | MERRIAM_CAP5 | 0.98583 | 0.92329 | -0.062542 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | MERRIAM_CAP5 | 0.98583 | 0.92329 | -0.062542 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | MERRIAM_CAP5 | 0.98583 | 0.92329 | -0.062542 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | MERRIAM_CAP5 | 0.98583 | 0.92329 | -0.062542 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | MERRIAM_CAP5 | 0.98583 | 0.92329 | -0.062542 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | MERRIAM_CAP5 | 0.98583 | 0.92329 | -0.062542 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | MERRIAM_CAP5 | 0.98583 | 0.92329 | -0.062542 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | MERRIAM_CAP5 | 0.98583 | 0.92329 | -0.062542 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | MERRIAM_CAP5 | 0.98583 | 0.92329 | -0.062542 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | MERRIAM_CAP5 | 0.98583 | 0.92329 | -0.062542 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | MERRIAM_CAP5 | 0.98583 | 0.92329 | -0.062542 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | MERRIAM_CAP5 | 0.98583 | 0.92329 | -0.062542 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | MERRIAM_CAP5 | 0.98583 | 0.92329 | -0.062542 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | MIDLAND6 | 0.98579 | 0.94982 | -0.035964 |  | 0.95 | 1.05 | 0.036307 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | MIDLAND6 | 0.98579 | 0.94982 | -0.035964 |  | 0.95 | 1.05 | 0.052743 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | MIDLAND6 | 0.98579 | 0.94982 | -0.035964 |  | 0.95 | 1.05 | 0.039345 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | MIDLAND6 | 0.98579 | 0.94982 | -0.035964 |  | 0.95 | 1.05 | 0.031366 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | MIDLAND6 | 0.98579 | 0.94982 | -0.035964 |  | 0.95 | 1.05 | 0.041888 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | MIDLAND6 | 0.98579 | 0.94982 | -0.035964 |  | 0.95 | 1.05 | 0.038797 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | MIDLAND6 | 0.98579 | 0.94982 | -0.035964 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | MIDLAND6 | 0.98579 | 0.94982 | -0.035964 |  | 0.95 | 1.05 | 0.067346 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | MIDLAND6 | 0.98579 | 0.94982 | -0.035964 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | MIDLAND6 | 0.98579 | 0.94982 | -0.035964 |  | 0.95 | 1.05 | 0.030851 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | MIDLAND6 | 0.98579 | 0.94982 | -0.035964 |  | 0.95 | 1.05 | 0.032161 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | MIDLAND6 | 0.98579 | 0.94982 | -0.035964 |  | 0.95 | 1.05 | 0.04067 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | MIDLAND6 | 0.98579 | 0.94982 | -0.035964 |  | 0.95 | 1.05 | 0.040569 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | MIDLAND6 | 0.98579 | 0.94982 | -0.035964 |  | 0.95 | 1.05 | 0.03086 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | MIDLAND6 | 0.98579 | 0.94982 | -0.035964 |  | 0.95 | 1.05 | 0.033223 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | MIDLAND6 | 0.98579 | 0.94982 | -0.035964 |  | 0.95 | 1.05 | 0.033733 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | MIDLAND6 | 0.98936 | 0.94979 | -0.039563 |  | 0.95 | 1.05 | 0.036307 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | MIDLAND6 | 0.98936 | 0.94979 | -0.039563 |  | 0.95 | 1.05 | 0.052743 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | MIDLAND6 | 0.98936 | 0.94979 | -0.039563 |  | 0.95 | 1.05 | 0.039345 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | MIDLAND6 | 0.98936 | 0.94979 | -0.039563 |  | 0.95 | 1.05 | 0.031366 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | MIDLAND6 | 0.98936 | 0.94979 | -0.039563 |  | 0.95 | 1.05 | 0.041888 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | MIDLAND6 | 0.98936 | 0.94979 | -0.039563 |  | 0.95 | 1.05 | 0.038797 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | MIDLAND6 | 0.98936 | 0.94979 | -0.039563 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | MIDLAND6 | 0.98936 | 0.94979 | -0.039563 |  | 0.95 | 1.05 | 0.067346 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | MIDLAND6 | 0.98936 | 0.94979 | -0.039563 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | MIDLAND6 | 0.98936 | 0.94979 | -0.039563 |  | 0.95 | 1.05 | 0.030851 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | MIDLAND6 | 0.98936 | 0.94979 | -0.039563 |  | 0.95 | 1.05 | 0.032161 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | MIDLAND6 | 0.98936 | 0.94979 | -0.039563 |  | 0.95 | 1.05 | 0.04067 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | MIDLAND6 | 0.98936 | 0.94979 | -0.039563 |  | 0.95 | 1.05 | 0.040569 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | MIDLAND6 | 0.98936 | 0.94979 | -0.039563 |  | 0.95 | 1.05 | 0.03086 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | MIDLAND6 | 0.98936 | 0.94979 | -0.039563 |  | 0.95 | 1.05 | 0.033223 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | MIDLAND6 | 0.98936 | 0.94979 | -0.039563 |  | 0.95 | 1.05 | 0.033733 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | MISNJCT5 | 0.97972 | 0.91382 | -0.065898 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | MISNJCT5 | 0.97972 | 0.91382 | -0.065898 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | MISNJCT5 | 0.97972 | 0.91382 | -0.065898 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | MISNJCT5 | 0.97972 | 0.91382 | -0.065898 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | MISNJCT5 | 0.97972 | 0.91382 | -0.065898 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | MISNJCT5 | 0.97972 | 0.91382 | -0.065898 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | MISNJCT5 | 0.97972 | 0.91382 | -0.065898 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | MISNJCT5 | 0.97972 | 0.91382 | -0.065898 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | MISNJCT5 | 0.97972 | 0.91382 | -0.065898 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | MISNJCT5 | 0.97972 | 0.91382 | -0.065898 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | MISNJCT5 | 0.97972 | 0.91382 | -0.065898 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | MISNJCT5 | 0.97972 | 0.91382 | -0.065898 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | MISNJCT5 | 0.97972 | 0.91382 | -0.065898 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | MISNJCT5 | 0.97972 | 0.91382 | -0.065898 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | MISNJCT5 | 0.97972 | 0.91382 | -0.065898 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | MISNJCT5 | 0.97972 | 0.91382 | -0.065898 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | MISNJCT5 | 0.97972 | 0.91382 | -0.065898 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | MISNJCT5 | 0.97972 | 0.91382 | -0.065898 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | MISNJCT5 | 0.97972 | 0.91382 | -0.065898 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | MISNJCT5 | 0.97972 | 0.91382 | -0.065898 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | MISNJCT5 | 0.97972 | 0.91382 | -0.065898 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | MISNJCT5 | 0.97972 | 0.91382 | -0.065898 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | MISNJCT5 | 0.97972 | 0.91382 | -0.065898 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | MISNJCT5 | 0.97972 | 0.91382 | -0.065898 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | MISNJCT5 | 0.97972 | 0.91382 | -0.065898 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | MON383 5 | 0.96535 | 0.92227 | -0.043073 |  | 0.925 | 1.05 | 0.033596 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | MON383 5 | 0.96535 | 0.92227 | -0.043073 |  | 0.925 | 1.05 | 0.040193 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | MON383 5 | 0.96535 | 0.92227 | -0.043073 |  | 0.925 | 1.05 | 0.088122 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | MON383 5 | 0.96535 | 0.92227 | -0.043073 |  | 0.925 | 1.05 | 0.074664 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | MON383 5 | 0.96535 | 0.92227 | -0.043073 |  | 0.925 | 1.05 | 0.068051 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | MON383 5 | 0.96535 | 0.92227 | -0.043073 |  | 0.925 | 1.05 | 0.035565 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | MON383 5 | 0.96535 | 0.92227 | -0.043073 |  | 0.925 | 1.05 | 0.033904 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | MON383 5 | 0.96535 | 0.92227 | -0.043073 |  | 0.925 | 1.05 | 0.16366 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | MON383 5 | 0.96535 | 0.92227 | -0.043073 |  | 0.925 | 1.05 | 0.045569 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | MON383 5 | 0.96535 | 0.92227 | -0.043073 |  | 0.925 | 1.05 | 0.13458 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | MON383 5 | 0.96535 | 0.92227 | -0.043073 |  | 0.925 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | MON383 5 | 0.96535 | 0.92227 | -0.043073 |  | 0.925 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | MON383 5 | 0.96535 | 0.92227 | -0.043073 |  | 0.925 | 1.05 | 0.068426 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | MON383 5 | 0.96535 | 0.92227 | -0.043073 |  | 0.925 | 1.05 | 0.035223 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | MON383 5 | 0.96535 | 0.92227 | -0.043073 |  | 0.925 | 1.05 | 0.034504 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | MON383 5 | 0.96565 | 0.92395 | -0.041696 |  | 0.925 | 1.05 | 0.040193 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | MON383 5 | 0.96565 | 0.92395 | -0.041696 |  | 0.925 | 1.05 | 0.088122 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | MON383 5 | 0.96565 | 0.92395 | -0.041696 |  | 0.925 | 1.05 | 0.074664 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | MON383 5 | 0.96565 | 0.92395 | -0.041696 |  | 0.925 | 1.05 | 0.068051 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | MON383 5 | 0.96565 | 0.92395 | -0.041696 |  | 0.925 | 1.05 | 0.034774 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | MON383 5 | 0.96565 | 0.92395 | -0.041696 |  | 0.925 | 1.05 | 0.033904 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | MON383 5 | 0.96565 | 0.92395 | -0.041696 |  | 0.925 | 1.05 | 0.16366 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | MON383 5 | 0.96565 | 0.92395 | -0.041696 |  | 0.925 | 1.05 | 0.045569 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | MON383 5 | 0.96565 | 0.92395 | -0.041696 |  | 0.925 | 1.05 | 0.13458 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | MON383 5 | 0.96565 | 0.92395 | -0.041696 |  | 0.925 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | MON383 5 | 0.96565 | 0.92395 | -0.041696 |  | 0.925 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | MON383 5 | 0.96565 | 0.92395 | -0.041696 |  | 0.925 | 1.05 | 0.068426 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | MON383 5 | 0.96565 | 0.92395 | -0.041696 |  | 0.925 | 1.05 | 0.035223 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | MON383 5 | 0.96565 | 0.92395 | -0.041696 |  | 0.925 | 1.05 | 0.034504 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | MON383 5 | 0.96602 | 0.92272 | -0.043295 |  | 0.925 | 1.05 | 0.033596 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.2 MVAR switched shunt at GROVE 5 161 kV; Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | MON383 5 | 0.96602 | 0.92272 | -0.043295 |  | 0.925 | 1.05 | 0.088122 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.2 MVAR switched shunt at GROVE 5 161 kV; Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | MON383 5 | 0.96602 | 0.92272 | -0.043295 |  | 0.925 | 1.05 | 0.030897 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.2 MVAR switched shunt at GROVE 5 161 kV; Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | MON383 5 | 0.96602 | 0.92272 | -0.043295 |  | 0.925 | 1.05 | 0.038719 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.2 MVAR switched shunt at GROVE 5 161 kV; Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | MON383 5 | 0.96602 | 0.92272 | -0.043295 |  | 0.925 | 1.05 | 0.035565 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.2 MVAR switched shunt at GROVE 5 161 kV; Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | MON383 5 | 0.96602 | 0.92272 | -0.043295 |  | 0.925 | 1.05 | 0.16366 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.2 MVAR switched shunt at GROVE 5 161 kV; Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | MON383 5 | 0.96602 | 0.92272 | -0.043295 |  | 0.925 | 1.05 | 0.038589 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.2 MVAR switched shunt at GROVE 5 161 kV; Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | MON383 5 | 0.96602 | 0.92272 | -0.043295 |  | 0.925 | 1.05 | 0.034208 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.2 MVAR switched shunt at GROVE 5 161 kV; Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | MON383 5 | 0.96527 | 0.9228 | -0.042471 |  | 0.925 | 1.05 | 0.033596 | P23:345:AECI:7JASPER:1182::: | Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | MON383 5 | 0.96527 | 0.9228 | -0.042471 |  | 0.925 | 1.05 | 0.056051 | P23:345:AECI:7JASPER:1182::: | Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | MON383 5 | 0.96527 | 0.9228 | -0.042471 |  | 0.925 | 1.05 | 0.030897 | P23:345:AECI:7JASPER:1182::: | Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | MON383 5 | 0.96527 | 0.9228 | -0.042471 |  | 0.925 | 1.05 | 0.038719 | P23:345:AECI:7JASPER:1182::: | Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | MON383 5 | 0.96527 | 0.9228 | -0.042471 |  | 0.925 | 1.05 | 0.035565 | P23:345:AECI:7JASPER:1182::: | Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | MON383 5 | 0.96527 | 0.9228 | -0.042471 |  | 0.925 | 1.05 | 0.082596 | P23:345:AECI:7JASPER:1182::: | Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | MON383 5 | 0.96527 | 0.9228 | -0.042471 |  | 0.925 | 1.05 | 0.038589 | P23:345:AECI:7JASPER:1182::: | Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | MON383 5 | 0.96527 | 0.9228 | -0.042471 |  | 0.925 | 1.05 | 0.034208 | P23:345:AECI:7JASPER:1182::: | Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | MONTGOM4 | 0.96512 | 0.91927 | -0.045852 |  | 0.93 | 1.05 | 0.091967 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | MONTGOM4 | 0.96512 | 0.91927 | -0.045852 |  | 0.93 | 1.05 | 0.033356 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | MONTGOM4 | 0.96512 | 0.91927 | -0.045852 |  | 0.93 | 1.05 | 0.044346 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | MONTGOM4 | 0.96512 | 0.91927 | -0.045852 |  | 0.93 | 1.05 | 0.058536 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | MONTGOM4 | 0.96512 | 0.91927 | -0.045852 |  | 0.93 | 1.05 | 0.059327 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | MONTGOM4 | 0.96512 | 0.91927 | -0.045852 |  | 0.93 | 1.05 | 0.041874 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | MONTGOM4 | 0.96512 | 0.91927 | -0.045852 |  | 0.93 | 1.05 | 0.046192 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | MONTGOM4 | 0.96512 | 0.91927 | -0.045852 |  | 0.93 | 1.05 | 0.12754 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | MONTGOM4 | 0.96512 | 0.91927 | -0.045852 |  | 0.93 | 1.05 | 0.047018 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | MONTGOM4 | 0.96512 | 0.91927 | -0.045852 |  | 0.93 | 1.05 | 0.056662 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | MONTGOM4 | 0.96512 | 0.91927 | -0.045852 |  | 0.93 | 1.05 | 0.056662 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | MONTGOM4 | 0.96512 | 0.91927 | -0.045852 |  | 0.93 | 1.05 | 0.056727 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | MONTGOM4 | 0.96512 | 0.91927 | -0.045852 |  | 0.93 | 1.05 | 0.074186 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | MONTGOM4 | 0.96512 | 0.91927 | -0.045852 |  | 0.93 | 1.05 | 0.040839 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | MONTGOM4 | 0.96512 | 0.91927 | -0.045852 |  | 0.93 | 1.05 | 0.03863 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | MONTGOM4 | 0.96512 | 0.91927 | -0.045852 |  | 0.93 | 1.05 | 0.042285 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | MONTGOM4 | 0.96512 | 0.91927 | -0.045852 |  | 0.93 | 1.05 | 0.042285 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | MONTGOM4 | 0.96512 | 0.91927 | -0.045852 |  | 0.93 | 1.05 | 0.050204 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | MONTGOM4 | 0.96512 | 0.91927 | -0.045852 |  | 0.93 | 1.05 | 0.058005 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | MONTGOM4 | 0.96512 | 0.91927 | -0.045852 |  | 0.93 | 1.05 | 0.041735 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | MONTGOM4 | 0.96512 | 0.91927 | -0.045852 |  | 0.93 | 1.05 | 0.057076 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | MONTGOM4 | 0.96512 | 0.91927 | -0.045852 |  | 0.93 | 1.05 | 0.050111 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | MONTGOM4 | 0.96512 | 0.91927 | -0.045852 |  | 0.93 | 1.05 | 0.06491 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | MONTGOM4 | 0.96512 | 0.91927 | -0.045852 |  | 0.93 | 1.05 | 0.051051 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | MONTGOM4 | 0.96512 | 0.91927 | -0.045852 |  | 0.93 | 1.05 | 0.036279 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | MONTGOM4 | 0.97374 | 0.92557 | -0.048165 |  | 0.93 | 1.05 | 0.035768 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | MONTGOM4 | 0.97374 | 0.92557 | -0.048165 |  | 0.93 | 1.05 | 0.088718 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | MONTGOM4 | 0.97374 | 0.92557 | -0.048165 |  | 0.93 | 1.05 | 0.031473 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | MONTGOM4 | 0.97374 | 0.92557 | -0.048165 |  | 0.93 | 1.05 | 0.034941 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | MONTGOM4 | 0.97374 | 0.92557 | -0.048165 |  | 0.93 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | MONTGOM4 | 0.97374 | 0.92557 | -0.048165 |  | 0.93 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | MONTGOM4 | 0.97374 | 0.92557 | -0.048165 |  | 0.93 | 1.05 | 0.049224 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | MONTGOM4 | 0.97374 | 0.92557 | -0.048165 |  | 0.93 | 1.05 | 0.038981 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | MONTGOM4 | 0.97374 | 0.92557 | -0.048165 |  | 0.93 | 1.05 | 0.040399 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | MONTGOM4 | 0.97374 | 0.92557 | -0.048165 |  | 0.93 | 1.05 | 0.031912 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | MONTGOM4 | 0.97374 | 0.92557 | -0.048165 |  | 0.93 | 1.05 | 0.034127 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | MONTGOM4 | 0.97374 | 0.92557 | -0.048165 |  | 0.93 | 1.05 | 0.047318 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | MONTGOM4 | 0.96753 | 0.92029 | -0.04724 |  | 0.93 | 1.05 | 0.040439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | MONTGOM4 | 0.96753 | 0.92029 | -0.04724 |  | 0.93 | 1.05 | 0.034853 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | MONTGOM4 | 0.96753 | 0.92029 | -0.04724 |  | 0.93 | 1.05 | 0.046783 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | MONTGOM4 | 0.96753 | 0.92029 | -0.04724 |  | 0.93 | 1.05 | 0.047615 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | MONTGOM4 | 0.96753 | 0.92029 | -0.04724 |  | 0.93 | 1.05 | 0.034938 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | MONTGOM4 | 0.96753 | 0.92029 | -0.04724 |  | 0.93 | 1.05 | 0.037875 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | MONTGOM4 | 0.96753 | 0.92029 | -0.04724 |  | 0.93 | 1.05 | 0.044022 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | MONTGOM4 | 0.96753 | 0.92029 | -0.04724 |  | 0.93 | 1.05 | 0.030552 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | MONTGOM4 | 0.96753 | 0.92029 | -0.04724 |  | 0.93 | 1.05 | 0.038531 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | MONTGOM4 | 0.96753 | 0.92029 | -0.04724 |  | 0.93 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | MONTGOM4 | 0.96753 | 0.92029 | -0.04724 |  | 0.93 | 1.05 | 0.062491 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | MONTGOM4 | 0.96753 | 0.92029 | -0.04724 |  | 0.93 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | MONTGOM4 | 0.96753 | 0.92029 | -0.04724 |  | 0.93 | 1.05 | 0.038129 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | MONTGOM4 | 0.96753 | 0.92029 | -0.04724 |  | 0.93 | 1.05 | 0.038066 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | MONTGOM4 | 0.96753 | 0.92029 | -0.04724 |  | 0.93 | 1.05 | 0.034955 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | MONTGOM4 | 0.96753 | 0.92029 | -0.04724 |  | 0.93 | 1.05 | 0.06281 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | MONTGOM4 | 0.96753 | 0.92029 | -0.04724 |  | 0.93 | 1.05 | 0.045309 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | MONTGOM4 | 0.96753 | 0.92029 | -0.04724 |  | 0.93 | 1.05 | 0.035805 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | MONTGOM4 | 0.96753 | 0.92029 | -0.04724 |  | 0.93 | 1.05 | 0.032364 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | MONTGOM4 | 0.96753 | 0.92029 | -0.04724 |  | 0.93 | 1.05 | 0.031815 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | MONTGOM4 | 0.96753 | 0.92029 | -0.04724 |  | 0.93 | 1.05 | 0.033886 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | MONTGOM4 | 0.96753 | 0.92029 | -0.04724 |  | 0.93 | 1.05 | 0.035554 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | MONTGOM4 | 0.97228 | 0.91392 | -0.058366 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | MONTGOM4 | 0.97228 | 0.91392 | -0.058366 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | MONTGOM4 | 0.97228 | 0.91392 | -0.058366 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | MONTGOM4 | 0.97228 | 0.91392 | -0.058366 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | MONTGOM4 | 0.97228 | 0.91392 | -0.058366 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | MONTGOM4 | 0.97228 | 0.91392 | -0.058366 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | MONTGOM4 | 0.97228 | 0.91392 | -0.058366 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | MONTGOM4 | 0.97228 | 0.91392 | -0.058366 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | MONTGOM4 | 0.97228 | 0.91392 | -0.058366 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | MONTGOM4 | 0.97228 | 0.91392 | -0.058366 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | MONTGOM4 | 0.97228 | 0.91392 | -0.058366 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | MONTGOM4 | 0.97228 | 0.91392 | -0.058366 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | MONTGOM4 | 0.97228 | 0.91392 | -0.058366 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | MONTGOM4 | 0.97228 | 0.91392 | -0.058366 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | MONTGOM4 | 0.97228 | 0.91392 | -0.058366 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | MONTGOM4 | 0.97228 | 0.91392 | -0.058366 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | MONTGOM4 | 0.97228 | 0.91392 | -0.058366 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | MONTGOM4 | 0.97228 | 0.91392 | -0.058366 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | MONTGOM4 | 0.97228 | 0.91392 | -0.058366 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | MONTGOM4 | 0.97228 | 0.91392 | -0.058366 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | MONTGOM4 | 0.97228 | 0.91392 | -0.058366 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | MONTGOM4 | 0.97228 | 0.91392 | -0.058366 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | MONTGOM4 | 0.97228 | 0.91392 | -0.058366 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | MONTGOM4 | 0.97228 | 0.91392 | -0.058366 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | MONTGOM4 | 0.97228 | 0.91392 | -0.058366 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | MOONLIT3 | 0.96959 | 0.92908 | -0.0405 |  | 0.93 | 1.05 | 0.036307 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | MOONLIT3 | 0.96959 | 0.92908 | -0.0405 |  | 0.93 | 1.05 | 0.052743 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | MOONLIT3 | 0.96959 | 0.92908 | -0.0405 |  | 0.93 | 1.05 | 0.039345 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | MOONLIT3 | 0.96959 | 0.92908 | -0.0405 |  | 0.93 | 1.05 | 0.031366 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | MOONLIT3 | 0.96959 | 0.92908 | -0.0405 |  | 0.93 | 1.05 | 0.041888 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | MOONLIT3 | 0.96959 | 0.92908 | -0.0405 |  | 0.93 | 1.05 | 0.038797 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | MOONLIT3 | 0.96959 | 0.92908 | -0.0405 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | MOONLIT3 | 0.96959 | 0.92908 | -0.0405 |  | 0.93 | 1.05 | 0.067346 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | MOONLIT3 | 0.96959 | 0.92908 | -0.0405 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | MOONLIT3 | 0.96959 | 0.92908 | -0.0405 |  | 0.93 | 1.05 | 0.030851 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | MOONLIT3 | 0.96959 | 0.92908 | -0.0405 |  | 0.93 | 1.05 | 0.032161 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | MOONLIT3 | 0.96959 | 0.92908 | -0.0405 |  | 0.93 | 1.05 | 0.04067 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | MOONLIT3 | 0.96959 | 0.92908 | -0.0405 |  | 0.93 | 1.05 | 0.040569 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | MOONLIT3 | 0.96959 | 0.92908 | -0.0405 |  | 0.93 | 1.05 | 0.03086 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | MOONLIT3 | 0.96959 | 0.92908 | -0.0405 |  | 0.93 | 1.05 | 0.033223 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | MOONLIT3 | 0.96959 | 0.92908 | -0.0405 |  | 0.93 | 1.05 | 0.033733 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | MOONLIT3 | 0.98468 | 0.92134 | -0.063347 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | MOONLIT3 | 0.98468 | 0.92134 | -0.063347 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | MOONLIT3 | 0.98468 | 0.92134 | -0.063347 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | MOONLIT3 | 0.98468 | 0.92134 | -0.063347 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | MOONLIT3 | 0.98468 | 0.92134 | -0.063347 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | MOONLIT3 | 0.98468 | 0.92134 | -0.063347 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | MOONLIT3 | 0.98468 | 0.92134 | -0.063347 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | MOONLIT3 | 0.98468 | 0.92134 | -0.063347 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | MOONLIT3 | 0.98468 | 0.92134 | -0.063347 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | MOONLIT3 | 0.98468 | 0.92134 | -0.063347 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | MOONLIT3 | 0.98468 | 0.92134 | -0.063347 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | MOONLIT3 | 0.98468 | 0.92134 | -0.063347 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | MOONLIT3 | 0.98468 | 0.92134 | -0.063347 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | MOONLIT3 | 0.98468 | 0.92134 | -0.063347 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | MOONLIT3 | 0.98468 | 0.92134 | -0.063347 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | MOONLIT3 | 0.98468 | 0.92134 | -0.063347 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | MOONLIT3 | 0.98468 | 0.92134 | -0.063347 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | MOONLIT3 | 0.98468 | 0.92134 | -0.063347 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | MOONLIT3 | 0.98468 | 0.92134 | -0.063347 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | MOONLIT3 | 0.98468 | 0.92134 | -0.063347 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | MOONLIT3 | 0.98468 | 0.92134 | -0.063347 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | MOONLIT3 | 0.98468 | 0.92134 | -0.063347 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | MOONLIT3 | 0.98468 | 0.92134 | -0.063347 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | MOONLIT3 | 0.98468 | 0.92134 | -0.063347 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | MOONLIT3 | 0.98468 | 0.92134 | -0.063347 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | MOONLT 5 | 0.9956 | 0.91947 | -0.076135 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | MOONLT 5 | 0.9956 | 0.91947 | -0.076135 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | MOONLT 5 | 0.9956 | 0.91947 | -0.076135 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | MOONLT 5 | 0.9956 | 0.91947 | -0.076135 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | MOONLT 5 | 0.9956 | 0.91947 | -0.076135 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | MOONLT 5 | 0.9956 | 0.91947 | -0.076135 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | MOONLT 5 | 0.9956 | 0.91947 | -0.076135 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | MOONLT 5 | 0.9956 | 0.91947 | -0.076135 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | MOONLT 5 | 0.9956 | 0.91947 | -0.076135 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | MOONLT 5 | 0.9956 | 0.91947 | -0.076135 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | MOONLT 5 | 0.9956 | 0.91947 | -0.076135 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | MOONLT 5 | 0.9956 | 0.91947 | -0.076135 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | MOONLT 5 | 0.9956 | 0.91947 | -0.076135 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | MOONLT 5 | 0.9956 | 0.91947 | -0.076135 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | MOONLT 5 | 0.9956 | 0.91947 | -0.076135 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | MOONLT 5 | 0.9956 | 0.91947 | -0.076135 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | MOONLT 5 | 0.9956 | 0.91947 | -0.076135 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | MOONLT 5 | 0.9956 | 0.91947 | -0.076135 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | MOONLT 5 | 0.9956 | 0.91947 | -0.076135 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | MOONLT 5 | 0.9956 | 0.91947 | -0.076135 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | MOONLT 5 | 0.9956 | 0.91947 | -0.076135 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | MOONLT 5 | 0.9956 | 0.91947 | -0.076135 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | MOONLT 5 | 0.9956 | 0.91947 | -0.076135 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | MOONLT 5 | 0.9956 | 0.91947 | -0.076135 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | MOONLT 5 | 0.9956 | 0.91947 | -0.076135 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | MORRIS 7 | 1.0018 | 0.94767 | -0.054174 |  | 0.95 | 1.05 | 0.039728 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | MORRIS 7 | 1.0018 | 0.94767 | -0.054174 |  | 0.95 | 1.05 | 0.040762 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | MORRIS 7 | 1.0018 | 0.94767 | -0.054174 |  | 0.95 | 1.05 | 0.030778 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | MORRIS 7 | 1.0018 | 0.94767 | -0.054174 |  | 0.95 | 1.05 | 0.034227 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | MORRIS 7 | 1.0018 | 0.94767 | -0.054174 |  | 0.95 | 1.05 | 0.037164 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | MORRIS 7 | 1.0018 | 0.94767 | -0.054174 |  | 0.95 | 1.05 | 0.031937 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | MORRIS 7 | 1.0018 | 0.94767 | -0.054174 |  | 0.95 | 1.05 | 0.03782 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | MORRIS 7 | 1.0018 | 0.94767 | -0.054174 |  | 0.95 | 1.05 | 0.036407 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | MORRIS 7 | 1.0018 | 0.94767 | -0.054174 |  | 0.95 | 1.05 | 0.053181 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | MORRIS 7 | 1.0018 | 0.94767 | -0.054174 |  | 0.95 | 1.05 | 0.036407 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | MORRIS 7 | 1.0018 | 0.94767 | -0.054174 |  | 0.95 | 1.05 | 0.037418 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | MORRIS 7 | 1.0018 | 0.94767 | -0.054174 |  | 0.95 | 1.05 | 0.037355 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | MORRIS 7 | 1.0018 | 0.94767 | -0.054174 |  | 0.95 | 1.05 | 0.032533 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | MORRIS 7 | 1.0018 | 0.94767 | -0.054174 |  | 0.95 | 1.05 | 0.031326 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | MORRIS 7 | 1.0018 | 0.94767 | -0.054174 |  | 0.95 | 1.05 | 0.035094 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | MORRIS 7 | 1.0018 | 0.94767 | -0.054174 |  | 0.95 | 1.05 | 0.031652 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | MORRIS 7 | 1.0018 | 0.94767 | -0.054174 |  | 0.95 | 1.05 | 0.031104 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | MORRIS 7 | 1.0018 | 0.94767 | -0.054174 |  | 0.95 | 1.05 | 0.033175 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | MORRIS 7 | 1.0018 | 0.94767 | -0.054174 |  | 0.95 | 1.05 | 0.034843 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | MORRIS 7 | 1.0048 | 0.94914 | -0.055679 |  | 0.95 | 1.05 | 0.03053 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | MORRIS 7 | 1.0048 | 0.94914 | -0.055679 |  | 0.95 | 1.05 | 0.044933 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | MORRIS 7 | 1.0048 | 0.94914 | -0.055679 |  | 0.95 | 1.05 | 0.047811 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | MORRIS 7 | 1.0048 | 0.94914 | -0.055679 |  | 0.95 | 1.05 | 0.09719 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | MORRIS 7 | 1.0048 | 0.94914 | -0.055679 |  | 0.95 | 1.05 | 0.069376 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | MORRIS 7 | 1.0048 | 0.94914 | -0.055679 |  | 0.95 | 1.05 | 0.04277 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | MORRIS 7 | 1.0048 | 0.94914 | -0.055679 |  | 0.95 | 1.05 | 0.071112 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | MORRIS 7 | 1.0048 | 0.94914 | -0.055679 |  | 0.95 | 1.05 | 0.039357 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | MORRIS 7 | 1.0048 | 0.94914 | -0.055679 |  | 0.95 | 1.05 | 0.04035 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | MORRIS 7 | 1.0048 | 0.94914 | -0.055679 |  | 0.95 | 1.05 | 0.052332 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | MORRIS 7 | 1.0048 | 0.94914 | -0.055679 |  | 0.95 | 1.05 | 0.045944 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | MORRIS 7 | 1.0048 | 0.94914 | -0.055679 |  | 0.95 | 1.05 | 0.038178 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | MORRIS 7 | 1.0048 | 0.94914 | -0.055679 |  | 0.95 | 1.05 | 0.13469 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | MORRIS 7 | 1.0048 | 0.94914 | -0.055679 |  | 0.95 | 1.05 | 0.03053 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | MORRIS 7 | 1.0048 | 0.94914 | -0.055679 |  | 0.95 | 1.05 | 0.038178 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | MORRIS 7 | 1.0048 | 0.94914 | -0.055679 |  | 0.95 | 1.05 | 0.037309 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | MORRIS 7 | 1.0048 | 0.94914 | -0.055679 |  | 0.95 | 1.05 | 0.040075 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | MORRIS 7 | 1.0048 | 0.94914 | -0.055679 |  | 0.95 | 1.05 | 0.053764 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | MORRIS 7 | 1.0048 | 0.94914 | -0.055679 |  | 0.95 | 1.05 | 0.071762 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | MORRIS 7 | 1.0048 | 0.94914 | -0.055679 |  | 0.95 | 1.05 | 0.047827 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | MORRIS 7 | 1.0048 | 0.94914 | -0.055679 |  | 0.95 | 1.05 | 0.047827 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | MORRIS 7 | 1.0048 | 0.94914 | -0.055679 |  | 0.95 | 1.05 | 0.070303 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | MORRIS 7 | 1.0048 | 0.94914 | -0.055679 |  | 0.95 | 1.05 | 0.040614 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | MORRIS 7 | 1.0048 | 0.94914 | -0.055679 |  | 0.95 | 1.05 | 0.039729 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | MORRIS 7 | 1.0048 | 0.94914 | -0.055679 |  | 0.95 | 1.05 | 0.049662 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | MORRIS 7 | 1.0048 | 0.94914 | -0.055679 |  | 0.95 | 1.05 | 0.042332 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | MORRIS 7 | 1.0048 | 0.94914 | -0.055679 |  | 0.95 | 1.05 | 0.048722 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | MORRIS 7 | 1.0048 | 0.94914 | -0.055679 |  | 0.95 | 1.05 | 0.038156 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | MORRIS 7 | 1.0048 | 0.94914 | -0.055679 |  | 0.95 | 1.05 | 0.036794 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | MORRIS 7 | 1.0033 | 0.94653 | -0.056783 |  | 0.95 | 1.05 | 0.036307 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | MORRIS 7 | 1.0033 | 0.94653 | -0.056783 |  | 0.95 | 1.05 | 0.052743 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | MORRIS 7 | 1.0033 | 0.94653 | -0.056783 |  | 0.95 | 1.05 | 0.039345 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | MORRIS 7 | 1.0033 | 0.94653 | -0.056783 |  | 0.95 | 1.05 | 0.031366 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | MORRIS 7 | 1.0033 | 0.94653 | -0.056783 |  | 0.95 | 1.05 | 0.041888 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | MORRIS 7 | 1.0033 | 0.94653 | -0.056783 |  | 0.95 | 1.05 | 0.038797 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | MORRIS 7 | 1.0033 | 0.94653 | -0.056783 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | MORRIS 7 | 1.0033 | 0.94653 | -0.056783 |  | 0.95 | 1.05 | 0.067346 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | MORRIS 7 | 1.0033 | 0.94653 | -0.056783 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | MORRIS 7 | 1.0033 | 0.94653 | -0.056783 |  | 0.95 | 1.05 | 0.030851 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | MORRIS 7 | 1.0033 | 0.94653 | -0.056783 |  | 0.95 | 1.05 | 0.032161 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | MORRIS 7 | 1.0033 | 0.94653 | -0.056783 |  | 0.95 | 1.05 | 0.04067 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | MORRIS 7 | 1.0033 | 0.94653 | -0.056783 |  | 0.95 | 1.05 | 0.040569 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | MORRIS 7 | 1.0033 | 0.94653 | -0.056783 |  | 0.95 | 1.05 | 0.03086 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | MORRIS 7 | 1.0033 | 0.94653 | -0.056783 |  | 0.95 | 1.05 | 0.033223 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | MORRIS 7 | 1.0033 | 0.94653 | -0.056783 |  | 0.95 | 1.05 | 0.033733 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | MOUND 2 | 0.99295 | 0.91881 | -0.07414 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | MOUND 2 | 0.99295 | 0.91881 | -0.07414 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | MOUND 2 | 0.99295 | 0.91881 | -0.07414 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | MOUND 2 | 0.99295 | 0.91881 | -0.07414 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | MOUND 2 | 0.99295 | 0.91881 | -0.07414 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | MOUND 2 | 0.99295 | 0.91881 | -0.07414 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | MOUND 2 | 0.99295 | 0.91881 | -0.07414 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | MOUND 2 | 0.99295 | 0.91881 | -0.07414 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | MOUND 2 | 0.99295 | 0.91881 | -0.07414 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | MOUND 2 | 0.99295 | 0.91881 | -0.07414 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | MOUND 2 | 0.99295 | 0.91881 | -0.07414 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | MOUND 2 | 0.99295 | 0.91881 | -0.07414 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | MOUND 2 | 0.99295 | 0.91881 | -0.07414 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | MOUND 2 | 0.99295 | 0.91881 | -0.07414 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | MOUND 2 | 0.99295 | 0.91881 | -0.07414 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | MOUND 2 | 0.99295 | 0.91881 | -0.07414 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | MOUND 2 | 0.99295 | 0.91881 | -0.07414 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | MOUND 2 | 0.99295 | 0.91881 | -0.07414 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | MOUND 2 | 0.99295 | 0.91881 | -0.07414 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | MOUND 2 | 0.99295 | 0.91881 | -0.07414 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | MOUND 2 | 0.99295 | 0.91881 | -0.07414 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | MOUND 2 | 0.99295 | 0.91881 | -0.07414 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | MOUND 2 | 0.99295 | 0.91881 | -0.07414 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | MOUND 2 | 0.99295 | 0.91881 | -0.07414 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | MOUND 2 | 0.99295 | 0.91881 | -0.07414 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | MOUND 4 | 0.97349 | 0.92626 | -0.047225 |  | 0.93 | 1.05 | 0.03053 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | MOUND 4 | 0.97349 | 0.92626 | -0.047225 |  | 0.93 | 1.05 | 0.044933 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | MOUND 4 | 0.97349 | 0.92626 | -0.047225 |  | 0.93 | 1.05 | 0.047811 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | MOUND 4 | 0.97349 | 0.92626 | -0.047225 |  | 0.93 | 1.05 | 0.09719 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | MOUND 4 | 0.97349 | 0.92626 | -0.047225 |  | 0.93 | 1.05 | 0.069376 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | MOUND 4 | 0.97349 | 0.92626 | -0.047225 |  | 0.93 | 1.05 | 0.04277 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | MOUND 4 | 0.97349 | 0.92626 | -0.047225 |  | 0.93 | 1.05 | 0.071112 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | MOUND 4 | 0.97349 | 0.92626 | -0.047225 |  | 0.93 | 1.05 | 0.039357 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | MOUND 4 | 0.97349 | 0.92626 | -0.047225 |  | 0.93 | 1.05 | 0.04035 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | MOUND 4 | 0.97349 | 0.92626 | -0.047225 |  | 0.93 | 1.05 | 0.052332 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | MOUND 4 | 0.97349 | 0.92626 | -0.047225 |  | 0.93 | 1.05 | 0.045944 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | MOUND 4 | 0.97349 | 0.92626 | -0.047225 |  | 0.93 | 1.05 | 0.038178 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | MOUND 4 | 0.97349 | 0.92626 | -0.047225 |  | 0.93 | 1.05 | 0.13469 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | MOUND 4 | 0.97349 | 0.92626 | -0.047225 |  | 0.93 | 1.05 | 0.03053 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | MOUND 4 | 0.97349 | 0.92626 | -0.047225 |  | 0.93 | 1.05 | 0.038178 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | MOUND 4 | 0.97349 | 0.92626 | -0.047225 |  | 0.93 | 1.05 | 0.037309 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | MOUND 4 | 0.97349 | 0.92626 | -0.047225 |  | 0.93 | 1.05 | 0.040075 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | MOUND 4 | 0.97349 | 0.92626 | -0.047225 |  | 0.93 | 1.05 | 0.053764 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | MOUND 4 | 0.97349 | 0.92626 | -0.047225 |  | 0.93 | 1.05 | 0.071762 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | MOUND 4 | 0.97349 | 0.92626 | -0.047225 |  | 0.93 | 1.05 | 0.047827 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | MOUND 4 | 0.97349 | 0.92626 | -0.047225 |  | 0.93 | 1.05 | 0.047827 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | MOUND 4 | 0.97349 | 0.92626 | -0.047225 |  | 0.93 | 1.05 | 0.070303 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | MOUND 4 | 0.97349 | 0.92626 | -0.047225 |  | 0.93 | 1.05 | 0.040614 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | MOUND 4 | 0.97349 | 0.92626 | -0.047225 |  | 0.93 | 1.05 | 0.039729 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | MOUND 4 | 0.97349 | 0.92626 | -0.047225 |  | 0.93 | 1.05 | 0.049662 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | MOUND 4 | 0.97349 | 0.92626 | -0.047225 |  | 0.93 | 1.05 | 0.042332 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | MOUND 4 | 0.97349 | 0.92626 | -0.047225 |  | 0.93 | 1.05 | 0.048722 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | MOUND 4 | 0.97349 | 0.92626 | -0.047225 |  | 0.93 | 1.05 | 0.038156 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | MOUND 4 | 0.97349 | 0.92626 | -0.047225 |  | 0.93 | 1.05 | 0.036794 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | MOUND 4 | 0.94924 | 0.89542 | -0.053817 |  | 0.93 | 1.05 | 0.044747 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | MOUND 4 | 0.94924 | 0.89542 | -0.053817 |  | 0.93 | 1.05 | 0.063323 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | MOUND 4 | 0.94924 | 0.89542 | -0.053817 |  | 0.93 | 1.05 | 0.043143 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | MOUND 4 | 0.94924 | 0.89542 | -0.053817 |  | 0.93 | 1.05 | 0.038771 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | MOUND 4 | 0.94924 | 0.89542 | -0.053817 |  | 0.93 | 1.05 | 0.038438 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | MOUND 4 | 0.94924 | 0.89542 | -0.053817 |  | 0.93 | 1.05 | 0.04552 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | MOUND 4 | 0.94924 | 0.89542 | -0.053817 |  | 0.93 | 1.05 | 0.03158 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | MOUND 4 | 0.94924 | 0.89542 | -0.053817 |  | 0.93 | 1.05 | 0.034131 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | MOUND 4 | 0.94924 | 0.89542 | -0.053817 |  | 0.93 | 1.05 | 0.042547 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | MOUND 4 | 0.94924 | 0.89542 | -0.053817 |  | 0.93 | 1.05 | 0.032964 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | MOUND 4 | 0.94924 | 0.89542 | -0.053817 |  | 0.93 | 1.05 | 0.041072 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | MOUND 4 | 0.94924 | 0.89542 | -0.053817 |  | 0.93 | 1.05 | 0.069811 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | MOUND 4 | 0.94924 | 0.89542 | -0.053817 |  | 0.93 | 1.05 | 0.041072 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | MOUND 4 | 0.94924 | 0.89542 | -0.053817 |  | 0.93 | 1.05 | 0.042352 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | MOUND 4 | 0.94924 | 0.89542 | -0.053817 |  | 0.93 | 1.05 | 0.041773 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | MOUND 4 | 0.94924 | 0.89542 | -0.053817 |  | 0.93 | 1.05 | 0.048747 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | MOUND 4 | 0.94924 | 0.89542 | -0.053817 |  | 0.93 | 1.05 | 0.044283 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | MOUND 4 | 0.94924 | 0.89542 | -0.053817 |  | 0.93 | 1.05 | 0.039667 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | MOUND 4 | 0.94924 | 0.89542 | -0.053817 |  | 0.93 | 1.05 | 0.031705 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | MOUND 4 | 0.94924 | 0.89542 | -0.053817 |  | 0.93 | 1.05 | 0.036041 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | MOUND 4 | 0.94924 | 0.89542 | -0.053817 |  | 0.93 | 1.05 | 0.035457 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | MOUND 4 | 0.94924 | 0.89542 | -0.053817 |  | 0.93 | 1.05 | 0.0376 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | MOUND 4 | 0.94924 | 0.89542 | -0.053817 |  | 0.93 | 1.05 | 0.039043 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | MOUND 4 | 0.94958 | 0.89642 | -0.053168 |  | 0.93 | 1.05 | 0.044747 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | MOUND 4 | 0.94958 | 0.89642 | -0.053168 |  | 0.93 | 1.05 | 0.038771 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | MOUND 4 | 0.94958 | 0.89642 | -0.053168 |  | 0.93 | 1.05 | 0.038438 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | MOUND 4 | 0.94958 | 0.89642 | -0.053168 |  | 0.93 | 1.05 | 0.030968 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | MOUND 4 | 0.94958 | 0.89642 | -0.053168 |  | 0.93 | 1.05 | 0.03158 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | MOUND 4 | 0.94958 | 0.89642 | -0.053168 |  | 0.93 | 1.05 | 0.034131 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | MOUND 4 | 0.94958 | 0.89642 | -0.053168 |  | 0.93 | 1.05 | 0.040933 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | MOUND 4 | 0.94958 | 0.89642 | -0.053168 |  | 0.93 | 1.05 | 0.032964 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | MOUND 4 | 0.94958 | 0.89642 | -0.053168 |  | 0.93 | 1.05 | 0.041072 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | MOUND 4 | 0.94958 | 0.89642 | -0.053168 |  | 0.93 | 1.05 | 0.041072 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | MOUND 4 | 0.94958 | 0.89642 | -0.053168 |  | 0.93 | 1.05 | 0.042352 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | MOUND 4 | 0.94958 | 0.89642 | -0.053168 |  | 0.93 | 1.05 | 0.041773 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | MOUND 4 | 0.94958 | 0.89642 | -0.053168 |  | 0.93 | 1.05 | 0.039667 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | MOUND 4 | 0.94958 | 0.89642 | -0.053168 |  | 0.93 | 1.05 | 0.031705 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | MOUND 4 | 0.94958 | 0.89642 | -0.053168 |  | 0.93 | 1.05 | 0.036041 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | MOUND 4 | 0.94958 | 0.89642 | -0.053168 |  | 0.93 | 1.05 | 0.035457 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | MOUND 4 | 0.94958 | 0.89642 | -0.053168 |  | 0.93 | 1.05 | 0.0376 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | MOUND 4 | 0.94958 | 0.89642 | -0.053168 |  | 0.93 | 1.05 | 0.039043 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | MOUND 4 | 0.97422 | 0.91547 | -0.058759 |  | 0.93 | 1.05 | 0.040439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | MOUND 4 | 0.97422 | 0.91547 | -0.058759 |  | 0.93 | 1.05 | 0.034853 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | MOUND 4 | 0.97422 | 0.91547 | -0.058759 |  | 0.93 | 1.05 | 0.046783 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | MOUND 4 | 0.97422 | 0.91547 | -0.058759 |  | 0.93 | 1.05 | 0.047615 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | MOUND 4 | 0.97422 | 0.91547 | -0.058759 |  | 0.93 | 1.05 | 0.034938 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | MOUND 4 | 0.97422 | 0.91547 | -0.058759 |  | 0.93 | 1.05 | 0.037875 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | MOUND 4 | 0.97422 | 0.91547 | -0.058759 |  | 0.93 | 1.05 | 0.044022 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | MOUND 4 | 0.97422 | 0.91547 | -0.058759 |  | 0.93 | 1.05 | 0.030552 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | MOUND 4 | 0.97422 | 0.91547 | -0.058759 |  | 0.93 | 1.05 | 0.038531 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | MOUND 4 | 0.97422 | 0.91547 | -0.058759 |  | 0.93 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | MOUND 4 | 0.97422 | 0.91547 | -0.058759 |  | 0.93 | 1.05 | 0.062491 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | MOUND 4 | 0.97422 | 0.91547 | -0.058759 |  | 0.93 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | MOUND 4 | 0.97422 | 0.91547 | -0.058759 |  | 0.93 | 1.05 | 0.038129 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | MOUND 4 | 0.97422 | 0.91547 | -0.058759 |  | 0.93 | 1.05 | 0.038066 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | MOUND 4 | 0.97422 | 0.91547 | -0.058759 |  | 0.93 | 1.05 | 0.034955 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | MOUND 4 | 0.97422 | 0.91547 | -0.058759 |  | 0.93 | 1.05 | 0.06281 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | MOUND 4 | 0.97422 | 0.91547 | -0.058759 |  | 0.93 | 1.05 | 0.045309 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | MOUND 4 | 0.97422 | 0.91547 | -0.058759 |  | 0.93 | 1.05 | 0.035805 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | MOUND 4 | 0.97422 | 0.91547 | -0.058759 |  | 0.93 | 1.05 | 0.032364 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | MOUND 4 | 0.97422 | 0.91547 | -0.058759 |  | 0.93 | 1.05 | 0.031815 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | MOUND 4 | 0.97422 | 0.91547 | -0.058759 |  | 0.93 | 1.05 | 0.033886 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | MOUND 4 | 0.97422 | 0.91547 | -0.058759 |  | 0.93 | 1.05 | 0.035554 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | MOUND 4 | 0.95917 | 0.87335 | -0.085813 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | MOUND 4 | 0.95917 | 0.87335 | -0.085813 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | MOUND 4 | 0.95917 | 0.87335 | -0.085813 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | MOUND 4 | 0.95917 | 0.87335 | -0.085813 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | MOUND 4 | 0.95917 | 0.87335 | -0.085813 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | MOUND 4 | 0.95917 | 0.87335 | -0.085813 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | MOUND 4 | 0.95917 | 0.87335 | -0.085813 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | MOUND 4 | 0.95917 | 0.87335 | -0.085813 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | MOUND 4 | 0.95917 | 0.87335 | -0.085813 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | MOUND 4 | 0.95917 | 0.87335 | -0.085813 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | MOUND 4 | 0.95917 | 0.87335 | -0.085813 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | MOUND 4 | 0.95917 | 0.87335 | -0.085813 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | MOUND 4 | 0.95917 | 0.87335 | -0.085813 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | MOUND 4 | 0.95917 | 0.87335 | -0.085813 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | MOUND 4 | 0.95917 | 0.87335 | -0.085813 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | MOUND 4 | 0.95917 | 0.87335 | -0.085813 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | MOUND 4 | 0.95917 | 0.87335 | -0.085813 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | MOUND 4 | 0.95917 | 0.87335 | -0.085813 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | MOUND 4 | 0.95917 | 0.87335 | -0.085813 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | MOUND 4 | 0.95917 | 0.87335 | -0.085813 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | MOUND 4 | 0.95917 | 0.87335 | -0.085813 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | MOUND 4 | 0.95917 | 0.87335 | -0.085813 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | MOUND 4 | 0.95917 | 0.87335 | -0.085813 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | MOUND 4 | 0.95917 | 0.87335 | -0.085813 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | MOUND 4 | 0.95917 | 0.87335 | -0.085813 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | MURLEN 5 | 0.96689 | 0.92244 | -0.044446 |  | 0.93 | 1.05 | 0.036307 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | MURLEN 5 | 0.96689 | 0.92244 | -0.044446 |  | 0.93 | 1.05 | 0.052743 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | MURLEN 5 | 0.96689 | 0.92244 | -0.044446 |  | 0.93 | 1.05 | 0.039345 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | MURLEN 5 | 0.96689 | 0.92244 | -0.044446 |  | 0.93 | 1.05 | 0.031366 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | MURLEN 5 | 0.96689 | 0.92244 | -0.044446 |  | 0.93 | 1.05 | 0.041888 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | MURLEN 5 | 0.96689 | 0.92244 | -0.044446 |  | 0.93 | 1.05 | 0.038797 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | MURLEN 5 | 0.96689 | 0.92244 | -0.044446 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | MURLEN 5 | 0.96689 | 0.92244 | -0.044446 |  | 0.93 | 1.05 | 0.067346 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | MURLEN 5 | 0.96689 | 0.92244 | -0.044446 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | MURLEN 5 | 0.96689 | 0.92244 | -0.044446 |  | 0.93 | 1.05 | 0.030851 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | MURLEN 5 | 0.96689 | 0.92244 | -0.044446 |  | 0.93 | 1.05 | 0.032161 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | MURLEN 5 | 0.96689 | 0.92244 | -0.044446 |  | 0.93 | 1.05 | 0.04067 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | MURLEN 5 | 0.96689 | 0.92244 | -0.044446 |  | 0.93 | 1.05 | 0.040569 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | MURLEN 5 | 0.96689 | 0.92244 | -0.044446 |  | 0.93 | 1.05 | 0.03086 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | MURLEN 5 | 0.96689 | 0.92244 | -0.044446 |  | 0.93 | 1.05 | 0.033223 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | MURLEN 5 | 0.96689 | 0.92244 | -0.044446 |  | 0.93 | 1.05 | 0.033733 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | MURLEN 5 | 0.97787 | 0.92607 | -0.051806 |  | 0.93 | 1.05 | 0.036307 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | MURLEN 5 | 0.97787 | 0.92607 | -0.051806 |  | 0.93 | 1.05 | 0.052743 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | MURLEN 5 | 0.97787 | 0.92607 | -0.051806 |  | 0.93 | 1.05 | 0.039345 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | MURLEN 5 | 0.97787 | 0.92607 | -0.051806 |  | 0.93 | 1.05 | 0.031366 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | MURLEN 5 | 0.97787 | 0.92607 | -0.051806 |  | 0.93 | 1.05 | 0.041888 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | MURLEN 5 | 0.97787 | 0.92607 | -0.051806 |  | 0.93 | 1.05 | 0.038797 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | MURLEN 5 | 0.97787 | 0.92607 | -0.051806 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | MURLEN 5 | 0.97787 | 0.92607 | -0.051806 |  | 0.93 | 1.05 | 0.067346 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | MURLEN 5 | 0.97787 | 0.92607 | -0.051806 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | MURLEN 5 | 0.97787 | 0.92607 | -0.051806 |  | 0.93 | 1.05 | 0.030851 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | MURLEN 5 | 0.97787 | 0.92607 | -0.051806 |  | 0.93 | 1.05 | 0.032161 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | MURLEN 5 | 0.97787 | 0.92607 | -0.051806 |  | 0.93 | 1.05 | 0.04067 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | MURLEN 5 | 0.97787 | 0.92607 | -0.051806 |  | 0.93 | 1.05 | 0.040569 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | MURLEN 5 | 0.97787 | 0.92607 | -0.051806 |  | 0.93 | 1.05 | 0.03086 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | MURLEN 5 | 0.97787 | 0.92607 | -0.051806 |  | 0.93 | 1.05 | 0.033223 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | MURLEN 5 | 0.97787 | 0.92607 | -0.051806 |  | 0.93 | 1.05 | 0.033733 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | MURLEN 5 | 0.98057 | 0.90747 | -0.073105 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | MURLEN 5 | 0.98057 | 0.90747 | -0.073105 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | MURLEN 5 | 0.98057 | 0.90747 | -0.073105 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | MURLEN 5 | 0.98057 | 0.90747 | -0.073105 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | MURLEN 5 | 0.98057 | 0.90747 | -0.073105 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | MURLEN 5 | 0.98057 | 0.90747 | -0.073105 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | MURLEN 5 | 0.98057 | 0.90747 | -0.073105 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | MURLEN 5 | 0.98057 | 0.90747 | -0.073105 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | MURLEN 5 | 0.98057 | 0.90747 | -0.073105 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | MURLEN 5 | 0.98057 | 0.90747 | -0.073105 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | MURLEN 5 | 0.98057 | 0.90747 | -0.073105 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | MURLEN 5 | 0.98057 | 0.90747 | -0.073105 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | MURLEN 5 | 0.98057 | 0.90747 | -0.073105 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | MURLEN 5 | 0.98057 | 0.90747 | -0.073105 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | MURLEN 5 | 0.98057 | 0.90747 | -0.073105 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | MURLEN 5 | 0.98057 | 0.90747 | -0.073105 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | MURLEN 5 | 0.98057 | 0.90747 | -0.073105 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | MURLEN 5 | 0.98057 | 0.90747 | -0.073105 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | MURLEN 5 | 0.98057 | 0.90747 | -0.073105 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | MURLEN 5 | 0.98057 | 0.90747 | -0.073105 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | MURLEN 5 | 0.98057 | 0.90747 | -0.073105 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | MURLEN 5 | 0.98057 | 0.90747 | -0.073105 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | MURLEN 5 | 0.98057 | 0.90747 | -0.073105 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | MURLEN 5 | 0.98057 | 0.90747 | -0.073105 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | MURLEN 5 | 0.98057 | 0.90747 | -0.073105 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | NEASTOTTW5 | 1.0066 | 0.91571 | -0.090906 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | NEASTOTTW5 | 1.0066 | 0.91571 | -0.090906 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | NEASTOTTW5 | 1.0066 | 0.91571 | -0.090906 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | NEASTOTTW5 | 1.0066 | 0.91571 | -0.090906 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | NEASTOTTW5 | 1.0066 | 0.91571 | -0.090906 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | NEASTOTTW5 | 1.0066 | 0.91571 | -0.090906 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | NEASTOTTW5 | 1.0066 | 0.91571 | -0.090906 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | NEASTOTTW5 | 1.0066 | 0.91571 | -0.090906 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | NEASTOTTW5 | 1.0066 | 0.91571 | -0.090906 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | NEASTOTTW5 | 1.0066 | 0.91571 | -0.090906 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | NEASTOTTW5 | 1.0066 | 0.91571 | -0.090906 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | NEASTOTTW5 | 1.0066 | 0.91571 | -0.090906 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | NEASTOTTW5 | 1.0066 | 0.91571 | -0.090906 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | NEASTOTTW5 | 1.0066 | 0.91571 | -0.090906 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | NEASTOTTW5 | 1.0066 | 0.91571 | -0.090906 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | NEASTOTTW5 | 1.0066 | 0.91571 | -0.090906 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | NEASTOTTW5 | 1.0066 | 0.91571 | -0.090906 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | NEASTOTTW5 | 1.0066 | 0.91571 | -0.090906 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | NEASTOTTW5 | 1.0066 | 0.91571 | -0.090906 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | NEASTOTTW5 | 1.0066 | 0.91571 | -0.090906 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | NEASTOTTW5 | 1.0066 | 0.91571 | -0.090906 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | NEASTOTTW5 | 1.0066 | 0.91571 | -0.090906 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | NEASTOTTW5 | 1.0066 | 0.91571 | -0.090906 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | NEASTOTTW5 | 1.0066 | 0.91571 | -0.090906 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | NEASTOTTW5 | 1.0066 | 0.91571 | -0.090906 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | NEO SPA5 | 0.97395 | 0.9185 | -0.055442 |  | 0.92 | 1.05 | 0.033596 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | NEO SPA5 | 0.97395 | 0.9185 | -0.055442 |  | 0.92 | 1.05 | 0.040193 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | NEO SPA5 | 0.97395 | 0.9185 | -0.055442 |  | 0.92 | 1.05 | 0.088122 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | NEO SPA5 | 0.97395 | 0.9185 | -0.055442 |  | 0.92 | 1.05 | 0.074664 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | NEO SPA5 | 0.97395 | 0.9185 | -0.055442 |  | 0.92 | 1.05 | 0.068051 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | NEO SPA5 | 0.97395 | 0.9185 | -0.055442 |  | 0.92 | 1.05 | 0.035565 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | NEO SPA5 | 0.97395 | 0.9185 | -0.055442 |  | 0.92 | 1.05 | 0.033904 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | NEO SPA5 | 0.97395 | 0.9185 | -0.055442 |  | 0.92 | 1.05 | 0.16366 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | NEO SPA5 | 0.97395 | 0.9185 | -0.055442 |  | 0.92 | 1.05 | 0.045569 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | NEO SPA5 | 0.97395 | 0.9185 | -0.055442 |  | 0.92 | 1.05 | 0.13458 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | NEO SPA5 | 0.97395 | 0.9185 | -0.055442 |  | 0.92 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | NEO SPA5 | 0.97395 | 0.9185 | -0.055442 |  | 0.92 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | NEO SPA5 | 0.97395 | 0.9185 | -0.055442 |  | 0.92 | 1.05 | 0.068426 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | NEO SPA5 | 0.97395 | 0.9185 | -0.055442 |  | 0.92 | 1.05 | 0.035223 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | NEO SPA5 | 0.97395 | 0.9185 | -0.055442 |  | 0.92 | 1.05 | 0.034504 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | NEO SPA5 | 0.97409 | 0.9197 | -0.054388 |  | 0.92 | 1.05 | 0.040193 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | NEO SPA5 | 0.97409 | 0.9197 | -0.054388 |  | 0.92 | 1.05 | 0.088122 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | NEO SPA5 | 0.97409 | 0.9197 | -0.054388 |  | 0.92 | 1.05 | 0.074664 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | NEO SPA5 | 0.97409 | 0.9197 | -0.054388 |  | 0.92 | 1.05 | 0.068051 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | NEO SPA5 | 0.97409 | 0.9197 | -0.054388 |  | 0.92 | 1.05 | 0.034774 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | NEO SPA5 | 0.97409 | 0.9197 | -0.054388 |  | 0.92 | 1.05 | 0.033904 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | NEO SPA5 | 0.97409 | 0.9197 | -0.054388 |  | 0.92 | 1.05 | 0.16366 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | NEO SPA5 | 0.97409 | 0.9197 | -0.054388 |  | 0.92 | 1.05 | 0.045569 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | NEO SPA5 | 0.97409 | 0.9197 | -0.054388 |  | 0.92 | 1.05 | 0.13458 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | NEO SPA5 | 0.97409 | 0.9197 | -0.054388 |  | 0.92 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | NEO SPA5 | 0.97409 | 0.9197 | -0.054388 |  | 0.92 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | NEO SPA5 | 0.97409 | 0.9197 | -0.054388 |  | 0.92 | 1.05 | 0.068426 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | NEO SPA5 | 0.97409 | 0.9197 | -0.054388 |  | 0.92 | 1.05 | 0.035223 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | NEO SPA5 | 0.97409 | 0.9197 | -0.054388 |  | 0.92 | 1.05 | 0.034504 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | NEO184 5 | 0.97276 | 0.9161 | -0.056657 |  | 0.925 | 1.05 | 0.033596 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | NEO184 5 | 0.97276 | 0.9161 | -0.056657 |  | 0.925 | 1.05 | 0.040193 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | NEO184 5 | 0.97276 | 0.9161 | -0.056657 |  | 0.925 | 1.05 | 0.088122 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | NEO184 5 | 0.97276 | 0.9161 | -0.056657 |  | 0.925 | 1.05 | 0.074664 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | NEO184 5 | 0.97276 | 0.9161 | -0.056657 |  | 0.925 | 1.05 | 0.068051 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | NEO184 5 | 0.97276 | 0.9161 | -0.056657 |  | 0.925 | 1.05 | 0.035565 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | NEO184 5 | 0.97276 | 0.9161 | -0.056657 |  | 0.925 | 1.05 | 0.033904 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | NEO184 5 | 0.97276 | 0.9161 | -0.056657 |  | 0.925 | 1.05 | 0.16366 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | NEO184 5 | 0.97276 | 0.9161 | -0.056657 |  | 0.925 | 1.05 | 0.045569 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | NEO184 5 | 0.97276 | 0.9161 | -0.056657 |  | 0.925 | 1.05 | 0.13458 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | NEO184 5 | 0.97276 | 0.9161 | -0.056657 |  | 0.925 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | NEO184 5 | 0.97276 | 0.9161 | -0.056657 |  | 0.925 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | NEO184 5 | 0.97276 | 0.9161 | -0.056657 |  | 0.925 | 1.05 | 0.068426 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | NEO184 5 | 0.97276 | 0.9161 | -0.056657 |  | 0.925 | 1.05 | 0.035223 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | NEO184 5 | 0.97276 | 0.9161 | -0.056657 |  | 0.925 | 1.05 | 0.034504 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | NEO184 5 | 0.9729 | 0.91725 | -0.055643 |  | 0.925 | 1.05 | 0.040193 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | NEO184 5 | 0.9729 | 0.91725 | -0.055643 |  | 0.925 | 1.05 | 0.088122 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | NEO184 5 | 0.9729 | 0.91725 | -0.055643 |  | 0.925 | 1.05 | 0.074664 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | NEO184 5 | 0.9729 | 0.91725 | -0.055643 |  | 0.925 | 1.05 | 0.068051 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | NEO184 5 | 0.9729 | 0.91725 | -0.055643 |  | 0.925 | 1.05 | 0.034774 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | NEO184 5 | 0.9729 | 0.91725 | -0.055643 |  | 0.925 | 1.05 | 0.033904 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | NEO184 5 | 0.9729 | 0.91725 | -0.055643 |  | 0.925 | 1.05 | 0.16366 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | NEO184 5 | 0.9729 | 0.91725 | -0.055643 |  | 0.925 | 1.05 | 0.045569 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | NEO184 5 | 0.9729 | 0.91725 | -0.055643 |  | 0.925 | 1.05 | 0.13458 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | NEO184 5 | 0.9729 | 0.91725 | -0.055643 |  | 0.925 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | NEO184 5 | 0.9729 | 0.91725 | -0.055643 |  | 0.925 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | NEO184 5 | 0.9729 | 0.91725 | -0.055643 |  | 0.925 | 1.05 | 0.068426 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | NEO184 5 | 0.9729 | 0.91725 | -0.055643 |  | 0.925 | 1.05 | 0.035223 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | NEO184 5 | 0.9729 | 0.91725 | -0.055643 |  | 0.925 | 1.05 | 0.034504 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | NEO184 5 | 0.97283 | 0.92295 | -0.049874 |  | 0.925 | 1.05 | 0.033596 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | NEO184 5 | 0.97283 | 0.92295 | -0.049874 |  | 0.925 | 1.05 | 0.040193 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | NEO184 5 | 0.97283 | 0.92295 | -0.049874 |  | 0.925 | 1.05 | 0.056051 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | NEO184 5 | 0.97283 | 0.92295 | -0.049874 |  | 0.925 | 1.05 | 0.074664 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | NEO184 5 | 0.97283 | 0.92295 | -0.049874 |  | 0.925 | 1.05 | 0.068051 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | NEO184 5 | 0.97283 | 0.92295 | -0.049874 |  | 0.925 | 1.05 | 0.035565 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | NEO184 5 | 0.97283 | 0.92295 | -0.049874 |  | 0.925 | 1.05 | 0.033904 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | NEO184 5 | 0.97283 | 0.92295 | -0.049874 |  | 0.925 | 1.05 | 0.082596 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | NEO184 5 | 0.97283 | 0.92295 | -0.049874 |  | 0.925 | 1.05 | 0.045569 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | NEO184 5 | 0.97283 | 0.92295 | -0.049874 |  | 0.925 | 1.05 | 0.13458 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | NEO184 5 | 0.97283 | 0.92295 | -0.049874 |  | 0.925 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | NEO184 5 | 0.97283 | 0.92295 | -0.049874 |  | 0.925 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | NEO184 5 | 0.97283 | 0.92295 | -0.049874 |  | 0.925 | 1.05 | 0.068426 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | NEO184 5 | 0.97283 | 0.92295 | -0.049874 |  | 0.925 | 1.05 | 0.035223 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | NEO184 5 | 0.97283 | 0.92295 | -0.049874 |  | 0.925 | 1.05 | 0.034504 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | NEO184 5 | 0.97459 | 0.92454 | -0.050053 |  | 0.925 | 1.05 | 0.033596 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.2 MVAR switched shunt at GROVE 5 161 kV; Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | NEO184 5 | 0.97459 | 0.92454 | -0.050053 |  | 0.925 | 1.05 | 0.088122 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.2 MVAR switched shunt at GROVE 5 161 kV; Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | NEO184 5 | 0.97459 | 0.92454 | -0.050053 |  | 0.925 | 1.05 | 0.030897 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.2 MVAR switched shunt at GROVE 5 161 kV; Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | NEO184 5 | 0.97459 | 0.92454 | -0.050053 |  | 0.925 | 1.05 | 0.038719 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.2 MVAR switched shunt at GROVE 5 161 kV; Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | NEO184 5 | 0.97459 | 0.92454 | -0.050053 |  | 0.925 | 1.05 | 0.035565 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.2 MVAR switched shunt at GROVE 5 161 kV; Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | NEO184 5 | 0.97459 | 0.92454 | -0.050053 |  | 0.925 | 1.05 | 0.16366 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.2 MVAR switched shunt at GROVE 5 161 kV; Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | NEO184 5 | 0.97459 | 0.92454 | -0.050053 |  | 0.925 | 1.05 | 0.038589 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.2 MVAR switched shunt at GROVE 5 161 kV; Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | NEO184 5 | 0.97459 | 0.92454 | -0.050053 |  | 0.925 | 1.05 | 0.034208 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.2 MVAR switched shunt at GROVE 5 161 kV; Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | NEOSHO 4 | 0.95115 | 0.90415 | -0.046997 |  | 0.93 | 1.05 | 0.091967 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | NEOSHO 4 | 0.95115 | 0.90415 | -0.046997 |  | 0.93 | 1.05 | 0.033356 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | NEOSHO 4 | 0.95115 | 0.90415 | -0.046997 |  | 0.93 | 1.05 | 0.044346 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | NEOSHO 4 | 0.95115 | 0.90415 | -0.046997 |  | 0.93 | 1.05 | 0.058536 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | NEOSHO 4 | 0.95115 | 0.90415 | -0.046997 |  | 0.93 | 1.05 | 0.059327 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | NEOSHO 4 | 0.95115 | 0.90415 | -0.046997 |  | 0.93 | 1.05 | 0.041874 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | NEOSHO 4 | 0.95115 | 0.90415 | -0.046997 |  | 0.93 | 1.05 | 0.046192 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | NEOSHO 4 | 0.95115 | 0.90415 | -0.046997 |  | 0.93 | 1.05 | 0.12754 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | NEOSHO 4 | 0.95115 | 0.90415 | -0.046997 |  | 0.93 | 1.05 | 0.047018 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | NEOSHO 4 | 0.95115 | 0.90415 | -0.046997 |  | 0.93 | 1.05 | 0.056662 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | NEOSHO 4 | 0.95115 | 0.90415 | -0.046997 |  | 0.93 | 1.05 | 0.056662 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | NEOSHO 4 | 0.95115 | 0.90415 | -0.046997 |  | 0.93 | 1.05 | 0.056727 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | NEOSHO 4 | 0.95115 | 0.90415 | -0.046997 |  | 0.93 | 1.05 | 0.074186 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | NEOSHO 4 | 0.95115 | 0.90415 | -0.046997 |  | 0.93 | 1.05 | 0.040839 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | NEOSHO 4 | 0.95115 | 0.90415 | -0.046997 |  | 0.93 | 1.05 | 0.03863 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | NEOSHO 4 | 0.95115 | 0.90415 | -0.046997 |  | 0.93 | 1.05 | 0.042285 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | NEOSHO 4 | 0.95115 | 0.90415 | -0.046997 |  | 0.93 | 1.05 | 0.042285 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | NEOSHO 4 | 0.95115 | 0.90415 | -0.046997 |  | 0.93 | 1.05 | 0.050204 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | NEOSHO 4 | 0.95115 | 0.90415 | -0.046997 |  | 0.93 | 1.05 | 0.058005 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | NEOSHO 4 | 0.95115 | 0.90415 | -0.046997 |  | 0.93 | 1.05 | 0.041735 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | NEOSHO 4 | 0.95115 | 0.90415 | -0.046997 |  | 0.93 | 1.05 | 0.057076 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | NEOSHO 4 | 0.95115 | 0.90415 | -0.046997 |  | 0.93 | 1.05 | 0.050111 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | NEOSHO 4 | 0.95115 | 0.90415 | -0.046997 |  | 0.93 | 1.05 | 0.06491 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | NEOSHO 4 | 0.95115 | 0.90415 | -0.046997 |  | 0.93 | 1.05 | 0.051051 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | NEOSHO 4 | 0.95115 | 0.90415 | -0.046997 |  | 0.93 | 1.05 | 0.036279 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | ASGI-2024-023 | NEOSHO 4 | 0.95369 | 0.90054 | -0.053145 |  | 0.93 | 1.05 | 0.079962 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | NEOSHO 4 | 0.95369 | 0.90054 | -0.053145 |  | 0.93 | 1.05 | 0.065323 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-068 | NEOSHO 4 | 0.95369 | 0.90054 | -0.053145 |  | 0.93 | 1.05 | 0.067422 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-071 | NEOSHO 4 | 0.95369 | 0.90054 | -0.053145 |  | 0.93 | 1.05 | 0.074668 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | NEOSHO 4 | 0.95369 | 0.90054 | -0.053145 |  | 0.93 | 1.05 | 0.053027 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-122 | NEOSHO 4 | 0.95369 | 0.90054 | -0.053145 |  | 0.93 | 1.05 | 0.082926 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-177 | NEOSHO 4 | 0.95369 | 0.90054 | -0.053145 |  | 0.93 | 1.05 | 0.084694 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-178 | NEOSHO 4 | 0.95369 | 0.90054 | -0.053145 |  | 0.93 | 1.05 | 0.078867 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | NEOSHO 4 | 0.95369 | 0.90054 | -0.053145 |  | 0.93 | 1.05 | 0.031571 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-220 | NEOSHO 4 | 0.95369 | 0.90054 | -0.053145 |  | 0.93 | 1.05 | 0.075331 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-232 | NEOSHO 4 | 0.95369 | 0.90054 | -0.053145 |  | 0.93 | 1.05 | 0.078906 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | NEOSHO 4 | 0.95369 | 0.90054 | -0.053145 |  | 0.93 | 1.05 | 0.065323 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | NEOSHO 4 | 0.95369 | 0.90054 | -0.053145 |  | 0.93 | 1.05 | 0.03431 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | NEOSHO 4 | 0.95369 | 0.90054 | -0.053145 |  | 0.93 | 1.05 | 0.031504 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | NEOSHO 4 | 0.95369 | 0.90054 | -0.053145 |  | 0.93 | 1.05 | 0.031504 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | NEOSHO 4 | 0.95369 | 0.90054 | -0.053145 |  | 0.93 | 1.05 | 0.030663 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | NEOSHO 4 | 0.95369 | 0.90054 | -0.053145 |  | 0.93 | 1.05 | 0.04269 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-376 | NEOSHO 4 | 0.95369 | 0.90054 | -0.053145 |  | 0.93 | 1.05 | 0.082476 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | NEOSHO 4 | 0.95501 | 0.90269 | -0.052323 |  | 0.93 | 1.05 | 0.035768 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | NEOSHO 4 | 0.95501 | 0.90269 | -0.052323 |  | 0.93 | 1.05 | 0.088718 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | NEOSHO 4 | 0.95501 | 0.90269 | -0.052323 |  | 0.93 | 1.05 | 0.031473 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | NEOSHO 4 | 0.95501 | 0.90269 | -0.052323 |  | 0.93 | 1.05 | 0.034941 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | NEOSHO 4 | 0.95501 | 0.90269 | -0.052323 |  | 0.93 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | NEOSHO 4 | 0.95501 | 0.90269 | -0.052323 |  | 0.93 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | NEOSHO 4 | 0.95501 | 0.90269 | -0.052323 |  | 0.93 | 1.05 | 0.049224 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | NEOSHO 4 | 0.95501 | 0.90269 | -0.052323 |  | 0.93 | 1.05 | 0.038981 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | NEOSHO 4 | 0.95501 | 0.90269 | -0.052323 |  | 0.93 | 1.05 | 0.040399 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | NEOSHO 4 | 0.95501 | 0.90269 | -0.052323 |  | 0.93 | 1.05 | 0.031912 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | NEOSHO 4 | 0.95501 | 0.90269 | -0.052323 |  | 0.93 | 1.05 | 0.034127 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | NEOSHO 4 | 0.95501 | 0.90269 | -0.052323 |  | 0.93 | 1.05 | 0.047318 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | NEOSHO 4 | 0.95178 | 0.89643 | -0.055349 |  | 0.93 | 1.05 | 0.040439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | NEOSHO 4 | 0.95178 | 0.89643 | -0.055349 |  | 0.93 | 1.05 | 0.034853 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | NEOSHO 4 | 0.95178 | 0.89643 | -0.055349 |  | 0.93 | 1.05 | 0.046783 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | NEOSHO 4 | 0.95178 | 0.89643 | -0.055349 |  | 0.93 | 1.05 | 0.047615 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | NEOSHO 4 | 0.95178 | 0.89643 | -0.055349 |  | 0.93 | 1.05 | 0.034938 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | NEOSHO 4 | 0.95178 | 0.89643 | -0.055349 |  | 0.93 | 1.05 | 0.037875 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | NEOSHO 4 | 0.95178 | 0.89643 | -0.055349 |  | 0.93 | 1.05 | 0.044022 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | NEOSHO 4 | 0.95178 | 0.89643 | -0.055349 |  | 0.93 | 1.05 | 0.030552 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | NEOSHO 4 | 0.95178 | 0.89643 | -0.055349 |  | 0.93 | 1.05 | 0.038531 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | NEOSHO 4 | 0.95178 | 0.89643 | -0.055349 |  | 0.93 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | NEOSHO 4 | 0.95178 | 0.89643 | -0.055349 |  | 0.93 | 1.05 | 0.062491 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | NEOSHO 4 | 0.95178 | 0.89643 | -0.055349 |  | 0.93 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | NEOSHO 4 | 0.95178 | 0.89643 | -0.055349 |  | 0.93 | 1.05 | 0.038129 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | NEOSHO 4 | 0.95178 | 0.89643 | -0.055349 |  | 0.93 | 1.05 | 0.038066 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | NEOSHO 4 | 0.95178 | 0.89643 | -0.055349 |  | 0.93 | 1.05 | 0.034955 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | NEOSHO 4 | 0.95178 | 0.89643 | -0.055349 |  | 0.93 | 1.05 | 0.06281 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | NEOSHO 4 | 0.95178 | 0.89643 | -0.055349 |  | 0.93 | 1.05 | 0.045309 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | NEOSHO 4 | 0.95178 | 0.89643 | -0.055349 |  | 0.93 | 1.05 | 0.035805 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | NEOSHO 4 | 0.95178 | 0.89643 | -0.055349 |  | 0.93 | 1.05 | 0.032364 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | NEOSHO 4 | 0.95178 | 0.89643 | -0.055349 |  | 0.93 | 1.05 | 0.031815 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | NEOSHO 4 | 0.95178 | 0.89643 | -0.055349 |  | 0.93 | 1.05 | 0.033886 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | NEOSHO 4 | 0.95178 | 0.89643 | -0.055349 |  | 0.93 | 1.05 | 0.035554 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | NEOSHO 4 | 0.95316 | 0.88168 | -0.071483 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | NEOSHO 4 | 0.95316 | 0.88168 | -0.071483 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | NEOSHO 4 | 0.95316 | 0.88168 | -0.071483 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | NEOSHO 4 | 0.95316 | 0.88168 | -0.071483 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | NEOSHO 4 | 0.95316 | 0.88168 | -0.071483 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | NEOSHO 4 | 0.95316 | 0.88168 | -0.071483 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | NEOSHO 4 | 0.95316 | 0.88168 | -0.071483 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | NEOSHO 4 | 0.95316 | 0.88168 | -0.071483 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | NEOSHO 4 | 0.95316 | 0.88168 | -0.071483 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | NEOSHO 4 | 0.95316 | 0.88168 | -0.071483 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | NEOSHO 4 | 0.95316 | 0.88168 | -0.071483 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | NEOSHO 4 | 0.95316 | 0.88168 | -0.071483 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | NEOSHO 4 | 0.95316 | 0.88168 | -0.071483 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | NEOSHO 4 | 0.95316 | 0.88168 | -0.071483 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | NEOSHO 4 | 0.95316 | 0.88168 | -0.071483 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | NEOSHO 4 | 0.95316 | 0.88168 | -0.071483 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | NEOSHO 4 | 0.95316 | 0.88168 | -0.071483 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | NEOSHO 4 | 0.95316 | 0.88168 | -0.071483 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | NEOSHO 4 | 0.95316 | 0.88168 | -0.071483 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | NEOSHO 4 | 0.95316 | 0.88168 | -0.071483 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | NEOSHO 4 | 0.95316 | 0.88168 | -0.071483 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | NEOSHO 4 | 0.95316 | 0.88168 | -0.071483 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | NEOSHO 4 | 0.95316 | 0.88168 | -0.071483 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | NEOSHO 4 | 0.95316 | 0.88168 | -0.071483 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | NEOSHO 4 | 0.95316 | 0.88168 | -0.071483 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | NEOSHO 5 | 0.99576 | 0.92254 | -0.073219 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | NEOSHO 5 | 0.99576 | 0.92254 | -0.073219 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | NEOSHO 5 | 0.99576 | 0.92254 | -0.073219 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | NEOSHO 5 | 0.99576 | 0.92254 | -0.073219 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | NEOSHO 5 | 0.99576 | 0.92254 | -0.073219 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | NEOSHO 5 | 0.99576 | 0.92254 | -0.073219 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | NEOSHO 5 | 0.99576 | 0.92254 | -0.073219 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | NEOSHO 5 | 0.99576 | 0.92254 | -0.073219 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | NEOSHO 5 | 0.99576 | 0.92254 | -0.073219 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | NEOSHO 5 | 0.99576 | 0.92254 | -0.073219 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | NEOSHO 5 | 0.99576 | 0.92254 | -0.073219 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | NEOSHO 5 | 0.99576 | 0.92254 | -0.073219 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | NEOSHO 5 | 0.99576 | 0.92254 | -0.073219 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | NEOSHO 5 | 0.99576 | 0.92254 | -0.073219 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | NEOSHO 5 | 0.99576 | 0.92254 | -0.073219 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | NEOSHO 5 | 0.99576 | 0.92254 | -0.073219 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | NEOSHO 5 | 0.99576 | 0.92254 | -0.073219 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | NEOSHO 5 | 0.99576 | 0.92254 | -0.073219 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | NEOSHO 5 | 0.99576 | 0.92254 | -0.073219 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | NEOSHO 5 | 0.99576 | 0.92254 | -0.073219 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | NEOSHO 5 | 0.99576 | 0.92254 | -0.073219 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | NEOSHO 5 | 0.99576 | 0.92254 | -0.073219 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | NEOSHO 5 | 0.99576 | 0.92254 | -0.073219 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | NEOSHO 5 | 0.99576 | 0.92254 | -0.073219 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | NEOSHO 5 | 0.99576 | 0.92254 | -0.073219 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | ASGI-2024-023 | NEOSHO 7 | 1.0037 | 0.94228 | -0.06143 |  | 0.95 | 1.05 | 0.079962 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | NEOSHO 7 | 1.0037 | 0.94228 | -0.06143 |  | 0.95 | 1.05 | 0.065323 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-068 | NEOSHO 7 | 1.0037 | 0.94228 | -0.06143 |  | 0.95 | 1.05 | 0.067422 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-071 | NEOSHO 7 | 1.0037 | 0.94228 | -0.06143 |  | 0.95 | 1.05 | 0.074668 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | NEOSHO 7 | 1.0037 | 0.94228 | -0.06143 |  | 0.95 | 1.05 | 0.053027 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-122 | NEOSHO 7 | 1.0037 | 0.94228 | -0.06143 |  | 0.95 | 1.05 | 0.082926 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-177 | NEOSHO 7 | 1.0037 | 0.94228 | -0.06143 |  | 0.95 | 1.05 | 0.084694 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-178 | NEOSHO 7 | 1.0037 | 0.94228 | -0.06143 |  | 0.95 | 1.05 | 0.078867 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | NEOSHO 7 | 1.0037 | 0.94228 | -0.06143 |  | 0.95 | 1.05 | 0.031571 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-220 | NEOSHO 7 | 1.0037 | 0.94228 | -0.06143 |  | 0.95 | 1.05 | 0.075331 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-232 | NEOSHO 7 | 1.0037 | 0.94228 | -0.06143 |  | 0.95 | 1.05 | 0.078906 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | NEOSHO 7 | 1.0037 | 0.94228 | -0.06143 |  | 0.95 | 1.05 | 0.065323 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | NEOSHO 7 | 1.0037 | 0.94228 | -0.06143 |  | 0.95 | 1.05 | 0.03431 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | NEOSHO 7 | 1.0037 | 0.94228 | -0.06143 |  | 0.95 | 1.05 | 0.031504 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | NEOSHO 7 | 1.0037 | 0.94228 | -0.06143 |  | 0.95 | 1.05 | 0.031504 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | NEOSHO 7 | 1.0037 | 0.94228 | -0.06143 |  | 0.95 | 1.05 | 0.030663 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | NEOSHO 7 | 1.0037 | 0.94228 | -0.06143 |  | 0.95 | 1.05 | 0.04269 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-376 | NEOSHO 7 | 1.0037 | 0.94228 | -0.06143 |  | 0.95 | 1.05 | 0.082476 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | ASGI-2024-023 | NEOSHO 7 | 1.0046 | 0.94653 | -0.058102 |  | 0.95 | 1.05 | 0.10682 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | NEOSHO 7 | 1.0046 | 0.94653 | -0.058102 |  | 0.95 | 1.05 | 0.084049 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-068 | NEOSHO 7 | 1.0046 | 0.94653 | -0.058102 |  | 0.95 | 1.05 | 0.087538 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-071 | NEOSHO 7 | 1.0046 | 0.94653 | -0.058102 |  | 0.95 | 1.05 | 0.099263 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | NEOSHO 7 | 1.0046 | 0.94653 | -0.058102 |  | 0.95 | 1.05 | 0.088785 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-122 | NEOSHO 7 | 1.0046 | 0.94653 | -0.058102 |  | 0.95 | 1.05 | 0.11321 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-177 | NEOSHO 7 | 1.0046 | 0.94653 | -0.058102 |  | 0.95 | 1.05 | 0.11622 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-178 | NEOSHO 7 | 1.0046 | 0.94653 | -0.058102 |  | 0.95 | 1.05 | 0.10702 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | NEOSHO 7 | 1.0046 | 0.94653 | -0.058102 |  | 0.95 | 1.05 | 0.031044 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-220 | NEOSHO 7 | 1.0046 | 0.94653 | -0.058102 |  | 0.95 | 1.05 | 0.10032 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-232 | NEOSHO 7 | 1.0046 | 0.94653 | -0.058102 |  | 0.95 | 1.05 | 0.10939 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | NEOSHO 7 | 1.0046 | 0.94653 | -0.058102 |  | 0.95 | 1.05 | 0.036829 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | NEOSHO 7 | 1.0046 | 0.94653 | -0.058102 |  | 0.95 | 1.05 | 0.084049 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | NEOSHO 7 | 1.0046 | 0.94653 | -0.058102 |  | 0.95 | 1.05 | 0.053387 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | NEOSHO 7 | 1.0046 | 0.94653 | -0.058102 |  | 0.95 | 1.05 | 0.042012 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | NEOSHO 7 | 1.0046 | 0.94653 | -0.058102 |  | 0.95 | 1.05 | 0.042012 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | NEOSHO 7 | 1.0046 | 0.94653 | -0.058102 |  | 0.95 | 1.05 | 0.031418 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | NEOSHO 7 | 1.0046 | 0.94653 | -0.058102 |  | 0.95 | 1.05 | 0.030073 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | NEOSHO 7 | 1.0046 | 0.94653 | -0.058102 |  | 0.95 | 1.05 | 0.047594 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-376 | NEOSHO 7 | 1.0046 | 0.94653 | -0.058102 |  | 0.95 | 1.05 | 0.11583 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | NEOSHO 7 | 1.0051 | 0.94422 | -0.060915 |  | 0.95 | 1.05 | 0.035768 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | NEOSHO 7 | 1.0051 | 0.94422 | -0.060915 |  | 0.95 | 1.05 | 0.088718 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | NEOSHO 7 | 1.0051 | 0.94422 | -0.060915 |  | 0.95 | 1.05 | 0.031473 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | NEOSHO 7 | 1.0051 | 0.94422 | -0.060915 |  | 0.95 | 1.05 | 0.034941 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | NEOSHO 7 | 1.0051 | 0.94422 | -0.060915 |  | 0.95 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | NEOSHO 7 | 1.0051 | 0.94422 | -0.060915 |  | 0.95 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | NEOSHO 7 | 1.0051 | 0.94422 | -0.060915 |  | 0.95 | 1.05 | 0.049224 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | NEOSHO 7 | 1.0051 | 0.94422 | -0.060915 |  | 0.95 | 1.05 | 0.038981 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | NEOSHO 7 | 1.0051 | 0.94422 | -0.060915 |  | 0.95 | 1.05 | 0.040399 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | NEOSHO 7 | 1.0051 | 0.94422 | -0.060915 |  | 0.95 | 1.05 | 0.031912 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | NEOSHO 7 | 1.0051 | 0.94422 | -0.060915 |  | 0.95 | 1.05 | 0.034127 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | NEOSHO 7 | 1.0051 | 0.94422 | -0.060915 |  | 0.95 | 1.05 | 0.047318 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | NEOSHO 7 | 1.002 | 0.937 | -0.065049 |  | 0.95 | 1.05 | 0.040439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | NEOSHO 7 | 1.002 | 0.937 | -0.065049 |  | 0.95 | 1.05 | 0.034853 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | NEOSHO 7 | 1.002 | 0.937 | -0.065049 |  | 0.95 | 1.05 | 0.046783 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | NEOSHO 7 | 1.002 | 0.937 | -0.065049 |  | 0.95 | 1.05 | 0.047615 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | NEOSHO 7 | 1.002 | 0.937 | -0.065049 |  | 0.95 | 1.05 | 0.034938 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | NEOSHO 7 | 1.002 | 0.937 | -0.065049 |  | 0.95 | 1.05 | 0.037875 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | NEOSHO 7 | 1.002 | 0.937 | -0.065049 |  | 0.95 | 1.05 | 0.044022 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | NEOSHO 7 | 1.002 | 0.937 | -0.065049 |  | 0.95 | 1.05 | 0.030552 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | NEOSHO 7 | 1.002 | 0.937 | -0.065049 |  | 0.95 | 1.05 | 0.038531 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | NEOSHO 7 | 1.002 | 0.937 | -0.065049 |  | 0.95 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | NEOSHO 7 | 1.002 | 0.937 | -0.065049 |  | 0.95 | 1.05 | 0.062491 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | NEOSHO 7 | 1.002 | 0.937 | -0.065049 |  | 0.95 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | NEOSHO 7 | 1.002 | 0.937 | -0.065049 |  | 0.95 | 1.05 | 0.038129 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | NEOSHO 7 | 1.002 | 0.937 | -0.065049 |  | 0.95 | 1.05 | 0.038066 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | NEOSHO 7 | 1.002 | 0.937 | -0.065049 |  | 0.95 | 1.05 | 0.034955 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | NEOSHO 7 | 1.002 | 0.937 | -0.065049 |  | 0.95 | 1.05 | 0.06281 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | NEOSHO 7 | 1.002 | 0.937 | -0.065049 |  | 0.95 | 1.05 | 0.045309 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | NEOSHO 7 | 1.002 | 0.937 | -0.065049 |  | 0.95 | 1.05 | 0.035805 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | NEOSHO 7 | 1.002 | 0.937 | -0.065049 |  | 0.95 | 1.05 | 0.032364 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | NEOSHO 7 | 1.002 | 0.937 | -0.065049 |  | 0.95 | 1.05 | 0.031815 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | NEOSHO 7 | 1.002 | 0.937 | -0.065049 |  | 0.95 | 1.05 | 0.033886 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | NEOSHO 7 | 1.002 | 0.937 | -0.065049 |  | 0.95 | 1.05 | 0.035554 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | NEOSHO 7 | 1.0033 | 0.91944 | -0.083863 |  | 0.95 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | NEOSHO 7 | 1.0033 | 0.91944 | -0.083863 |  | 0.95 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | NEOSHO 7 | 1.0033 | 0.91944 | -0.083863 |  | 0.95 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | NEOSHO 7 | 1.0033 | 0.91944 | -0.083863 |  | 0.95 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | NEOSHO 7 | 1.0033 | 0.91944 | -0.083863 |  | 0.95 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | NEOSHO 7 | 1.0033 | 0.91944 | -0.083863 |  | 0.95 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | NEOSHO 7 | 1.0033 | 0.91944 | -0.083863 |  | 0.95 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | NEOSHO 7 | 1.0033 | 0.91944 | -0.083863 |  | 0.95 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | NEOSHO 7 | 1.0033 | 0.91944 | -0.083863 |  | 0.95 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | NEOSHO 7 | 1.0033 | 0.91944 | -0.083863 |  | 0.95 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | NEOSHO 7 | 1.0033 | 0.91944 | -0.083863 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | NEOSHO 7 | 1.0033 | 0.91944 | -0.083863 |  | 0.95 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | NEOSHO 7 | 1.0033 | 0.91944 | -0.083863 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | NEOSHO 7 | 1.0033 | 0.91944 | -0.083863 |  | 0.95 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | NEOSHO 7 | 1.0033 | 0.91944 | -0.083863 |  | 0.95 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | NEOSHO 7 | 1.0033 | 0.91944 | -0.083863 |  | 0.95 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | NEOSHO 7 | 1.0033 | 0.91944 | -0.083863 |  | 0.95 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | NEOSHO 7 | 1.0033 | 0.91944 | -0.083863 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | NEOSHO 7 | 1.0033 | 0.91944 | -0.083863 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | NEOSHO 7 | 1.0033 | 0.91944 | -0.083863 |  | 0.95 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | NEOSHO 7 | 1.0033 | 0.91944 | -0.083863 |  | 0.95 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | NEOSHO 7 | 1.0033 | 0.91944 | -0.083863 |  | 0.95 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | NEOSHO 7 | 1.0033 | 0.91944 | -0.083863 |  | 0.95 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | NEOSHO 7 | 1.0033 | 0.91944 | -0.083863 |  | 0.95 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | NEOSHO 7 | 1.0033 | 0.91944 | -0.083863 |  | 0.95 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | ASGI-2024-023 | NEOSHON2 | 0.96002 | 0.91122 | -0.048803 |  | 0.93 | 1.05 | 0.079962 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | NEOSHON2 | 0.96002 | 0.91122 | -0.048803 |  | 0.93 | 1.05 | 0.065323 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-068 | NEOSHON2 | 0.96002 | 0.91122 | -0.048803 |  | 0.93 | 1.05 | 0.067422 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-071 | NEOSHON2 | 0.96002 | 0.91122 | -0.048803 |  | 0.93 | 1.05 | 0.074668 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | NEOSHON2 | 0.96002 | 0.91122 | -0.048803 |  | 0.93 | 1.05 | 0.053027 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-122 | NEOSHON2 | 0.96002 | 0.91122 | -0.048803 |  | 0.93 | 1.05 | 0.082926 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-177 | NEOSHON2 | 0.96002 | 0.91122 | -0.048803 |  | 0.93 | 1.05 | 0.084694 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-178 | NEOSHON2 | 0.96002 | 0.91122 | -0.048803 |  | 0.93 | 1.05 | 0.078867 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | NEOSHON2 | 0.96002 | 0.91122 | -0.048803 |  | 0.93 | 1.05 | 0.031571 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-220 | NEOSHON2 | 0.96002 | 0.91122 | -0.048803 |  | 0.93 | 1.05 | 0.075331 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-232 | NEOSHON2 | 0.96002 | 0.91122 | -0.048803 |  | 0.93 | 1.05 | 0.078906 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | NEOSHON2 | 0.96002 | 0.91122 | -0.048803 |  | 0.93 | 1.05 | 0.065323 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | NEOSHON2 | 0.96002 | 0.91122 | -0.048803 |  | 0.93 | 1.05 | 0.03431 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | NEOSHON2 | 0.96002 | 0.91122 | -0.048803 |  | 0.93 | 1.05 | 0.031504 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | NEOSHON2 | 0.96002 | 0.91122 | -0.048803 |  | 0.93 | 1.05 | 0.031504 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | NEOSHON2 | 0.96002 | 0.91122 | -0.048803 |  | 0.93 | 1.05 | 0.030663 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | NEOSHON2 | 0.96002 | 0.91122 | -0.048803 |  | 0.93 | 1.05 | 0.04269 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-376 | NEOSHON2 | 0.96002 | 0.91122 | -0.048803 |  | 0.93 | 1.05 | 0.082476 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | ASGI-2024-023 | NEOSHON2 | 0.96084 | 0.91443 | -0.04641 |  | 0.93 | 1.05 | 0.10682 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | NEOSHON2 | 0.96084 | 0.91443 | -0.04641 |  | 0.93 | 1.05 | 0.084049 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-068 | NEOSHON2 | 0.96084 | 0.91443 | -0.04641 |  | 0.93 | 1.05 | 0.087538 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-071 | NEOSHON2 | 0.96084 | 0.91443 | -0.04641 |  | 0.93 | 1.05 | 0.099263 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | NEOSHON2 | 0.96084 | 0.91443 | -0.04641 |  | 0.93 | 1.05 | 0.088785 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-122 | NEOSHON2 | 0.96084 | 0.91443 | -0.04641 |  | 0.93 | 1.05 | 0.11321 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-177 | NEOSHON2 | 0.96084 | 0.91443 | -0.04641 |  | 0.93 | 1.05 | 0.11622 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-178 | NEOSHON2 | 0.96084 | 0.91443 | -0.04641 |  | 0.93 | 1.05 | 0.10702 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | NEOSHON2 | 0.96084 | 0.91443 | -0.04641 |  | 0.93 | 1.05 | 0.031044 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-220 | NEOSHON2 | 0.96084 | 0.91443 | -0.04641 |  | 0.93 | 1.05 | 0.10032 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-232 | NEOSHON2 | 0.96084 | 0.91443 | -0.04641 |  | 0.93 | 1.05 | 0.10939 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | NEOSHON2 | 0.96084 | 0.91443 | -0.04641 |  | 0.93 | 1.05 | 0.036829 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | NEOSHON2 | 0.96084 | 0.91443 | -0.04641 |  | 0.93 | 1.05 | 0.084049 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | NEOSHON2 | 0.96084 | 0.91443 | -0.04641 |  | 0.93 | 1.05 | 0.053387 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | NEOSHON2 | 0.96084 | 0.91443 | -0.04641 |  | 0.93 | 1.05 | 0.042012 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | NEOSHON2 | 0.96084 | 0.91443 | -0.04641 |  | 0.93 | 1.05 | 0.042012 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | NEOSHON2 | 0.96084 | 0.91443 | -0.04641 |  | 0.93 | 1.05 | 0.031418 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | NEOSHON2 | 0.96084 | 0.91443 | -0.04641 |  | 0.93 | 1.05 | 0.030073 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | NEOSHON2 | 0.96084 | 0.91443 | -0.04641 |  | 0.93 | 1.05 | 0.047594 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-376 | NEOSHON2 | 0.96084 | 0.91443 | -0.04641 |  | 0.93 | 1.05 | 0.11583 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | NEOSHON2 | 0.96143 | 0.91353 | -0.0479 |  | 0.93 | 1.05 | 0.035768 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | NEOSHON2 | 0.96143 | 0.91353 | -0.0479 |  | 0.93 | 1.05 | 0.088718 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | NEOSHON2 | 0.96143 | 0.91353 | -0.0479 |  | 0.93 | 1.05 | 0.031473 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | NEOSHON2 | 0.96143 | 0.91353 | -0.0479 |  | 0.93 | 1.05 | 0.034941 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | NEOSHON2 | 0.96143 | 0.91353 | -0.0479 |  | 0.93 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | NEOSHON2 | 0.96143 | 0.91353 | -0.0479 |  | 0.93 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | NEOSHON2 | 0.96143 | 0.91353 | -0.0479 |  | 0.93 | 1.05 | 0.049224 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | NEOSHON2 | 0.96143 | 0.91353 | -0.0479 |  | 0.93 | 1.05 | 0.038981 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | NEOSHON2 | 0.96143 | 0.91353 | -0.0479 |  | 0.93 | 1.05 | 0.040399 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | NEOSHON2 | 0.96143 | 0.91353 | -0.0479 |  | 0.93 | 1.05 | 0.031912 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | NEOSHON2 | 0.96143 | 0.91353 | -0.0479 |  | 0.93 | 1.05 | 0.034127 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | NEOSHON2 | 0.96143 | 0.91353 | -0.0479 |  | 0.93 | 1.05 | 0.047318 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | NEOSHON2 | 0.95845 | 0.90738 | -0.051068 |  | 0.93 | 1.05 | 0.040439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | NEOSHON2 | 0.95845 | 0.90738 | -0.051068 |  | 0.93 | 1.05 | 0.034853 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | NEOSHON2 | 0.95845 | 0.90738 | -0.051068 |  | 0.93 | 1.05 | 0.046783 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | NEOSHON2 | 0.95845 | 0.90738 | -0.051068 |  | 0.93 | 1.05 | 0.047615 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | NEOSHON2 | 0.95845 | 0.90738 | -0.051068 |  | 0.93 | 1.05 | 0.034938 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | NEOSHON2 | 0.95845 | 0.90738 | -0.051068 |  | 0.93 | 1.05 | 0.037875 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | NEOSHON2 | 0.95845 | 0.90738 | -0.051068 |  | 0.93 | 1.05 | 0.044022 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | NEOSHON2 | 0.95845 | 0.90738 | -0.051068 |  | 0.93 | 1.05 | 0.030552 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | NEOSHON2 | 0.95845 | 0.90738 | -0.051068 |  | 0.93 | 1.05 | 0.038531 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | NEOSHON2 | 0.95845 | 0.90738 | -0.051068 |  | 0.93 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | NEOSHON2 | 0.95845 | 0.90738 | -0.051068 |  | 0.93 | 1.05 | 0.062491 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | NEOSHON2 | 0.95845 | 0.90738 | -0.051068 |  | 0.93 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | NEOSHON2 | 0.95845 | 0.90738 | -0.051068 |  | 0.93 | 1.05 | 0.038129 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | NEOSHON2 | 0.95845 | 0.90738 | -0.051068 |  | 0.93 | 1.05 | 0.038066 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | NEOSHON2 | 0.95845 | 0.90738 | -0.051068 |  | 0.93 | 1.05 | 0.034955 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | NEOSHON2 | 0.95845 | 0.90738 | -0.051068 |  | 0.93 | 1.05 | 0.06281 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | NEOSHON2 | 0.95845 | 0.90738 | -0.051068 |  | 0.93 | 1.05 | 0.045309 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | NEOSHON2 | 0.95845 | 0.90738 | -0.051068 |  | 0.93 | 1.05 | 0.035805 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | NEOSHON2 | 0.95845 | 0.90738 | -0.051068 |  | 0.93 | 1.05 | 0.032364 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | NEOSHON2 | 0.95845 | 0.90738 | -0.051068 |  | 0.93 | 1.05 | 0.031815 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | NEOSHON2 | 0.95845 | 0.90738 | -0.051068 |  | 0.93 | 1.05 | 0.033886 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | NEOSHON2 | 0.95845 | 0.90738 | -0.051068 |  | 0.93 | 1.05 | 0.035554 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | NEOSHON2 | 0.95982 | 0.89389 | -0.065934 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | NEOSHON2 | 0.95982 | 0.89389 | -0.065934 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | NEOSHON2 | 0.95982 | 0.89389 | -0.065934 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | NEOSHON2 | 0.95982 | 0.89389 | -0.065934 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | NEOSHON2 | 0.95982 | 0.89389 | -0.065934 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | NEOSHON2 | 0.95982 | 0.89389 | -0.065934 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | NEOSHON2 | 0.95982 | 0.89389 | -0.065934 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | NEOSHON2 | 0.95982 | 0.89389 | -0.065934 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | NEOSHON2 | 0.95982 | 0.89389 | -0.065934 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | NEOSHON2 | 0.95982 | 0.89389 | -0.065934 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | NEOSHON2 | 0.95982 | 0.89389 | -0.065934 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | NEOSHON2 | 0.95982 | 0.89389 | -0.065934 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | NEOSHON2 | 0.95982 | 0.89389 | -0.065934 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | NEOSHON2 | 0.95982 | 0.89389 | -0.065934 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | NEOSHON2 | 0.95982 | 0.89389 | -0.065934 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | NEOSHON2 | 0.95982 | 0.89389 | -0.065934 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | NEOSHON2 | 0.95982 | 0.89389 | -0.065934 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | NEOSHON2 | 0.95982 | 0.89389 | -0.065934 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | NEOSHON2 | 0.95982 | 0.89389 | -0.065934 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | NEOSHON2 | 0.95982 | 0.89389 | -0.065934 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | NEOSHON2 | 0.95982 | 0.89389 | -0.065934 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | NEOSHON2 | 0.95982 | 0.89389 | -0.065934 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | NEOSHON2 | 0.95982 | 0.89389 | -0.065934 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | NEOSHON2 | 0.95982 | 0.89389 | -0.065934 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | NEOSHON2 | 0.95982 | 0.89389 | -0.065934 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | NEOSHON4 | 0.95121 | 0.90422 | -0.046982 |  | 0.93 | 1.05 | 0.091967 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | NEOSHON4 | 0.95121 | 0.90422 | -0.046982 |  | 0.93 | 1.05 | 0.033356 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | NEOSHON4 | 0.95121 | 0.90422 | -0.046982 |  | 0.93 | 1.05 | 0.044346 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | NEOSHON4 | 0.95121 | 0.90422 | -0.046982 |  | 0.93 | 1.05 | 0.058536 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | NEOSHON4 | 0.95121 | 0.90422 | -0.046982 |  | 0.93 | 1.05 | 0.059327 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | NEOSHON4 | 0.95121 | 0.90422 | -0.046982 |  | 0.93 | 1.05 | 0.041874 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | NEOSHON4 | 0.95121 | 0.90422 | -0.046982 |  | 0.93 | 1.05 | 0.046192 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | NEOSHON4 | 0.95121 | 0.90422 | -0.046982 |  | 0.93 | 1.05 | 0.12754 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | NEOSHON4 | 0.95121 | 0.90422 | -0.046982 |  | 0.93 | 1.05 | 0.047018 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | NEOSHON4 | 0.95121 | 0.90422 | -0.046982 |  | 0.93 | 1.05 | 0.056662 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | NEOSHON4 | 0.95121 | 0.90422 | -0.046982 |  | 0.93 | 1.05 | 0.056662 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | NEOSHON4 | 0.95121 | 0.90422 | -0.046982 |  | 0.93 | 1.05 | 0.056727 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | NEOSHON4 | 0.95121 | 0.90422 | -0.046982 |  | 0.93 | 1.05 | 0.074186 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | NEOSHON4 | 0.95121 | 0.90422 | -0.046982 |  | 0.93 | 1.05 | 0.040839 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | NEOSHON4 | 0.95121 | 0.90422 | -0.046982 |  | 0.93 | 1.05 | 0.03863 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | NEOSHON4 | 0.95121 | 0.90422 | -0.046982 |  | 0.93 | 1.05 | 0.042285 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | NEOSHON4 | 0.95121 | 0.90422 | -0.046982 |  | 0.93 | 1.05 | 0.042285 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | NEOSHON4 | 0.95121 | 0.90422 | -0.046982 |  | 0.93 | 1.05 | 0.050204 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | NEOSHON4 | 0.95121 | 0.90422 | -0.046982 |  | 0.93 | 1.05 | 0.058005 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | NEOSHON4 | 0.95121 | 0.90422 | -0.046982 |  | 0.93 | 1.05 | 0.041735 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | NEOSHON4 | 0.95121 | 0.90422 | -0.046982 |  | 0.93 | 1.05 | 0.057076 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | NEOSHON4 | 0.95121 | 0.90422 | -0.046982 |  | 0.93 | 1.05 | 0.050111 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | NEOSHON4 | 0.95121 | 0.90422 | -0.046982 |  | 0.93 | 1.05 | 0.06491 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | NEOSHON4 | 0.95121 | 0.90422 | -0.046982 |  | 0.93 | 1.05 | 0.051051 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | NEOSHON4 | 0.95121 | 0.90422 | -0.046982 |  | 0.93 | 1.05 | 0.036279 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | ASGI-2024-023 | NEOSHON4 | 0.95375 | 0.90062 | -0.053128 |  | 0.93 | 1.05 | 0.079962 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | NEOSHON4 | 0.95375 | 0.90062 | -0.053128 |  | 0.93 | 1.05 | 0.065323 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-068 | NEOSHON4 | 0.95375 | 0.90062 | -0.053128 |  | 0.93 | 1.05 | 0.067422 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-071 | NEOSHON4 | 0.95375 | 0.90062 | -0.053128 |  | 0.93 | 1.05 | 0.074668 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | NEOSHON4 | 0.95375 | 0.90062 | -0.053128 |  | 0.93 | 1.05 | 0.053027 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-122 | NEOSHON4 | 0.95375 | 0.90062 | -0.053128 |  | 0.93 | 1.05 | 0.082926 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-177 | NEOSHON4 | 0.95375 | 0.90062 | -0.053128 |  | 0.93 | 1.05 | 0.084694 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-178 | NEOSHON4 | 0.95375 | 0.90062 | -0.053128 |  | 0.93 | 1.05 | 0.078867 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | NEOSHON4 | 0.95375 | 0.90062 | -0.053128 |  | 0.93 | 1.05 | 0.031571 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-220 | NEOSHON4 | 0.95375 | 0.90062 | -0.053128 |  | 0.93 | 1.05 | 0.075331 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-232 | NEOSHON4 | 0.95375 | 0.90062 | -0.053128 |  | 0.93 | 1.05 | 0.078906 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | NEOSHON4 | 0.95375 | 0.90062 | -0.053128 |  | 0.93 | 1.05 | 0.065323 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | NEOSHON4 | 0.95375 | 0.90062 | -0.053128 |  | 0.93 | 1.05 | 0.03431 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | NEOSHON4 | 0.95375 | 0.90062 | -0.053128 |  | 0.93 | 1.05 | 0.031504 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | NEOSHON4 | 0.95375 | 0.90062 | -0.053128 |  | 0.93 | 1.05 | 0.031504 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | NEOSHON4 | 0.95375 | 0.90062 | -0.053128 |  | 0.93 | 1.05 | 0.030663 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | NEOSHON4 | 0.95375 | 0.90062 | -0.053128 |  | 0.93 | 1.05 | 0.04269 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-376 | NEOSHON4 | 0.95375 | 0.90062 | -0.053128 |  | 0.93 | 1.05 | 0.082476 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | NEOSHON4 | 0.95508 | 0.90277 | -0.052308 |  | 0.93 | 1.05 | 0.035768 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | NEOSHON4 | 0.95508 | 0.90277 | -0.052308 |  | 0.93 | 1.05 | 0.088718 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | NEOSHON4 | 0.95508 | 0.90277 | -0.052308 |  | 0.93 | 1.05 | 0.031473 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | NEOSHON4 | 0.95508 | 0.90277 | -0.052308 |  | 0.93 | 1.05 | 0.034941 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | NEOSHON4 | 0.95508 | 0.90277 | -0.052308 |  | 0.93 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | NEOSHON4 | 0.95508 | 0.90277 | -0.052308 |  | 0.93 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | NEOSHON4 | 0.95508 | 0.90277 | -0.052308 |  | 0.93 | 1.05 | 0.049224 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | NEOSHON4 | 0.95508 | 0.90277 | -0.052308 |  | 0.93 | 1.05 | 0.038981 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | NEOSHON4 | 0.95508 | 0.90277 | -0.052308 |  | 0.93 | 1.05 | 0.040399 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | NEOSHON4 | 0.95508 | 0.90277 | -0.052308 |  | 0.93 | 1.05 | 0.031912 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | NEOSHON4 | 0.95508 | 0.90277 | -0.052308 |  | 0.93 | 1.05 | 0.034127 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | NEOSHON4 | 0.95508 | 0.90277 | -0.052308 |  | 0.93 | 1.05 | 0.047318 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | NEOSHON4 | 0.95183 | 0.8965 | -0.055333 |  | 0.93 | 1.05 | 0.040439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | NEOSHON4 | 0.95183 | 0.8965 | -0.055333 |  | 0.93 | 1.05 | 0.034853 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | NEOSHON4 | 0.95183 | 0.8965 | -0.055333 |  | 0.93 | 1.05 | 0.046783 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | NEOSHON4 | 0.95183 | 0.8965 | -0.055333 |  | 0.93 | 1.05 | 0.047615 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | NEOSHON4 | 0.95183 | 0.8965 | -0.055333 |  | 0.93 | 1.05 | 0.034938 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | NEOSHON4 | 0.95183 | 0.8965 | -0.055333 |  | 0.93 | 1.05 | 0.037875 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | NEOSHON4 | 0.95183 | 0.8965 | -0.055333 |  | 0.93 | 1.05 | 0.044022 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | NEOSHON4 | 0.95183 | 0.8965 | -0.055333 |  | 0.93 | 1.05 | 0.030552 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | NEOSHON4 | 0.95183 | 0.8965 | -0.055333 |  | 0.93 | 1.05 | 0.038531 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | NEOSHON4 | 0.95183 | 0.8965 | -0.055333 |  | 0.93 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | NEOSHON4 | 0.95183 | 0.8965 | -0.055333 |  | 0.93 | 1.05 | 0.062491 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | NEOSHON4 | 0.95183 | 0.8965 | -0.055333 |  | 0.93 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | NEOSHON4 | 0.95183 | 0.8965 | -0.055333 |  | 0.93 | 1.05 | 0.038129 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | NEOSHON4 | 0.95183 | 0.8965 | -0.055333 |  | 0.93 | 1.05 | 0.038066 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | NEOSHON4 | 0.95183 | 0.8965 | -0.055333 |  | 0.93 | 1.05 | 0.034955 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | NEOSHON4 | 0.95183 | 0.8965 | -0.055333 |  | 0.93 | 1.05 | 0.06281 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | NEOSHON4 | 0.95183 | 0.8965 | -0.055333 |  | 0.93 | 1.05 | 0.045309 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | NEOSHON4 | 0.95183 | 0.8965 | -0.055333 |  | 0.93 | 1.05 | 0.035805 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | NEOSHON4 | 0.95183 | 0.8965 | -0.055333 |  | 0.93 | 1.05 | 0.032364 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | NEOSHON4 | 0.95183 | 0.8965 | -0.055333 |  | 0.93 | 1.05 | 0.031815 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | NEOSHON4 | 0.95183 | 0.8965 | -0.055333 |  | 0.93 | 1.05 | 0.033886 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | NEOSHON4 | 0.95183 | 0.8965 | -0.055333 |  | 0.93 | 1.05 | 0.035554 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | NEOSHON4 | 0.95322 | 0.88175 | -0.071468 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | NEOSHON4 | 0.95322 | 0.88175 | -0.071468 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | NEOSHON4 | 0.95322 | 0.88175 | -0.071468 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | NEOSHON4 | 0.95322 | 0.88175 | -0.071468 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | NEOSHON4 | 0.95322 | 0.88175 | -0.071468 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | NEOSHON4 | 0.95322 | 0.88175 | -0.071468 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | NEOSHON4 | 0.95322 | 0.88175 | -0.071468 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | NEOSHON4 | 0.95322 | 0.88175 | -0.071468 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | NEOSHON4 | 0.95322 | 0.88175 | -0.071468 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | NEOSHON4 | 0.95322 | 0.88175 | -0.071468 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | NEOSHON4 | 0.95322 | 0.88175 | -0.071468 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | NEOSHON4 | 0.95322 | 0.88175 | -0.071468 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | NEOSHON4 | 0.95322 | 0.88175 | -0.071468 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | NEOSHON4 | 0.95322 | 0.88175 | -0.071468 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | NEOSHON4 | 0.95322 | 0.88175 | -0.071468 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | NEOSHON4 | 0.95322 | 0.88175 | -0.071468 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | NEOSHON4 | 0.95322 | 0.88175 | -0.071468 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | NEOSHON4 | 0.95322 | 0.88175 | -0.071468 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | NEOSHON4 | 0.95322 | 0.88175 | -0.071468 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | NEOSHON4 | 0.95322 | 0.88175 | -0.071468 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | NEOSHON4 | 0.95322 | 0.88175 | -0.071468 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | NEOSHON4 | 0.95322 | 0.88175 | -0.071468 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | NEOSHON4 | 0.95322 | 0.88175 | -0.071468 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | NEOSHON4 | 0.95322 | 0.88175 | -0.071468 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | NEOSHON4 | 0.95322 | 0.88175 | -0.071468 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | ASGI-2024-023 | NEOSHOS2 | 0.96003 | 0.91124 | -0.048796 |  | 0.93 | 1.05 | 0.079962 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | NEOSHOS2 | 0.96003 | 0.91124 | -0.048796 |  | 0.93 | 1.05 | 0.065323 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-068 | NEOSHOS2 | 0.96003 | 0.91124 | -0.048796 |  | 0.93 | 1.05 | 0.067422 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-071 | NEOSHOS2 | 0.96003 | 0.91124 | -0.048796 |  | 0.93 | 1.05 | 0.074668 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | NEOSHOS2 | 0.96003 | 0.91124 | -0.048796 |  | 0.93 | 1.05 | 0.053027 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-122 | NEOSHOS2 | 0.96003 | 0.91124 | -0.048796 |  | 0.93 | 1.05 | 0.082926 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-177 | NEOSHOS2 | 0.96003 | 0.91124 | -0.048796 |  | 0.93 | 1.05 | 0.084694 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-178 | NEOSHOS2 | 0.96003 | 0.91124 | -0.048796 |  | 0.93 | 1.05 | 0.078867 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | NEOSHOS2 | 0.96003 | 0.91124 | -0.048796 |  | 0.93 | 1.05 | 0.031571 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-220 | NEOSHOS2 | 0.96003 | 0.91124 | -0.048796 |  | 0.93 | 1.05 | 0.075331 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-232 | NEOSHOS2 | 0.96003 | 0.91124 | -0.048796 |  | 0.93 | 1.05 | 0.078906 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | NEOSHOS2 | 0.96003 | 0.91124 | -0.048796 |  | 0.93 | 1.05 | 0.065323 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | NEOSHOS2 | 0.96003 | 0.91124 | -0.048796 |  | 0.93 | 1.05 | 0.03431 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | NEOSHOS2 | 0.96003 | 0.91124 | -0.048796 |  | 0.93 | 1.05 | 0.031504 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | NEOSHOS2 | 0.96003 | 0.91124 | -0.048796 |  | 0.93 | 1.05 | 0.031504 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | NEOSHOS2 | 0.96003 | 0.91124 | -0.048796 |  | 0.93 | 1.05 | 0.030663 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | NEOSHOS2 | 0.96003 | 0.91124 | -0.048796 |  | 0.93 | 1.05 | 0.04269 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-376 | NEOSHOS2 | 0.96003 | 0.91124 | -0.048796 |  | 0.93 | 1.05 | 0.082476 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | ASGI-2024-023 | NEOSHOS2 | 0.96085 | 0.91445 | -0.046404 |  | 0.93 | 1.05 | 0.10682 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | NEOSHOS2 | 0.96085 | 0.91445 | -0.046404 |  | 0.93 | 1.05 | 0.084049 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-068 | NEOSHOS2 | 0.96085 | 0.91445 | -0.046404 |  | 0.93 | 1.05 | 0.087538 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-071 | NEOSHOS2 | 0.96085 | 0.91445 | -0.046404 |  | 0.93 | 1.05 | 0.099263 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | NEOSHOS2 | 0.96085 | 0.91445 | -0.046404 |  | 0.93 | 1.05 | 0.088785 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-122 | NEOSHOS2 | 0.96085 | 0.91445 | -0.046404 |  | 0.93 | 1.05 | 0.11321 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-177 | NEOSHOS2 | 0.96085 | 0.91445 | -0.046404 |  | 0.93 | 1.05 | 0.11622 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-178 | NEOSHOS2 | 0.96085 | 0.91445 | -0.046404 |  | 0.93 | 1.05 | 0.10702 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | NEOSHOS2 | 0.96085 | 0.91445 | -0.046404 |  | 0.93 | 1.05 | 0.031044 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-220 | NEOSHOS2 | 0.96085 | 0.91445 | -0.046404 |  | 0.93 | 1.05 | 0.10032 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-232 | NEOSHOS2 | 0.96085 | 0.91445 | -0.046404 |  | 0.93 | 1.05 | 0.10939 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | NEOSHOS2 | 0.96085 | 0.91445 | -0.046404 |  | 0.93 | 1.05 | 0.036829 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | NEOSHOS2 | 0.96085 | 0.91445 | -0.046404 |  | 0.93 | 1.05 | 0.084049 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | NEOSHOS2 | 0.96085 | 0.91445 | -0.046404 |  | 0.93 | 1.05 | 0.053387 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | NEOSHOS2 | 0.96085 | 0.91445 | -0.046404 |  | 0.93 | 1.05 | 0.042012 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | NEOSHOS2 | 0.96085 | 0.91445 | -0.046404 |  | 0.93 | 1.05 | 0.042012 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | NEOSHOS2 | 0.96085 | 0.91445 | -0.046404 |  | 0.93 | 1.05 | 0.031418 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | NEOSHOS2 | 0.96085 | 0.91445 | -0.046404 |  | 0.93 | 1.05 | 0.030073 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | NEOSHOS2 | 0.96085 | 0.91445 | -0.046404 |  | 0.93 | 1.05 | 0.047594 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-376 | NEOSHOS2 | 0.96085 | 0.91445 | -0.046404 |  | 0.93 | 1.05 | 0.11583 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | NEOSHOS2 | 0.96144 | 0.91355 | -0.047893 |  | 0.93 | 1.05 | 0.035768 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | NEOSHOS2 | 0.96144 | 0.91355 | -0.047893 |  | 0.93 | 1.05 | 0.088718 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | NEOSHOS2 | 0.96144 | 0.91355 | -0.047893 |  | 0.93 | 1.05 | 0.031473 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | NEOSHOS2 | 0.96144 | 0.91355 | -0.047893 |  | 0.93 | 1.05 | 0.034941 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | NEOSHOS2 | 0.96144 | 0.91355 | -0.047893 |  | 0.93 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | NEOSHOS2 | 0.96144 | 0.91355 | -0.047893 |  | 0.93 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | NEOSHOS2 | 0.96144 | 0.91355 | -0.047893 |  | 0.93 | 1.05 | 0.049224 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | NEOSHOS2 | 0.96144 | 0.91355 | -0.047893 |  | 0.93 | 1.05 | 0.038981 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | NEOSHOS2 | 0.96144 | 0.91355 | -0.047893 |  | 0.93 | 1.05 | 0.040399 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | NEOSHOS2 | 0.96144 | 0.91355 | -0.047893 |  | 0.93 | 1.05 | 0.031912 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | NEOSHOS2 | 0.96144 | 0.91355 | -0.047893 |  | 0.93 | 1.05 | 0.034127 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | NEOSHOS2 | 0.96144 | 0.91355 | -0.047893 |  | 0.93 | 1.05 | 0.047318 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | NEOSHOS2 | 0.95845 | 0.90739 | -0.051062 |  | 0.93 | 1.05 | 0.040439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | NEOSHOS2 | 0.95845 | 0.90739 | -0.051062 |  | 0.93 | 1.05 | 0.034853 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | NEOSHOS2 | 0.95845 | 0.90739 | -0.051062 |  | 0.93 | 1.05 | 0.046783 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | NEOSHOS2 | 0.95845 | 0.90739 | -0.051062 |  | 0.93 | 1.05 | 0.047615 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | NEOSHOS2 | 0.95845 | 0.90739 | -0.051062 |  | 0.93 | 1.05 | 0.034938 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | NEOSHOS2 | 0.95845 | 0.90739 | -0.051062 |  | 0.93 | 1.05 | 0.037875 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | NEOSHOS2 | 0.95845 | 0.90739 | -0.051062 |  | 0.93 | 1.05 | 0.044022 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | NEOSHOS2 | 0.95845 | 0.90739 | -0.051062 |  | 0.93 | 1.05 | 0.030552 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | NEOSHOS2 | 0.95845 | 0.90739 | -0.051062 |  | 0.93 | 1.05 | 0.038531 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | NEOSHOS2 | 0.95845 | 0.90739 | -0.051062 |  | 0.93 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | NEOSHOS2 | 0.95845 | 0.90739 | -0.051062 |  | 0.93 | 1.05 | 0.062491 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | NEOSHOS2 | 0.95845 | 0.90739 | -0.051062 |  | 0.93 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | NEOSHOS2 | 0.95845 | 0.90739 | -0.051062 |  | 0.93 | 1.05 | 0.038129 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | NEOSHOS2 | 0.95845 | 0.90739 | -0.051062 |  | 0.93 | 1.05 | 0.038066 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | NEOSHOS2 | 0.95845 | 0.90739 | -0.051062 |  | 0.93 | 1.05 | 0.034955 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | NEOSHOS2 | 0.95845 | 0.90739 | -0.051062 |  | 0.93 | 1.05 | 0.06281 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | NEOSHOS2 | 0.95845 | 0.90739 | -0.051062 |  | 0.93 | 1.05 | 0.045309 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | NEOSHOS2 | 0.95845 | 0.90739 | -0.051062 |  | 0.93 | 1.05 | 0.035805 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | NEOSHOS2 | 0.95845 | 0.90739 | -0.051062 |  | 0.93 | 1.05 | 0.032364 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | NEOSHOS2 | 0.95845 | 0.90739 | -0.051062 |  | 0.93 | 1.05 | 0.031815 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | NEOSHOS2 | 0.95845 | 0.90739 | -0.051062 |  | 0.93 | 1.05 | 0.033886 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | NEOSHOS2 | 0.95845 | 0.90739 | -0.051062 |  | 0.93 | 1.05 | 0.035554 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | NEOSHOS2 | 0.95983 | 0.8939 | -0.065925 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | NEOSHOS2 | 0.95983 | 0.8939 | -0.065925 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | NEOSHOS2 | 0.95983 | 0.8939 | -0.065925 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | NEOSHOS2 | 0.95983 | 0.8939 | -0.065925 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | NEOSHOS2 | 0.95983 | 0.8939 | -0.065925 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | NEOSHOS2 | 0.95983 | 0.8939 | -0.065925 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | NEOSHOS2 | 0.95983 | 0.8939 | -0.065925 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | NEOSHOS2 | 0.95983 | 0.8939 | -0.065925 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | NEOSHOS2 | 0.95983 | 0.8939 | -0.065925 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | NEOSHOS2 | 0.95983 | 0.8939 | -0.065925 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | NEOSHOS2 | 0.95983 | 0.8939 | -0.065925 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | NEOSHOS2 | 0.95983 | 0.8939 | -0.065925 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | NEOSHOS2 | 0.95983 | 0.8939 | -0.065925 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | NEOSHOS2 | 0.95983 | 0.8939 | -0.065925 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | NEOSHOS2 | 0.95983 | 0.8939 | -0.065925 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | NEOSHOS2 | 0.95983 | 0.8939 | -0.065925 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | NEOSHOS2 | 0.95983 | 0.8939 | -0.065925 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | NEOSHOS2 | 0.95983 | 0.8939 | -0.065925 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | NEOSHOS2 | 0.95983 | 0.8939 | -0.065925 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | NEOSHOS2 | 0.95983 | 0.8939 | -0.065925 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | NEOSHOS2 | 0.95983 | 0.8939 | -0.065925 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | NEOSHOS2 | 0.95983 | 0.8939 | -0.065925 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | NEOSHOS2 | 0.95983 | 0.8939 | -0.065925 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | NEOSHOS2 | 0.95983 | 0.8939 | -0.065925 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | NEOSHOS2 | 0.95983 | 0.8939 | -0.065925 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | NEOSHOS4 | 0.95131 | 0.9043 | -0.047007 |  | 0.93 | 1.05 | 0.091967 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | NEOSHOS4 | 0.95131 | 0.9043 | -0.047007 |  | 0.93 | 1.05 | 0.033356 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | NEOSHOS4 | 0.95131 | 0.9043 | -0.047007 |  | 0.93 | 1.05 | 0.044346 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | NEOSHOS4 | 0.95131 | 0.9043 | -0.047007 |  | 0.93 | 1.05 | 0.058536 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | NEOSHOS4 | 0.95131 | 0.9043 | -0.047007 |  | 0.93 | 1.05 | 0.059327 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | NEOSHOS4 | 0.95131 | 0.9043 | -0.047007 |  | 0.93 | 1.05 | 0.041874 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | NEOSHOS4 | 0.95131 | 0.9043 | -0.047007 |  | 0.93 | 1.05 | 0.046192 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | NEOSHOS4 | 0.95131 | 0.9043 | -0.047007 |  | 0.93 | 1.05 | 0.12754 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | NEOSHOS4 | 0.95131 | 0.9043 | -0.047007 |  | 0.93 | 1.05 | 0.047018 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | NEOSHOS4 | 0.95131 | 0.9043 | -0.047007 |  | 0.93 | 1.05 | 0.056662 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | NEOSHOS4 | 0.95131 | 0.9043 | -0.047007 |  | 0.93 | 1.05 | 0.056662 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | NEOSHOS4 | 0.95131 | 0.9043 | -0.047007 |  | 0.93 | 1.05 | 0.056727 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | NEOSHOS4 | 0.95131 | 0.9043 | -0.047007 |  | 0.93 | 1.05 | 0.074186 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | NEOSHOS4 | 0.95131 | 0.9043 | -0.047007 |  | 0.93 | 1.05 | 0.040839 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | NEOSHOS4 | 0.95131 | 0.9043 | -0.047007 |  | 0.93 | 1.05 | 0.03863 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | NEOSHOS4 | 0.95131 | 0.9043 | -0.047007 |  | 0.93 | 1.05 | 0.042285 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | NEOSHOS4 | 0.95131 | 0.9043 | -0.047007 |  | 0.93 | 1.05 | 0.042285 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | NEOSHOS4 | 0.95131 | 0.9043 | -0.047007 |  | 0.93 | 1.05 | 0.050204 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | NEOSHOS4 | 0.95131 | 0.9043 | -0.047007 |  | 0.93 | 1.05 | 0.058005 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | NEOSHOS4 | 0.95131 | 0.9043 | -0.047007 |  | 0.93 | 1.05 | 0.041735 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | NEOSHOS4 | 0.95131 | 0.9043 | -0.047007 |  | 0.93 | 1.05 | 0.057076 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | NEOSHOS4 | 0.95131 | 0.9043 | -0.047007 |  | 0.93 | 1.05 | 0.050111 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | NEOSHOS4 | 0.95131 | 0.9043 | -0.047007 |  | 0.93 | 1.05 | 0.06491 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | NEOSHOS4 | 0.95131 | 0.9043 | -0.047007 |  | 0.93 | 1.05 | 0.051051 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | NEOSHOS4 | 0.95131 | 0.9043 | -0.047007 |  | 0.93 | 1.05 | 0.036279 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | ASGI-2024-023 | NEOSHOS4 | 0.95385 | 0.9007 | -0.053152 |  | 0.93 | 1.05 | 0.079962 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | NEOSHOS4 | 0.95385 | 0.9007 | -0.053152 |  | 0.93 | 1.05 | 0.065323 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-068 | NEOSHOS4 | 0.95385 | 0.9007 | -0.053152 |  | 0.93 | 1.05 | 0.067422 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-071 | NEOSHOS4 | 0.95385 | 0.9007 | -0.053152 |  | 0.93 | 1.05 | 0.074668 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | NEOSHOS4 | 0.95385 | 0.9007 | -0.053152 |  | 0.93 | 1.05 | 0.053027 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-122 | NEOSHOS4 | 0.95385 | 0.9007 | -0.053152 |  | 0.93 | 1.05 | 0.082926 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-177 | NEOSHOS4 | 0.95385 | 0.9007 | -0.053152 |  | 0.93 | 1.05 | 0.084694 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-178 | NEOSHOS4 | 0.95385 | 0.9007 | -0.053152 |  | 0.93 | 1.05 | 0.078867 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | NEOSHOS4 | 0.95385 | 0.9007 | -0.053152 |  | 0.93 | 1.05 | 0.031571 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-220 | NEOSHOS4 | 0.95385 | 0.9007 | -0.053152 |  | 0.93 | 1.05 | 0.075331 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-232 | NEOSHOS4 | 0.95385 | 0.9007 | -0.053152 |  | 0.93 | 1.05 | 0.078906 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | NEOSHOS4 | 0.95385 | 0.9007 | -0.053152 |  | 0.93 | 1.05 | 0.065323 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | NEOSHOS4 | 0.95385 | 0.9007 | -0.053152 |  | 0.93 | 1.05 | 0.03431 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | NEOSHOS4 | 0.95385 | 0.9007 | -0.053152 |  | 0.93 | 1.05 | 0.031504 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | NEOSHOS4 | 0.95385 | 0.9007 | -0.053152 |  | 0.93 | 1.05 | 0.031504 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | NEOSHOS4 | 0.95385 | 0.9007 | -0.053152 |  | 0.93 | 1.05 | 0.030663 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | NEOSHOS4 | 0.95385 | 0.9007 | -0.053152 |  | 0.93 | 1.05 | 0.04269 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-376 | NEOSHOS4 | 0.95385 | 0.9007 | -0.053152 |  | 0.93 | 1.05 | 0.082476 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | NEOSHOS4 | 0.95856 | 0.92911 | -0.029444 |  | 0.95 | 1.05 | 0.149 | System Intact | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | NEOSHOS4 | 0.95518 | 0.90285 | -0.052329 |  | 0.93 | 1.05 | 0.035768 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | NEOSHOS4 | 0.95518 | 0.90285 | -0.052329 |  | 0.93 | 1.05 | 0.088718 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | NEOSHOS4 | 0.95518 | 0.90285 | -0.052329 |  | 0.93 | 1.05 | 0.031473 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | NEOSHOS4 | 0.95518 | 0.90285 | -0.052329 |  | 0.93 | 1.05 | 0.034941 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | NEOSHOS4 | 0.95518 | 0.90285 | -0.052329 |  | 0.93 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | NEOSHOS4 | 0.95518 | 0.90285 | -0.052329 |  | 0.93 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | NEOSHOS4 | 0.95518 | 0.90285 | -0.052329 |  | 0.93 | 1.05 | 0.049224 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | NEOSHOS4 | 0.95518 | 0.90285 | -0.052329 |  | 0.93 | 1.05 | 0.038981 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | NEOSHOS4 | 0.95518 | 0.90285 | -0.052329 |  | 0.93 | 1.05 | 0.040399 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | NEOSHOS4 | 0.95518 | 0.90285 | -0.052329 |  | 0.93 | 1.05 | 0.031912 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | NEOSHOS4 | 0.95518 | 0.90285 | -0.052329 |  | 0.93 | 1.05 | 0.034127 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | NEOSHOS4 | 0.95518 | 0.90285 | -0.052329 |  | 0.93 | 1.05 | 0.047318 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | NEOSHOS4 | 0.95194 | 0.89659 | -0.055351 |  | 0.93 | 1.05 | 0.040439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | NEOSHOS4 | 0.95194 | 0.89659 | -0.055351 |  | 0.93 | 1.05 | 0.034853 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | NEOSHOS4 | 0.95194 | 0.89659 | -0.055351 |  | 0.93 | 1.05 | 0.046783 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | NEOSHOS4 | 0.95194 | 0.89659 | -0.055351 |  | 0.93 | 1.05 | 0.047615 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | NEOSHOS4 | 0.95194 | 0.89659 | -0.055351 |  | 0.93 | 1.05 | 0.034938 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | NEOSHOS4 | 0.95194 | 0.89659 | -0.055351 |  | 0.93 | 1.05 | 0.037875 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | NEOSHOS4 | 0.95194 | 0.89659 | -0.055351 |  | 0.93 | 1.05 | 0.044022 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | NEOSHOS4 | 0.95194 | 0.89659 | -0.055351 |  | 0.93 | 1.05 | 0.030552 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | NEOSHOS4 | 0.95194 | 0.89659 | -0.055351 |  | 0.93 | 1.05 | 0.038531 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | NEOSHOS4 | 0.95194 | 0.89659 | -0.055351 |  | 0.93 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | NEOSHOS4 | 0.95194 | 0.89659 | -0.055351 |  | 0.93 | 1.05 | 0.062491 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | NEOSHOS4 | 0.95194 | 0.89659 | -0.055351 |  | 0.93 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | NEOSHOS4 | 0.95194 | 0.89659 | -0.055351 |  | 0.93 | 1.05 | 0.038129 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | NEOSHOS4 | 0.95194 | 0.89659 | -0.055351 |  | 0.93 | 1.05 | 0.038066 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | NEOSHOS4 | 0.95194 | 0.89659 | -0.055351 |  | 0.93 | 1.05 | 0.034955 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | NEOSHOS4 | 0.95194 | 0.89659 | -0.055351 |  | 0.93 | 1.05 | 0.06281 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | NEOSHOS4 | 0.95194 | 0.89659 | -0.055351 |  | 0.93 | 1.05 | 0.045309 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | NEOSHOS4 | 0.95194 | 0.89659 | -0.055351 |  | 0.93 | 1.05 | 0.035805 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | NEOSHOS4 | 0.95194 | 0.89659 | -0.055351 |  | 0.93 | 1.05 | 0.032364 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | NEOSHOS4 | 0.95194 | 0.89659 | -0.055351 |  | 0.93 | 1.05 | 0.031815 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | NEOSHOS4 | 0.95194 | 0.89659 | -0.055351 |  | 0.93 | 1.05 | 0.033886 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | NEOSHOS4 | 0.95194 | 0.89659 | -0.055351 |  | 0.93 | 1.05 | 0.035554 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | NEOSHOS4 | 0.95333 | 0.88185 | -0.071481 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | NEOSHOS4 | 0.95333 | 0.88185 | -0.071481 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | NEOSHOS4 | 0.95333 | 0.88185 | -0.071481 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | NEOSHOS4 | 0.95333 | 0.88185 | -0.071481 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | NEOSHOS4 | 0.95333 | 0.88185 | -0.071481 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | NEOSHOS4 | 0.95333 | 0.88185 | -0.071481 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | NEOSHOS4 | 0.95333 | 0.88185 | -0.071481 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | NEOSHOS4 | 0.95333 | 0.88185 | -0.071481 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | NEOSHOS4 | 0.95333 | 0.88185 | -0.071481 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | NEOSHOS4 | 0.95333 | 0.88185 | -0.071481 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | NEOSHOS4 | 0.95333 | 0.88185 | -0.071481 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | NEOSHOS4 | 0.95333 | 0.88185 | -0.071481 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | NEOSHOS4 | 0.95333 | 0.88185 | -0.071481 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | NEOSHOS4 | 0.95333 | 0.88185 | -0.071481 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | NEOSHOS4 | 0.95333 | 0.88185 | -0.071481 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | NEOSHOS4 | 0.95333 | 0.88185 | -0.071481 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | NEOSHOS4 | 0.95333 | 0.88185 | -0.071481 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | NEOSHOS4 | 0.95333 | 0.88185 | -0.071481 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | NEOSHOS4 | 0.95333 | 0.88185 | -0.071481 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | NEOSHOS4 | 0.95333 | 0.88185 | -0.071481 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | NEOSHOS4 | 0.95333 | 0.88185 | -0.071481 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | NEOSHOS4 | 0.95333 | 0.88185 | -0.071481 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | NEOSHOS4 | 0.95333 | 0.88185 | -0.071481 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | NEOSHOS4 | 0.95333 | 0.88185 | -0.071481 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | NEOSHOS4 | 0.95333 | 0.88185 | -0.071481 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | NEVADA 5 | 0.9667 | 0.91832 | -0.048386 |  | 0.93 | 1.05 | 0.036307 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | NEVADA 5 | 0.9667 | 0.91832 | -0.048386 |  | 0.93 | 1.05 | 0.052743 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | NEVADA 5 | 0.9667 | 0.91832 | -0.048386 |  | 0.93 | 1.05 | 0.039345 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | NEVADA 5 | 0.9667 | 0.91832 | -0.048386 |  | 0.93 | 1.05 | 0.031366 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | NEVADA 5 | 0.9667 | 0.91832 | -0.048386 |  | 0.93 | 1.05 | 0.041888 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | NEVADA 5 | 0.9667 | 0.91832 | -0.048386 |  | 0.93 | 1.05 | 0.038797 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | NEVADA 5 | 0.9667 | 0.91832 | -0.048386 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | NEVADA 5 | 0.9667 | 0.91832 | -0.048386 |  | 0.93 | 1.05 | 0.067346 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | NEVADA 5 | 0.9667 | 0.91832 | -0.048386 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | NEVADA 5 | 0.9667 | 0.91832 | -0.048386 |  | 0.93 | 1.05 | 0.030851 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | NEVADA 5 | 0.9667 | 0.91832 | -0.048386 |  | 0.93 | 1.05 | 0.032161 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | NEVADA 5 | 0.9667 | 0.91832 | -0.048386 |  | 0.93 | 1.05 | 0.04067 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | NEVADA 5 | 0.9667 | 0.91832 | -0.048386 |  | 0.93 | 1.05 | 0.040569 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | NEVADA 5 | 0.9667 | 0.91832 | -0.048386 |  | 0.93 | 1.05 | 0.03086 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | NEVADA 5 | 0.9667 | 0.91832 | -0.048386 |  | 0.93 | 1.05 | 0.033223 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | NEVADA 5 | 0.9667 | 0.91832 | -0.048386 |  | 0.93 | 1.05 | 0.033733 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | NEVADA 5 | 0.9696 | 0.91896 | -0.050642 |  | 0.93 | 1.05 | 0.03053 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | NEVADA 5 | 0.9696 | 0.91896 | -0.050642 |  | 0.93 | 1.05 | 0.044933 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | NEVADA 5 | 0.9696 | 0.91896 | -0.050642 |  | 0.93 | 1.05 | 0.047811 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | NEVADA 5 | 0.9696 | 0.91896 | -0.050642 |  | 0.93 | 1.05 | 0.09719 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | NEVADA 5 | 0.9696 | 0.91896 | -0.050642 |  | 0.93 | 1.05 | 0.069376 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | NEVADA 5 | 0.9696 | 0.91896 | -0.050642 |  | 0.93 | 1.05 | 0.04277 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | NEVADA 5 | 0.9696 | 0.91896 | -0.050642 |  | 0.93 | 1.05 | 0.071112 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | NEVADA 5 | 0.9696 | 0.91896 | -0.050642 |  | 0.93 | 1.05 | 0.039357 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | NEVADA 5 | 0.9696 | 0.91896 | -0.050642 |  | 0.93 | 1.05 | 0.04035 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | NEVADA 5 | 0.9696 | 0.91896 | -0.050642 |  | 0.93 | 1.05 | 0.052332 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | NEVADA 5 | 0.9696 | 0.91896 | -0.050642 |  | 0.93 | 1.05 | 0.045944 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | NEVADA 5 | 0.9696 | 0.91896 | -0.050642 |  | 0.93 | 1.05 | 0.038178 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | NEVADA 5 | 0.9696 | 0.91896 | -0.050642 |  | 0.93 | 1.05 | 0.13469 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | NEVADA 5 | 0.9696 | 0.91896 | -0.050642 |  | 0.93 | 1.05 | 0.03053 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | NEVADA 5 | 0.9696 | 0.91896 | -0.050642 |  | 0.93 | 1.05 | 0.038178 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | NEVADA 5 | 0.9696 | 0.91896 | -0.050642 |  | 0.93 | 1.05 | 0.037309 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | NEVADA 5 | 0.9696 | 0.91896 | -0.050642 |  | 0.93 | 1.05 | 0.040075 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | NEVADA 5 | 0.9696 | 0.91896 | -0.050642 |  | 0.93 | 1.05 | 0.053764 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | NEVADA 5 | 0.9696 | 0.91896 | -0.050642 |  | 0.93 | 1.05 | 0.071762 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | NEVADA 5 | 0.9696 | 0.91896 | -0.050642 |  | 0.93 | 1.05 | 0.047827 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | NEVADA 5 | 0.9696 | 0.91896 | -0.050642 |  | 0.93 | 1.05 | 0.047827 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | NEVADA 5 | 0.9696 | 0.91896 | -0.050642 |  | 0.93 | 1.05 | 0.070303 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | NEVADA 5 | 0.9696 | 0.91896 | -0.050642 |  | 0.93 | 1.05 | 0.040614 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | NEVADA 5 | 0.9696 | 0.91896 | -0.050642 |  | 0.93 | 1.05 | 0.039729 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | NEVADA 5 | 0.9696 | 0.91896 | -0.050642 |  | 0.93 | 1.05 | 0.049662 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | NEVADA 5 | 0.9696 | 0.91896 | -0.050642 |  | 0.93 | 1.05 | 0.042332 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | NEVADA 5 | 0.9696 | 0.91896 | -0.050642 |  | 0.93 | 1.05 | 0.048722 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | NEVADA 5 | 0.9696 | 0.91896 | -0.050642 |  | 0.93 | 1.05 | 0.038156 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | NEVADA 5 | 0.9696 | 0.91896 | -0.050642 |  | 0.93 | 1.05 | 0.036794 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | NEVADA 5 | 0.96308 | 0.92145 | -0.041629 |  | 0.93 | 1.05 | 0.036307 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | NEVADA 5 | 0.96308 | 0.92145 | -0.041629 |  | 0.93 | 1.05 | 0.052743 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | NEVADA 5 | 0.96308 | 0.92145 | -0.041629 |  | 0.93 | 1.05 | 0.039345 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | NEVADA 5 | 0.96308 | 0.92145 | -0.041629 |  | 0.93 | 1.05 | 0.031366 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | NEVADA 5 | 0.96308 | 0.92145 | -0.041629 |  | 0.93 | 1.05 | 0.041888 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | NEVADA 5 | 0.96308 | 0.92145 | -0.041629 |  | 0.93 | 1.05 | 0.038797 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | NEVADA 5 | 0.96308 | 0.92145 | -0.041629 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | NEVADA 5 | 0.96308 | 0.92145 | -0.041629 |  | 0.93 | 1.05 | 0.067346 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | NEVADA 5 | 0.96308 | 0.92145 | -0.041629 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | NEVADA 5 | 0.96308 | 0.92145 | -0.041629 |  | 0.93 | 1.05 | 0.030851 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | NEVADA 5 | 0.96308 | 0.92145 | -0.041629 |  | 0.93 | 1.05 | 0.032161 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | NEVADA 5 | 0.96308 | 0.92145 | -0.041629 |  | 0.93 | 1.05 | 0.04067 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | NEVADA 5 | 0.96308 | 0.92145 | -0.041629 |  | 0.93 | 1.05 | 0.040569 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | NEVADA 5 | 0.96308 | 0.92145 | -0.041629 |  | 0.93 | 1.05 | 0.03086 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | NEVADA 5 | 0.96308 | 0.92145 | -0.041629 |  | 0.93 | 1.05 | 0.033223 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | NEVADA 5 | 0.96308 | 0.92145 | -0.041629 |  | 0.93 | 1.05 | 0.033733 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | NEVADA 5 | 0.96521 | 0.92671 | -0.038498 |  | 0.93 | 1.05 | 0.036307 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | NEVADA 5 | 0.96521 | 0.92671 | -0.038498 |  | 0.93 | 1.05 | 0.052743 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | NEVADA 5 | 0.96521 | 0.92671 | -0.038498 |  | 0.93 | 1.05 | 0.039345 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | NEVADA 5 | 0.96521 | 0.92671 | -0.038498 |  | 0.93 | 1.05 | 0.031366 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | NEVADA 5 | 0.96521 | 0.92671 | -0.038498 |  | 0.93 | 1.05 | 0.041888 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | NEVADA 5 | 0.96521 | 0.92671 | -0.038498 |  | 0.93 | 1.05 | 0.038797 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | NEVADA 5 | 0.96521 | 0.92671 | -0.038498 |  | 0.93 | 1.05 | 0.030557 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | NEVADA 5 | 0.96521 | 0.92671 | -0.038498 |  | 0.93 | 1.05 | 0.067346 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | NEVADA 5 | 0.96521 | 0.92671 | -0.038498 |  | 0.93 | 1.05 | 0.030557 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | NEVADA 5 | 0.96521 | 0.92671 | -0.038498 |  | 0.93 | 1.05 | 0.030851 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | NEVADA 5 | 0.96521 | 0.92671 | -0.038498 |  | 0.93 | 1.05 | 0.032161 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | NEVADA 5 | 0.96521 | 0.92671 | -0.038498 |  | 0.93 | 1.05 | 0.04067 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | NEVADA 5 | 0.96521 | 0.92671 | -0.038498 |  | 0.93 | 1.05 | 0.040569 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | NEVADA 5 | 0.96521 | 0.92671 | -0.038498 |  | 0.93 | 1.05 | 0.03086 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | NEVADA 5 | 0.96521 | 0.92671 | -0.038498 |  | 0.93 | 1.05 | 0.033223 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | NEVADA 5 | 0.96521 | 0.92671 | -0.038498 |  | 0.93 | 1.05 | 0.033733 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | NEVADA 5 | 0.96732 | 0.89381 | -0.073509 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | NEVADA 5 | 0.96732 | 0.89381 | -0.073509 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | NEVADA 5 | 0.96732 | 0.89381 | -0.073509 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | NEVADA 5 | 0.96732 | 0.89381 | -0.073509 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | NEVADA 5 | 0.96732 | 0.89381 | -0.073509 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | NEVADA 5 | 0.96732 | 0.89381 | -0.073509 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | NEVADA 5 | 0.96732 | 0.89381 | -0.073509 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | NEVADA 5 | 0.96732 | 0.89381 | -0.073509 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | NEVADA 5 | 0.96732 | 0.89381 | -0.073509 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | NEVADA 5 | 0.96732 | 0.89381 | -0.073509 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | NEVADA 5 | 0.96732 | 0.89381 | -0.073509 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | NEVADA 5 | 0.96732 | 0.89381 | -0.073509 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | NEVADA 5 | 0.96732 | 0.89381 | -0.073509 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | NEVADA 5 | 0.96732 | 0.89381 | -0.073509 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | NEVADA 5 | 0.96732 | 0.89381 | -0.073509 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | NEVADA 5 | 0.96732 | 0.89381 | -0.073509 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | NEVADA 5 | 0.96732 | 0.89381 | -0.073509 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | NEVADA 5 | 0.96732 | 0.89381 | -0.073509 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | NEVADA 5 | 0.96732 | 0.89381 | -0.073509 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | NEVADA 5 | 0.96732 | 0.89381 | -0.073509 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | NEVADA 5 | 0.96732 | 0.89381 | -0.073509 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | NEVADA 5 | 0.96732 | 0.89381 | -0.073509 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | NEVADA 5 | 0.96732 | 0.89381 | -0.073509 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | NEVADA 5 | 0.96732 | 0.89381 | -0.073509 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | NEVADA 5 | 0.96732 | 0.89381 | -0.073509 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | NINN1WF7 | 1.0065 | 0.94656 | -0.059888 |  | 0.95 | 1.05 | 0.040439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | NINN1WF7 | 1.0065 | 0.94656 | -0.059888 |  | 0.95 | 1.05 | 0.034853 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | NINN1WF7 | 1.0065 | 0.94656 | -0.059888 |  | 0.95 | 1.05 | 0.046783 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | NINN1WF7 | 1.0065 | 0.94656 | -0.059888 |  | 0.95 | 1.05 | 0.047615 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | NINN1WF7 | 1.0065 | 0.94656 | -0.059888 |  | 0.95 | 1.05 | 0.034938 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | NINN1WF7 | 1.0065 | 0.94656 | -0.059888 |  | 0.95 | 1.05 | 0.037875 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | NINN1WF7 | 1.0065 | 0.94656 | -0.059888 |  | 0.95 | 1.05 | 0.044022 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | NINN1WF7 | 1.0065 | 0.94656 | -0.059888 |  | 0.95 | 1.05 | 0.030552 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | NINN1WF7 | 1.0065 | 0.94656 | -0.059888 |  | 0.95 | 1.05 | 0.038531 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | NINN1WF7 | 1.0065 | 0.94656 | -0.059888 |  | 0.95 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | NINN1WF7 | 1.0065 | 0.94656 | -0.059888 |  | 0.95 | 1.05 | 0.062491 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | NINN1WF7 | 1.0065 | 0.94656 | -0.059888 |  | 0.95 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | NINN1WF7 | 1.0065 | 0.94656 | -0.059888 |  | 0.95 | 1.05 | 0.038129 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | NINN1WF7 | 1.0065 | 0.94656 | -0.059888 |  | 0.95 | 1.05 | 0.038066 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | NINN1WF7 | 1.0065 | 0.94656 | -0.059888 |  | 0.95 | 1.05 | 0.034955 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | NINN1WF7 | 1.0065 | 0.94656 | -0.059888 |  | 0.95 | 1.05 | 0.06281 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | NINN1WF7 | 1.0065 | 0.94656 | -0.059888 |  | 0.95 | 1.05 | 0.045309 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | NINN1WF7 | 1.0065 | 0.94656 | -0.059888 |  | 0.95 | 1.05 | 0.035805 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | NINN1WF7 | 1.0065 | 0.94656 | -0.059888 |  | 0.95 | 1.05 | 0.032364 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | NINN1WF7 | 1.0065 | 0.94656 | -0.059888 |  | 0.95 | 1.05 | 0.031815 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | NINN1WF7 | 1.0065 | 0.94656 | -0.059888 |  | 0.95 | 1.05 | 0.033886 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | NINN1WF7 | 1.0065 | 0.94656 | -0.059888 |  | 0.95 | 1.05 | 0.035554 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | NINN1WF7 | 1.0065 | 0.94805 | -0.05842 |  | 0.95 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | NINN1WF7 | 1.0065 | 0.94805 | -0.05842 |  | 0.95 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | NINN1WF7 | 1.0065 | 0.94805 | -0.05842 |  | 0.95 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | NINN1WF7 | 1.0065 | 0.94805 | -0.05842 |  | 0.95 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | NINN1WF7 | 1.0065 | 0.94805 | -0.05842 |  | 0.95 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | NINN1WF7 | 1.0065 | 0.94805 | -0.05842 |  | 0.95 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | NINN1WF7 | 1.0065 | 0.94805 | -0.05842 |  | 0.95 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | NINN1WF7 | 1.0065 | 0.94805 | -0.05842 |  | 0.95 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | NINN1WF7 | 1.0065 | 0.94805 | -0.05842 |  | 0.95 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | NINN1WF7 | 1.0065 | 0.94805 | -0.05842 |  | 0.95 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | NINN1WF7 | 1.0065 | 0.94805 | -0.05842 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | NINN1WF7 | 1.0065 | 0.94805 | -0.05842 |  | 0.95 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | NINN1WF7 | 1.0065 | 0.94805 | -0.05842 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | NINN1WF7 | 1.0065 | 0.94805 | -0.05842 |  | 0.95 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | NINN1WF7 | 1.0065 | 0.94805 | -0.05842 |  | 0.95 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | NINN1WF7 | 1.0065 | 0.94805 | -0.05842 |  | 0.95 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | NINN1WF7 | 1.0065 | 0.94805 | -0.05842 |  | 0.95 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | NINN1WF7 | 1.0065 | 0.94805 | -0.05842 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | NINN1WF7 | 1.0065 | 0.94805 | -0.05842 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | NINN1WF7 | 1.0065 | 0.94805 | -0.05842 |  | 0.95 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | NINN1WF7 | 1.0065 | 0.94805 | -0.05842 |  | 0.95 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | NINN1WF7 | 1.0065 | 0.94805 | -0.05842 |  | 0.95 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | NINN1WF7 | 1.0065 | 0.94805 | -0.05842 |  | 0.95 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | NINN1WF7 | 1.0065 | 0.94805 | -0.05842 |  | 0.95 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | NINN1WF7 | 1.0065 | 0.94805 | -0.05842 |  | 0.95 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | NLOUISB5 | 0.99422 | 0.90779 | -0.086427 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | NLOUISB5 | 0.99422 | 0.90779 | -0.086427 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | NLOUISB5 | 0.99422 | 0.90779 | -0.086427 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | NLOUISB5 | 0.99422 | 0.90779 | -0.086427 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | NLOUISB5 | 0.99422 | 0.90779 | -0.086427 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | NLOUISB5 | 0.99422 | 0.90779 | -0.086427 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | NLOUISB5 | 0.99422 | 0.90779 | -0.086427 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | NLOUISB5 | 0.99422 | 0.90779 | -0.086427 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | NLOUISB5 | 0.99422 | 0.90779 | -0.086427 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | NLOUISB5 | 0.99422 | 0.90779 | -0.086427 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | NLOUISB5 | 0.99422 | 0.90779 | -0.086427 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | NLOUISB5 | 0.99422 | 0.90779 | -0.086427 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | NLOUISB5 | 0.99422 | 0.90779 | -0.086427 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | NLOUISB5 | 0.99422 | 0.90779 | -0.086427 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | NLOUISB5 | 0.99422 | 0.90779 | -0.086427 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | NLOUISB5 | 0.99422 | 0.90779 | -0.086427 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | NLOUISB5 | 0.99422 | 0.90779 | -0.086427 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | NLOUISB5 | 0.99422 | 0.90779 | -0.086427 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | NLOUISB5 | 0.99422 | 0.90779 | -0.086427 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | NLOUISB5 | 0.99422 | 0.90779 | -0.086427 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | NLOUISB5 | 0.99422 | 0.90779 | -0.086427 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | NLOUISB5 | 0.99422 | 0.90779 | -0.086427 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | NLOUISB5 | 0.99422 | 0.90779 | -0.086427 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | NLOUISB5 | 0.99422 | 0.90779 | -0.086427 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | NLOUISB5 | 0.99422 | 0.90779 | -0.086427 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | NOL435 5 | 0.9733 | 0.90711 | -0.066195 |  | 0.925 | 1.05 | 0.033596 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | NOL435 5 | 0.9733 | 0.90711 | -0.066195 |  | 0.925 | 1.05 | 0.040193 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | NOL435 5 | 0.9733 | 0.90711 | -0.066195 |  | 0.925 | 1.05 | 0.088122 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | NOL435 5 | 0.9733 | 0.90711 | -0.066195 |  | 0.925 | 1.05 | 0.074664 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | NOL435 5 | 0.9733 | 0.90711 | -0.066195 |  | 0.925 | 1.05 | 0.068051 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | NOL435 5 | 0.9733 | 0.90711 | -0.066195 |  | 0.925 | 1.05 | 0.035565 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | NOL435 5 | 0.9733 | 0.90711 | -0.066195 |  | 0.925 | 1.05 | 0.033904 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | NOL435 5 | 0.9733 | 0.90711 | -0.066195 |  | 0.925 | 1.05 | 0.16366 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | NOL435 5 | 0.9733 | 0.90711 | -0.066195 |  | 0.925 | 1.05 | 0.045569 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | NOL435 5 | 0.9733 | 0.90711 | -0.066195 |  | 0.925 | 1.05 | 0.13458 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | NOL435 5 | 0.9733 | 0.90711 | -0.066195 |  | 0.925 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | NOL435 5 | 0.9733 | 0.90711 | -0.066195 |  | 0.925 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | NOL435 5 | 0.9733 | 0.90711 | -0.066195 |  | 0.925 | 1.05 | 0.068426 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | NOL435 5 | 0.9733 | 0.90711 | -0.066195 |  | 0.925 | 1.05 | 0.035223 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | NOL435 5 | 0.9733 | 0.90711 | -0.066195 |  | 0.925 | 1.05 | 0.034504 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | NOL435 5 | 0.97346 | 0.90804 | -0.065421 |  | 0.925 | 1.05 | 0.040193 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | NOL435 5 | 0.97346 | 0.90804 | -0.065421 |  | 0.925 | 1.05 | 0.088122 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | NOL435 5 | 0.97346 | 0.90804 | -0.065421 |  | 0.925 | 1.05 | 0.074664 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | NOL435 5 | 0.97346 | 0.90804 | -0.065421 |  | 0.925 | 1.05 | 0.068051 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | NOL435 5 | 0.97346 | 0.90804 | -0.065421 |  | 0.925 | 1.05 | 0.034774 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | NOL435 5 | 0.97346 | 0.90804 | -0.065421 |  | 0.925 | 1.05 | 0.033904 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | NOL435 5 | 0.97346 | 0.90804 | -0.065421 |  | 0.925 | 1.05 | 0.16366 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | NOL435 5 | 0.97346 | 0.90804 | -0.065421 |  | 0.925 | 1.05 | 0.045569 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | NOL435 5 | 0.97346 | 0.90804 | -0.065421 |  | 0.925 | 1.05 | 0.13458 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | NOL435 5 | 0.97346 | 0.90804 | -0.065421 |  | 0.925 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | NOL435 5 | 0.97346 | 0.90804 | -0.065421 |  | 0.925 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | NOL435 5 | 0.97346 | 0.90804 | -0.065421 |  | 0.925 | 1.05 | 0.068426 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | NOL435 5 | 0.97346 | 0.90804 | -0.065421 |  | 0.925 | 1.05 | 0.035223 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | NOL435 5 | 0.97346 | 0.90804 | -0.065421 |  | 0.925 | 1.05 | 0.034504 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | NOL435 5 | 0.97341 | 0.91244 | -0.060965 |  | 0.925 | 1.05 | 0.033596 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | NOL435 5 | 0.97341 | 0.91244 | -0.060965 |  | 0.925 | 1.05 | 0.040193 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | NOL435 5 | 0.97341 | 0.91244 | -0.060965 |  | 0.925 | 1.05 | 0.056051 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | NOL435 5 | 0.97341 | 0.91244 | -0.060965 |  | 0.925 | 1.05 | 0.074664 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | NOL435 5 | 0.97341 | 0.91244 | -0.060965 |  | 0.925 | 1.05 | 0.068051 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | NOL435 5 | 0.97341 | 0.91244 | -0.060965 |  | 0.925 | 1.05 | 0.035565 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | NOL435 5 | 0.97341 | 0.91244 | -0.060965 |  | 0.925 | 1.05 | 0.033904 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | NOL435 5 | 0.97341 | 0.91244 | -0.060965 |  | 0.925 | 1.05 | 0.082596 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | NOL435 5 | 0.97341 | 0.91244 | -0.060965 |  | 0.925 | 1.05 | 0.045569 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | NOL435 5 | 0.97341 | 0.91244 | -0.060965 |  | 0.925 | 1.05 | 0.13458 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | NOL435 5 | 0.97341 | 0.91244 | -0.060965 |  | 0.925 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | NOL435 5 | 0.97341 | 0.91244 | -0.060965 |  | 0.925 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | NOL435 5 | 0.97341 | 0.91244 | -0.060965 |  | 0.925 | 1.05 | 0.068426 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | NOL435 5 | 0.97341 | 0.91244 | -0.060965 |  | 0.925 | 1.05 | 0.035223 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | NOL435 5 | 0.97341 | 0.91244 | -0.060965 |  | 0.925 | 1.05 | 0.034504 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | ASGI-2024-023 | NOL435 5 | 0.9787 | 0.91985 | -0.058853 |  | 0.925 | 1.05 | 0.079962 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | NOL435 5 | 0.9787 | 0.91985 | -0.058853 |  | 0.925 | 1.05 | 0.065323 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-068 | NOL435 5 | 0.9787 | 0.91985 | -0.058853 |  | 0.925 | 1.05 | 0.067422 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-071 | NOL435 5 | 0.9787 | 0.91985 | -0.058853 |  | 0.925 | 1.05 | 0.074668 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | NOL435 5 | 0.9787 | 0.91985 | -0.058853 |  | 0.925 | 1.05 | 0.053027 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-122 | NOL435 5 | 0.9787 | 0.91985 | -0.058853 |  | 0.925 | 1.05 | 0.082926 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-177 | NOL435 5 | 0.9787 | 0.91985 | -0.058853 |  | 0.925 | 1.05 | 0.084694 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-178 | NOL435 5 | 0.9787 | 0.91985 | -0.058853 |  | 0.925 | 1.05 | 0.078867 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | NOL435 5 | 0.9787 | 0.91985 | -0.058853 |  | 0.925 | 1.05 | 0.031571 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-220 | NOL435 5 | 0.9787 | 0.91985 | -0.058853 |  | 0.925 | 1.05 | 0.075331 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-232 | NOL435 5 | 0.9787 | 0.91985 | -0.058853 |  | 0.925 | 1.05 | 0.078906 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | NOL435 5 | 0.9787 | 0.91985 | -0.058853 |  | 0.925 | 1.05 | 0.065323 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | NOL435 5 | 0.9787 | 0.91985 | -0.058853 |  | 0.925 | 1.05 | 0.03431 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | NOL435 5 | 0.9787 | 0.91985 | -0.058853 |  | 0.925 | 1.05 | 0.031504 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | NOL435 5 | 0.9787 | 0.91985 | -0.058853 |  | 0.925 | 1.05 | 0.031504 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | NOL435 5 | 0.9787 | 0.91985 | -0.058853 |  | 0.925 | 1.05 | 0.030663 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | NOL435 5 | 0.9787 | 0.91985 | -0.058853 |  | 0.925 | 1.05 | 0.04269 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-376 | NOL435 5 | 0.9787 | 0.91985 | -0.058853 |  | 0.925 | 1.05 | 0.082476 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | NOL435 5 | 0.97649 | 0.91903 | -0.057461 |  | 0.925 | 1.05 | 0.033596 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.2 MVAR switched shunt at GROVE 5 161 kV; Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | NOL435 5 | 0.97649 | 0.91903 | -0.057461 |  | 0.925 | 1.05 | 0.088122 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.2 MVAR switched shunt at GROVE 5 161 kV; Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | NOL435 5 | 0.97649 | 0.91903 | -0.057461 |  | 0.925 | 1.05 | 0.030897 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.2 MVAR switched shunt at GROVE 5 161 kV; Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | NOL435 5 | 0.97649 | 0.91903 | -0.057461 |  | 0.925 | 1.05 | 0.038719 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.2 MVAR switched shunt at GROVE 5 161 kV; Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | NOL435 5 | 0.97649 | 0.91903 | -0.057461 |  | 0.925 | 1.05 | 0.035565 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.2 MVAR switched shunt at GROVE 5 161 kV; Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | NOL435 5 | 0.97649 | 0.91903 | -0.057461 |  | 0.925 | 1.05 | 0.16366 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.2 MVAR switched shunt at GROVE 5 161 kV; Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | NOL435 5 | 0.97649 | 0.91903 | -0.057461 |  | 0.925 | 1.05 | 0.038589 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.2 MVAR switched shunt at GROVE 5 161 kV; Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | NOL435 5 | 0.97649 | 0.91903 | -0.057461 |  | 0.925 | 1.05 | 0.034208 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.2 MVAR switched shunt at GROVE 5 161 kV; Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | NP-GLAZIR_G2 | 0.69601 | 0.67252 | -0.023493 |  | 0.9 | 1.05 | 0.035768 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | NP-GLAZIR_G2 | 0.69601 | 0.67252 | -0.023493 |  | 0.9 | 1.05 | 0.088718 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | NP-GLAZIR_G2 | 0.69601 | 0.67252 | -0.023493 |  | 0.9 | 1.05 | 0.031473 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | NP-GLAZIR_G2 | 0.69601 | 0.67252 | -0.023493 |  | 0.9 | 1.05 | 0.034941 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | NP-GLAZIR_G2 | 0.69601 | 0.67252 | -0.023493 |  | 0.9 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | NP-GLAZIR_G2 | 0.69601 | 0.67252 | -0.023493 |  | 0.9 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | NP-GLAZIR_G2 | 0.69601 | 0.67252 | -0.023493 |  | 0.9 | 1.05 | 0.049224 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | NP-GLAZIR_G2 | 0.69601 | 0.67252 | -0.023493 |  | 0.9 | 1.05 | 0.038981 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | NP-GLAZIR_G2 | 0.69601 | 0.67252 | -0.023493 |  | 0.9 | 1.05 | 0.040399 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | NP-GLAZIR_G2 | 0.69601 | 0.67252 | -0.023493 |  | 0.9 | 1.05 | 0.031912 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | NP-GLAZIR_G2 | 0.69601 | 0.67252 | -0.023493 |  | 0.9 | 1.05 | 0.034127 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | NP-GLAZIR_G2 | 0.69601 | 0.67252 | -0.023493 |  | 0.9 | 1.05 | 0.047318 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | NP-LIPSCOMB2 | 0.65882 | 0.63439 | -0.024431 |  | 0.9 | 1.05 | 0.035768 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | NP-LIPSCOMB2 | 0.65882 | 0.63439 | -0.024431 |  | 0.9 | 1.05 | 0.088718 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | NP-LIPSCOMB2 | 0.65882 | 0.63439 | -0.024431 |  | 0.9 | 1.05 | 0.031473 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | NP-LIPSCOMB2 | 0.65882 | 0.63439 | -0.024431 |  | 0.9 | 1.05 | 0.034941 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | NP-LIPSCOMB2 | 0.65882 | 0.63439 | -0.024431 |  | 0.9 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | NP-LIPSCOMB2 | 0.65882 | 0.63439 | -0.024431 |  | 0.9 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | NP-LIPSCOMB2 | 0.65882 | 0.63439 | -0.024431 |  | 0.9 | 1.05 | 0.049224 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | NP-LIPSCOMB2 | 0.65882 | 0.63439 | -0.024431 |  | 0.9 | 1.05 | 0.038981 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | NP-LIPSCOMB2 | 0.65882 | 0.63439 | -0.024431 |  | 0.9 | 1.05 | 0.040399 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | NP-LIPSCOMB2 | 0.65882 | 0.63439 | -0.024431 |  | 0.9 | 1.05 | 0.031912 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | NP-LIPSCOMB2 | 0.65882 | 0.63439 | -0.024431 |  | 0.9 | 1.05 | 0.034127 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | NP-LIPSCOMB2 | 0.65882 | 0.63439 | -0.024431 |  | 0.9 | 1.05 | 0.047318 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | NP-LIPSCOMB2 | 0.66435 | 0.65088 | -0.01347 |  | 0.9 | 1.05 | 0.031368 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | NP-LIPSCOMB2 | 0.66435 | 0.65088 | -0.01347 |  | 0.9 | 1.05 | 0.091379 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | NP-LIPSCOMB2 | 0.66435 | 0.65088 | -0.01347 |  | 0.9 | 1.05 | 0.031906 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | NP-LIPSCOMB2 | 0.66435 | 0.65088 | -0.01347 |  | 0.9 | 1.05 | 0.043802 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | NP-LIPSCOMB2 | 0.66435 | 0.65088 | -0.01347 |  | 0.9 | 1.05 | 0.043802 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | NP-LIPSCOMB2 | 0.66435 | 0.65088 | -0.01347 |  | 0.9 | 1.05 | 0.046604 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | NP-LIPSCOMB2 | 0.66435 | 0.65088 | -0.01347 |  | 0.9 | 1.05 | 0.035506 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | NP-LIPSCOMB2 | 0.66435 | 0.65088 | -0.01347 |  | 0.9 | 1.05 | 0.036166 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | NP-LIPSCOMB2 | 0.66435 | 0.65088 | -0.01347 |  | 0.9 | 1.05 | 0.030768 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | NP-LIPSCOMB2 | 0.66435 | 0.65088 | -0.01347 |  | 0.9 | 1.05 | 0.043347 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | NP-LIPS_SHA2 | 0.65882 | 0.63439 | -0.024431 |  | 0.9 | 1.05 | 0.035768 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | NP-LIPS_SHA2 | 0.65882 | 0.63439 | -0.024431 |  | 0.9 | 1.05 | 0.088718 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | NP-LIPS_SHA2 | 0.65882 | 0.63439 | -0.024431 |  | 0.9 | 1.05 | 0.031473 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | NP-LIPS_SHA2 | 0.65882 | 0.63439 | -0.024431 |  | 0.9 | 1.05 | 0.034941 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | NP-LIPS_SHA2 | 0.65882 | 0.63439 | -0.024431 |  | 0.9 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | NP-LIPS_SHA2 | 0.65882 | 0.63439 | -0.024431 |  | 0.9 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | NP-LIPS_SHA2 | 0.65882 | 0.63439 | -0.024431 |  | 0.9 | 1.05 | 0.049224 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | NP-LIPS_SHA2 | 0.65882 | 0.63439 | -0.024431 |  | 0.9 | 1.05 | 0.038981 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | NP-LIPS_SHA2 | 0.65882 | 0.63439 | -0.024431 |  | 0.9 | 1.05 | 0.040399 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | NP-LIPS_SHA2 | 0.65882 | 0.63439 | -0.024431 |  | 0.9 | 1.05 | 0.031912 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | NP-LIPS_SHA2 | 0.65882 | 0.63439 | -0.024431 |  | 0.9 | 1.05 | 0.034127 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | NP-LIPS_SHA2 | 0.65882 | 0.63439 | -0.024431 |  | 0.9 | 1.05 | 0.047318 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | NP-LIPS_SHA2 | 0.66435 | 0.65088 | -0.01347 |  | 0.9 | 1.05 | 0.031368 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | NP-LIPS_SHA2 | 0.66435 | 0.65088 | -0.01347 |  | 0.9 | 1.05 | 0.091379 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | NP-LIPS_SHA2 | 0.66435 | 0.65088 | -0.01347 |  | 0.9 | 1.05 | 0.031906 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | NP-LIPS_SHA2 | 0.66435 | 0.65088 | -0.01347 |  | 0.9 | 1.05 | 0.043802 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | NP-LIPS_SHA2 | 0.66435 | 0.65088 | -0.01347 |  | 0.9 | 1.05 | 0.043802 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | NP-LIPS_SHA2 | 0.66435 | 0.65088 | -0.01347 |  | 0.9 | 1.05 | 0.046604 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | NP-LIPS_SHA2 | 0.66435 | 0.65088 | -0.01347 |  | 0.9 | 1.05 | 0.035506 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | NP-LIPS_SHA2 | 0.66435 | 0.65088 | -0.01347 |  | 0.9 | 1.05 | 0.036166 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | NP-LIPS_SHA2 | 0.66435 | 0.65088 | -0.01347 |  | 0.9 | 1.05 | 0.030768 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | NP-LIPS_SHA2 | 0.66435 | 0.65088 | -0.01347 |  | 0.9 | 1.05 | 0.043347 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | NP-LUCKY_CR2 | 0.7825 | 0.76151 | -0.02099 |  | 0.9 | 1.05 | 0.035768 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | NP-LUCKY_CR2 | 0.7825 | 0.76151 | -0.02099 |  | 0.9 | 1.05 | 0.088718 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | NP-LUCKY_CR2 | 0.7825 | 0.76151 | -0.02099 |  | 0.9 | 1.05 | 0.031473 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | NP-LUCKY_CR2 | 0.7825 | 0.76151 | -0.02099 |  | 0.9 | 1.05 | 0.034941 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | NP-LUCKY_CR2 | 0.7825 | 0.76151 | -0.02099 |  | 0.9 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | NP-LUCKY_CR2 | 0.7825 | 0.76151 | -0.02099 |  | 0.9 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | NP-LUCKY_CR2 | 0.7825 | 0.76151 | -0.02099 |  | 0.9 | 1.05 | 0.049224 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | NP-LUCKY_CR2 | 0.7825 | 0.76151 | -0.02099 |  | 0.9 | 1.05 | 0.038981 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | NP-LUCKY_CR2 | 0.7825 | 0.76151 | -0.02099 |  | 0.9 | 1.05 | 0.040399 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | NP-LUCKY_CR2 | 0.7825 | 0.76151 | -0.02099 |  | 0.9 | 1.05 | 0.031912 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | NP-LUCKY_CR2 | 0.7825 | 0.76151 | -0.02099 |  | 0.9 | 1.05 | 0.034127 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | NP-LUCKY_CR2 | 0.7825 | 0.76151 | -0.02099 |  | 0.9 | 1.05 | 0.047318 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | NP-LUCKY_G 2 | 0.78264 | 0.76165 | -0.020985 |  | 0.9 | 1.05 | 0.035768 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | NP-LUCKY_G 2 | 0.78264 | 0.76165 | -0.020985 |  | 0.9 | 1.05 | 0.088718 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | NP-LUCKY_G 2 | 0.78264 | 0.76165 | -0.020985 |  | 0.9 | 1.05 | 0.031473 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | NP-LUCKY_G 2 | 0.78264 | 0.76165 | -0.020985 |  | 0.9 | 1.05 | 0.034941 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | NP-LUCKY_G 2 | 0.78264 | 0.76165 | -0.020985 |  | 0.9 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | NP-LUCKY_G 2 | 0.78264 | 0.76165 | -0.020985 |  | 0.9 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | NP-LUCKY_G 2 | 0.78264 | 0.76165 | -0.020985 |  | 0.9 | 1.05 | 0.049224 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | NP-LUCKY_G 2 | 0.78264 | 0.76165 | -0.020985 |  | 0.9 | 1.05 | 0.038981 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | NP-LUCKY_G 2 | 0.78264 | 0.76165 | -0.020985 |  | 0.9 | 1.05 | 0.040399 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | NP-LUCKY_G 2 | 0.78264 | 0.76165 | -0.020985 |  | 0.9 | 1.05 | 0.031912 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | NP-LUCKY_G 2 | 0.78264 | 0.76165 | -0.020985 |  | 0.9 | 1.05 | 0.034127 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | NP-LUCKY_G 2 | 0.78264 | 0.76165 | -0.020985 |  | 0.9 | 1.05 | 0.047318 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | NP-SHATTUCK2 | 0.63802 | 0.61312 | -0.024899 |  | 0.9 | 1.05 | 0.035768 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | NP-SHATTUCK2 | 0.63802 | 0.61312 | -0.024899 |  | 0.9 | 1.05 | 0.088718 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | NP-SHATTUCK2 | 0.63802 | 0.61312 | -0.024899 |  | 0.9 | 1.05 | 0.031473 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | NP-SHATTUCK2 | 0.63802 | 0.61312 | -0.024899 |  | 0.9 | 1.05 | 0.034941 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | NP-SHATTUCK2 | 0.63802 | 0.61312 | -0.024899 |  | 0.9 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | NP-SHATTUCK2 | 0.63802 | 0.61312 | -0.024899 |  | 0.9 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | NP-SHATTUCK2 | 0.63802 | 0.61312 | -0.024899 |  | 0.9 | 1.05 | 0.049224 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | NP-SHATTUCK2 | 0.63802 | 0.61312 | -0.024899 |  | 0.9 | 1.05 | 0.038981 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | NP-SHATTUCK2 | 0.63802 | 0.61312 | -0.024899 |  | 0.9 | 1.05 | 0.040399 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | NP-SHATTUCK2 | 0.63802 | 0.61312 | -0.024899 |  | 0.9 | 1.05 | 0.031912 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | NP-SHATTUCK2 | 0.63802 | 0.61312 | -0.024899 |  | 0.9 | 1.05 | 0.034127 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | NP-SHATTUCK2 | 0.63802 | 0.61312 | -0.024899 |  | 0.9 | 1.05 | 0.047318 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | NP-SHATTUCK2 | 0.64368 | 0.62993 | -0.013751 |  | 0.9 | 1.05 | 0.031368 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | NP-SHATTUCK2 | 0.64368 | 0.62993 | -0.013751 |  | 0.9 | 1.05 | 0.091379 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | NP-SHATTUCK2 | 0.64368 | 0.62993 | -0.013751 |  | 0.9 | 1.05 | 0.031906 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | NP-SHATTUCK2 | 0.64368 | 0.62993 | -0.013751 |  | 0.9 | 1.05 | 0.043802 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | NP-SHATTUCK2 | 0.64368 | 0.62993 | -0.013751 |  | 0.9 | 1.05 | 0.043802 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | NP-SHATTUCK2 | 0.64368 | 0.62993 | -0.013751 |  | 0.9 | 1.05 | 0.046604 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | NP-SHATTUCK2 | 0.64368 | 0.62993 | -0.013751 |  | 0.9 | 1.05 | 0.035506 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | NP-SHATTUCK2 | 0.64368 | 0.62993 | -0.013751 |  | 0.9 | 1.05 | 0.036166 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | NP-SHATTUCK2 | 0.64368 | 0.62993 | -0.013751 |  | 0.9 | 1.05 | 0.030768 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | NP-SHATTUCK2 | 0.64368 | 0.62993 | -0.013751 |  | 0.9 | 1.05 | 0.043347 | P42:345:OKGE:SB_DGSE7385:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | NP-SUB_A 2 | 0.8457 | 0.82664 | -0.019063 |  | 0.9 | 1.05 | 0.035768 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | NP-SUB_A 2 | 0.8457 | 0.82664 | -0.019063 |  | 0.9 | 1.05 | 0.088718 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | NP-SUB_A 2 | 0.8457 | 0.82664 | -0.019063 |  | 0.9 | 1.05 | 0.031473 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | NP-SUB_A 2 | 0.8457 | 0.82664 | -0.019063 |  | 0.9 | 1.05 | 0.034941 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | NP-SUB_A 2 | 0.8457 | 0.82664 | -0.019063 |  | 0.9 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | NP-SUB_A 2 | 0.8457 | 0.82664 | -0.019063 |  | 0.9 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | NP-SUB_A 2 | 0.8457 | 0.82664 | -0.019063 |  | 0.9 | 1.05 | 0.049224 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | NP-SUB_A 2 | 0.8457 | 0.82664 | -0.019063 |  | 0.9 | 1.05 | 0.038981 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | NP-SUB_A 2 | 0.8457 | 0.82664 | -0.019063 |  | 0.9 | 1.05 | 0.040399 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | NP-SUB_A 2 | 0.8457 | 0.82664 | -0.019063 |  | 0.9 | 1.05 | 0.031912 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | NP-SUB_A 2 | 0.8457 | 0.82664 | -0.019063 |  | 0.9 | 1.05 | 0.034127 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | NP-SUB_A 2 | 0.8457 | 0.82664 | -0.019063 |  | 0.9 | 1.05 | 0.047318 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | NP-VALERO_P2 | 0.66664 | 0.6424 | -0.024243 |  | 0.9 | 1.05 | 0.035768 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | NP-VALERO_P2 | 0.66664 | 0.6424 | -0.024243 |  | 0.9 | 1.05 | 0.088718 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | NP-VALERO_P2 | 0.66664 | 0.6424 | -0.024243 |  | 0.9 | 1.05 | 0.031473 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | NP-VALERO_P2 | 0.66664 | 0.6424 | -0.024243 |  | 0.9 | 1.05 | 0.034941 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | NP-VALERO_P2 | 0.66664 | 0.6424 | -0.024243 |  | 0.9 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | NP-VALERO_P2 | 0.66664 | 0.6424 | -0.024243 |  | 0.9 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | NP-VALERO_P2 | 0.66664 | 0.6424 | -0.024243 |  | 0.9 | 1.05 | 0.049224 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | NP-VALERO_P2 | 0.66664 | 0.6424 | -0.024243 |  | 0.9 | 1.05 | 0.038981 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | NP-VALERO_P2 | 0.66664 | 0.6424 | -0.024243 |  | 0.9 | 1.05 | 0.040399 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | NP-VALERO_P2 | 0.66664 | 0.6424 | -0.024243 |  | 0.9 | 1.05 | 0.031912 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | NP-VALERO_P2 | 0.66664 | 0.6424 | -0.024243 |  | 0.9 | 1.05 | 0.034127 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | NP-VALERO_P2 | 0.66664 | 0.6424 | -0.024243 |  | 0.9 | 1.05 | 0.047318 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | NRSS7 | 1.0059 | 0.94964 | -0.056239 |  | 0.95 | 1.05 | 0.035768 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | NRSS7 | 1.0059 | 0.94964 | -0.056239 |  | 0.95 | 1.05 | 0.088718 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | NRSS7 | 1.0059 | 0.94964 | -0.056239 |  | 0.95 | 1.05 | 0.031473 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | NRSS7 | 1.0059 | 0.94964 | -0.056239 |  | 0.95 | 1.05 | 0.034941 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | NRSS7 | 1.0059 | 0.94964 | -0.056239 |  | 0.95 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | NRSS7 | 1.0059 | 0.94964 | -0.056239 |  | 0.95 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | NRSS7 | 1.0059 | 0.94964 | -0.056239 |  | 0.95 | 1.05 | 0.049224 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | NRSS7 | 1.0059 | 0.94964 | -0.056239 |  | 0.95 | 1.05 | 0.038981 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | NRSS7 | 1.0059 | 0.94964 | -0.056239 |  | 0.95 | 1.05 | 0.040399 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | NRSS7 | 1.0059 | 0.94964 | -0.056239 |  | 0.95 | 1.05 | 0.031912 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | NRSS7 | 1.0059 | 0.94964 | -0.056239 |  | 0.95 | 1.05 | 0.034127 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | NRSS7 | 1.0059 | 0.94964 | -0.056239 |  | 0.95 | 1.05 | 0.047318 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | NRSS7 | 1.0016 | 0.94094 | -0.060655 |  | 0.95 | 1.05 | 0.040439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | NRSS7 | 1.0016 | 0.94094 | -0.060655 |  | 0.95 | 1.05 | 0.034853 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | NRSS7 | 1.0016 | 0.94094 | -0.060655 |  | 0.95 | 1.05 | 0.046783 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | NRSS7 | 1.0016 | 0.94094 | -0.060655 |  | 0.95 | 1.05 | 0.047615 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | NRSS7 | 1.0016 | 0.94094 | -0.060655 |  | 0.95 | 1.05 | 0.034938 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | NRSS7 | 1.0016 | 0.94094 | -0.060655 |  | 0.95 | 1.05 | 0.037875 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | NRSS7 | 1.0016 | 0.94094 | -0.060655 |  | 0.95 | 1.05 | 0.044022 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | NRSS7 | 1.0016 | 0.94094 | -0.060655 |  | 0.95 | 1.05 | 0.030552 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | NRSS7 | 1.0016 | 0.94094 | -0.060655 |  | 0.95 | 1.05 | 0.038531 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | NRSS7 | 1.0016 | 0.94094 | -0.060655 |  | 0.95 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | NRSS7 | 1.0016 | 0.94094 | -0.060655 |  | 0.95 | 1.05 | 0.062491 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | NRSS7 | 1.0016 | 0.94094 | -0.060655 |  | 0.95 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | NRSS7 | 1.0016 | 0.94094 | -0.060655 |  | 0.95 | 1.05 | 0.038129 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | NRSS7 | 1.0016 | 0.94094 | -0.060655 |  | 0.95 | 1.05 | 0.038066 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | NRSS7 | 1.0016 | 0.94094 | -0.060655 |  | 0.95 | 1.05 | 0.034955 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | NRSS7 | 1.0016 | 0.94094 | -0.060655 |  | 0.95 | 1.05 | 0.06281 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | NRSS7 | 1.0016 | 0.94094 | -0.060655 |  | 0.95 | 1.05 | 0.045309 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | NRSS7 | 1.0016 | 0.94094 | -0.060655 |  | 0.95 | 1.05 | 0.035805 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | NRSS7 | 1.0016 | 0.94094 | -0.060655 |  | 0.95 | 1.05 | 0.032364 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | NRSS7 | 1.0016 | 0.94094 | -0.060655 |  | 0.95 | 1.05 | 0.031815 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | NRSS7 | 1.0016 | 0.94094 | -0.060655 |  | 0.95 | 1.05 | 0.033886 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | NRSS7 | 1.0016 | 0.94094 | -0.060655 |  | 0.95 | 1.05 | 0.035554 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | NRSS7 | 1.0046 | 0.9291 | -0.0755 |  | 0.95 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | NRSS7 | 1.0046 | 0.9291 | -0.0755 |  | 0.95 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | NRSS7 | 1.0046 | 0.9291 | -0.0755 |  | 0.95 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | NRSS7 | 1.0046 | 0.9291 | -0.0755 |  | 0.95 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | NRSS7 | 1.0046 | 0.9291 | -0.0755 |  | 0.95 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | NRSS7 | 1.0046 | 0.9291 | -0.0755 |  | 0.95 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | NRSS7 | 1.0046 | 0.9291 | -0.0755 |  | 0.95 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | NRSS7 | 1.0046 | 0.9291 | -0.0755 |  | 0.95 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | NRSS7 | 1.0046 | 0.9291 | -0.0755 |  | 0.95 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | NRSS7 | 1.0046 | 0.9291 | -0.0755 |  | 0.95 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | NRSS7 | 1.0046 | 0.9291 | -0.0755 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | NRSS7 | 1.0046 | 0.9291 | -0.0755 |  | 0.95 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | NRSS7 | 1.0046 | 0.9291 | -0.0755 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | NRSS7 | 1.0046 | 0.9291 | -0.0755 |  | 0.95 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | NRSS7 | 1.0046 | 0.9291 | -0.0755 |  | 0.95 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | NRSS7 | 1.0046 | 0.9291 | -0.0755 |  | 0.95 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | NRSS7 | 1.0046 | 0.9291 | -0.0755 |  | 0.95 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | NRSS7 | 1.0046 | 0.9291 | -0.0755 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | NRSS7 | 1.0046 | 0.9291 | -0.0755 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | NRSS7 | 1.0046 | 0.9291 | -0.0755 |  | 0.95 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | NRSS7 | 1.0046 | 0.9291 | -0.0755 |  | 0.95 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | NRSS7 | 1.0046 | 0.9291 | -0.0755 |  | 0.95 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | NRSS7 | 1.0046 | 0.9291 | -0.0755 |  | 0.95 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | NRSS7 | 1.0046 | 0.9291 | -0.0755 |  | 0.95 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | NRSS7 | 1.0046 | 0.9291 | -0.0755 |  | 0.95 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | OLATHE 5 | 0.96608 | 0.92409 | -0.041985 |  | 0.93 | 1.05 | 0.036307 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | OLATHE 5 | 0.96608 | 0.92409 | -0.041985 |  | 0.93 | 1.05 | 0.052743 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | OLATHE 5 | 0.96608 | 0.92409 | -0.041985 |  | 0.93 | 1.05 | 0.039345 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | OLATHE 5 | 0.96608 | 0.92409 | -0.041985 |  | 0.93 | 1.05 | 0.031366 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | OLATHE 5 | 0.96608 | 0.92409 | -0.041985 |  | 0.93 | 1.05 | 0.041888 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | OLATHE 5 | 0.96608 | 0.92409 | -0.041985 |  | 0.93 | 1.05 | 0.038797 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | OLATHE 5 | 0.96608 | 0.92409 | -0.041985 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | OLATHE 5 | 0.96608 | 0.92409 | -0.041985 |  | 0.93 | 1.05 | 0.067346 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | OLATHE 5 | 0.96608 | 0.92409 | -0.041985 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | OLATHE 5 | 0.96608 | 0.92409 | -0.041985 |  | 0.93 | 1.05 | 0.030851 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | OLATHE 5 | 0.96608 | 0.92409 | -0.041985 |  | 0.93 | 1.05 | 0.032161 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | OLATHE 5 | 0.96608 | 0.92409 | -0.041985 |  | 0.93 | 1.05 | 0.04067 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | OLATHE 5 | 0.96608 | 0.92409 | -0.041985 |  | 0.93 | 1.05 | 0.040569 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | OLATHE 5 | 0.96608 | 0.92409 | -0.041985 |  | 0.93 | 1.05 | 0.03086 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | OLATHE 5 | 0.96608 | 0.92409 | -0.041985 |  | 0.93 | 1.05 | 0.033223 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | OLATHE 5 | 0.96608 | 0.92409 | -0.041985 |  | 0.93 | 1.05 | 0.033733 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | OLATHE 5 | 0.97628 | 0.92729 | -0.048988 |  | 0.93 | 1.05 | 0.036307 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | OLATHE 5 | 0.97628 | 0.92729 | -0.048988 |  | 0.93 | 1.05 | 0.052743 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | OLATHE 5 | 0.97628 | 0.92729 | -0.048988 |  | 0.93 | 1.05 | 0.039345 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | OLATHE 5 | 0.97628 | 0.92729 | -0.048988 |  | 0.93 | 1.05 | 0.031366 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | OLATHE 5 | 0.97628 | 0.92729 | -0.048988 |  | 0.93 | 1.05 | 0.041888 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | OLATHE 5 | 0.97628 | 0.92729 | -0.048988 |  | 0.93 | 1.05 | 0.038797 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | OLATHE 5 | 0.97628 | 0.92729 | -0.048988 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | OLATHE 5 | 0.97628 | 0.92729 | -0.048988 |  | 0.93 | 1.05 | 0.067346 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | OLATHE 5 | 0.97628 | 0.92729 | -0.048988 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | OLATHE 5 | 0.97628 | 0.92729 | -0.048988 |  | 0.93 | 1.05 | 0.030851 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | OLATHE 5 | 0.97628 | 0.92729 | -0.048988 |  | 0.93 | 1.05 | 0.032161 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | OLATHE 5 | 0.97628 | 0.92729 | -0.048988 |  | 0.93 | 1.05 | 0.04067 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | OLATHE 5 | 0.97628 | 0.92729 | -0.048988 |  | 0.93 | 1.05 | 0.040569 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | OLATHE 5 | 0.97628 | 0.92729 | -0.048988 |  | 0.93 | 1.05 | 0.03086 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | OLATHE 5 | 0.97628 | 0.92729 | -0.048988 |  | 0.93 | 1.05 | 0.033223 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | OLATHE 5 | 0.97628 | 0.92729 | -0.048988 |  | 0.93 | 1.05 | 0.033733 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | OLATHE 5 | 0.97897 | 0.90779 | -0.071182 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | OLATHE 5 | 0.97897 | 0.90779 | -0.071182 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | OLATHE 5 | 0.97897 | 0.90779 | -0.071182 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | OLATHE 5 | 0.97897 | 0.90779 | -0.071182 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | OLATHE 5 | 0.97897 | 0.90779 | -0.071182 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | OLATHE 5 | 0.97897 | 0.90779 | -0.071182 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | OLATHE 5 | 0.97897 | 0.90779 | -0.071182 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | OLATHE 5 | 0.97897 | 0.90779 | -0.071182 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | OLATHE 5 | 0.97897 | 0.90779 | -0.071182 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | OLATHE 5 | 0.97897 | 0.90779 | -0.071182 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | OLATHE 5 | 0.97897 | 0.90779 | -0.071182 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | OLATHE 5 | 0.97897 | 0.90779 | -0.071182 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | OLATHE 5 | 0.97897 | 0.90779 | -0.071182 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | OLATHE 5 | 0.97897 | 0.90779 | -0.071182 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | OLATHE 5 | 0.97897 | 0.90779 | -0.071182 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | OLATHE 5 | 0.97897 | 0.90779 | -0.071182 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | OLATHE 5 | 0.97897 | 0.90779 | -0.071182 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | OLATHE 5 | 0.97897 | 0.90779 | -0.071182 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | OLATHE 5 | 0.97897 | 0.90779 | -0.071182 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | OLATHE 5 | 0.97897 | 0.90779 | -0.071182 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | OLATHE 5 | 0.97897 | 0.90779 | -0.071182 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | OLATHE 5 | 0.97897 | 0.90779 | -0.071182 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | OLATHE 5 | 0.97897 | 0.90779 | -0.071182 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | OLATHE 5 | 0.97897 | 0.90779 | -0.071182 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | OLATHE 5 | 0.97897 | 0.90779 | -0.071182 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | OPENSKY7 | 0.98175 | 0.91124 | -0.070513 |  | 0.92 | 1.05 | 0.035768 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | OPENSKY7 | 0.98175 | 0.91124 | -0.070513 |  | 0.92 | 1.05 | 0.088718 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | OPENSKY7 | 0.98175 | 0.91124 | -0.070513 |  | 0.92 | 1.05 | 0.031473 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | OPENSKY7 | 0.98175 | 0.91124 | -0.070513 |  | 0.92 | 1.05 | 0.034941 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | OPENSKY7 | 0.98175 | 0.91124 | -0.070513 |  | 0.92 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | OPENSKY7 | 0.98175 | 0.91124 | -0.070513 |  | 0.92 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | OPENSKY7 | 0.98175 | 0.91124 | -0.070513 |  | 0.92 | 1.05 | 0.049224 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | OPENSKY7 | 0.98175 | 0.91124 | -0.070513 |  | 0.92 | 1.05 | 0.038981 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | OPENSKY7 | 0.98175 | 0.91124 | -0.070513 |  | 0.92 | 1.05 | 0.040399 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | OPENSKY7 | 0.98175 | 0.91124 | -0.070513 |  | 0.92 | 1.05 | 0.031912 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | OPENSKY7 | 0.98175 | 0.91124 | -0.070513 |  | 0.92 | 1.05 | 0.034127 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | OPENSKY7 | 0.98175 | 0.91124 | -0.070513 |  | 0.92 | 1.05 | 0.047318 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | ASGI-2024-023 | ORDNCE 2 | 0.9558 | 0.90625 | -0.049549 |  | 0.93 | 1.05 | 0.079962 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | ORDNCE 2 | 0.9558 | 0.90625 | -0.049549 |  | 0.93 | 1.05 | 0.065323 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-068 | ORDNCE 2 | 0.9558 | 0.90625 | -0.049549 |  | 0.93 | 1.05 | 0.067422 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-071 | ORDNCE 2 | 0.9558 | 0.90625 | -0.049549 |  | 0.93 | 1.05 | 0.074668 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | ORDNCE 2 | 0.9558 | 0.90625 | -0.049549 |  | 0.93 | 1.05 | 0.053027 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-122 | ORDNCE 2 | 0.9558 | 0.90625 | -0.049549 |  | 0.93 | 1.05 | 0.082926 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-177 | ORDNCE 2 | 0.9558 | 0.90625 | -0.049549 |  | 0.93 | 1.05 | 0.084694 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-178 | ORDNCE 2 | 0.9558 | 0.90625 | -0.049549 |  | 0.93 | 1.05 | 0.078867 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | ORDNCE 2 | 0.9558 | 0.90625 | -0.049549 |  | 0.93 | 1.05 | 0.031571 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-220 | ORDNCE 2 | 0.9558 | 0.90625 | -0.049549 |  | 0.93 | 1.05 | 0.075331 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-232 | ORDNCE 2 | 0.9558 | 0.90625 | -0.049549 |  | 0.93 | 1.05 | 0.078906 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | ORDNCE 2 | 0.9558 | 0.90625 | -0.049549 |  | 0.93 | 1.05 | 0.065323 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | ORDNCE 2 | 0.9558 | 0.90625 | -0.049549 |  | 0.93 | 1.05 | 0.03431 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | ORDNCE 2 | 0.9558 | 0.90625 | -0.049549 |  | 0.93 | 1.05 | 0.031504 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | ORDNCE 2 | 0.9558 | 0.90625 | -0.049549 |  | 0.93 | 1.05 | 0.031504 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | ORDNCE 2 | 0.9558 | 0.90625 | -0.049549 |  | 0.93 | 1.05 | 0.030663 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | ORDNCE 2 | 0.9558 | 0.90625 | -0.049549 |  | 0.93 | 1.05 | 0.04269 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-376 | ORDNCE 2 | 0.9558 | 0.90625 | -0.049549 |  | 0.93 | 1.05 | 0.082476 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | ASGI-2024-023 | ORDNCE 2 | 0.95663 | 0.90952 | -0.047117 |  | 0.93 | 1.05 | 0.10682 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | ORDNCE 2 | 0.95663 | 0.90952 | -0.047117 |  | 0.93 | 1.05 | 0.084049 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-068 | ORDNCE 2 | 0.95663 | 0.90952 | -0.047117 |  | 0.93 | 1.05 | 0.087538 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-071 | ORDNCE 2 | 0.95663 | 0.90952 | -0.047117 |  | 0.93 | 1.05 | 0.099263 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | ORDNCE 2 | 0.95663 | 0.90952 | -0.047117 |  | 0.93 | 1.05 | 0.088785 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-122 | ORDNCE 2 | 0.95663 | 0.90952 | -0.047117 |  | 0.93 | 1.05 | 0.11321 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-177 | ORDNCE 2 | 0.95663 | 0.90952 | -0.047117 |  | 0.93 | 1.05 | 0.11622 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-178 | ORDNCE 2 | 0.95663 | 0.90952 | -0.047117 |  | 0.93 | 1.05 | 0.10702 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | ORDNCE 2 | 0.95663 | 0.90952 | -0.047117 |  | 0.93 | 1.05 | 0.031044 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-220 | ORDNCE 2 | 0.95663 | 0.90952 | -0.047117 |  | 0.93 | 1.05 | 0.10032 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-232 | ORDNCE 2 | 0.95663 | 0.90952 | -0.047117 |  | 0.93 | 1.05 | 0.10939 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | ORDNCE 2 | 0.95663 | 0.90952 | -0.047117 |  | 0.93 | 1.05 | 0.036829 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | ORDNCE 2 | 0.95663 | 0.90952 | -0.047117 |  | 0.93 | 1.05 | 0.084049 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | ORDNCE 2 | 0.95663 | 0.90952 | -0.047117 |  | 0.93 | 1.05 | 0.053387 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | ORDNCE 2 | 0.95663 | 0.90952 | -0.047117 |  | 0.93 | 1.05 | 0.042012 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | ORDNCE 2 | 0.95663 | 0.90952 | -0.047117 |  | 0.93 | 1.05 | 0.042012 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | ORDNCE 2 | 0.95663 | 0.90952 | -0.047117 |  | 0.93 | 1.05 | 0.031418 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | ORDNCE 2 | 0.95663 | 0.90952 | -0.047117 |  | 0.93 | 1.05 | 0.030073 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | ORDNCE 2 | 0.95663 | 0.90952 | -0.047117 |  | 0.93 | 1.05 | 0.047594 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-376 | ORDNCE 2 | 0.95663 | 0.90952 | -0.047117 |  | 0.93 | 1.05 | 0.11583 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | ORDNCE 2 | 0.95723 | 0.9086 | -0.048629 |  | 0.93 | 1.05 | 0.035768 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | ORDNCE 2 | 0.95723 | 0.9086 | -0.048629 |  | 0.93 | 1.05 | 0.088718 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | ORDNCE 2 | 0.95723 | 0.9086 | -0.048629 |  | 0.93 | 1.05 | 0.031473 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | ORDNCE 2 | 0.95723 | 0.9086 | -0.048629 |  | 0.93 | 1.05 | 0.034941 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | ORDNCE 2 | 0.95723 | 0.9086 | -0.048629 |  | 0.93 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | ORDNCE 2 | 0.95723 | 0.9086 | -0.048629 |  | 0.93 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | ORDNCE 2 | 0.95723 | 0.9086 | -0.048629 |  | 0.93 | 1.05 | 0.049224 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | ORDNCE 2 | 0.95723 | 0.9086 | -0.048629 |  | 0.93 | 1.05 | 0.038981 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | ORDNCE 2 | 0.95723 | 0.9086 | -0.048629 |  | 0.93 | 1.05 | 0.040399 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | ORDNCE 2 | 0.95723 | 0.9086 | -0.048629 |  | 0.93 | 1.05 | 0.031912 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | ORDNCE 2 | 0.95723 | 0.9086 | -0.048629 |  | 0.93 | 1.05 | 0.034127 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | ORDNCE 2 | 0.95723 | 0.9086 | -0.048629 |  | 0.93 | 1.05 | 0.047318 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | ORDNCE 2 | 0.9542 | 0.90235 | -0.051853 |  | 0.93 | 1.05 | 0.040439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | ORDNCE 2 | 0.9542 | 0.90235 | -0.051853 |  | 0.93 | 1.05 | 0.034853 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | ORDNCE 2 | 0.9542 | 0.90235 | -0.051853 |  | 0.93 | 1.05 | 0.046783 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | ORDNCE 2 | 0.9542 | 0.90235 | -0.051853 |  | 0.93 | 1.05 | 0.047615 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | ORDNCE 2 | 0.9542 | 0.90235 | -0.051853 |  | 0.93 | 1.05 | 0.034938 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | ORDNCE 2 | 0.9542 | 0.90235 | -0.051853 |  | 0.93 | 1.05 | 0.037875 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | ORDNCE 2 | 0.9542 | 0.90235 | -0.051853 |  | 0.93 | 1.05 | 0.044022 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | ORDNCE 2 | 0.9542 | 0.90235 | -0.051853 |  | 0.93 | 1.05 | 0.030552 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | ORDNCE 2 | 0.9542 | 0.90235 | -0.051853 |  | 0.93 | 1.05 | 0.038531 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | ORDNCE 2 | 0.9542 | 0.90235 | -0.051853 |  | 0.93 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | ORDNCE 2 | 0.9542 | 0.90235 | -0.051853 |  | 0.93 | 1.05 | 0.062491 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | ORDNCE 2 | 0.9542 | 0.90235 | -0.051853 |  | 0.93 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | ORDNCE 2 | 0.9542 | 0.90235 | -0.051853 |  | 0.93 | 1.05 | 0.038129 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | ORDNCE 2 | 0.9542 | 0.90235 | -0.051853 |  | 0.93 | 1.05 | 0.038066 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | ORDNCE 2 | 0.9542 | 0.90235 | -0.051853 |  | 0.93 | 1.05 | 0.034955 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | ORDNCE 2 | 0.9542 | 0.90235 | -0.051853 |  | 0.93 | 1.05 | 0.06281 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | ORDNCE 2 | 0.9542 | 0.90235 | -0.051853 |  | 0.93 | 1.05 | 0.045309 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | ORDNCE 2 | 0.9542 | 0.90235 | -0.051853 |  | 0.93 | 1.05 | 0.035805 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | ORDNCE 2 | 0.9542 | 0.90235 | -0.051853 |  | 0.93 | 1.05 | 0.032364 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | ORDNCE 2 | 0.9542 | 0.90235 | -0.051853 |  | 0.93 | 1.05 | 0.031815 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | ORDNCE 2 | 0.9542 | 0.90235 | -0.051853 |  | 0.93 | 1.05 | 0.033886 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | ORDNCE 2 | 0.9542 | 0.90235 | -0.051853 |  | 0.93 | 1.05 | 0.035554 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | ORDNCE 2 | 0.9556 | 0.88864 | -0.066958 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | ORDNCE 2 | 0.9556 | 0.88864 | -0.066958 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | ORDNCE 2 | 0.9556 | 0.88864 | -0.066958 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | ORDNCE 2 | 0.9556 | 0.88864 | -0.066958 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | ORDNCE 2 | 0.9556 | 0.88864 | -0.066958 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | ORDNCE 2 | 0.9556 | 0.88864 | -0.066958 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | ORDNCE 2 | 0.9556 | 0.88864 | -0.066958 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | ORDNCE 2 | 0.9556 | 0.88864 | -0.066958 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | ORDNCE 2 | 0.9556 | 0.88864 | -0.066958 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | ORDNCE 2 | 0.9556 | 0.88864 | -0.066958 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | ORDNCE 2 | 0.9556 | 0.88864 | -0.066958 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | ORDNCE 2 | 0.9556 | 0.88864 | -0.066958 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | ORDNCE 2 | 0.9556 | 0.88864 | -0.066958 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | ORDNCE 2 | 0.9556 | 0.88864 | -0.066958 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | ORDNCE 2 | 0.9556 | 0.88864 | -0.066958 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | ORDNCE 2 | 0.9556 | 0.88864 | -0.066958 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | ORDNCE 2 | 0.9556 | 0.88864 | -0.066958 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | ORDNCE 2 | 0.9556 | 0.88864 | -0.066958 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | ORDNCE 2 | 0.9556 | 0.88864 | -0.066958 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | ORDNCE 2 | 0.9556 | 0.88864 | -0.066958 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | ORDNCE 2 | 0.9556 | 0.88864 | -0.066958 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | ORDNCE 2 | 0.9556 | 0.88864 | -0.066958 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | ORDNCE 2 | 0.9556 | 0.88864 | -0.066958 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | ORDNCE 2 | 0.9556 | 0.88864 | -0.066958 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | ORDNCE 2 | 0.9556 | 0.88864 | -0.066958 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | ASGI-2024-023 | ORDNJCT2 | 0.95631 | 0.90679 | -0.04952 |  | 0.93 | 1.05 | 0.079962 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | ORDNJCT2 | 0.95631 | 0.90679 | -0.04952 |  | 0.93 | 1.05 | 0.065323 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-068 | ORDNJCT2 | 0.95631 | 0.90679 | -0.04952 |  | 0.93 | 1.05 | 0.067422 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-071 | ORDNJCT2 | 0.95631 | 0.90679 | -0.04952 |  | 0.93 | 1.05 | 0.074668 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | ORDNJCT2 | 0.95631 | 0.90679 | -0.04952 |  | 0.93 | 1.05 | 0.053027 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-122 | ORDNJCT2 | 0.95631 | 0.90679 | -0.04952 |  | 0.93 | 1.05 | 0.082926 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-177 | ORDNJCT2 | 0.95631 | 0.90679 | -0.04952 |  | 0.93 | 1.05 | 0.084694 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-178 | ORDNJCT2 | 0.95631 | 0.90679 | -0.04952 |  | 0.93 | 1.05 | 0.078867 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | ORDNJCT2 | 0.95631 | 0.90679 | -0.04952 |  | 0.93 | 1.05 | 0.031571 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-220 | ORDNJCT2 | 0.95631 | 0.90679 | -0.04952 |  | 0.93 | 1.05 | 0.075331 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-232 | ORDNJCT2 | 0.95631 | 0.90679 | -0.04952 |  | 0.93 | 1.05 | 0.078906 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | ORDNJCT2 | 0.95631 | 0.90679 | -0.04952 |  | 0.93 | 1.05 | 0.065323 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | ORDNJCT2 | 0.95631 | 0.90679 | -0.04952 |  | 0.93 | 1.05 | 0.03431 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | ORDNJCT2 | 0.95631 | 0.90679 | -0.04952 |  | 0.93 | 1.05 | 0.031504 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | ORDNJCT2 | 0.95631 | 0.90679 | -0.04952 |  | 0.93 | 1.05 | 0.031504 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | ORDNJCT2 | 0.95631 | 0.90679 | -0.04952 |  | 0.93 | 1.05 | 0.030663 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | ORDNJCT2 | 0.95631 | 0.90679 | -0.04952 |  | 0.93 | 1.05 | 0.04269 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-376 | ORDNJCT2 | 0.95631 | 0.90679 | -0.04952 |  | 0.93 | 1.05 | 0.082476 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | ASGI-2024-023 | ORDNJCT2 | 0.95714 | 0.91005 | -0.04709 |  | 0.93 | 1.05 | 0.10682 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | ORDNJCT2 | 0.95714 | 0.91005 | -0.04709 |  | 0.93 | 1.05 | 0.084049 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-068 | ORDNJCT2 | 0.95714 | 0.91005 | -0.04709 |  | 0.93 | 1.05 | 0.087538 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-071 | ORDNJCT2 | 0.95714 | 0.91005 | -0.04709 |  | 0.93 | 1.05 | 0.099263 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | ORDNJCT2 | 0.95714 | 0.91005 | -0.04709 |  | 0.93 | 1.05 | 0.088785 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-122 | ORDNJCT2 | 0.95714 | 0.91005 | -0.04709 |  | 0.93 | 1.05 | 0.11321 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-177 | ORDNJCT2 | 0.95714 | 0.91005 | -0.04709 |  | 0.93 | 1.05 | 0.11622 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-178 | ORDNJCT2 | 0.95714 | 0.91005 | -0.04709 |  | 0.93 | 1.05 | 0.10702 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | ORDNJCT2 | 0.95714 | 0.91005 | -0.04709 |  | 0.93 | 1.05 | 0.031044 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-220 | ORDNJCT2 | 0.95714 | 0.91005 | -0.04709 |  | 0.93 | 1.05 | 0.10032 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-232 | ORDNJCT2 | 0.95714 | 0.91005 | -0.04709 |  | 0.93 | 1.05 | 0.10939 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | ORDNJCT2 | 0.95714 | 0.91005 | -0.04709 |  | 0.93 | 1.05 | 0.036829 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | ORDNJCT2 | 0.95714 | 0.91005 | -0.04709 |  | 0.93 | 1.05 | 0.084049 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | ORDNJCT2 | 0.95714 | 0.91005 | -0.04709 |  | 0.93 | 1.05 | 0.053387 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | ORDNJCT2 | 0.95714 | 0.91005 | -0.04709 |  | 0.93 | 1.05 | 0.042012 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | ORDNJCT2 | 0.95714 | 0.91005 | -0.04709 |  | 0.93 | 1.05 | 0.042012 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | ORDNJCT2 | 0.95714 | 0.91005 | -0.04709 |  | 0.93 | 1.05 | 0.031418 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | ORDNJCT2 | 0.95714 | 0.91005 | -0.04709 |  | 0.93 | 1.05 | 0.030073 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | ORDNJCT2 | 0.95714 | 0.91005 | -0.04709 |  | 0.93 | 1.05 | 0.047594 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-376 | ORDNJCT2 | 0.95714 | 0.91005 | -0.04709 |  | 0.93 | 1.05 | 0.11583 | P23:500:EES-EAI:KEO:B4921::EHV: | Add 0.2 MVAR switched shunt at ALTAMNS2 69 kV; Add 0.02 MVAR switched shunt at NEOSHON2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | ORDNJCT2 | 0.95774 | 0.90914 | -0.048601 |  | 0.93 | 1.05 | 0.035768 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | ORDNJCT2 | 0.95774 | 0.90914 | -0.048601 |  | 0.93 | 1.05 | 0.088718 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | ORDNJCT2 | 0.95774 | 0.90914 | -0.048601 |  | 0.93 | 1.05 | 0.031473 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | ORDNJCT2 | 0.95774 | 0.90914 | -0.048601 |  | 0.93 | 1.05 | 0.034941 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | ORDNJCT2 | 0.95774 | 0.90914 | -0.048601 |  | 0.93 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | ORDNJCT2 | 0.95774 | 0.90914 | -0.048601 |  | 0.93 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | ORDNJCT2 | 0.95774 | 0.90914 | -0.048601 |  | 0.93 | 1.05 | 0.049224 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | ORDNJCT2 | 0.95774 | 0.90914 | -0.048601 |  | 0.93 | 1.05 | 0.038981 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | ORDNJCT2 | 0.95774 | 0.90914 | -0.048601 |  | 0.93 | 1.05 | 0.040399 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | ORDNJCT2 | 0.95774 | 0.90914 | -0.048601 |  | 0.93 | 1.05 | 0.031912 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | ORDNJCT2 | 0.95774 | 0.90914 | -0.048601 |  | 0.93 | 1.05 | 0.034127 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | ORDNJCT2 | 0.95774 | 0.90914 | -0.048601 |  | 0.93 | 1.05 | 0.047318 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | ORDNJCT2 | 0.95471 | 0.90289 | -0.051823 |  | 0.93 | 1.05 | 0.040439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | ORDNJCT2 | 0.95471 | 0.90289 | -0.051823 |  | 0.93 | 1.05 | 0.034853 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | ORDNJCT2 | 0.95471 | 0.90289 | -0.051823 |  | 0.93 | 1.05 | 0.046783 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | ORDNJCT2 | 0.95471 | 0.90289 | -0.051823 |  | 0.93 | 1.05 | 0.047615 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | ORDNJCT2 | 0.95471 | 0.90289 | -0.051823 |  | 0.93 | 1.05 | 0.034938 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | ORDNJCT2 | 0.95471 | 0.90289 | -0.051823 |  | 0.93 | 1.05 | 0.037875 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | ORDNJCT2 | 0.95471 | 0.90289 | -0.051823 |  | 0.93 | 1.05 | 0.044022 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | ORDNJCT2 | 0.95471 | 0.90289 | -0.051823 |  | 0.93 | 1.05 | 0.030552 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | ORDNJCT2 | 0.95471 | 0.90289 | -0.051823 |  | 0.93 | 1.05 | 0.038531 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | ORDNJCT2 | 0.95471 | 0.90289 | -0.051823 |  | 0.93 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | ORDNJCT2 | 0.95471 | 0.90289 | -0.051823 |  | 0.93 | 1.05 | 0.062491 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | ORDNJCT2 | 0.95471 | 0.90289 | -0.051823 |  | 0.93 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | ORDNJCT2 | 0.95471 | 0.90289 | -0.051823 |  | 0.93 | 1.05 | 0.038129 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | ORDNJCT2 | 0.95471 | 0.90289 | -0.051823 |  | 0.93 | 1.05 | 0.038066 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | ORDNJCT2 | 0.95471 | 0.90289 | -0.051823 |  | 0.93 | 1.05 | 0.034955 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | ORDNJCT2 | 0.95471 | 0.90289 | -0.051823 |  | 0.93 | 1.05 | 0.06281 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | ORDNJCT2 | 0.95471 | 0.90289 | -0.051823 |  | 0.93 | 1.05 | 0.045309 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | ORDNJCT2 | 0.95471 | 0.90289 | -0.051823 |  | 0.93 | 1.05 | 0.035805 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | ORDNJCT2 | 0.95471 | 0.90289 | -0.051823 |  | 0.93 | 1.05 | 0.032364 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | ORDNJCT2 | 0.95471 | 0.90289 | -0.051823 |  | 0.93 | 1.05 | 0.031815 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | ORDNJCT2 | 0.95471 | 0.90289 | -0.051823 |  | 0.93 | 1.05 | 0.033886 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | ORDNJCT2 | 0.95471 | 0.90289 | -0.051823 |  | 0.93 | 1.05 | 0.035554 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | ORDNJCT2 | 0.9561 | 0.88919 | -0.066919 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | ORDNJCT2 | 0.9561 | 0.88919 | -0.066919 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | ORDNJCT2 | 0.9561 | 0.88919 | -0.066919 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | ORDNJCT2 | 0.9561 | 0.88919 | -0.066919 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | ORDNJCT2 | 0.9561 | 0.88919 | -0.066919 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | ORDNJCT2 | 0.9561 | 0.88919 | -0.066919 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | ORDNJCT2 | 0.9561 | 0.88919 | -0.066919 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | ORDNJCT2 | 0.9561 | 0.88919 | -0.066919 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | ORDNJCT2 | 0.9561 | 0.88919 | -0.066919 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | ORDNJCT2 | 0.9561 | 0.88919 | -0.066919 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | ORDNJCT2 | 0.9561 | 0.88919 | -0.066919 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | ORDNJCT2 | 0.9561 | 0.88919 | -0.066919 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | ORDNJCT2 | 0.9561 | 0.88919 | -0.066919 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | ORDNJCT2 | 0.9561 | 0.88919 | -0.066919 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | ORDNJCT2 | 0.9561 | 0.88919 | -0.066919 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | ORDNJCT2 | 0.9561 | 0.88919 | -0.066919 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | ORDNJCT2 | 0.9561 | 0.88919 | -0.066919 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | ORDNJCT2 | 0.9561 | 0.88919 | -0.066919 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | ORDNJCT2 | 0.9561 | 0.88919 | -0.066919 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | ORDNJCT2 | 0.9561 | 0.88919 | -0.066919 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | ORDNJCT2 | 0.9561 | 0.88919 | -0.066919 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | ORDNJCT2 | 0.9561 | 0.88919 | -0.066919 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | ORDNJCT2 | 0.9561 | 0.88919 | -0.066919 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | ORDNJCT2 | 0.9561 | 0.88919 | -0.066919 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | ORDNJCT2 | 0.9561 | 0.88919 | -0.066919 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | OSAGE 3 | 0.97176 | 0.89401 | -0.077758 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | OSAGE 3 | 0.97176 | 0.89401 | -0.077758 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | OSAGE 3 | 0.97176 | 0.89401 | -0.077758 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | OSAGE 3 | 0.97176 | 0.89401 | -0.077758 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | OSAGE 3 | 0.97176 | 0.89401 | -0.077758 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | OSAGE 3 | 0.97176 | 0.89401 | -0.077758 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | OSAGE 3 | 0.97176 | 0.89401 | -0.077758 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | OSAGE 3 | 0.97176 | 0.89401 | -0.077758 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | OSAGE 3 | 0.97176 | 0.89401 | -0.077758 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | OSAGE 3 | 0.97176 | 0.89401 | -0.077758 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | OSAGE 3 | 0.97176 | 0.89401 | -0.077758 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | OSAGE 3 | 0.97176 | 0.89401 | -0.077758 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | OSAGE 3 | 0.97176 | 0.89401 | -0.077758 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | OSAGE 3 | 0.97176 | 0.89401 | -0.077758 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | OSAGE 3 | 0.97176 | 0.89401 | -0.077758 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | OSAGE 3 | 0.97176 | 0.89401 | -0.077758 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | OSAGE 3 | 0.97176 | 0.89401 | -0.077758 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | OSAGE 3 | 0.97176 | 0.89401 | -0.077758 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | OSAGE 3 | 0.97176 | 0.89401 | -0.077758 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | OSAGE 3 | 0.97176 | 0.89401 | -0.077758 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | OSAGE 3 | 0.97176 | 0.89401 | -0.077758 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | OSAGE 3 | 0.97176 | 0.89401 | -0.077758 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | OSAGE 3 | 0.97176 | 0.89401 | -0.077758 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | OSAGE 3 | 0.97176 | 0.89401 | -0.077758 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | OSAGE 3 | 0.97176 | 0.89401 | -0.077758 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | OSAGE J3 | 0.97271 | 0.89503 | -0.077673 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | OSAGE J3 | 0.97271 | 0.89503 | -0.077673 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | OSAGE J3 | 0.97271 | 0.89503 | -0.077673 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | OSAGE J3 | 0.97271 | 0.89503 | -0.077673 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | OSAGE J3 | 0.97271 | 0.89503 | -0.077673 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | OSAGE J3 | 0.97271 | 0.89503 | -0.077673 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | OSAGE J3 | 0.97271 | 0.89503 | -0.077673 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | OSAGE J3 | 0.97271 | 0.89503 | -0.077673 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | OSAGE J3 | 0.97271 | 0.89503 | -0.077673 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | OSAGE J3 | 0.97271 | 0.89503 | -0.077673 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | OSAGE J3 | 0.97271 | 0.89503 | -0.077673 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | OSAGE J3 | 0.97271 | 0.89503 | -0.077673 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | OSAGE J3 | 0.97271 | 0.89503 | -0.077673 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | OSAGE J3 | 0.97271 | 0.89503 | -0.077673 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | OSAGE J3 | 0.97271 | 0.89503 | -0.077673 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | OSAGE J3 | 0.97271 | 0.89503 | -0.077673 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | OSAGE J3 | 0.97271 | 0.89503 | -0.077673 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | OSAGE J3 | 0.97271 | 0.89503 | -0.077673 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | OSAGE J3 | 0.97271 | 0.89503 | -0.077673 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | OSAGE J3 | 0.97271 | 0.89503 | -0.077673 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | OSAGE J3 | 0.97271 | 0.89503 | -0.077673 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | OSAGE J3 | 0.97271 | 0.89503 | -0.077673 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | OSAGE J3 | 0.97271 | 0.89503 | -0.077673 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | OSAGE J3 | 0.97271 | 0.89503 | -0.077673 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | OSAGE J3 | 0.97271 | 0.89503 | -0.077673 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | OSAWAT 5 | 0.98974 | 0.92552 | -0.064218 |  | 0.93 | 1.05 | 0.036307 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | OSAWAT 5 | 0.98974 | 0.92552 | -0.064218 |  | 0.93 | 1.05 | 0.052743 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | OSAWAT 5 | 0.98974 | 0.92552 | -0.064218 |  | 0.93 | 1.05 | 0.039345 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | OSAWAT 5 | 0.98974 | 0.92552 | -0.064218 |  | 0.93 | 1.05 | 0.031366 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | OSAWAT 5 | 0.98974 | 0.92552 | -0.064218 |  | 0.93 | 1.05 | 0.041888 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | OSAWAT 5 | 0.98974 | 0.92552 | -0.064218 |  | 0.93 | 1.05 | 0.038797 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | OSAWAT 5 | 0.98974 | 0.92552 | -0.064218 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | OSAWAT 5 | 0.98974 | 0.92552 | -0.064218 |  | 0.93 | 1.05 | 0.067346 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | OSAWAT 5 | 0.98974 | 0.92552 | -0.064218 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | OSAWAT 5 | 0.98974 | 0.92552 | -0.064218 |  | 0.93 | 1.05 | 0.030851 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | OSAWAT 5 | 0.98974 | 0.92552 | -0.064218 |  | 0.93 | 1.05 | 0.032161 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | OSAWAT 5 | 0.98974 | 0.92552 | -0.064218 |  | 0.93 | 1.05 | 0.04067 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | OSAWAT 5 | 0.98974 | 0.92552 | -0.064218 |  | 0.93 | 1.05 | 0.040569 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | OSAWAT 5 | 0.98974 | 0.92552 | -0.064218 |  | 0.93 | 1.05 | 0.03086 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | OSAWAT 5 | 0.98974 | 0.92552 | -0.064218 |  | 0.93 | 1.05 | 0.033223 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | OSAWAT 5 | 0.98974 | 0.92552 | -0.064218 |  | 0.93 | 1.05 | 0.033733 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | OSAWAT 5 | 0.99973 | 0.92733 | -0.072399 |  | 0.93 | 1.05 | 0.036307 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | OSAWAT 5 | 0.99973 | 0.92733 | -0.072399 |  | 0.93 | 1.05 | 0.052743 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | OSAWAT 5 | 0.99973 | 0.92733 | -0.072399 |  | 0.93 | 1.05 | 0.039345 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | OSAWAT 5 | 0.99973 | 0.92733 | -0.072399 |  | 0.93 | 1.05 | 0.031366 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | OSAWAT 5 | 0.99973 | 0.92733 | -0.072399 |  | 0.93 | 1.05 | 0.041888 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | OSAWAT 5 | 0.99973 | 0.92733 | -0.072399 |  | 0.93 | 1.05 | 0.038797 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | OSAWAT 5 | 0.99973 | 0.92733 | -0.072399 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | OSAWAT 5 | 0.99973 | 0.92733 | -0.072399 |  | 0.93 | 1.05 | 0.067346 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | OSAWAT 5 | 0.99973 | 0.92733 | -0.072399 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | OSAWAT 5 | 0.99973 | 0.92733 | -0.072399 |  | 0.93 | 1.05 | 0.030851 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | OSAWAT 5 | 0.99973 | 0.92733 | -0.072399 |  | 0.93 | 1.05 | 0.032161 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | OSAWAT 5 | 0.99973 | 0.92733 | -0.072399 |  | 0.93 | 1.05 | 0.04067 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | OSAWAT 5 | 0.99973 | 0.92733 | -0.072399 |  | 0.93 | 1.05 | 0.040569 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | OSAWAT 5 | 0.99973 | 0.92733 | -0.072399 |  | 0.93 | 1.05 | 0.03086 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | OSAWAT 5 | 0.99973 | 0.92733 | -0.072399 |  | 0.93 | 1.05 | 0.033223 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | OSAWAT 5 | 0.99973 | 0.92733 | -0.072399 |  | 0.93 | 1.05 | 0.033733 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | OSAWAT 5 | 1.0024 | 0.90502 | -0.097351 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | OSAWAT 5 | 1.0024 | 0.90502 | -0.097351 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | OSAWAT 5 | 1.0024 | 0.90502 | -0.097351 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | OSAWAT 5 | 1.0024 | 0.90502 | -0.097351 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | OSAWAT 5 | 1.0024 | 0.90502 | -0.097351 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | OSAWAT 5 | 1.0024 | 0.90502 | -0.097351 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | OSAWAT 5 | 1.0024 | 0.90502 | -0.097351 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | OSAWAT 5 | 1.0024 | 0.90502 | -0.097351 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | OSAWAT 5 | 1.0024 | 0.90502 | -0.097351 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | OSAWAT 5 | 1.0024 | 0.90502 | -0.097351 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | OSAWAT 5 | 1.0024 | 0.90502 | -0.097351 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | OSAWAT 5 | 1.0024 | 0.90502 | -0.097351 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | OSAWAT 5 | 1.0024 | 0.90502 | -0.097351 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | OSAWAT 5 | 1.0024 | 0.90502 | -0.097351 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | OSAWAT 5 | 1.0024 | 0.90502 | -0.097351 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | OSAWAT 5 | 1.0024 | 0.90502 | -0.097351 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | OSAWAT 5 | 1.0024 | 0.90502 | -0.097351 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | OSAWAT 5 | 1.0024 | 0.90502 | -0.097351 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | OSAWAT 5 | 1.0024 | 0.90502 | -0.097351 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | OSAWAT 5 | 1.0024 | 0.90502 | -0.097351 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | OSAWAT 5 | 1.0024 | 0.90502 | -0.097351 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | OSAWAT 5 | 1.0024 | 0.90502 | -0.097351 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | OSAWAT 5 | 1.0024 | 0.90502 | -0.097351 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | OSAWAT 5 | 1.0024 | 0.90502 | -0.097351 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | OSAWAT 5 | 1.0024 | 0.90502 | -0.097351 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | OSAWTM_CAP5 | 0.99086 | 0.92657 | -0.064292 |  | 0.93 | 1.05 | 0.036307 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | OSAWTM_CAP5 | 0.99086 | 0.92657 | -0.064292 |  | 0.93 | 1.05 | 0.052743 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | OSAWTM_CAP5 | 0.99086 | 0.92657 | -0.064292 |  | 0.93 | 1.05 | 0.039345 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | OSAWTM_CAP5 | 0.99086 | 0.92657 | -0.064292 |  | 0.93 | 1.05 | 0.031366 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | OSAWTM_CAP5 | 0.99086 | 0.92657 | -0.064292 |  | 0.93 | 1.05 | 0.041888 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | OSAWTM_CAP5 | 0.99086 | 0.92657 | -0.064292 |  | 0.93 | 1.05 | 0.038797 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | OSAWTM_CAP5 | 0.99086 | 0.92657 | -0.064292 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | OSAWTM_CAP5 | 0.99086 | 0.92657 | -0.064292 |  | 0.93 | 1.05 | 0.067346 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | OSAWTM_CAP5 | 0.99086 | 0.92657 | -0.064292 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | OSAWTM_CAP5 | 0.99086 | 0.92657 | -0.064292 |  | 0.93 | 1.05 | 0.030851 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | OSAWTM_CAP5 | 0.99086 | 0.92657 | -0.064292 |  | 0.93 | 1.05 | 0.032161 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | OSAWTM_CAP5 | 0.99086 | 0.92657 | -0.064292 |  | 0.93 | 1.05 | 0.04067 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | OSAWTM_CAP5 | 0.99086 | 0.92657 | -0.064292 |  | 0.93 | 1.05 | 0.040569 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | OSAWTM_CAP5 | 0.99086 | 0.92657 | -0.064292 |  | 0.93 | 1.05 | 0.03086 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | OSAWTM_CAP5 | 0.99086 | 0.92657 | -0.064292 |  | 0.93 | 1.05 | 0.033223 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | OSAWTM_CAP5 | 0.99086 | 0.92657 | -0.064292 |  | 0.93 | 1.05 | 0.033733 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | OSAWTM_CAP5 | 1.0009 | 0.92839 | -0.072482 |  | 0.93 | 1.05 | 0.036307 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | OSAWTM_CAP5 | 1.0009 | 0.92839 | -0.072482 |  | 0.93 | 1.05 | 0.052743 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | OSAWTM_CAP5 | 1.0009 | 0.92839 | -0.072482 |  | 0.93 | 1.05 | 0.039345 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | OSAWTM_CAP5 | 1.0009 | 0.92839 | -0.072482 |  | 0.93 | 1.05 | 0.031366 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | OSAWTM_CAP5 | 1.0009 | 0.92839 | -0.072482 |  | 0.93 | 1.05 | 0.041888 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | OSAWTM_CAP5 | 1.0009 | 0.92839 | -0.072482 |  | 0.93 | 1.05 | 0.038797 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | OSAWTM_CAP5 | 1.0009 | 0.92839 | -0.072482 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | OSAWTM_CAP5 | 1.0009 | 0.92839 | -0.072482 |  | 0.93 | 1.05 | 0.067346 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | OSAWTM_CAP5 | 1.0009 | 0.92839 | -0.072482 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | OSAWTM_CAP5 | 1.0009 | 0.92839 | -0.072482 |  | 0.93 | 1.05 | 0.030851 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | OSAWTM_CAP5 | 1.0009 | 0.92839 | -0.072482 |  | 0.93 | 1.05 | 0.032161 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | OSAWTM_CAP5 | 1.0009 | 0.92839 | -0.072482 |  | 0.93 | 1.05 | 0.04067 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | OSAWTM_CAP5 | 1.0009 | 0.92839 | -0.072482 |  | 0.93 | 1.05 | 0.040569 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | OSAWTM_CAP5 | 1.0009 | 0.92839 | -0.072482 |  | 0.93 | 1.05 | 0.03086 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | OSAWTM_CAP5 | 1.0009 | 0.92839 | -0.072482 |  | 0.93 | 1.05 | 0.033223 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | OSAWTM_CAP5 | 1.0009 | 0.92839 | -0.072482 |  | 0.93 | 1.05 | 0.033733 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | OSAWTM_CAP5 | 1.0035 | 0.90606 | -0.097462 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | OSAWTM_CAP5 | 1.0035 | 0.90606 | -0.097462 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | OSAWTM_CAP5 | 1.0035 | 0.90606 | -0.097462 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | OSAWTM_CAP5 | 1.0035 | 0.90606 | -0.097462 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | OSAWTM_CAP5 | 1.0035 | 0.90606 | -0.097462 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | OSAWTM_CAP5 | 1.0035 | 0.90606 | -0.097462 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | OSAWTM_CAP5 | 1.0035 | 0.90606 | -0.097462 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | OSAWTM_CAP5 | 1.0035 | 0.90606 | -0.097462 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | OSAWTM_CAP5 | 1.0035 | 0.90606 | -0.097462 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | OSAWTM_CAP5 | 1.0035 | 0.90606 | -0.097462 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | OSAWTM_CAP5 | 1.0035 | 0.90606 | -0.097462 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | OSAWTM_CAP5 | 1.0035 | 0.90606 | -0.097462 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | OSAWTM_CAP5 | 1.0035 | 0.90606 | -0.097462 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | OSAWTM_CAP5 | 1.0035 | 0.90606 | -0.097462 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | OSAWTM_CAP5 | 1.0035 | 0.90606 | -0.097462 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | OSAWTM_CAP5 | 1.0035 | 0.90606 | -0.097462 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | OSAWTM_CAP5 | 1.0035 | 0.90606 | -0.097462 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | OSAWTM_CAP5 | 1.0035 | 0.90606 | -0.097462 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | OSAWTM_CAP5 | 1.0035 | 0.90606 | -0.097462 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | OSAWTM_CAP5 | 1.0035 | 0.90606 | -0.097462 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | OSAWTM_CAP5 | 1.0035 | 0.90606 | -0.097462 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | OSAWTM_CAP5 | 1.0035 | 0.90606 | -0.097462 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | OSAWTM_CAP5 | 1.0035 | 0.90606 | -0.097462 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | OSAWTM_CAP5 | 1.0035 | 0.90606 | -0.097462 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | OSAWTM_CAP5 | 1.0035 | 0.90606 | -0.097462 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | OTTRCRK3 | 0.97681 | 0.91657 | -0.06024 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | OTTRCRK3 | 0.97681 | 0.91657 | -0.06024 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | OTTRCRK3 | 0.97681 | 0.91657 | -0.06024 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | OTTRCRK3 | 0.97681 | 0.91657 | -0.06024 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | OTTRCRK3 | 0.97681 | 0.91657 | -0.06024 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | OTTRCRK3 | 0.97681 | 0.91657 | -0.06024 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | OTTRCRK3 | 0.97681 | 0.91657 | -0.06024 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | OTTRCRK3 | 0.97681 | 0.91657 | -0.06024 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | OTTRCRK3 | 0.97681 | 0.91657 | -0.06024 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | OTTRCRK3 | 0.97681 | 0.91657 | -0.06024 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | OTTRCRK3 | 0.97681 | 0.91657 | -0.06024 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | OTTRCRK3 | 0.97681 | 0.91657 | -0.06024 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | OTTRCRK3 | 0.97681 | 0.91657 | -0.06024 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | OTTRCRK3 | 0.97681 | 0.91657 | -0.06024 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | OTTRCRK3 | 0.97681 | 0.91657 | -0.06024 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | OTTRCRK3 | 0.97681 | 0.91657 | -0.06024 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | OTTRCRK3 | 0.97681 | 0.91657 | -0.06024 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | OTTRCRK3 | 0.97681 | 0.91657 | -0.06024 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | OTTRCRK3 | 0.97681 | 0.91657 | -0.06024 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | OTTRCRK3 | 0.97681 | 0.91657 | -0.06024 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | OTTRCRK3 | 0.97681 | 0.91657 | -0.06024 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | OTTRCRK3 | 0.97681 | 0.91657 | -0.06024 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | OTTRCRK3 | 0.97681 | 0.91657 | -0.06024 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | OTTRCRK3 | 0.97681 | 0.91657 | -0.06024 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | OTTRCRK3 | 0.97681 | 0.91657 | -0.06024 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | OTTRCRK4 | 0.97324 | 0.91846 | -0.054784 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | OTTRCRK4 | 0.97324 | 0.91846 | -0.054784 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | OTTRCRK4 | 0.97324 | 0.91846 | -0.054784 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | OTTRCRK4 | 0.97324 | 0.91846 | -0.054784 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | OTTRCRK4 | 0.97324 | 0.91846 | -0.054784 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | OTTRCRK4 | 0.97324 | 0.91846 | -0.054784 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | OTTRCRK4 | 0.97324 | 0.91846 | -0.054784 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | OTTRCRK4 | 0.97324 | 0.91846 | -0.054784 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | OTTRCRK4 | 0.97324 | 0.91846 | -0.054784 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | OTTRCRK4 | 0.97324 | 0.91846 | -0.054784 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | OTTRCRK4 | 0.97324 | 0.91846 | -0.054784 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | OTTRCRK4 | 0.97324 | 0.91846 | -0.054784 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | OTTRCRK4 | 0.97324 | 0.91846 | -0.054784 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | OTTRCRK4 | 0.97324 | 0.91846 | -0.054784 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | OTTRCRK4 | 0.97324 | 0.91846 | -0.054784 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | OTTRCRK4 | 0.97324 | 0.91846 | -0.054784 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | OTTRCRK4 | 0.97324 | 0.91846 | -0.054784 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | OTTRCRK4 | 0.97324 | 0.91846 | -0.054784 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | OTTRCRK4 | 0.97324 | 0.91846 | -0.054784 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | OTTRCRK4 | 0.97324 | 0.91846 | -0.054784 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | OTTRCRK4 | 0.97324 | 0.91846 | -0.054784 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | OTTRCRK4 | 0.97324 | 0.91846 | -0.054784 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | OTTRCRK4 | 0.97324 | 0.91846 | -0.054784 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | OTTRCRK4 | 0.97324 | 0.91846 | -0.054784 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | OTTRCRK4 | 0.97324 | 0.91846 | -0.054784 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | OVERLPK5 | 0.98055 | 0.91621 | -0.064339 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | OVERLPK5 | 0.98055 | 0.91621 | -0.064339 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | OVERLPK5 | 0.98055 | 0.91621 | -0.064339 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | OVERLPK5 | 0.98055 | 0.91621 | -0.064339 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | OVERLPK5 | 0.98055 | 0.91621 | -0.064339 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | OVERLPK5 | 0.98055 | 0.91621 | -0.064339 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | OVERLPK5 | 0.98055 | 0.91621 | -0.064339 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | OVERLPK5 | 0.98055 | 0.91621 | -0.064339 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | OVERLPK5 | 0.98055 | 0.91621 | -0.064339 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | OVERLPK5 | 0.98055 | 0.91621 | -0.064339 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | OVERLPK5 | 0.98055 | 0.91621 | -0.064339 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | OVERLPK5 | 0.98055 | 0.91621 | -0.064339 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | OVERLPK5 | 0.98055 | 0.91621 | -0.064339 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | OVERLPK5 | 0.98055 | 0.91621 | -0.064339 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | OVERLPK5 | 0.98055 | 0.91621 | -0.064339 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | OVERLPK5 | 0.98055 | 0.91621 | -0.064339 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | OVERLPK5 | 0.98055 | 0.91621 | -0.064339 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | OVERLPK5 | 0.98055 | 0.91621 | -0.064339 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | OVERLPK5 | 0.98055 | 0.91621 | -0.064339 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | OVERLPK5 | 0.98055 | 0.91621 | -0.064339 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | OVERLPK5 | 0.98055 | 0.91621 | -0.064339 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | OVERLPK5 | 0.98055 | 0.91621 | -0.064339 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | OVERLPK5 | 0.98055 | 0.91621 | -0.064339 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | OVERLPK5 | 0.98055 | 0.91621 | -0.064339 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | OVERLPK5 | 0.98055 | 0.91621 | -0.064339 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | OXFORD 5 | 0.96773 | 0.92434 | -0.043394 |  | 0.93 | 1.05 | 0.036307 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | OXFORD 5 | 0.96773 | 0.92434 | -0.043394 |  | 0.93 | 1.05 | 0.052743 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | OXFORD 5 | 0.96773 | 0.92434 | -0.043394 |  | 0.93 | 1.05 | 0.039345 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | OXFORD 5 | 0.96773 | 0.92434 | -0.043394 |  | 0.93 | 1.05 | 0.031366 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | OXFORD 5 | 0.96773 | 0.92434 | -0.043394 |  | 0.93 | 1.05 | 0.041888 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | OXFORD 5 | 0.96773 | 0.92434 | -0.043394 |  | 0.93 | 1.05 | 0.038797 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | OXFORD 5 | 0.96773 | 0.92434 | -0.043394 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | OXFORD 5 | 0.96773 | 0.92434 | -0.043394 |  | 0.93 | 1.05 | 0.067346 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | OXFORD 5 | 0.96773 | 0.92434 | -0.043394 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | OXFORD 5 | 0.96773 | 0.92434 | -0.043394 |  | 0.93 | 1.05 | 0.030851 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | OXFORD 5 | 0.96773 | 0.92434 | -0.043394 |  | 0.93 | 1.05 | 0.032161 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | OXFORD 5 | 0.96773 | 0.92434 | -0.043394 |  | 0.93 | 1.05 | 0.04067 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | OXFORD 5 | 0.96773 | 0.92434 | -0.043394 |  | 0.93 | 1.05 | 0.040569 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | OXFORD 5 | 0.96773 | 0.92434 | -0.043394 |  | 0.93 | 1.05 | 0.03086 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | OXFORD 5 | 0.96773 | 0.92434 | -0.043394 |  | 0.93 | 1.05 | 0.033223 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | OXFORD 5 | 0.96773 | 0.92434 | -0.043394 |  | 0.93 | 1.05 | 0.033733 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | OXFORD 5 | 0.97854 | 0.92841 | -0.050137 |  | 0.93 | 1.05 | 0.036307 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | OXFORD 5 | 0.97854 | 0.92841 | -0.050137 |  | 0.93 | 1.05 | 0.052743 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | OXFORD 5 | 0.97854 | 0.92841 | -0.050137 |  | 0.93 | 1.05 | 0.039345 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | OXFORD 5 | 0.97854 | 0.92841 | -0.050137 |  | 0.93 | 1.05 | 0.031366 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | OXFORD 5 | 0.97854 | 0.92841 | -0.050137 |  | 0.93 | 1.05 | 0.041888 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | OXFORD 5 | 0.97854 | 0.92841 | -0.050137 |  | 0.93 | 1.05 | 0.038797 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | OXFORD 5 | 0.97854 | 0.92841 | -0.050137 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | OXFORD 5 | 0.97854 | 0.92841 | -0.050137 |  | 0.93 | 1.05 | 0.067346 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | OXFORD 5 | 0.97854 | 0.92841 | -0.050137 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | OXFORD 5 | 0.97854 | 0.92841 | -0.050137 |  | 0.93 | 1.05 | 0.030851 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | OXFORD 5 | 0.97854 | 0.92841 | -0.050137 |  | 0.93 | 1.05 | 0.032161 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | OXFORD 5 | 0.97854 | 0.92841 | -0.050137 |  | 0.93 | 1.05 | 0.04067 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | OXFORD 5 | 0.97854 | 0.92841 | -0.050137 |  | 0.93 | 1.05 | 0.040569 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | OXFORD 5 | 0.97854 | 0.92841 | -0.050137 |  | 0.93 | 1.05 | 0.03086 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | OXFORD 5 | 0.97854 | 0.92841 | -0.050137 |  | 0.93 | 1.05 | 0.033223 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | OXFORD 5 | 0.97854 | 0.92841 | -0.050137 |  | 0.93 | 1.05 | 0.033733 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | OXFORD 5 | 0.98061 | 0.90445 | -0.076166 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | OXFORD 5 | 0.98061 | 0.90445 | -0.076166 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | OXFORD 5 | 0.98061 | 0.90445 | -0.076166 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | OXFORD 5 | 0.98061 | 0.90445 | -0.076166 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | OXFORD 5 | 0.98061 | 0.90445 | -0.076166 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | OXFORD 5 | 0.98061 | 0.90445 | -0.076166 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | OXFORD 5 | 0.98061 | 0.90445 | -0.076166 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | OXFORD 5 | 0.98061 | 0.90445 | -0.076166 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | OXFORD 5 | 0.98061 | 0.90445 | -0.076166 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | OXFORD 5 | 0.98061 | 0.90445 | -0.076166 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | OXFORD 5 | 0.98061 | 0.90445 | -0.076166 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | OXFORD 5 | 0.98061 | 0.90445 | -0.076166 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | OXFORD 5 | 0.98061 | 0.90445 | -0.076166 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | OXFORD 5 | 0.98061 | 0.90445 | -0.076166 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | OXFORD 5 | 0.98061 | 0.90445 | -0.076166 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | OXFORD 5 | 0.98061 | 0.90445 | -0.076166 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | OXFORD 5 | 0.98061 | 0.90445 | -0.076166 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | OXFORD 5 | 0.98061 | 0.90445 | -0.076166 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | OXFORD 5 | 0.98061 | 0.90445 | -0.076166 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | OXFORD 5 | 0.98061 | 0.90445 | -0.076166 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | OXFORD 5 | 0.98061 | 0.90445 | -0.076166 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | OXFORD 5 | 0.98061 | 0.90445 | -0.076166 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | OXFORD 5 | 0.98061 | 0.90445 | -0.076166 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | OXFORD 5 | 0.98061 | 0.90445 | -0.076166 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | OXFORD 5 | 0.98061 | 0.90445 | -0.076166 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | PAOLA 5 | 0.98953 | 0.92532 | -0.064205 |  | 0.93 | 1.05 | 0.036307 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | PAOLA 5 | 0.98953 | 0.92532 | -0.064205 |  | 0.93 | 1.05 | 0.052743 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | PAOLA 5 | 0.98953 | 0.92532 | -0.064205 |  | 0.93 | 1.05 | 0.039345 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | PAOLA 5 | 0.98953 | 0.92532 | -0.064205 |  | 0.93 | 1.05 | 0.031366 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | PAOLA 5 | 0.98953 | 0.92532 | -0.064205 |  | 0.93 | 1.05 | 0.041888 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | PAOLA 5 | 0.98953 | 0.92532 | -0.064205 |  | 0.93 | 1.05 | 0.038797 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | PAOLA 5 | 0.98953 | 0.92532 | -0.064205 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | PAOLA 5 | 0.98953 | 0.92532 | -0.064205 |  | 0.93 | 1.05 | 0.067346 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | PAOLA 5 | 0.98953 | 0.92532 | -0.064205 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | PAOLA 5 | 0.98953 | 0.92532 | -0.064205 |  | 0.93 | 1.05 | 0.030851 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | PAOLA 5 | 0.98953 | 0.92532 | -0.064205 |  | 0.93 | 1.05 | 0.032161 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | PAOLA 5 | 0.98953 | 0.92532 | -0.064205 |  | 0.93 | 1.05 | 0.04067 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | PAOLA 5 | 0.98953 | 0.92532 | -0.064205 |  | 0.93 | 1.05 | 0.040569 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | PAOLA 5 | 0.98953 | 0.92532 | -0.064205 |  | 0.93 | 1.05 | 0.03086 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | PAOLA 5 | 0.98953 | 0.92532 | -0.064205 |  | 0.93 | 1.05 | 0.033223 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | PAOLA 5 | 0.98953 | 0.92532 | -0.064205 |  | 0.93 | 1.05 | 0.033733 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | PAOLA 5 | 0.99952 | 0.92713 | -0.072384 |  | 0.93 | 1.05 | 0.036307 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | PAOLA 5 | 0.99952 | 0.92713 | -0.072384 |  | 0.93 | 1.05 | 0.052743 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | PAOLA 5 | 0.99952 | 0.92713 | -0.072384 |  | 0.93 | 1.05 | 0.039345 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | PAOLA 5 | 0.99952 | 0.92713 | -0.072384 |  | 0.93 | 1.05 | 0.031366 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | PAOLA 5 | 0.99952 | 0.92713 | -0.072384 |  | 0.93 | 1.05 | 0.041888 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | PAOLA 5 | 0.99952 | 0.92713 | -0.072384 |  | 0.93 | 1.05 | 0.038797 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | PAOLA 5 | 0.99952 | 0.92713 | -0.072384 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | PAOLA 5 | 0.99952 | 0.92713 | -0.072384 |  | 0.93 | 1.05 | 0.067346 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | PAOLA 5 | 0.99952 | 0.92713 | -0.072384 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | PAOLA 5 | 0.99952 | 0.92713 | -0.072384 |  | 0.93 | 1.05 | 0.030851 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | PAOLA 5 | 0.99952 | 0.92713 | -0.072384 |  | 0.93 | 1.05 | 0.032161 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | PAOLA 5 | 0.99952 | 0.92713 | -0.072384 |  | 0.93 | 1.05 | 0.04067 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | PAOLA 5 | 0.99952 | 0.92713 | -0.072384 |  | 0.93 | 1.05 | 0.040569 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | PAOLA 5 | 0.99952 | 0.92713 | -0.072384 |  | 0.93 | 1.05 | 0.03086 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | PAOLA 5 | 0.99952 | 0.92713 | -0.072384 |  | 0.93 | 1.05 | 0.033223 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | PAOLA 5 | 0.99952 | 0.92713 | -0.072384 |  | 0.93 | 1.05 | 0.033733 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | PAOLA 5 | 1.0022 | 0.90483 | -0.097331 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | PAOLA 5 | 1.0022 | 0.90483 | -0.097331 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | PAOLA 5 | 1.0022 | 0.90483 | -0.097331 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | PAOLA 5 | 1.0022 | 0.90483 | -0.097331 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | PAOLA 5 | 1.0022 | 0.90483 | -0.097331 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | PAOLA 5 | 1.0022 | 0.90483 | -0.097331 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | PAOLA 5 | 1.0022 | 0.90483 | -0.097331 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | PAOLA 5 | 1.0022 | 0.90483 | -0.097331 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | PAOLA 5 | 1.0022 | 0.90483 | -0.097331 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | PAOLA 5 | 1.0022 | 0.90483 | -0.097331 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | PAOLA 5 | 1.0022 | 0.90483 | -0.097331 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | PAOLA 5 | 1.0022 | 0.90483 | -0.097331 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | PAOLA 5 | 1.0022 | 0.90483 | -0.097331 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | PAOLA 5 | 1.0022 | 0.90483 | -0.097331 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | PAOLA 5 | 1.0022 | 0.90483 | -0.097331 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | PAOLA 5 | 1.0022 | 0.90483 | -0.097331 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | PAOLA 5 | 1.0022 | 0.90483 | -0.097331 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | PAOLA 5 | 1.0022 | 0.90483 | -0.097331 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | PAOLA 5 | 1.0022 | 0.90483 | -0.097331 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | PAOLA 5 | 1.0022 | 0.90483 | -0.097331 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | PAOLA 5 | 1.0022 | 0.90483 | -0.097331 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | PAOLA 5 | 1.0022 | 0.90483 | -0.097331 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | PAOLA 5 | 1.0022 | 0.90483 | -0.097331 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | PAOLA 5 | 1.0022 | 0.90483 | -0.097331 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | PAOLA 5 | 1.0022 | 0.90483 | -0.097331 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | PECULR 5 | 1.0042 | 0.92764 | -0.076579 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | PECULR 5 | 1.0042 | 0.92764 | -0.076579 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | PECULR 5 | 1.0042 | 0.92764 | -0.076579 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | PECULR 5 | 1.0042 | 0.92764 | -0.076579 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | PECULR 5 | 1.0042 | 0.92764 | -0.076579 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | PECULR 5 | 1.0042 | 0.92764 | -0.076579 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | PECULR 5 | 1.0042 | 0.92764 | -0.076579 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | PECULR 5 | 1.0042 | 0.92764 | -0.076579 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | PECULR 5 | 1.0042 | 0.92764 | -0.076579 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | PECULR 5 | 1.0042 | 0.92764 | -0.076579 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | PECULR 5 | 1.0042 | 0.92764 | -0.076579 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | PECULR 5 | 1.0042 | 0.92764 | -0.076579 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | PECULR 5 | 1.0042 | 0.92764 | -0.076579 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | PECULR 5 | 1.0042 | 0.92764 | -0.076579 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | PECULR 5 | 1.0042 | 0.92764 | -0.076579 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | PECULR 5 | 1.0042 | 0.92764 | -0.076579 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | PECULR 5 | 1.0042 | 0.92764 | -0.076579 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | PECULR 5 | 1.0042 | 0.92764 | -0.076579 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | PECULR 5 | 1.0042 | 0.92764 | -0.076579 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | PECULR 5 | 1.0042 | 0.92764 | -0.076579 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | PECULR 5 | 1.0042 | 0.92764 | -0.076579 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | PECULR 5 | 1.0042 | 0.92764 | -0.076579 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | PECULR 5 | 1.0042 | 0.92764 | -0.076579 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | PECULR 5 | 1.0042 | 0.92764 | -0.076579 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | PECULR 5 | 1.0042 | 0.92764 | -0.076579 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | PECULR 7 | 0.97231 | 0.93711 | -0.035196 |  | 0.95 | 1.05 | 0.036307 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | PECULR 7 | 0.97231 | 0.93711 | -0.035196 |  | 0.95 | 1.05 | 0.052743 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | PECULR 7 | 0.97231 | 0.93711 | -0.035196 |  | 0.95 | 1.05 | 0.039345 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | PECULR 7 | 0.97231 | 0.93711 | -0.035196 |  | 0.95 | 1.05 | 0.031366 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | PECULR 7 | 0.97231 | 0.93711 | -0.035196 |  | 0.95 | 1.05 | 0.041888 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | PECULR 7 | 0.97231 | 0.93711 | -0.035196 |  | 0.95 | 1.05 | 0.038797 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | PECULR 7 | 0.97231 | 0.93711 | -0.035196 |  | 0.95 | 1.05 | 0.030557 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | PECULR 7 | 0.97231 | 0.93711 | -0.035196 |  | 0.95 | 1.05 | 0.067346 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | PECULR 7 | 0.97231 | 0.93711 | -0.035196 |  | 0.95 | 1.05 | 0.030557 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | PECULR 7 | 0.97231 | 0.93711 | -0.035196 |  | 0.95 | 1.05 | 0.030851 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | PECULR 7 | 0.97231 | 0.93711 | -0.035196 |  | 0.95 | 1.05 | 0.032161 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | PECULR 7 | 0.97231 | 0.93711 | -0.035196 |  | 0.95 | 1.05 | 0.04067 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | PECULR 7 | 0.97231 | 0.93711 | -0.035196 |  | 0.95 | 1.05 | 0.040569 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | PECULR 7 | 0.97231 | 0.93711 | -0.035196 |  | 0.95 | 1.05 | 0.03086 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | PECULR 7 | 0.97231 | 0.93711 | -0.035196 |  | 0.95 | 1.05 | 0.033223 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | PECULR 7 | 0.97231 | 0.93711 | -0.035196 |  | 0.95 | 1.05 | 0.033733 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | PECULR 7 | 0.9692 | 0.93119 | -0.038017 |  | 0.95 | 1.05 | 0.040762 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | PECULR 7 | 0.9692 | 0.93119 | -0.038017 |  | 0.95 | 1.05 | 0.030778 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | PECULR 7 | 0.9692 | 0.93119 | -0.038017 |  | 0.95 | 1.05 | 0.031937 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | PECULR 7 | 0.9692 | 0.93119 | -0.038017 |  | 0.95 | 1.05 | 0.053181 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | PECULR 7 | 0.9692 | 0.93119 | -0.038017 |  | 0.95 | 1.05 | 0.032533 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | PECULR 7 | 0.9692 | 0.93119 | -0.038017 |  | 0.95 | 1.05 | 0.031326 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | PECULR 7 | 0.9759 | 0.9292 | -0.046707 |  | 0.95 | 1.05 | 0.036307 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | PECULR 7 | 0.9759 | 0.9292 | -0.046707 |  | 0.95 | 1.05 | 0.052743 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | PECULR 7 | 0.9759 | 0.9292 | -0.046707 |  | 0.95 | 1.05 | 0.039345 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | PECULR 7 | 0.9759 | 0.9292 | -0.046707 |  | 0.95 | 1.05 | 0.031366 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | PECULR 7 | 0.9759 | 0.9292 | -0.046707 |  | 0.95 | 1.05 | 0.041888 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | PECULR 7 | 0.9759 | 0.9292 | -0.046707 |  | 0.95 | 1.05 | 0.038797 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | PECULR 7 | 0.9759 | 0.9292 | -0.046707 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | PECULR 7 | 0.9759 | 0.9292 | -0.046707 |  | 0.95 | 1.05 | 0.067346 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | PECULR 7 | 0.9759 | 0.9292 | -0.046707 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | PECULR 7 | 0.9759 | 0.9292 | -0.046707 |  | 0.95 | 1.05 | 0.030851 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | PECULR 7 | 0.9759 | 0.9292 | -0.046707 |  | 0.95 | 1.05 | 0.032161 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | PECULR 7 | 0.9759 | 0.9292 | -0.046707 |  | 0.95 | 1.05 | 0.04067 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | PECULR 7 | 0.9759 | 0.9292 | -0.046707 |  | 0.95 | 1.05 | 0.040569 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | PECULR 7 | 0.9759 | 0.9292 | -0.046707 |  | 0.95 | 1.05 | 0.03086 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | PECULR 7 | 0.9759 | 0.9292 | -0.046707 |  | 0.95 | 1.05 | 0.033223 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | PECULR 7 | 0.9759 | 0.9292 | -0.046707 |  | 0.95 | 1.05 | 0.033733 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | PECULR 7 | 0.97783 | 0.8964 | -0.081433 |  | 0.95 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | PECULR 7 | 0.97783 | 0.8964 | -0.081433 |  | 0.95 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | PECULR 7 | 0.97783 | 0.8964 | -0.081433 |  | 0.95 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | PECULR 7 | 0.97783 | 0.8964 | -0.081433 |  | 0.95 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | PECULR 7 | 0.97783 | 0.8964 | -0.081433 |  | 0.95 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | PECULR 7 | 0.97783 | 0.8964 | -0.081433 |  | 0.95 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | PECULR 7 | 0.97783 | 0.8964 | -0.081433 |  | 0.95 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | PECULR 7 | 0.97783 | 0.8964 | -0.081433 |  | 0.95 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | PECULR 7 | 0.97783 | 0.8964 | -0.081433 |  | 0.95 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | PECULR 7 | 0.97783 | 0.8964 | -0.081433 |  | 0.95 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | PECULR 7 | 0.97783 | 0.8964 | -0.081433 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | PECULR 7 | 0.97783 | 0.8964 | -0.081433 |  | 0.95 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | PECULR 7 | 0.97783 | 0.8964 | -0.081433 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | PECULR 7 | 0.97783 | 0.8964 | -0.081433 |  | 0.95 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | PECULR 7 | 0.97783 | 0.8964 | -0.081433 |  | 0.95 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | PECULR 7 | 0.97783 | 0.8964 | -0.081433 |  | 0.95 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | PECULR 7 | 0.97783 | 0.8964 | -0.081433 |  | 0.95 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | PECULR 7 | 0.97783 | 0.8964 | -0.081433 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | PECULR 7 | 0.97783 | 0.8964 | -0.081433 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | PECULR 7 | 0.97783 | 0.8964 | -0.081433 |  | 0.95 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | PECULR 7 | 0.97783 | 0.8964 | -0.081433 |  | 0.95 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | PECULR 7 | 0.97783 | 0.8964 | -0.081433 |  | 0.95 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | PECULR 7 | 0.97783 | 0.8964 | -0.081433 |  | 0.95 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | PECULR 7 | 0.97783 | 0.8964 | -0.081433 |  | 0.95 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | PECULR 7 | 0.97783 | 0.8964 | -0.081433 |  | 0.95 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | PECULR 7 | 0.97087 | 0.93474 | -0.036127 |  | 0.95 | 1.05 | 0.036307 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | PECULR 7 | 0.97087 | 0.93474 | -0.036127 |  | 0.95 | 1.05 | 0.052743 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | PECULR 7 | 0.97087 | 0.93474 | -0.036127 |  | 0.95 | 1.05 | 0.039345 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | PECULR 7 | 0.97087 | 0.93474 | -0.036127 |  | 0.95 | 1.05 | 0.031366 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | PECULR 7 | 0.97087 | 0.93474 | -0.036127 |  | 0.95 | 1.05 | 0.041888 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | PECULR 7 | 0.97087 | 0.93474 | -0.036127 |  | 0.95 | 1.05 | 0.038797 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | PECULR 7 | 0.97087 | 0.93474 | -0.036127 |  | 0.95 | 1.05 | 0.030557 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | PECULR 7 | 0.97087 | 0.93474 | -0.036127 |  | 0.95 | 1.05 | 0.067346 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | PECULR 7 | 0.97087 | 0.93474 | -0.036127 |  | 0.95 | 1.05 | 0.030557 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | PECULR 7 | 0.97087 | 0.93474 | -0.036127 |  | 0.95 | 1.05 | 0.030851 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | PECULR 7 | 0.97087 | 0.93474 | -0.036127 |  | 0.95 | 1.05 | 0.032161 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | PECULR 7 | 0.97087 | 0.93474 | -0.036127 |  | 0.95 | 1.05 | 0.04067 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | PECULR 7 | 0.97087 | 0.93474 | -0.036127 |  | 0.95 | 1.05 | 0.040569 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | PECULR 7 | 0.97087 | 0.93474 | -0.036127 |  | 0.95 | 1.05 | 0.03086 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | PECULR 7 | 0.97087 | 0.93474 | -0.036127 |  | 0.95 | 1.05 | 0.033223 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | PECULR 7 | 0.97087 | 0.93474 | -0.036127 |  | 0.95 | 1.05 | 0.033733 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | PFLUMM 5 | 0.98285 | 0.91886 | -0.063997 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | PFLUMM 5 | 0.98285 | 0.91886 | -0.063997 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | PFLUMM 5 | 0.98285 | 0.91886 | -0.063997 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | PFLUMM 5 | 0.98285 | 0.91886 | -0.063997 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | PFLUMM 5 | 0.98285 | 0.91886 | -0.063997 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | PFLUMM 5 | 0.98285 | 0.91886 | -0.063997 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | PFLUMM 5 | 0.98285 | 0.91886 | -0.063997 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | PFLUMM 5 | 0.98285 | 0.91886 | -0.063997 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | PFLUMM 5 | 0.98285 | 0.91886 | -0.063997 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | PFLUMM 5 | 0.98285 | 0.91886 | -0.063997 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | PFLUMM 5 | 0.98285 | 0.91886 | -0.063997 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | PFLUMM 5 | 0.98285 | 0.91886 | -0.063997 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | PFLUMM 5 | 0.98285 | 0.91886 | -0.063997 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | PFLUMM 5 | 0.98285 | 0.91886 | -0.063997 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | PFLUMM 5 | 0.98285 | 0.91886 | -0.063997 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | PFLUMM 5 | 0.98285 | 0.91886 | -0.063997 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | PFLUMM 5 | 0.98285 | 0.91886 | -0.063997 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | PFLUMM 5 | 0.98285 | 0.91886 | -0.063997 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | PFLUMM 5 | 0.98285 | 0.91886 | -0.063997 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | PFLUMM 5 | 0.98285 | 0.91886 | -0.063997 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | PFLUMM 5 | 0.98285 | 0.91886 | -0.063997 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | PFLUMM 5 | 0.98285 | 0.91886 | -0.063997 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | PFLUMM 5 | 0.98285 | 0.91886 | -0.063997 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | PFLUMM 5 | 0.98285 | 0.91886 | -0.063997 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | PFLUMM 5 | 0.98285 | 0.91886 | -0.063997 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | ASGI-2024-023 | PHILL 7 | 0.9764 | 0.94661 | -0.02979 |  | 0.95 | 1.05 | 0.042651 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1 | Add 0.02 MVAR switched shunt at PHILL 7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | PHILL 7 | 0.9764 | 0.94661 | -0.02979 |  | 0.95 | 1.05 | 0.037101 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1 | Add 0.02 MVAR switched shunt at PHILL 7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-068 | PHILL 7 | 0.9764 | 0.94661 | -0.02979 |  | 0.95 | 1.05 | 0.03842 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1 | Add 0.02 MVAR switched shunt at PHILL 7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-071 | PHILL 7 | 0.9764 | 0.94661 | -0.02979 |  | 0.95 | 1.05 | 0.042496 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1 | Add 0.02 MVAR switched shunt at PHILL 7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-122 | PHILL 7 | 0.9764 | 0.94661 | -0.02979 |  | 0.95 | 1.05 | 0.047877 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1 | Add 0.02 MVAR switched shunt at PHILL 7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-177 | PHILL 7 | 0.9764 | 0.94661 | -0.02979 |  | 0.95 | 1.05 | 0.049112 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1 | Add 0.02 MVAR switched shunt at PHILL 7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-178 | PHILL 7 | 0.9764 | 0.94661 | -0.02979 |  | 0.95 | 1.05 | 0.04656 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1 | Add 0.02 MVAR switched shunt at PHILL 7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-220 | PHILL 7 | 0.9764 | 0.94661 | -0.02979 |  | 0.95 | 1.05 | 0.04282 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1 | Add 0.02 MVAR switched shunt at PHILL 7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-232 | PHILL 7 | 0.9764 | 0.94661 | -0.02979 |  | 0.95 | 1.05 | 0.051563 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1 | Add 0.02 MVAR switched shunt at PHILL 7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | PHILL 7 | 0.9764 | 0.94661 | -0.02979 |  | 0.95 | 1.05 | 0.033373 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1 | Add 0.02 MVAR switched shunt at PHILL 7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | PHILL 7 | 0.9764 | 0.94661 | -0.02979 |  | 0.95 | 1.05 | 0.037101 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1 | Add 0.02 MVAR switched shunt at PHILL 7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-376 | PHILL 7 | 0.9764 | 0.94661 | -0.02979 |  | 0.95 | 1.05 | 0.054826 | P23:345:GMO:SIBLEY_R3-8::SIBLEY-PHILL-OVERTON_1 | Add 0.02 MVAR switched shunt at PHILL 7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | PHILL 7 | 0.97531 | 0.94169 | -0.033622 |  | 0.95 | 1.05 | 0.040762 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | PHILL 7 | 0.97531 | 0.94169 | -0.033622 |  | 0.95 | 1.05 | 0.030778 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | PHILL 7 | 0.97531 | 0.94169 | -0.033622 |  | 0.95 | 1.05 | 0.031937 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | PHILL 7 | 0.97531 | 0.94169 | -0.033622 |  | 0.95 | 1.05 | 0.053181 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | PHILL 7 | 0.97531 | 0.94169 | -0.033622 |  | 0.95 | 1.05 | 0.032533 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | PHILL 7 | 0.97531 | 0.94169 | -0.033622 |  | 0.95 | 1.05 | 0.031326 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | PHILL 7 | 0.98131 | 0.94167 | -0.03964 |  | 0.95 | 1.05 | 0.036307 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | PHILL 7 | 0.98131 | 0.94167 | -0.03964 |  | 0.95 | 1.05 | 0.052743 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | PHILL 7 | 0.98131 | 0.94167 | -0.03964 |  | 0.95 | 1.05 | 0.039345 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | PHILL 7 | 0.98131 | 0.94167 | -0.03964 |  | 0.95 | 1.05 | 0.031366 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | PHILL 7 | 0.98131 | 0.94167 | -0.03964 |  | 0.95 | 1.05 | 0.041888 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | PHILL 7 | 0.98131 | 0.94167 | -0.03964 |  | 0.95 | 1.05 | 0.038797 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | PHILL 7 | 0.98131 | 0.94167 | -0.03964 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | PHILL 7 | 0.98131 | 0.94167 | -0.03964 |  | 0.95 | 1.05 | 0.067346 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | PHILL 7 | 0.98131 | 0.94167 | -0.03964 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | PHILL 7 | 0.98131 | 0.94167 | -0.03964 |  | 0.95 | 1.05 | 0.030851 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | PHILL 7 | 0.98131 | 0.94167 | -0.03964 |  | 0.95 | 1.05 | 0.032161 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | PHILL 7 | 0.98131 | 0.94167 | -0.03964 |  | 0.95 | 1.05 | 0.04067 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | PHILL 7 | 0.98131 | 0.94167 | -0.03964 |  | 0.95 | 1.05 | 0.040569 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | PHILL 7 | 0.98131 | 0.94167 | -0.03964 |  | 0.95 | 1.05 | 0.03086 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | PHILL 7 | 0.98131 | 0.94167 | -0.03964 |  | 0.95 | 1.05 | 0.033223 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | PHILL 7 | 0.98131 | 0.94167 | -0.03964 |  | 0.95 | 1.05 | 0.033733 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | PHILL 7 | 0.98187 | 0.91187 | -0.070003 |  | 0.95 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | PHILL 7 | 0.98187 | 0.91187 | -0.070003 |  | 0.95 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | PHILL 7 | 0.98187 | 0.91187 | -0.070003 |  | 0.95 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | PHILL 7 | 0.98187 | 0.91187 | -0.070003 |  | 0.95 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | PHILL 7 | 0.98187 | 0.91187 | -0.070003 |  | 0.95 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | PHILL 7 | 0.98187 | 0.91187 | -0.070003 |  | 0.95 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | PHILL 7 | 0.98187 | 0.91187 | -0.070003 |  | 0.95 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | PHILL 7 | 0.98187 | 0.91187 | -0.070003 |  | 0.95 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | PHILL 7 | 0.98187 | 0.91187 | -0.070003 |  | 0.95 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | PHILL 7 | 0.98187 | 0.91187 | -0.070003 |  | 0.95 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | PHILL 7 | 0.98187 | 0.91187 | -0.070003 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | PHILL 7 | 0.98187 | 0.91187 | -0.070003 |  | 0.95 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | PHILL 7 | 0.98187 | 0.91187 | -0.070003 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | PHILL 7 | 0.98187 | 0.91187 | -0.070003 |  | 0.95 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | PHILL 7 | 0.98187 | 0.91187 | -0.070003 |  | 0.95 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | PHILL 7 | 0.98187 | 0.91187 | -0.070003 |  | 0.95 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | PHILL 7 | 0.98187 | 0.91187 | -0.070003 |  | 0.95 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | PHILL 7 | 0.98187 | 0.91187 | -0.070003 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | PHILL 7 | 0.98187 | 0.91187 | -0.070003 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | PHILL 7 | 0.98187 | 0.91187 | -0.070003 |  | 0.95 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | PHILL 7 | 0.98187 | 0.91187 | -0.070003 |  | 0.95 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | PHILL 7 | 0.98187 | 0.91187 | -0.070003 |  | 0.95 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | PHILL 7 | 0.98187 | 0.91187 | -0.070003 |  | 0.95 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | PHILL 7 | 0.98187 | 0.91187 | -0.070003 |  | 0.95 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | PHILL 7 | 0.98187 | 0.91187 | -0.070003 |  | 0.95 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | PHILL 7 | 0.97773 | 0.94664 | -0.031093 |  | 0.95 | 1.05 | 0.036307 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | PHILL 7 | 0.97773 | 0.94664 | -0.031093 |  | 0.95 | 1.05 | 0.052743 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | PHILL 7 | 0.97773 | 0.94664 | -0.031093 |  | 0.95 | 1.05 | 0.039345 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | PHILL 7 | 0.97773 | 0.94664 | -0.031093 |  | 0.95 | 1.05 | 0.031366 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | PHILL 7 | 0.97773 | 0.94664 | -0.031093 |  | 0.95 | 1.05 | 0.041888 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | PHILL 7 | 0.97773 | 0.94664 | -0.031093 |  | 0.95 | 1.05 | 0.038797 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | PHILL 7 | 0.97773 | 0.94664 | -0.031093 |  | 0.95 | 1.05 | 0.030557 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | PHILL 7 | 0.97773 | 0.94664 | -0.031093 |  | 0.95 | 1.05 | 0.067346 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | PHILL 7 | 0.97773 | 0.94664 | -0.031093 |  | 0.95 | 1.05 | 0.030557 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | PHILL 7 | 0.97773 | 0.94664 | -0.031093 |  | 0.95 | 1.05 | 0.030851 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | PHILL 7 | 0.97773 | 0.94664 | -0.031093 |  | 0.95 | 1.05 | 0.032161 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | PHILL 7 | 0.97773 | 0.94664 | -0.031093 |  | 0.95 | 1.05 | 0.04067 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | PHILL 7 | 0.97773 | 0.94664 | -0.031093 |  | 0.95 | 1.05 | 0.040569 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | PHILL 7 | 0.97773 | 0.94664 | -0.031093 |  | 0.95 | 1.05 | 0.03086 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | PHILL 7 | 0.97773 | 0.94664 | -0.031093 |  | 0.95 | 1.05 | 0.033223 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | PHILL 7 | 0.97773 | 0.94664 | -0.031093 |  | 0.95 | 1.05 | 0.033733 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | PLSTVAL5 | 1.0105 | 0.92692 | -0.08355 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | PLSTVAL5 | 1.0105 | 0.92692 | -0.08355 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | PLSTVAL5 | 1.0105 | 0.92692 | -0.08355 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | PLSTVAL5 | 1.0105 | 0.92692 | -0.08355 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | PLSTVAL5 | 1.0105 | 0.92692 | -0.08355 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | PLSTVAL5 | 1.0105 | 0.92692 | -0.08355 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | PLSTVAL5 | 1.0105 | 0.92692 | -0.08355 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | PLSTVAL5 | 1.0105 | 0.92692 | -0.08355 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | PLSTVAL5 | 1.0105 | 0.92692 | -0.08355 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | PLSTVAL5 | 1.0105 | 0.92692 | -0.08355 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | PLSTVAL5 | 1.0105 | 0.92692 | -0.08355 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | PLSTVAL5 | 1.0105 | 0.92692 | -0.08355 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | PLSTVAL5 | 1.0105 | 0.92692 | -0.08355 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | PLSTVAL5 | 1.0105 | 0.92692 | -0.08355 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | PLSTVAL5 | 1.0105 | 0.92692 | -0.08355 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | PLSTVAL5 | 1.0105 | 0.92692 | -0.08355 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | PLSTVAL5 | 1.0105 | 0.92692 | -0.08355 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | PLSTVAL5 | 1.0105 | 0.92692 | -0.08355 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | PLSTVAL5 | 1.0105 | 0.92692 | -0.08355 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | PLSTVAL5 | 1.0105 | 0.92692 | -0.08355 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | PLSTVAL5 | 1.0105 | 0.92692 | -0.08355 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | PLSTVAL5 | 1.0105 | 0.92692 | -0.08355 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | PLSTVAL5 | 1.0105 | 0.92692 | -0.08355 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | PLSTVAL5 | 1.0105 | 0.92692 | -0.08355 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | PLSTVAL5 | 1.0105 | 0.92692 | -0.08355 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | PRAIRIE3 | 0.96581 | 0.86865 | -0.097154 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | PRAIRIE3 | 0.96581 | 0.86865 | -0.097154 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | PRAIRIE3 | 0.96581 | 0.86865 | -0.097154 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | PRAIRIE3 | 0.96581 | 0.86865 | -0.097154 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | PRAIRIE3 | 0.96581 | 0.86865 | -0.097154 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | PRAIRIE3 | 0.96581 | 0.86865 | -0.097154 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | PRAIRIE3 | 0.96581 | 0.86865 | -0.097154 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | PRAIRIE3 | 0.96581 | 0.86865 | -0.097154 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | PRAIRIE3 | 0.96581 | 0.86865 | -0.097154 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | PRAIRIE3 | 0.96581 | 0.86865 | -0.097154 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | PRAIRIE3 | 0.96581 | 0.86865 | -0.097154 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | PRAIRIE3 | 0.96581 | 0.86865 | -0.097154 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | PRAIRIE3 | 0.96581 | 0.86865 | -0.097154 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | PRAIRIE3 | 0.96581 | 0.86865 | -0.097154 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | PRAIRIE3 | 0.96581 | 0.86865 | -0.097154 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | PRAIRIE3 | 0.96581 | 0.86865 | -0.097154 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | PRAIRIE3 | 0.96581 | 0.86865 | -0.097154 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | PRAIRIE3 | 0.96581 | 0.86865 | -0.097154 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | PRAIRIE3 | 0.96581 | 0.86865 | -0.097154 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | PRAIRIE3 | 0.96581 | 0.86865 | -0.097154 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | PRAIRIE3 | 0.96581 | 0.86865 | -0.097154 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | PRAIRIE3 | 0.96581 | 0.86865 | -0.097154 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | PRAIRIE3 | 0.96581 | 0.86865 | -0.097154 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | PRAIRIE3 | 0.96581 | 0.86865 | -0.097154 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | PRAIRIE3 | 0.96581 | 0.86865 | -0.097154 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | PRY-JCT4 | 0.94056 | 0.9154 | -0.025158 |  | 0.92 | 1.05 | 0.038424 | Single 509752 INOLATP4 138 509790 CATOOSA4 138 1 | Add 57 MVAR switched shunt at GUAVA 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | PRY_CRK4 | 0.91285 | 0.88577 | -0.027072 |  | 0.92 | 1.05 | 0.038424 | Single 509752 INOLATP4 138 509790 CATOOSA4 138 1 | Add 57 MVAR switched shunt at GUAVA 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | PRY_CRK4 | 0.92327 | 0.8978 | -0.025471 |  | 0.92 | 1.05 | 0.038424 | Single 509752 INOLATP4 138 510442 GUAVA4 138 1 | Add 57 MVAR switched shunt at GUAVA 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | QUARRY 5 | 0.97353 | 0.92656 | -0.046969 |  | 0.93 | 1.05 | 0.036307 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | QUARRY 5 | 0.97353 | 0.92656 | -0.046969 |  | 0.93 | 1.05 | 0.052743 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | QUARRY 5 | 0.97353 | 0.92656 | -0.046969 |  | 0.93 | 1.05 | 0.039345 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | QUARRY 5 | 0.97353 | 0.92656 | -0.046969 |  | 0.93 | 1.05 | 0.031366 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | QUARRY 5 | 0.97353 | 0.92656 | -0.046969 |  | 0.93 | 1.05 | 0.041888 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | QUARRY 5 | 0.97353 | 0.92656 | -0.046969 |  | 0.93 | 1.05 | 0.038797 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | QUARRY 5 | 0.97353 | 0.92656 | -0.046969 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | QUARRY 5 | 0.97353 | 0.92656 | -0.046969 |  | 0.93 | 1.05 | 0.067346 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | QUARRY 5 | 0.97353 | 0.92656 | -0.046969 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | QUARRY 5 | 0.97353 | 0.92656 | -0.046969 |  | 0.93 | 1.05 | 0.030851 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | QUARRY 5 | 0.97353 | 0.92656 | -0.046969 |  | 0.93 | 1.05 | 0.032161 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | QUARRY 5 | 0.97353 | 0.92656 | -0.046969 |  | 0.93 | 1.05 | 0.04067 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | QUARRY 5 | 0.97353 | 0.92656 | -0.046969 |  | 0.93 | 1.05 | 0.040569 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | QUARRY 5 | 0.97353 | 0.92656 | -0.046969 |  | 0.93 | 1.05 | 0.03086 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | QUARRY 5 | 0.97353 | 0.92656 | -0.046969 |  | 0.93 | 1.05 | 0.033223 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | QUARRY 5 | 0.97353 | 0.92656 | -0.046969 |  | 0.93 | 1.05 | 0.033733 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | QUARRY 5 | 0.98779 | 0.91288 | -0.074919 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | QUARRY 5 | 0.98779 | 0.91288 | -0.074919 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | QUARRY 5 | 0.98779 | 0.91288 | -0.074919 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | QUARRY 5 | 0.98779 | 0.91288 | -0.074919 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | QUARRY 5 | 0.98779 | 0.91288 | -0.074919 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | QUARRY 5 | 0.98779 | 0.91288 | -0.074919 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | QUARRY 5 | 0.98779 | 0.91288 | -0.074919 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | QUARRY 5 | 0.98779 | 0.91288 | -0.074919 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | QUARRY 5 | 0.98779 | 0.91288 | -0.074919 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | QUARRY 5 | 0.98779 | 0.91288 | -0.074919 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | QUARRY 5 | 0.98779 | 0.91288 | -0.074919 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | QUARRY 5 | 0.98779 | 0.91288 | -0.074919 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | QUARRY 5 | 0.98779 | 0.91288 | -0.074919 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | QUARRY 5 | 0.98779 | 0.91288 | -0.074919 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | QUARRY 5 | 0.98779 | 0.91288 | -0.074919 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | QUARRY 5 | 0.98779 | 0.91288 | -0.074919 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | QUARRY 5 | 0.98779 | 0.91288 | -0.074919 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | QUARRY 5 | 0.98779 | 0.91288 | -0.074919 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | QUARRY 5 | 0.98779 | 0.91288 | -0.074919 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | QUARRY 5 | 0.98779 | 0.91288 | -0.074919 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | QUARRY 5 | 0.98779 | 0.91288 | -0.074919 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | QUARRY 5 | 0.98779 | 0.91288 | -0.074919 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | QUARRY 5 | 0.98779 | 0.91288 | -0.074919 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | QUARRY 5 | 0.98779 | 0.91288 | -0.074919 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | QUARRY 5 | 0.98779 | 0.91288 | -0.074919 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | READING3 | 0.96806 | 0.88176 | -0.086302 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | READING3 | 0.96806 | 0.88176 | -0.086302 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | READING3 | 0.96806 | 0.88176 | -0.086302 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | READING3 | 0.96806 | 0.88176 | -0.086302 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | READING3 | 0.96806 | 0.88176 | -0.086302 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | READING3 | 0.96806 | 0.88176 | -0.086302 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | READING3 | 0.96806 | 0.88176 | -0.086302 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | READING3 | 0.96806 | 0.88176 | -0.086302 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | READING3 | 0.96806 | 0.88176 | -0.086302 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | READING3 | 0.96806 | 0.88176 | -0.086302 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | READING3 | 0.96806 | 0.88176 | -0.086302 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | READING3 | 0.96806 | 0.88176 | -0.086302 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | READING3 | 0.96806 | 0.88176 | -0.086302 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | READING3 | 0.96806 | 0.88176 | -0.086302 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | READING3 | 0.96806 | 0.88176 | -0.086302 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | READING3 | 0.96806 | 0.88176 | -0.086302 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | READING3 | 0.96806 | 0.88176 | -0.086302 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | READING3 | 0.96806 | 0.88176 | -0.086302 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | READING3 | 0.96806 | 0.88176 | -0.086302 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | READING3 | 0.96806 | 0.88176 | -0.086302 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | READING3 | 0.96806 | 0.88176 | -0.086302 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | READING3 | 0.96806 | 0.88176 | -0.086302 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | READING3 | 0.96806 | 0.88176 | -0.086302 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | READING3 | 0.96806 | 0.88176 | -0.086302 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | READING3 | 0.96806 | 0.88176 | -0.086302 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | REDEL 5 | 0.99124 | 0.91137 | -0.07987 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | REDEL 5 | 0.99124 | 0.91137 | -0.07987 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | REDEL 5 | 0.99124 | 0.91137 | -0.07987 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | REDEL 5 | 0.99124 | 0.91137 | -0.07987 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | REDEL 5 | 0.99124 | 0.91137 | -0.07987 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | REDEL 5 | 0.99124 | 0.91137 | -0.07987 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | REDEL 5 | 0.99124 | 0.91137 | -0.07987 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | REDEL 5 | 0.99124 | 0.91137 | -0.07987 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | REDEL 5 | 0.99124 | 0.91137 | -0.07987 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | REDEL 5 | 0.99124 | 0.91137 | -0.07987 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | REDEL 5 | 0.99124 | 0.91137 | -0.07987 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | REDEL 5 | 0.99124 | 0.91137 | -0.07987 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | REDEL 5 | 0.99124 | 0.91137 | -0.07987 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | REDEL 5 | 0.99124 | 0.91137 | -0.07987 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | REDEL 5 | 0.99124 | 0.91137 | -0.07987 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | REDEL 5 | 0.99124 | 0.91137 | -0.07987 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | REDEL 5 | 0.99124 | 0.91137 | -0.07987 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | REDEL 5 | 0.99124 | 0.91137 | -0.07987 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | REDEL 5 | 0.99124 | 0.91137 | -0.07987 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | REDEL 5 | 0.99124 | 0.91137 | -0.07987 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | REDEL 5 | 0.99124 | 0.91137 | -0.07987 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | REDEL 5 | 0.99124 | 0.91137 | -0.07987 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | REDEL 5 | 0.99124 | 0.91137 | -0.07987 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | REDEL 5 | 0.99124 | 0.91137 | -0.07987 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | REDEL 5 | 0.99124 | 0.91137 | -0.07987 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | REEDER 5 | 0.98045 | 0.91616 | -0.064296 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | REEDER 5 | 0.98045 | 0.91616 | -0.064296 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | REEDER 5 | 0.98045 | 0.91616 | -0.064296 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | REEDER 5 | 0.98045 | 0.91616 | -0.064296 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | REEDER 5 | 0.98045 | 0.91616 | -0.064296 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | REEDER 5 | 0.98045 | 0.91616 | -0.064296 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | REEDER 5 | 0.98045 | 0.91616 | -0.064296 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | REEDER 5 | 0.98045 | 0.91616 | -0.064296 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | REEDER 5 | 0.98045 | 0.91616 | -0.064296 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | REEDER 5 | 0.98045 | 0.91616 | -0.064296 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | REEDER 5 | 0.98045 | 0.91616 | -0.064296 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | REEDER 5 | 0.98045 | 0.91616 | -0.064296 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | REEDER 5 | 0.98045 | 0.91616 | -0.064296 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | REEDER 5 | 0.98045 | 0.91616 | -0.064296 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | REEDER 5 | 0.98045 | 0.91616 | -0.064296 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | REEDER 5 | 0.98045 | 0.91616 | -0.064296 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | REEDER 5 | 0.98045 | 0.91616 | -0.064296 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | REEDER 5 | 0.98045 | 0.91616 | -0.064296 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | REEDER 5 | 0.98045 | 0.91616 | -0.064296 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | REEDER 5 | 0.98045 | 0.91616 | -0.064296 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | REEDER 5 | 0.98045 | 0.91616 | -0.064296 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | REEDER 5 | 0.98045 | 0.91616 | -0.064296 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | REEDER 5 | 0.98045 | 0.91616 | -0.064296 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | REEDER 5 | 0.98045 | 0.91616 | -0.064296 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | REEDER 5 | 0.98045 | 0.91616 | -0.064296 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | RENFROW7 | 0.98621 | 0.90555 | -0.080664 |  | 0.92 | 1.05 | 0.091967 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | RENFROW7 | 0.98621 | 0.90555 | -0.080664 |  | 0.92 | 1.05 | 0.033356 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | RENFROW7 | 0.98621 | 0.90555 | -0.080664 |  | 0.92 | 1.05 | 0.044346 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | RENFROW7 | 0.98621 | 0.90555 | -0.080664 |  | 0.92 | 1.05 | 0.058536 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | RENFROW7 | 0.98621 | 0.90555 | -0.080664 |  | 0.92 | 1.05 | 0.059327 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | RENFROW7 | 0.98621 | 0.90555 | -0.080664 |  | 0.92 | 1.05 | 0.041874 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | RENFROW7 | 0.98621 | 0.90555 | -0.080664 |  | 0.92 | 1.05 | 0.046192 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | RENFROW7 | 0.98621 | 0.90555 | -0.080664 |  | 0.92 | 1.05 | 0.12754 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | RENFROW7 | 0.98621 | 0.90555 | -0.080664 |  | 0.92 | 1.05 | 0.047018 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | RENFROW7 | 0.98621 | 0.90555 | -0.080664 |  | 0.92 | 1.05 | 0.056662 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | RENFROW7 | 0.98621 | 0.90555 | -0.080664 |  | 0.92 | 1.05 | 0.056662 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | RENFROW7 | 0.98621 | 0.90555 | -0.080664 |  | 0.92 | 1.05 | 0.056727 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | RENFROW7 | 0.98621 | 0.90555 | -0.080664 |  | 0.92 | 1.05 | 0.074186 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | RENFROW7 | 0.98621 | 0.90555 | -0.080664 |  | 0.92 | 1.05 | 0.040839 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | RENFROW7 | 0.98621 | 0.90555 | -0.080664 |  | 0.92 | 1.05 | 0.03863 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | RENFROW7 | 0.98621 | 0.90555 | -0.080664 |  | 0.92 | 1.05 | 0.042285 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | RENFROW7 | 0.98621 | 0.90555 | -0.080664 |  | 0.92 | 1.05 | 0.042285 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | RENFROW7 | 0.98621 | 0.90555 | -0.080664 |  | 0.92 | 1.05 | 0.050204 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | RENFROW7 | 0.98621 | 0.90555 | -0.080664 |  | 0.92 | 1.05 | 0.058005 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | RENFROW7 | 0.98621 | 0.90555 | -0.080664 |  | 0.92 | 1.05 | 0.041735 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | RENFROW7 | 0.98621 | 0.90555 | -0.080664 |  | 0.92 | 1.05 | 0.057076 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | RENFROW7 | 0.98621 | 0.90555 | -0.080664 |  | 0.92 | 1.05 | 0.050111 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | RENFROW7 | 0.98621 | 0.90555 | -0.080664 |  | 0.92 | 1.05 | 0.06491 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | RENFROW7 | 0.98621 | 0.90555 | -0.080664 |  | 0.92 | 1.05 | 0.051051 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | RENFROW7 | 0.98621 | 0.90555 | -0.080664 |  | 0.92 | 1.05 | 0.036279 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | RENFROW7 | 0.99354 | 0.90409 | -0.08945 |  | 0.92 | 1.05 | 0.035768 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | RENFROW7 | 0.99354 | 0.90409 | -0.08945 |  | 0.92 | 1.05 | 0.088718 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | RENFROW7 | 0.99354 | 0.90409 | -0.08945 |  | 0.92 | 1.05 | 0.031473 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | RENFROW7 | 0.99354 | 0.90409 | -0.08945 |  | 0.92 | 1.05 | 0.034941 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | RENFROW7 | 0.99354 | 0.90409 | -0.08945 |  | 0.92 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | RENFROW7 | 0.99354 | 0.90409 | -0.08945 |  | 0.92 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | RENFROW7 | 0.99354 | 0.90409 | -0.08945 |  | 0.92 | 1.05 | 0.049224 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | RENFROW7 | 0.99354 | 0.90409 | -0.08945 |  | 0.92 | 1.05 | 0.038981 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | RENFROW7 | 0.99354 | 0.90409 | -0.08945 |  | 0.92 | 1.05 | 0.040399 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | RENFROW7 | 0.99354 | 0.90409 | -0.08945 |  | 0.92 | 1.05 | 0.031912 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | RENFROW7 | 0.99354 | 0.90409 | -0.08945 |  | 0.92 | 1.05 | 0.034127 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | RENFROW7 | 0.99354 | 0.90409 | -0.08945 |  | 0.92 | 1.05 | 0.047318 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | RILEY 5 | 0.96506 | 0.92675 | -0.038309 |  | 0.93 | 1.05 | 0.036307 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | RILEY 5 | 0.96506 | 0.92675 | -0.038309 |  | 0.93 | 1.05 | 0.052743 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | RILEY 5 | 0.96506 | 0.92675 | -0.038309 |  | 0.93 | 1.05 | 0.039345 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | RILEY 5 | 0.96506 | 0.92675 | -0.038309 |  | 0.93 | 1.05 | 0.031366 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | RILEY 5 | 0.96506 | 0.92675 | -0.038309 |  | 0.93 | 1.05 | 0.041888 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | RILEY 5 | 0.96506 | 0.92675 | -0.038309 |  | 0.93 | 1.05 | 0.038797 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | RILEY 5 | 0.96506 | 0.92675 | -0.038309 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | RILEY 5 | 0.96506 | 0.92675 | -0.038309 |  | 0.93 | 1.05 | 0.067346 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | RILEY 5 | 0.96506 | 0.92675 | -0.038309 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | RILEY 5 | 0.96506 | 0.92675 | -0.038309 |  | 0.93 | 1.05 | 0.030851 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | RILEY 5 | 0.96506 | 0.92675 | -0.038309 |  | 0.93 | 1.05 | 0.032161 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | RILEY 5 | 0.96506 | 0.92675 | -0.038309 |  | 0.93 | 1.05 | 0.04067 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | RILEY 5 | 0.96506 | 0.92675 | -0.038309 |  | 0.93 | 1.05 | 0.040569 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | RILEY 5 | 0.96506 | 0.92675 | -0.038309 |  | 0.93 | 1.05 | 0.03086 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | RILEY 5 | 0.96506 | 0.92675 | -0.038309 |  | 0.93 | 1.05 | 0.033223 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | RILEY 5 | 0.96506 | 0.92675 | -0.038309 |  | 0.93 | 1.05 | 0.033733 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | RILEY 5 | 0.97373 | 0.92822 | -0.045516 |  | 0.93 | 1.05 | 0.036307 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | RILEY 5 | 0.97373 | 0.92822 | -0.045516 |  | 0.93 | 1.05 | 0.052743 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | RILEY 5 | 0.97373 | 0.92822 | -0.045516 |  | 0.93 | 1.05 | 0.039345 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | RILEY 5 | 0.97373 | 0.92822 | -0.045516 |  | 0.93 | 1.05 | 0.031366 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | RILEY 5 | 0.97373 | 0.92822 | -0.045516 |  | 0.93 | 1.05 | 0.041888 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | RILEY 5 | 0.97373 | 0.92822 | -0.045516 |  | 0.93 | 1.05 | 0.038797 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | RILEY 5 | 0.97373 | 0.92822 | -0.045516 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | RILEY 5 | 0.97373 | 0.92822 | -0.045516 |  | 0.93 | 1.05 | 0.067346 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | RILEY 5 | 0.97373 | 0.92822 | -0.045516 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | RILEY 5 | 0.97373 | 0.92822 | -0.045516 |  | 0.93 | 1.05 | 0.030851 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | RILEY 5 | 0.97373 | 0.92822 | -0.045516 |  | 0.93 | 1.05 | 0.032161 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | RILEY 5 | 0.97373 | 0.92822 | -0.045516 |  | 0.93 | 1.05 | 0.04067 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | RILEY 5 | 0.97373 | 0.92822 | -0.045516 |  | 0.93 | 1.05 | 0.040569 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | RILEY 5 | 0.97373 | 0.92822 | -0.045516 |  | 0.93 | 1.05 | 0.03086 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | RILEY 5 | 0.97373 | 0.92822 | -0.045516 |  | 0.93 | 1.05 | 0.033223 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | RILEY 5 | 0.97373 | 0.92822 | -0.045516 |  | 0.93 | 1.05 | 0.033733 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | RILEY 5 | 0.97637 | 0.90942 | -0.066947 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | RILEY 5 | 0.97637 | 0.90942 | -0.066947 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | RILEY 5 | 0.97637 | 0.90942 | -0.066947 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | RILEY 5 | 0.97637 | 0.90942 | -0.066947 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | RILEY 5 | 0.97637 | 0.90942 | -0.066947 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | RILEY 5 | 0.97637 | 0.90942 | -0.066947 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | RILEY 5 | 0.97637 | 0.90942 | -0.066947 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | RILEY 5 | 0.97637 | 0.90942 | -0.066947 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | RILEY 5 | 0.97637 | 0.90942 | -0.066947 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | RILEY 5 | 0.97637 | 0.90942 | -0.066947 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | RILEY 5 | 0.97637 | 0.90942 | -0.066947 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | RILEY 5 | 0.97637 | 0.90942 | -0.066947 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | RILEY 5 | 0.97637 | 0.90942 | -0.066947 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | RILEY 5 | 0.97637 | 0.90942 | -0.066947 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | RILEY 5 | 0.97637 | 0.90942 | -0.066947 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | RILEY 5 | 0.97637 | 0.90942 | -0.066947 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | RILEY 5 | 0.97637 | 0.90942 | -0.066947 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | RILEY 5 | 0.97637 | 0.90942 | -0.066947 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | RILEY 5 | 0.97637 | 0.90942 | -0.066947 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | RILEY 5 | 0.97637 | 0.90942 | -0.066947 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | RILEY 5 | 0.97637 | 0.90942 | -0.066947 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | RILEY 5 | 0.97637 | 0.90942 | -0.066947 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | RILEY 5 | 0.97637 | 0.90942 | -0.066947 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | RILEY 5 | 0.97637 | 0.90942 | -0.066947 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | RILEY 5 | 0.97637 | 0.90942 | -0.066947 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | RNM393 5 | 0.97516 | 0.92256 | -0.0526 |  | 0.925 | 1.05 | 0.033596 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | RNM393 5 | 0.97516 | 0.92256 | -0.0526 |  | 0.925 | 1.05 | 0.040193 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | RNM393 5 | 0.97516 | 0.92256 | -0.0526 |  | 0.925 | 1.05 | 0.088122 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | RNM393 5 | 0.97516 | 0.92256 | -0.0526 |  | 0.925 | 1.05 | 0.074664 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | RNM393 5 | 0.97516 | 0.92256 | -0.0526 |  | 0.925 | 1.05 | 0.068051 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | RNM393 5 | 0.97516 | 0.92256 | -0.0526 |  | 0.925 | 1.05 | 0.035565 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | RNM393 5 | 0.97516 | 0.92256 | -0.0526 |  | 0.925 | 1.05 | 0.033904 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | RNM393 5 | 0.97516 | 0.92256 | -0.0526 |  | 0.925 | 1.05 | 0.16366 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | RNM393 5 | 0.97516 | 0.92256 | -0.0526 |  | 0.925 | 1.05 | 0.045569 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | RNM393 5 | 0.97516 | 0.92256 | -0.0526 |  | 0.925 | 1.05 | 0.13458 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | RNM393 5 | 0.97516 | 0.92256 | -0.0526 |  | 0.925 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | RNM393 5 | 0.97516 | 0.92256 | -0.0526 |  | 0.925 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | RNM393 5 | 0.97516 | 0.92256 | -0.0526 |  | 0.925 | 1.05 | 0.068426 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | RNM393 5 | 0.97516 | 0.92256 | -0.0526 |  | 0.925 | 1.05 | 0.035223 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | RNM393 5 | 0.97516 | 0.92256 | -0.0526 |  | 0.925 | 1.05 | 0.034504 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | RNM393 5 | 0.97528 | 0.92385 | -0.051423 |  | 0.925 | 1.05 | 0.040193 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | RNM393 5 | 0.97528 | 0.92385 | -0.051423 |  | 0.925 | 1.05 | 0.088122 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | RNM393 5 | 0.97528 | 0.92385 | -0.051423 |  | 0.925 | 1.05 | 0.074664 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | RNM393 5 | 0.97528 | 0.92385 | -0.051423 |  | 0.925 | 1.05 | 0.068051 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | RNM393 5 | 0.97528 | 0.92385 | -0.051423 |  | 0.925 | 1.05 | 0.034774 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | RNM393 5 | 0.97528 | 0.92385 | -0.051423 |  | 0.925 | 1.05 | 0.033904 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | RNM393 5 | 0.97528 | 0.92385 | -0.051423 |  | 0.925 | 1.05 | 0.16366 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | RNM393 5 | 0.97528 | 0.92385 | -0.051423 |  | 0.925 | 1.05 | 0.045569 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | RNM393 5 | 0.97528 | 0.92385 | -0.051423 |  | 0.925 | 1.05 | 0.13458 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | RNM393 5 | 0.97528 | 0.92385 | -0.051423 |  | 0.925 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | RNM393 5 | 0.97528 | 0.92385 | -0.051423 |  | 0.925 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | RNM393 5 | 0.97528 | 0.92385 | -0.051423 |  | 0.925 | 1.05 | 0.068426 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | RNM393 5 | 0.97528 | 0.92385 | -0.051423 |  | 0.925 | 1.05 | 0.035223 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | RNM393 5 | 0.97528 | 0.92385 | -0.051423 |  | 0.925 | 1.05 | 0.034504 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | ROCKPT-4 | 0.83473 | 0.80373 | -0.031002 |  | 0.92 | 1.05 | 0.038424 | Single 509752 INOLATP4 138 509790 CATOOSA4 138 1 | Add 57 MVAR switched shunt at GUAVA 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | ROCKPT-4 | 0.85153 | 0.82292 | -0.028614 |  | 0.92 | 1.05 | 0.038424 | Single 509752 INOLATP4 138 510442 GUAVA4 138 1 | Add 57 MVAR switched shunt at GUAVA 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | ROEPARK5 | 0.9884 | 0.92728 | -0.061122 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | ROEPARK5 | 0.9884 | 0.92728 | -0.061122 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | ROEPARK5 | 0.9884 | 0.92728 | -0.061122 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | ROEPARK5 | 0.9884 | 0.92728 | -0.061122 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | ROEPARK5 | 0.9884 | 0.92728 | -0.061122 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | ROEPARK5 | 0.9884 | 0.92728 | -0.061122 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | ROEPARK5 | 0.9884 | 0.92728 | -0.061122 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | ROEPARK5 | 0.9884 | 0.92728 | -0.061122 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | ROEPARK5 | 0.9884 | 0.92728 | -0.061122 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | ROEPARK5 | 0.9884 | 0.92728 | -0.061122 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | ROEPARK5 | 0.9884 | 0.92728 | -0.061122 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | ROEPARK5 | 0.9884 | 0.92728 | -0.061122 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | ROEPARK5 | 0.9884 | 0.92728 | -0.061122 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | ROEPARK5 | 0.9884 | 0.92728 | -0.061122 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | ROEPARK5 | 0.9884 | 0.92728 | -0.061122 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | ROEPARK5 | 0.9884 | 0.92728 | -0.061122 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | ROEPARK5 | 0.9884 | 0.92728 | -0.061122 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | ROEPARK5 | 0.9884 | 0.92728 | -0.061122 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | ROEPARK5 | 0.9884 | 0.92728 | -0.061122 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | ROEPARK5 | 0.9884 | 0.92728 | -0.061122 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | ROEPARK5 | 0.9884 | 0.92728 | -0.061122 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | ROEPARK5 | 0.9884 | 0.92728 | -0.061122 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | ROEPARK5 | 0.9884 | 0.92728 | -0.061122 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | ROEPARK5 | 0.9884 | 0.92728 | -0.061122 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | ROEPARK5 | 0.9884 | 0.92728 | -0.061122 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | S.OTTWA5 | 1.0062 | 0.91406 | -0.092123 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | S.OTTWA5 | 1.0062 | 0.91406 | -0.092123 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | S.OTTWA5 | 1.0062 | 0.91406 | -0.092123 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | S.OTTWA5 | 1.0062 | 0.91406 | -0.092123 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | S.OTTWA5 | 1.0062 | 0.91406 | -0.092123 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | S.OTTWA5 | 1.0062 | 0.91406 | -0.092123 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | S.OTTWA5 | 1.0062 | 0.91406 | -0.092123 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | S.OTTWA5 | 1.0062 | 0.91406 | -0.092123 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | S.OTTWA5 | 1.0062 | 0.91406 | -0.092123 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | S.OTTWA5 | 1.0062 | 0.91406 | -0.092123 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | S.OTTWA5 | 1.0062 | 0.91406 | -0.092123 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | S.OTTWA5 | 1.0062 | 0.91406 | -0.092123 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | S.OTTWA5 | 1.0062 | 0.91406 | -0.092123 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | S.OTTWA5 | 1.0062 | 0.91406 | -0.092123 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | S.OTTWA5 | 1.0062 | 0.91406 | -0.092123 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | S.OTTWA5 | 1.0062 | 0.91406 | -0.092123 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | S.OTTWA5 | 1.0062 | 0.91406 | -0.092123 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | S.OTTWA5 | 1.0062 | 0.91406 | -0.092123 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | S.OTTWA5 | 1.0062 | 0.91406 | -0.092123 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | S.OTTWA5 | 1.0062 | 0.91406 | -0.092123 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | S.OTTWA5 | 1.0062 | 0.91406 | -0.092123 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | S.OTTWA5 | 1.0062 | 0.91406 | -0.092123 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | S.OTTWA5 | 1.0062 | 0.91406 | -0.092123 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | S.OTTWA5 | 1.0062 | 0.91406 | -0.092123 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | S.OTTWA5 | 1.0062 | 0.91406 | -0.092123 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | SCRANTN3 | 0.97777 | 0.90812 | -0.069651 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | SCRANTN3 | 0.97777 | 0.90812 | -0.069651 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | SCRANTN3 | 0.97777 | 0.90812 | -0.069651 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | SCRANTN3 | 0.97777 | 0.90812 | -0.069651 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | SCRANTN3 | 0.97777 | 0.90812 | -0.069651 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | SCRANTN3 | 0.97777 | 0.90812 | -0.069651 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | SCRANTN3 | 0.97777 | 0.90812 | -0.069651 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | SCRANTN3 | 0.97777 | 0.90812 | -0.069651 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | SCRANTN3 | 0.97777 | 0.90812 | -0.069651 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | SCRANTN3 | 0.97777 | 0.90812 | -0.069651 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | SCRANTN3 | 0.97777 | 0.90812 | -0.069651 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | SCRANTN3 | 0.97777 | 0.90812 | -0.069651 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | SCRANTN3 | 0.97777 | 0.90812 | -0.069651 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | SCRANTN3 | 0.97777 | 0.90812 | -0.069651 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | SCRANTN3 | 0.97777 | 0.90812 | -0.069651 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | SCRANTN3 | 0.97777 | 0.90812 | -0.069651 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | SCRANTN3 | 0.97777 | 0.90812 | -0.069651 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | SCRANTN3 | 0.97777 | 0.90812 | -0.069651 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | SCRANTN3 | 0.97777 | 0.90812 | -0.069651 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | SCRANTN3 | 0.97777 | 0.90812 | -0.069651 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | SCRANTN3 | 0.97777 | 0.90812 | -0.069651 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | SCRANTN3 | 0.97777 | 0.90812 | -0.069651 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | SCRANTN3 | 0.97777 | 0.90812 | -0.069651 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | SCRANTN3 | 0.97777 | 0.90812 | -0.069651 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | SCRANTN3 | 0.97777 | 0.90812 | -0.069651 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | SE1GREE2 | 0.97358 | 0.92963 | -0.043948 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | SE1GREE2 | 0.97358 | 0.92963 | -0.043948 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | SE1GREE2 | 0.97358 | 0.92963 | -0.043948 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | SE1GREE2 | 0.97358 | 0.92963 | -0.043948 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | SE1GREE2 | 0.97358 | 0.92963 | -0.043948 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | SE1GREE2 | 0.97358 | 0.92963 | -0.043948 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | SE1GREE2 | 0.97358 | 0.92963 | -0.043948 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | SE1GREE2 | 0.97358 | 0.92963 | -0.043948 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | SE1GREE2 | 0.97358 | 0.92963 | -0.043948 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | SE1GREE2 | 0.97358 | 0.92963 | -0.043948 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | SE1GREE2 | 0.97358 | 0.92963 | -0.043948 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | SE1GREE2 | 0.97358 | 0.92963 | -0.043948 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | SE1GREE2 | 0.97358 | 0.92963 | -0.043948 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | SE1GREE2 | 0.97358 | 0.92963 | -0.043948 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | SE1GREE2 | 0.97358 | 0.92963 | -0.043948 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | SE1GREE2 | 0.97358 | 0.92963 | -0.043948 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | SE1GREE2 | 0.97358 | 0.92963 | -0.043948 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | SE1GREE2 | 0.97358 | 0.92963 | -0.043948 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | SE1GREE2 | 0.97358 | 0.92963 | -0.043948 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | SE1GREE2 | 0.97358 | 0.92963 | -0.043948 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | SE1GREE2 | 0.97358 | 0.92963 | -0.043948 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | SE1GREE2 | 0.97358 | 0.92963 | -0.043948 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | SE1GREE2 | 0.97358 | 0.92963 | -0.043948 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | SE1GREE2 | 0.97358 | 0.92963 | -0.043948 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | SE1GREE2 | 0.97358 | 0.92963 | -0.043948 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | SEOTTWA5 | 1.0068 | 0.9159 | -0.090886 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | SEOTTWA5 | 1.0068 | 0.9159 | -0.090886 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | SEOTTWA5 | 1.0068 | 0.9159 | -0.090886 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | SEOTTWA5 | 1.0068 | 0.9159 | -0.090886 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | SEOTTWA5 | 1.0068 | 0.9159 | -0.090886 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | SEOTTWA5 | 1.0068 | 0.9159 | -0.090886 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | SEOTTWA5 | 1.0068 | 0.9159 | -0.090886 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | SEOTTWA5 | 1.0068 | 0.9159 | -0.090886 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | SEOTTWA5 | 1.0068 | 0.9159 | -0.090886 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | SEOTTWA5 | 1.0068 | 0.9159 | -0.090886 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | SEOTTWA5 | 1.0068 | 0.9159 | -0.090886 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | SEOTTWA5 | 1.0068 | 0.9159 | -0.090886 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | SEOTTWA5 | 1.0068 | 0.9159 | -0.090886 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | SEOTTWA5 | 1.0068 | 0.9159 | -0.090886 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | SEOTTWA5 | 1.0068 | 0.9159 | -0.090886 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | SEOTTWA5 | 1.0068 | 0.9159 | -0.090886 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | SEOTTWA5 | 1.0068 | 0.9159 | -0.090886 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | SEOTTWA5 | 1.0068 | 0.9159 | -0.090886 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | SEOTTWA5 | 1.0068 | 0.9159 | -0.090886 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | SEOTTWA5 | 1.0068 | 0.9159 | -0.090886 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | SEOTTWA5 | 1.0068 | 0.9159 | -0.090886 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | SEOTTWA5 | 1.0068 | 0.9159 | -0.090886 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | SEOTTWA5 | 1.0068 | 0.9159 | -0.090886 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | SEOTTWA5 | 1.0068 | 0.9159 | -0.090886 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | SEOTTWA5 | 1.0068 | 0.9159 | -0.090886 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | SHAWNEE5 | 0.98771 | 0.92933 | -0.058384 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | SHAWNEE5 | 0.98771 | 0.92933 | -0.058384 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | SHAWNEE5 | 0.98771 | 0.92933 | -0.058384 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | SHAWNEE5 | 0.98771 | 0.92933 | -0.058384 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | SHAWNEE5 | 0.98771 | 0.92933 | -0.058384 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | SHAWNEE5 | 0.98771 | 0.92933 | -0.058384 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | SHAWNEE5 | 0.98771 | 0.92933 | -0.058384 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | SHAWNEE5 | 0.98771 | 0.92933 | -0.058384 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | SHAWNEE5 | 0.98771 | 0.92933 | -0.058384 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | SHAWNEE5 | 0.98771 | 0.92933 | -0.058384 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | SHAWNEE5 | 0.98771 | 0.92933 | -0.058384 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | SHAWNEE5 | 0.98771 | 0.92933 | -0.058384 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | SHAWNEE5 | 0.98771 | 0.92933 | -0.058384 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | SHAWNEE5 | 0.98771 | 0.92933 | -0.058384 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | SHAWNEE5 | 0.98771 | 0.92933 | -0.058384 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | SHAWNEE5 | 0.98771 | 0.92933 | -0.058384 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | SHAWNEE5 | 0.98771 | 0.92933 | -0.058384 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | SHAWNEE5 | 0.98771 | 0.92933 | -0.058384 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | SHAWNEE5 | 0.98771 | 0.92933 | -0.058384 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | SHAWNEE5 | 0.98771 | 0.92933 | -0.058384 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | SHAWNEE5 | 0.98771 | 0.92933 | -0.058384 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | SHAWNEE5 | 0.98771 | 0.92933 | -0.058384 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | SHAWNEE5 | 0.98771 | 0.92933 | -0.058384 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | SHAWNEE5 | 0.98771 | 0.92933 | -0.058384 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | SHAWNEE5 | 0.98771 | 0.92933 | -0.058384 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | SHWNMSN5 | 0.98551 | 0.9251 | -0.060403 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | SHWNMSN5 | 0.98551 | 0.9251 | -0.060403 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | SHWNMSN5 | 0.98551 | 0.9251 | -0.060403 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | SHWNMSN5 | 0.98551 | 0.9251 | -0.060403 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | SHWNMSN5 | 0.98551 | 0.9251 | -0.060403 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | SHWNMSN5 | 0.98551 | 0.9251 | -0.060403 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | SHWNMSN5 | 0.98551 | 0.9251 | -0.060403 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | SHWNMSN5 | 0.98551 | 0.9251 | -0.060403 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | SHWNMSN5 | 0.98551 | 0.9251 | -0.060403 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | SHWNMSN5 | 0.98551 | 0.9251 | -0.060403 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | SHWNMSN5 | 0.98551 | 0.9251 | -0.060403 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | SHWNMSN5 | 0.98551 | 0.9251 | -0.060403 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | SHWNMSN5 | 0.98551 | 0.9251 | -0.060403 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | SHWNMSN5 | 0.98551 | 0.9251 | -0.060403 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | SHWNMSN5 | 0.98551 | 0.9251 | -0.060403 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | SHWNMSN5 | 0.98551 | 0.9251 | -0.060403 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | SHWNMSN5 | 0.98551 | 0.9251 | -0.060403 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | SHWNMSN5 | 0.98551 | 0.9251 | -0.060403 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | SHWNMSN5 | 0.98551 | 0.9251 | -0.060403 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | SHWNMSN5 | 0.98551 | 0.9251 | -0.060403 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | SHWNMSN5 | 0.98551 | 0.9251 | -0.060403 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | SHWNMSN5 | 0.98551 | 0.9251 | -0.060403 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | SHWNMSN5 | 0.98551 | 0.9251 | -0.060403 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | SHWNMSN5 | 0.98551 | 0.9251 | -0.060403 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | SHWNMSN5 | 0.98551 | 0.9251 | -0.060403 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | SIBLEYRD2 | 0.97646 | 0.90914 | -0.067318 |  | 0.925 | 1.05 | 0.033596 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | SIBLEYRD2 | 0.97646 | 0.90914 | -0.067318 |  | 0.925 | 1.05 | 0.040193 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | SIBLEYRD2 | 0.97646 | 0.90914 | -0.067318 |  | 0.925 | 1.05 | 0.088122 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | SIBLEYRD2 | 0.97646 | 0.90914 | -0.067318 |  | 0.925 | 1.05 | 0.074664 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | SIBLEYRD2 | 0.97646 | 0.90914 | -0.067318 |  | 0.925 | 1.05 | 0.068051 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | SIBLEYRD2 | 0.97646 | 0.90914 | -0.067318 |  | 0.925 | 1.05 | 0.035565 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | SIBLEYRD2 | 0.97646 | 0.90914 | -0.067318 |  | 0.925 | 1.05 | 0.033904 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | SIBLEYRD2 | 0.97646 | 0.90914 | -0.067318 |  | 0.925 | 1.05 | 0.16366 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | SIBLEYRD2 | 0.97646 | 0.90914 | -0.067318 |  | 0.925 | 1.05 | 0.045569 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | SIBLEYRD2 | 0.97646 | 0.90914 | -0.067318 |  | 0.925 | 1.05 | 0.13458 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | SIBLEYRD2 | 0.97646 | 0.90914 | -0.067318 |  | 0.925 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | SIBLEYRD2 | 0.97646 | 0.90914 | -0.067318 |  | 0.925 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | SIBLEYRD2 | 0.97646 | 0.90914 | -0.067318 |  | 0.925 | 1.05 | 0.068426 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | SIBLEYRD2 | 0.97646 | 0.90914 | -0.067318 |  | 0.925 | 1.05 | 0.035223 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | SIBLEYRD2 | 0.97646 | 0.90914 | -0.067318 |  | 0.925 | 1.05 | 0.034504 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | SIBLEYRD2 | 0.97663 | 0.91006 | -0.066567 |  | 0.925 | 1.05 | 0.040193 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | SIBLEYRD2 | 0.97663 | 0.91006 | -0.066567 |  | 0.925 | 1.05 | 0.088122 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | SIBLEYRD2 | 0.97663 | 0.91006 | -0.066567 |  | 0.925 | 1.05 | 0.074664 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | SIBLEYRD2 | 0.97663 | 0.91006 | -0.066567 |  | 0.925 | 1.05 | 0.068051 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | SIBLEYRD2 | 0.97663 | 0.91006 | -0.066567 |  | 0.925 | 1.05 | 0.034774 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | SIBLEYRD2 | 0.97663 | 0.91006 | -0.066567 |  | 0.925 | 1.05 | 0.033904 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | SIBLEYRD2 | 0.97663 | 0.91006 | -0.066567 |  | 0.925 | 1.05 | 0.16366 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | SIBLEYRD2 | 0.97663 | 0.91006 | -0.066567 |  | 0.925 | 1.05 | 0.045569 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | SIBLEYRD2 | 0.97663 | 0.91006 | -0.066567 |  | 0.925 | 1.05 | 0.13458 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | SIBLEYRD2 | 0.97663 | 0.91006 | -0.066567 |  | 0.925 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | SIBLEYRD2 | 0.97663 | 0.91006 | -0.066567 |  | 0.925 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | SIBLEYRD2 | 0.97663 | 0.91006 | -0.066567 |  | 0.925 | 1.05 | 0.068426 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | SIBLEYRD2 | 0.97663 | 0.91006 | -0.066567 |  | 0.925 | 1.05 | 0.035223 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | SIBLEYRD2 | 0.97663 | 0.91006 | -0.066567 |  | 0.925 | 1.05 | 0.034504 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | SIBLEYRD2 | 0.97656 | 0.91419 | -0.062374 |  | 0.925 | 1.05 | 0.033596 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | SIBLEYRD2 | 0.97656 | 0.91419 | -0.062374 |  | 0.925 | 1.05 | 0.040193 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | SIBLEYRD2 | 0.97656 | 0.91419 | -0.062374 |  | 0.925 | 1.05 | 0.056051 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | SIBLEYRD2 | 0.97656 | 0.91419 | -0.062374 |  | 0.925 | 1.05 | 0.074664 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | SIBLEYRD2 | 0.97656 | 0.91419 | -0.062374 |  | 0.925 | 1.05 | 0.068051 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | SIBLEYRD2 | 0.97656 | 0.91419 | -0.062374 |  | 0.925 | 1.05 | 0.035565 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | SIBLEYRD2 | 0.97656 | 0.91419 | -0.062374 |  | 0.925 | 1.05 | 0.033904 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | SIBLEYRD2 | 0.97656 | 0.91419 | -0.062374 |  | 0.925 | 1.05 | 0.082596 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | SIBLEYRD2 | 0.97656 | 0.91419 | -0.062374 |  | 0.925 | 1.05 | 0.045569 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | SIBLEYRD2 | 0.97656 | 0.91419 | -0.062374 |  | 0.925 | 1.05 | 0.13458 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | SIBLEYRD2 | 0.97656 | 0.91419 | -0.062374 |  | 0.925 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | SIBLEYRD2 | 0.97656 | 0.91419 | -0.062374 |  | 0.925 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | SIBLEYRD2 | 0.97656 | 0.91419 | -0.062374 |  | 0.925 | 1.05 | 0.068426 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | SIBLEYRD2 | 0.97656 | 0.91419 | -0.062374 |  | 0.925 | 1.05 | 0.035223 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | SIBLEYRD2 | 0.97656 | 0.91419 | -0.062374 |  | 0.925 | 1.05 | 0.034504 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | ASGI-2024-023 | SIBLEYRD2 | 0.98212 | 0.92178 | -0.06034 |  | 0.925 | 1.05 | 0.079962 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | SIBLEYRD2 | 0.98212 | 0.92178 | -0.06034 |  | 0.925 | 1.05 | 0.065323 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-068 | SIBLEYRD2 | 0.98212 | 0.92178 | -0.06034 |  | 0.925 | 1.05 | 0.067422 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-071 | SIBLEYRD2 | 0.98212 | 0.92178 | -0.06034 |  | 0.925 | 1.05 | 0.074668 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | SIBLEYRD2 | 0.98212 | 0.92178 | -0.06034 |  | 0.925 | 1.05 | 0.053027 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-122 | SIBLEYRD2 | 0.98212 | 0.92178 | -0.06034 |  | 0.925 | 1.05 | 0.082926 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-177 | SIBLEYRD2 | 0.98212 | 0.92178 | -0.06034 |  | 0.925 | 1.05 | 0.084694 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-178 | SIBLEYRD2 | 0.98212 | 0.92178 | -0.06034 |  | 0.925 | 1.05 | 0.078867 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | SIBLEYRD2 | 0.98212 | 0.92178 | -0.06034 |  | 0.925 | 1.05 | 0.031571 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-220 | SIBLEYRD2 | 0.98212 | 0.92178 | -0.06034 |  | 0.925 | 1.05 | 0.075331 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-232 | SIBLEYRD2 | 0.98212 | 0.92178 | -0.06034 |  | 0.925 | 1.05 | 0.078906 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | SIBLEYRD2 | 0.98212 | 0.92178 | -0.06034 |  | 0.925 | 1.05 | 0.065323 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | SIBLEYRD2 | 0.98212 | 0.92178 | -0.06034 |  | 0.925 | 1.05 | 0.03431 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | SIBLEYRD2 | 0.98212 | 0.92178 | -0.06034 |  | 0.925 | 1.05 | 0.031504 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | SIBLEYRD2 | 0.98212 | 0.92178 | -0.06034 |  | 0.925 | 1.05 | 0.031504 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | SIBLEYRD2 | 0.98212 | 0.92178 | -0.06034 |  | 0.925 | 1.05 | 0.030663 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | SIBLEYRD2 | 0.98212 | 0.92178 | -0.06034 |  | 0.925 | 1.05 | 0.04269 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-376 | SIBLEYRD2 | 0.98212 | 0.92178 | -0.06034 |  | 0.925 | 1.05 | 0.082476 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | SIBLEYRD2 | 0.97983 | 0.92137 | -0.058452 |  | 0.925 | 1.05 | 0.033596 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.2 MVAR switched shunt at GROVE 5 161 kV; Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | SIBLEYRD2 | 0.97983 | 0.92137 | -0.058452 |  | 0.925 | 1.05 | 0.088122 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.2 MVAR switched shunt at GROVE 5 161 kV; Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | SIBLEYRD2 | 0.97983 | 0.92137 | -0.058452 |  | 0.925 | 1.05 | 0.030897 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.2 MVAR switched shunt at GROVE 5 161 kV; Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | SIBLEYRD2 | 0.97983 | 0.92137 | -0.058452 |  | 0.925 | 1.05 | 0.038719 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.2 MVAR switched shunt at GROVE 5 161 kV; Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | SIBLEYRD2 | 0.97983 | 0.92137 | -0.058452 |  | 0.925 | 1.05 | 0.035565 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.2 MVAR switched shunt at GROVE 5 161 kV; Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | SIBLEYRD2 | 0.97983 | 0.92137 | -0.058452 |  | 0.925 | 1.05 | 0.16366 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.2 MVAR switched shunt at GROVE 5 161 kV; Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | SIBLEYRD2 | 0.97983 | 0.92137 | -0.058452 |  | 0.925 | 1.05 | 0.038589 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.2 MVAR switched shunt at GROVE 5 161 kV; Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | SIBLEYRD2 | 0.97983 | 0.92137 | -0.058452 |  | 0.925 | 1.05 | 0.034208 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.2 MVAR switched shunt at GROVE 5 161 kV; Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | SIBLEYRD5 | 0.97711 | 0.90994 | -0.067164 |  | 0.925 | 1.05 | 0.033596 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | SIBLEYRD5 | 0.97711 | 0.90994 | -0.067164 |  | 0.925 | 1.05 | 0.040193 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | SIBLEYRD5 | 0.97711 | 0.90994 | -0.067164 |  | 0.925 | 1.05 | 0.088122 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | SIBLEYRD5 | 0.97711 | 0.90994 | -0.067164 |  | 0.925 | 1.05 | 0.074664 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | SIBLEYRD5 | 0.97711 | 0.90994 | -0.067164 |  | 0.925 | 1.05 | 0.068051 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | SIBLEYRD5 | 0.97711 | 0.90994 | -0.067164 |  | 0.925 | 1.05 | 0.035565 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | SIBLEYRD5 | 0.97711 | 0.90994 | -0.067164 |  | 0.925 | 1.05 | 0.033904 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | SIBLEYRD5 | 0.97711 | 0.90994 | -0.067164 |  | 0.925 | 1.05 | 0.16366 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | SIBLEYRD5 | 0.97711 | 0.90994 | -0.067164 |  | 0.925 | 1.05 | 0.045569 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | SIBLEYRD5 | 0.97711 | 0.90994 | -0.067164 |  | 0.925 | 1.05 | 0.13458 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | SIBLEYRD5 | 0.97711 | 0.90994 | -0.067164 |  | 0.925 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | SIBLEYRD5 | 0.97711 | 0.90994 | -0.067164 |  | 0.925 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | SIBLEYRD5 | 0.97711 | 0.90994 | -0.067164 |  | 0.925 | 1.05 | 0.068426 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | SIBLEYRD5 | 0.97711 | 0.90994 | -0.067164 |  | 0.925 | 1.05 | 0.035223 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | SIBLEYRD5 | 0.97711 | 0.90994 | -0.067164 |  | 0.925 | 1.05 | 0.034504 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | SIBLEYRD5 | 0.97727 | 0.91086 | -0.066416 |  | 0.925 | 1.05 | 0.040193 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | SIBLEYRD5 | 0.97727 | 0.91086 | -0.066416 |  | 0.925 | 1.05 | 0.088122 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | SIBLEYRD5 | 0.97727 | 0.91086 | -0.066416 |  | 0.925 | 1.05 | 0.074664 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | SIBLEYRD5 | 0.97727 | 0.91086 | -0.066416 |  | 0.925 | 1.05 | 0.068051 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | SIBLEYRD5 | 0.97727 | 0.91086 | -0.066416 |  | 0.925 | 1.05 | 0.034774 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | SIBLEYRD5 | 0.97727 | 0.91086 | -0.066416 |  | 0.925 | 1.05 | 0.033904 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | SIBLEYRD5 | 0.97727 | 0.91086 | -0.066416 |  | 0.925 | 1.05 | 0.16366 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | SIBLEYRD5 | 0.97727 | 0.91086 | -0.066416 |  | 0.925 | 1.05 | 0.045569 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | SIBLEYRD5 | 0.97727 | 0.91086 | -0.066416 |  | 0.925 | 1.05 | 0.13458 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | SIBLEYRD5 | 0.97727 | 0.91086 | -0.066416 |  | 0.925 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | SIBLEYRD5 | 0.97727 | 0.91086 | -0.066416 |  | 0.925 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | SIBLEYRD5 | 0.97727 | 0.91086 | -0.066416 |  | 0.925 | 1.05 | 0.068426 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | SIBLEYRD5 | 0.97727 | 0.91086 | -0.066416 |  | 0.925 | 1.05 | 0.035223 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | SIBLEYRD5 | 0.97727 | 0.91086 | -0.066416 |  | 0.925 | 1.05 | 0.034504 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | SIBLEYRD5 | 0.97721 | 0.91498 | -0.062233 |  | 0.925 | 1.05 | 0.033596 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | SIBLEYRD5 | 0.97721 | 0.91498 | -0.062233 |  | 0.925 | 1.05 | 0.040193 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | SIBLEYRD5 | 0.97721 | 0.91498 | -0.062233 |  | 0.925 | 1.05 | 0.056051 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | SIBLEYRD5 | 0.97721 | 0.91498 | -0.062233 |  | 0.925 | 1.05 | 0.074664 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | SIBLEYRD5 | 0.97721 | 0.91498 | -0.062233 |  | 0.925 | 1.05 | 0.068051 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | SIBLEYRD5 | 0.97721 | 0.91498 | -0.062233 |  | 0.925 | 1.05 | 0.035565 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | SIBLEYRD5 | 0.97721 | 0.91498 | -0.062233 |  | 0.925 | 1.05 | 0.033904 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | SIBLEYRD5 | 0.97721 | 0.91498 | -0.062233 |  | 0.925 | 1.05 | 0.082596 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | SIBLEYRD5 | 0.97721 | 0.91498 | -0.062233 |  | 0.925 | 1.05 | 0.045569 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | SIBLEYRD5 | 0.97721 | 0.91498 | -0.062233 |  | 0.925 | 1.05 | 0.13458 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | SIBLEYRD5 | 0.97721 | 0.91498 | -0.062233 |  | 0.925 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | SIBLEYRD5 | 0.97721 | 0.91498 | -0.062233 |  | 0.925 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | SIBLEYRD5 | 0.97721 | 0.91498 | -0.062233 |  | 0.925 | 1.05 | 0.068426 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | SIBLEYRD5 | 0.97721 | 0.91498 | -0.062233 |  | 0.925 | 1.05 | 0.035223 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | SIBLEYRD5 | 0.97721 | 0.91498 | -0.062233 |  | 0.925 | 1.05 | 0.034504 | P23:345:AECI:7BLACKBERRY:653::: | Add 6 MVAR switched shunt at SIBLEYRD2 69 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | ASGI-2024-023 | SIBLEYRD5 | 0.98276 | 0.92255 | -0.060207 |  | 0.925 | 1.05 | 0.079962 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | SIBLEYRD5 | 0.98276 | 0.92255 | -0.060207 |  | 0.925 | 1.05 | 0.065323 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-068 | SIBLEYRD5 | 0.98276 | 0.92255 | -0.060207 |  | 0.925 | 1.05 | 0.067422 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-071 | SIBLEYRD5 | 0.98276 | 0.92255 | -0.060207 |  | 0.925 | 1.05 | 0.074668 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | SIBLEYRD5 | 0.98276 | 0.92255 | -0.060207 |  | 0.925 | 1.05 | 0.053027 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-122 | SIBLEYRD5 | 0.98276 | 0.92255 | -0.060207 |  | 0.925 | 1.05 | 0.082926 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-177 | SIBLEYRD5 | 0.98276 | 0.92255 | -0.060207 |  | 0.925 | 1.05 | 0.084694 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-178 | SIBLEYRD5 | 0.98276 | 0.92255 | -0.060207 |  | 0.925 | 1.05 | 0.078867 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | SIBLEYRD5 | 0.98276 | 0.92255 | -0.060207 |  | 0.925 | 1.05 | 0.031571 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-220 | SIBLEYRD5 | 0.98276 | 0.92255 | -0.060207 |  | 0.925 | 1.05 | 0.075331 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-232 | SIBLEYRD5 | 0.98276 | 0.92255 | -0.060207 |  | 0.925 | 1.05 | 0.078906 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | SIBLEYRD5 | 0.98276 | 0.92255 | -0.060207 |  | 0.925 | 1.05 | 0.065323 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | SIBLEYRD5 | 0.98276 | 0.92255 | -0.060207 |  | 0.925 | 1.05 | 0.03431 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | SIBLEYRD5 | 0.98276 | 0.92255 | -0.060207 |  | 0.925 | 1.05 | 0.031504 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | SIBLEYRD5 | 0.98276 | 0.92255 | -0.060207 |  | 0.925 | 1.05 | 0.031504 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | SIBLEYRD5 | 0.98276 | 0.92255 | -0.060207 |  | 0.925 | 1.05 | 0.030663 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | SIBLEYRD5 | 0.98276 | 0.92255 | -0.060207 |  | 0.925 | 1.05 | 0.04269 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-376 | SIBLEYRD5 | 0.98276 | 0.92255 | -0.060207 |  | 0.925 | 1.05 | 0.082476 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 0.2 MVAR switched shunt at GROVE 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | SIBLEYRD5 | 0.98046 | 0.92214 | -0.058323 |  | 0.925 | 1.05 | 0.033596 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.2 MVAR switched shunt at GROVE 5 161 kV; Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | SIBLEYRD5 | 0.98046 | 0.92214 | -0.058323 |  | 0.925 | 1.05 | 0.088122 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.2 MVAR switched shunt at GROVE 5 161 kV; Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | SIBLEYRD5 | 0.98046 | 0.92214 | -0.058323 |  | 0.925 | 1.05 | 0.030897 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.2 MVAR switched shunt at GROVE 5 161 kV; Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | SIBLEYRD5 | 0.98046 | 0.92214 | -0.058323 |  | 0.925 | 1.05 | 0.038719 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.2 MVAR switched shunt at GROVE 5 161 kV; Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | SIBLEYRD5 | 0.98046 | 0.92214 | -0.058323 |  | 0.925 | 1.05 | 0.035565 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.2 MVAR switched shunt at GROVE 5 161 kV; Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | SIBLEYRD5 | 0.98046 | 0.92214 | -0.058323 |  | 0.925 | 1.05 | 0.16366 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.2 MVAR switched shunt at GROVE 5 161 kV; Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | SIBLEYRD5 | 0.98046 | 0.92214 | -0.058323 |  | 0.925 | 1.05 | 0.038589 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.2 MVAR switched shunt at GROVE 5 161 kV; Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | SIBLEYRD5 | 0.98046 | 0.92214 | -0.058323 |  | 0.925 | 1.05 | 0.034208 | P23:345:AECI:7BLACKBERRY:656::: | Add 0.2 MVAR switched shunt at GROVE 5 161 kV; Add 0.04 MVAR switched shunt at AUR124 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | SOUTHTN3 | 0.98593 | 0.91995 | -0.065986 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | SOUTHTN3 | 0.98593 | 0.91995 | -0.065986 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | SOUTHTN3 | 0.98593 | 0.91995 | -0.065986 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | SOUTHTN3 | 0.98593 | 0.91995 | -0.065986 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | SOUTHTN3 | 0.98593 | 0.91995 | -0.065986 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | SOUTHTN3 | 0.98593 | 0.91995 | -0.065986 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | SOUTHTN3 | 0.98593 | 0.91995 | -0.065986 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | SOUTHTN3 | 0.98593 | 0.91995 | -0.065986 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | SOUTHTN3 | 0.98593 | 0.91995 | -0.065986 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | SOUTHTN3 | 0.98593 | 0.91995 | -0.065986 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | SOUTHTN3 | 0.98593 | 0.91995 | -0.065986 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | SOUTHTN3 | 0.98593 | 0.91995 | -0.065986 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | SOUTHTN3 | 0.98593 | 0.91995 | -0.065986 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | SOUTHTN3 | 0.98593 | 0.91995 | -0.065986 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | SOUTHTN3 | 0.98593 | 0.91995 | -0.065986 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | SOUTHTN3 | 0.98593 | 0.91995 | -0.065986 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | SOUTHTN3 | 0.98593 | 0.91995 | -0.065986 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | SOUTHTN3 | 0.98593 | 0.91995 | -0.065986 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | SOUTHTN3 | 0.98593 | 0.91995 | -0.065986 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | SOUTHTN3 | 0.98593 | 0.91995 | -0.065986 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | SOUTHTN3 | 0.98593 | 0.91995 | -0.065986 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | SOUTHTN3 | 0.98593 | 0.91995 | -0.065986 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | SOUTHTN3 | 0.98593 | 0.91995 | -0.065986 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | SOUTHTN3 | 0.98593 | 0.91995 | -0.065986 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | SOUTHTN3 | 0.98593 | 0.91995 | -0.065986 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | SPRGHL 5 | 0.9895 | 0.90929 | -0.080218 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | SPRGHL 5 | 0.9895 | 0.90929 | -0.080218 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | SPRGHL 5 | 0.9895 | 0.90929 | -0.080218 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | SPRGHL 5 | 0.9895 | 0.90929 | -0.080218 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | SPRGHL 5 | 0.9895 | 0.90929 | -0.080218 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | SPRGHL 5 | 0.9895 | 0.90929 | -0.080218 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | SPRGHL 5 | 0.9895 | 0.90929 | -0.080218 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | SPRGHL 5 | 0.9895 | 0.90929 | -0.080218 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | SPRGHL 5 | 0.9895 | 0.90929 | -0.080218 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | SPRGHL 5 | 0.9895 | 0.90929 | -0.080218 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | SPRGHL 5 | 0.9895 | 0.90929 | -0.080218 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | SPRGHL 5 | 0.9895 | 0.90929 | -0.080218 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | SPRGHL 5 | 0.9895 | 0.90929 | -0.080218 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | SPRGHL 5 | 0.9895 | 0.90929 | -0.080218 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | SPRGHL 5 | 0.9895 | 0.90929 | -0.080218 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | SPRGHL 5 | 0.9895 | 0.90929 | -0.080218 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | SPRGHL 5 | 0.9895 | 0.90929 | -0.080218 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | SPRGHL 5 | 0.9895 | 0.90929 | -0.080218 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | SPRGHL 5 | 0.9895 | 0.90929 | -0.080218 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | SPRGHL 5 | 0.9895 | 0.90929 | -0.080218 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | SPRGHL 5 | 0.9895 | 0.90929 | -0.080218 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | SPRGHL 5 | 0.9895 | 0.90929 | -0.080218 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | SPRGHL 5 | 0.9895 | 0.90929 | -0.080218 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | SPRGHL 5 | 0.9895 | 0.90929 | -0.080218 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | SPRGHL 5 | 0.9895 | 0.90929 | -0.080218 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | SPRINT15 | 0.96603 | 0.92808 | -0.037947 |  | 0.93 | 1.05 | 0.036307 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | SPRINT15 | 0.96603 | 0.92808 | -0.037947 |  | 0.93 | 1.05 | 0.052743 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | SPRINT15 | 0.96603 | 0.92808 | -0.037947 |  | 0.93 | 1.05 | 0.039345 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | SPRINT15 | 0.96603 | 0.92808 | -0.037947 |  | 0.93 | 1.05 | 0.031366 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | SPRINT15 | 0.96603 | 0.92808 | -0.037947 |  | 0.93 | 1.05 | 0.041888 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | SPRINT15 | 0.96603 | 0.92808 | -0.037947 |  | 0.93 | 1.05 | 0.038797 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | SPRINT15 | 0.96603 | 0.92808 | -0.037947 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | SPRINT15 | 0.96603 | 0.92808 | -0.037947 |  | 0.93 | 1.05 | 0.067346 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | SPRINT15 | 0.96603 | 0.92808 | -0.037947 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | SPRINT15 | 0.96603 | 0.92808 | -0.037947 |  | 0.93 | 1.05 | 0.030851 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | SPRINT15 | 0.96603 | 0.92808 | -0.037947 |  | 0.93 | 1.05 | 0.032161 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | SPRINT15 | 0.96603 | 0.92808 | -0.037947 |  | 0.93 | 1.05 | 0.04067 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | SPRINT15 | 0.96603 | 0.92808 | -0.037947 |  | 0.93 | 1.05 | 0.040569 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | SPRINT15 | 0.96603 | 0.92808 | -0.037947 |  | 0.93 | 1.05 | 0.03086 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | SPRINT15 | 0.96603 | 0.92808 | -0.037947 |  | 0.93 | 1.05 | 0.033223 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | SPRINT15 | 0.96603 | 0.92808 | -0.037947 |  | 0.93 | 1.05 | 0.033733 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | SPRINT15 | 0.97454 | 0.92935 | -0.045186 |  | 0.93 | 1.05 | 0.036307 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | SPRINT15 | 0.97454 | 0.92935 | -0.045186 |  | 0.93 | 1.05 | 0.052743 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | SPRINT15 | 0.97454 | 0.92935 | -0.045186 |  | 0.93 | 1.05 | 0.039345 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | SPRINT15 | 0.97454 | 0.92935 | -0.045186 |  | 0.93 | 1.05 | 0.031366 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | SPRINT15 | 0.97454 | 0.92935 | -0.045186 |  | 0.93 | 1.05 | 0.041888 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | SPRINT15 | 0.97454 | 0.92935 | -0.045186 |  | 0.93 | 1.05 | 0.038797 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | SPRINT15 | 0.97454 | 0.92935 | -0.045186 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | SPRINT15 | 0.97454 | 0.92935 | -0.045186 |  | 0.93 | 1.05 | 0.067346 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | SPRINT15 | 0.97454 | 0.92935 | -0.045186 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | SPRINT15 | 0.97454 | 0.92935 | -0.045186 |  | 0.93 | 1.05 | 0.030851 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | SPRINT15 | 0.97454 | 0.92935 | -0.045186 |  | 0.93 | 1.05 | 0.032161 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | SPRINT15 | 0.97454 | 0.92935 | -0.045186 |  | 0.93 | 1.05 | 0.04067 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | SPRINT15 | 0.97454 | 0.92935 | -0.045186 |  | 0.93 | 1.05 | 0.040569 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | SPRINT15 | 0.97454 | 0.92935 | -0.045186 |  | 0.93 | 1.05 | 0.03086 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | SPRINT15 | 0.97454 | 0.92935 | -0.045186 |  | 0.93 | 1.05 | 0.033223 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | SPRINT15 | 0.97454 | 0.92935 | -0.045186 |  | 0.93 | 1.05 | 0.033733 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | SPRINT15 | 0.97713 | 0.91045 | -0.066679 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | SPRINT15 | 0.97713 | 0.91045 | -0.066679 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | SPRINT15 | 0.97713 | 0.91045 | -0.066679 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | SPRINT15 | 0.97713 | 0.91045 | -0.066679 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | SPRINT15 | 0.97713 | 0.91045 | -0.066679 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | SPRINT15 | 0.97713 | 0.91045 | -0.066679 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | SPRINT15 | 0.97713 | 0.91045 | -0.066679 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | SPRINT15 | 0.97713 | 0.91045 | -0.066679 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | SPRINT15 | 0.97713 | 0.91045 | -0.066679 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | SPRINT15 | 0.97713 | 0.91045 | -0.066679 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | SPRINT15 | 0.97713 | 0.91045 | -0.066679 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | SPRINT15 | 0.97713 | 0.91045 | -0.066679 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | SPRINT15 | 0.97713 | 0.91045 | -0.066679 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | SPRINT15 | 0.97713 | 0.91045 | -0.066679 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | SPRINT15 | 0.97713 | 0.91045 | -0.066679 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | SPRINT15 | 0.97713 | 0.91045 | -0.066679 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | SPRINT15 | 0.97713 | 0.91045 | -0.066679 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | SPRINT15 | 0.97713 | 0.91045 | -0.066679 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | SPRINT15 | 0.97713 | 0.91045 | -0.066679 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | SPRINT15 | 0.97713 | 0.91045 | -0.066679 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | SPRINT15 | 0.97713 | 0.91045 | -0.066679 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | SPRINT15 | 0.97713 | 0.91045 | -0.066679 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | SPRINT15 | 0.97713 | 0.91045 | -0.066679 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | SPRINT15 | 0.97713 | 0.91045 | -0.066679 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | SPRINT15 | 0.97713 | 0.91045 | -0.066679 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | SPRINT25 | 0.96599 | 0.92803 | -0.037961 |  | 0.93 | 1.05 | 0.036307 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | SPRINT25 | 0.96599 | 0.92803 | -0.037961 |  | 0.93 | 1.05 | 0.052743 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | SPRINT25 | 0.96599 | 0.92803 | -0.037961 |  | 0.93 | 1.05 | 0.039345 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | SPRINT25 | 0.96599 | 0.92803 | -0.037961 |  | 0.93 | 1.05 | 0.031366 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | SPRINT25 | 0.96599 | 0.92803 | -0.037961 |  | 0.93 | 1.05 | 0.041888 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | SPRINT25 | 0.96599 | 0.92803 | -0.037961 |  | 0.93 | 1.05 | 0.038797 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | SPRINT25 | 0.96599 | 0.92803 | -0.037961 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | SPRINT25 | 0.96599 | 0.92803 | -0.037961 |  | 0.93 | 1.05 | 0.067346 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | SPRINT25 | 0.96599 | 0.92803 | -0.037961 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | SPRINT25 | 0.96599 | 0.92803 | -0.037961 |  | 0.93 | 1.05 | 0.030851 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | SPRINT25 | 0.96599 | 0.92803 | -0.037961 |  | 0.93 | 1.05 | 0.032161 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | SPRINT25 | 0.96599 | 0.92803 | -0.037961 |  | 0.93 | 1.05 | 0.04067 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | SPRINT25 | 0.96599 | 0.92803 | -0.037961 |  | 0.93 | 1.05 | 0.040569 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | SPRINT25 | 0.96599 | 0.92803 | -0.037961 |  | 0.93 | 1.05 | 0.03086 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | SPRINT25 | 0.96599 | 0.92803 | -0.037961 |  | 0.93 | 1.05 | 0.033223 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | SPRINT25 | 0.96599 | 0.92803 | -0.037961 |  | 0.93 | 1.05 | 0.033733 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | SPRINT25 | 0.97451 | 0.92931 | -0.045199 |  | 0.93 | 1.05 | 0.036307 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | SPRINT25 | 0.97451 | 0.92931 | -0.045199 |  | 0.93 | 1.05 | 0.052743 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | SPRINT25 | 0.97451 | 0.92931 | -0.045199 |  | 0.93 | 1.05 | 0.039345 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | SPRINT25 | 0.97451 | 0.92931 | -0.045199 |  | 0.93 | 1.05 | 0.031366 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | SPRINT25 | 0.97451 | 0.92931 | -0.045199 |  | 0.93 | 1.05 | 0.041888 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | SPRINT25 | 0.97451 | 0.92931 | -0.045199 |  | 0.93 | 1.05 | 0.038797 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | SPRINT25 | 0.97451 | 0.92931 | -0.045199 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | SPRINT25 | 0.97451 | 0.92931 | -0.045199 |  | 0.93 | 1.05 | 0.067346 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | SPRINT25 | 0.97451 | 0.92931 | -0.045199 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | SPRINT25 | 0.97451 | 0.92931 | -0.045199 |  | 0.93 | 1.05 | 0.030851 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | SPRINT25 | 0.97451 | 0.92931 | -0.045199 |  | 0.93 | 1.05 | 0.032161 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | SPRINT25 | 0.97451 | 0.92931 | -0.045199 |  | 0.93 | 1.05 | 0.04067 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | SPRINT25 | 0.97451 | 0.92931 | -0.045199 |  | 0.93 | 1.05 | 0.040569 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | SPRINT25 | 0.97451 | 0.92931 | -0.045199 |  | 0.93 | 1.05 | 0.03086 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | SPRINT25 | 0.97451 | 0.92931 | -0.045199 |  | 0.93 | 1.05 | 0.033223 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | SPRINT25 | 0.97451 | 0.92931 | -0.045199 |  | 0.93 | 1.05 | 0.033733 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | SPRINT25 | 0.9771 | 0.91041 | -0.06669 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | SPRINT25 | 0.9771 | 0.91041 | -0.06669 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | SPRINT25 | 0.9771 | 0.91041 | -0.06669 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | SPRINT25 | 0.9771 | 0.91041 | -0.06669 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | SPRINT25 | 0.9771 | 0.91041 | -0.06669 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | SPRINT25 | 0.9771 | 0.91041 | -0.06669 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | SPRINT25 | 0.9771 | 0.91041 | -0.06669 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | SPRINT25 | 0.9771 | 0.91041 | -0.06669 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | SPRINT25 | 0.9771 | 0.91041 | -0.06669 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | SPRINT25 | 0.9771 | 0.91041 | -0.06669 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | SPRINT25 | 0.9771 | 0.91041 | -0.06669 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | SPRINT25 | 0.9771 | 0.91041 | -0.06669 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | SPRINT25 | 0.9771 | 0.91041 | -0.06669 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | SPRINT25 | 0.9771 | 0.91041 | -0.06669 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | SPRINT25 | 0.9771 | 0.91041 | -0.06669 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | SPRINT25 | 0.9771 | 0.91041 | -0.06669 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | SPRINT25 | 0.9771 | 0.91041 | -0.06669 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | SPRINT25 | 0.9771 | 0.91041 | -0.06669 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | SPRINT25 | 0.9771 | 0.91041 | -0.06669 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | SPRINT25 | 0.9771 | 0.91041 | -0.06669 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | SPRINT25 | 0.9771 | 0.91041 | -0.06669 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | SPRINT25 | 0.9771 | 0.91041 | -0.06669 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | SPRINT25 | 0.9771 | 0.91041 | -0.06669 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | SPRINT25 | 0.9771 | 0.91041 | -0.06669 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | SPRINT25 | 0.9771 | 0.91041 | -0.06669 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | STHTOWN5 | 0.98891 | 0.92293 | -0.065975 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | STHTOWN5 | 0.98891 | 0.92293 | -0.065975 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | STHTOWN5 | 0.98891 | 0.92293 | -0.065975 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | STHTOWN5 | 0.98891 | 0.92293 | -0.065975 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | STHTOWN5 | 0.98891 | 0.92293 | -0.065975 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | STHTOWN5 | 0.98891 | 0.92293 | -0.065975 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | STHTOWN5 | 0.98891 | 0.92293 | -0.065975 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | STHTOWN5 | 0.98891 | 0.92293 | -0.065975 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | STHTOWN5 | 0.98891 | 0.92293 | -0.065975 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | STHTOWN5 | 0.98891 | 0.92293 | -0.065975 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | STHTOWN5 | 0.98891 | 0.92293 | -0.065975 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | STHTOWN5 | 0.98891 | 0.92293 | -0.065975 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | STHTOWN5 | 0.98891 | 0.92293 | -0.065975 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | STHTOWN5 | 0.98891 | 0.92293 | -0.065975 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | STHTOWN5 | 0.98891 | 0.92293 | -0.065975 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | STHTOWN5 | 0.98891 | 0.92293 | -0.065975 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | STHTOWN5 | 0.98891 | 0.92293 | -0.065975 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | STHTOWN5 | 0.98891 | 0.92293 | -0.065975 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | STHTOWN5 | 0.98891 | 0.92293 | -0.065975 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | STHTOWN5 | 0.98891 | 0.92293 | -0.065975 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | STHTOWN5 | 0.98891 | 0.92293 | -0.065975 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | STHTOWN5 | 0.98891 | 0.92293 | -0.065975 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | STHTOWN5 | 0.98891 | 0.92293 | -0.065975 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | STHTOWN5 | 0.98891 | 0.92293 | -0.065975 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | STHTOWN5 | 0.98891 | 0.92293 | -0.065975 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | STHTOWN_CAP5 | 0.99004 | 0.92399 | -0.066051 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | STHTOWN_CAP5 | 0.99004 | 0.92399 | -0.066051 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | STHTOWN_CAP5 | 0.99004 | 0.92399 | -0.066051 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | STHTOWN_CAP5 | 0.99004 | 0.92399 | -0.066051 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | STHTOWN_CAP5 | 0.99004 | 0.92399 | -0.066051 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | STHTOWN_CAP5 | 0.99004 | 0.92399 | -0.066051 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | STHTOWN_CAP5 | 0.99004 | 0.92399 | -0.066051 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | STHTOWN_CAP5 | 0.99004 | 0.92399 | -0.066051 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | STHTOWN_CAP5 | 0.99004 | 0.92399 | -0.066051 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | STHTOWN_CAP5 | 0.99004 | 0.92399 | -0.066051 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | STHTOWN_CAP5 | 0.99004 | 0.92399 | -0.066051 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | STHTOWN_CAP5 | 0.99004 | 0.92399 | -0.066051 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | STHTOWN_CAP5 | 0.99004 | 0.92399 | -0.066051 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | STHTOWN_CAP5 | 0.99004 | 0.92399 | -0.066051 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | STHTOWN_CAP5 | 0.99004 | 0.92399 | -0.066051 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | STHTOWN_CAP5 | 0.99004 | 0.92399 | -0.066051 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | STHTOWN_CAP5 | 0.99004 | 0.92399 | -0.066051 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | STHTOWN_CAP5 | 0.99004 | 0.92399 | -0.066051 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | STHTOWN_CAP5 | 0.99004 | 0.92399 | -0.066051 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | STHTOWN_CAP5 | 0.99004 | 0.92399 | -0.066051 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | STHTOWN_CAP5 | 0.99004 | 0.92399 | -0.066051 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | STHTOWN_CAP5 | 0.99004 | 0.92399 | -0.066051 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | STHTOWN_CAP5 | 0.99004 | 0.92399 | -0.066051 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | STHTOWN_CAP5 | 0.99004 | 0.92399 | -0.066051 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | STHTOWN_CAP5 | 0.99004 | 0.92399 | -0.066051 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | STILWEL5 | 0.99392 | 0.91036 | -0.083556 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | STILWEL5 | 0.99392 | 0.91036 | -0.083556 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | STILWEL5 | 0.99392 | 0.91036 | -0.083556 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | STILWEL5 | 0.99392 | 0.91036 | -0.083556 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | STILWEL5 | 0.99392 | 0.91036 | -0.083556 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | STILWEL5 | 0.99392 | 0.91036 | -0.083556 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | STILWEL5 | 0.99392 | 0.91036 | -0.083556 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | STILWEL5 | 0.99392 | 0.91036 | -0.083556 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | STILWEL5 | 0.99392 | 0.91036 | -0.083556 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | STILWEL5 | 0.99392 | 0.91036 | -0.083556 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | STILWEL5 | 0.99392 | 0.91036 | -0.083556 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | STILWEL5 | 0.99392 | 0.91036 | -0.083556 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | STILWEL5 | 0.99392 | 0.91036 | -0.083556 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | STILWEL5 | 0.99392 | 0.91036 | -0.083556 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | STILWEL5 | 0.99392 | 0.91036 | -0.083556 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | STILWEL5 | 0.99392 | 0.91036 | -0.083556 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | STILWEL5 | 0.99392 | 0.91036 | -0.083556 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | STILWEL5 | 0.99392 | 0.91036 | -0.083556 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | STILWEL5 | 0.99392 | 0.91036 | -0.083556 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | STILWEL5 | 0.99392 | 0.91036 | -0.083556 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | STILWEL5 | 0.99392 | 0.91036 | -0.083556 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | STILWEL5 | 0.99392 | 0.91036 | -0.083556 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | STILWEL5 | 0.99392 | 0.91036 | -0.083556 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | STILWEL5 | 0.99392 | 0.91036 | -0.083556 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | STILWEL5 | 0.99392 | 0.91036 | -0.083556 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | STILWEL7 | 0.96467 | 0.9238 | -0.040871 |  | 0.95 | 1.05 | 0.040762 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | STILWEL7 | 0.96467 | 0.9238 | -0.040871 |  | 0.95 | 1.05 | 0.030778 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | STILWEL7 | 0.96467 | 0.9238 | -0.040871 |  | 0.95 | 1.05 | 0.031937 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | STILWEL7 | 0.96467 | 0.9238 | -0.040871 |  | 0.95 | 1.05 | 0.053181 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | STILWEL7 | 0.96467 | 0.9238 | -0.040871 |  | 0.95 | 1.05 | 0.032533 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | STILWEL7 | 0.96467 | 0.9238 | -0.040871 |  | 0.95 | 1.05 | 0.031326 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | STILWEL7 | 0.95078 | 0.9005 | -0.050283 |  | 0.95 | 1.05 | 0.036307 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | STILWEL7 | 0.95078 | 0.9005 | -0.050283 |  | 0.95 | 1.05 | 0.052743 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | STILWEL7 | 0.95078 | 0.9005 | -0.050283 |  | 0.95 | 1.05 | 0.039345 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | STILWEL7 | 0.95078 | 0.9005 | -0.050283 |  | 0.95 | 1.05 | 0.031366 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | STILWEL7 | 0.95078 | 0.9005 | -0.050283 |  | 0.95 | 1.05 | 0.041888 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | STILWEL7 | 0.95078 | 0.9005 | -0.050283 |  | 0.95 | 1.05 | 0.038797 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | STILWEL7 | 0.95078 | 0.9005 | -0.050283 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | STILWEL7 | 0.95078 | 0.9005 | -0.050283 |  | 0.95 | 1.05 | 0.067346 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | STILWEL7 | 0.95078 | 0.9005 | -0.050283 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | STILWEL7 | 0.95078 | 0.9005 | -0.050283 |  | 0.95 | 1.05 | 0.030851 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | STILWEL7 | 0.95078 | 0.9005 | -0.050283 |  | 0.95 | 1.05 | 0.032161 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | STILWEL7 | 0.95078 | 0.9005 | -0.050283 |  | 0.95 | 1.05 | 0.04067 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | STILWEL7 | 0.95078 | 0.9005 | -0.050283 |  | 0.95 | 1.05 | 0.040569 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | STILWEL7 | 0.95078 | 0.9005 | -0.050283 |  | 0.95 | 1.05 | 0.03086 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | STILWEL7 | 0.95078 | 0.9005 | -0.050283 |  | 0.95 | 1.05 | 0.033223 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | STILWEL7 | 0.95078 | 0.9005 | -0.050283 |  | 0.95 | 1.05 | 0.033733 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | STILWEL7 | 0.97097 | 0.91803 | -0.05294 |  | 0.95 | 1.05 | 0.036307 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | STILWEL7 | 0.97097 | 0.91803 | -0.05294 |  | 0.95 | 1.05 | 0.052743 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | STILWEL7 | 0.97097 | 0.91803 | -0.05294 |  | 0.95 | 1.05 | 0.039345 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | STILWEL7 | 0.97097 | 0.91803 | -0.05294 |  | 0.95 | 1.05 | 0.031366 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | STILWEL7 | 0.97097 | 0.91803 | -0.05294 |  | 0.95 | 1.05 | 0.041888 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | STILWEL7 | 0.97097 | 0.91803 | -0.05294 |  | 0.95 | 1.05 | 0.038797 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | STILWEL7 | 0.97097 | 0.91803 | -0.05294 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | STILWEL7 | 0.97097 | 0.91803 | -0.05294 |  | 0.95 | 1.05 | 0.067346 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | STILWEL7 | 0.97097 | 0.91803 | -0.05294 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | STILWEL7 | 0.97097 | 0.91803 | -0.05294 |  | 0.95 | 1.05 | 0.030851 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | STILWEL7 | 0.97097 | 0.91803 | -0.05294 |  | 0.95 | 1.05 | 0.032161 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | STILWEL7 | 0.97097 | 0.91803 | -0.05294 |  | 0.95 | 1.05 | 0.04067 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | STILWEL7 | 0.97097 | 0.91803 | -0.05294 |  | 0.95 | 1.05 | 0.040569 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | STILWEL7 | 0.97097 | 0.91803 | -0.05294 |  | 0.95 | 1.05 | 0.03086 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | STILWEL7 | 0.97097 | 0.91803 | -0.05294 |  | 0.95 | 1.05 | 0.033223 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | STILWEL7 | 0.97097 | 0.91803 | -0.05294 |  | 0.95 | 1.05 | 0.033733 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | STILWEL7 | 0.97519 | 0.88333 | -0.091853 |  | 0.95 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | STILWEL7 | 0.97519 | 0.88333 | -0.091853 |  | 0.95 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | STILWEL7 | 0.97519 | 0.88333 | -0.091853 |  | 0.95 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | STILWEL7 | 0.97519 | 0.88333 | -0.091853 |  | 0.95 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | STILWEL7 | 0.97519 | 0.88333 | -0.091853 |  | 0.95 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | STILWEL7 | 0.97519 | 0.88333 | -0.091853 |  | 0.95 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | STILWEL7 | 0.97519 | 0.88333 | -0.091853 |  | 0.95 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | STILWEL7 | 0.97519 | 0.88333 | -0.091853 |  | 0.95 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | STILWEL7 | 0.97519 | 0.88333 | -0.091853 |  | 0.95 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | STILWEL7 | 0.97519 | 0.88333 | -0.091853 |  | 0.95 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | STILWEL7 | 0.97519 | 0.88333 | -0.091853 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | STILWEL7 | 0.97519 | 0.88333 | -0.091853 |  | 0.95 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | STILWEL7 | 0.97519 | 0.88333 | -0.091853 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | STILWEL7 | 0.97519 | 0.88333 | -0.091853 |  | 0.95 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | STILWEL7 | 0.97519 | 0.88333 | -0.091853 |  | 0.95 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | STILWEL7 | 0.97519 | 0.88333 | -0.091853 |  | 0.95 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | STILWEL7 | 0.97519 | 0.88333 | -0.091853 |  | 0.95 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | STILWEL7 | 0.97519 | 0.88333 | -0.091853 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | STILWEL7 | 0.97519 | 0.88333 | -0.091853 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | STILWEL7 | 0.97519 | 0.88333 | -0.091853 |  | 0.95 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | STILWEL7 | 0.97519 | 0.88333 | -0.091853 |  | 0.95 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | STILWEL7 | 0.97519 | 0.88333 | -0.091853 |  | 0.95 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | STILWEL7 | 0.97519 | 0.88333 | -0.091853 |  | 0.95 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | STILWEL7 | 0.97519 | 0.88333 | -0.091853 |  | 0.95 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | STILWEL7 | 0.97519 | 0.88333 | -0.091853 |  | 0.95 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | STILWEL7 | 0.96448 | 0.9242 | -0.040282 |  | 0.95 | 1.05 | 0.036307 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | STILWEL7 | 0.96448 | 0.9242 | -0.040282 |  | 0.95 | 1.05 | 0.052743 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | STILWEL7 | 0.96448 | 0.9242 | -0.040282 |  | 0.95 | 1.05 | 0.039345 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | STILWEL7 | 0.96448 | 0.9242 | -0.040282 |  | 0.95 | 1.05 | 0.031366 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | STILWEL7 | 0.96448 | 0.9242 | -0.040282 |  | 0.95 | 1.05 | 0.041888 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | STILWEL7 | 0.96448 | 0.9242 | -0.040282 |  | 0.95 | 1.05 | 0.038797 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | STILWEL7 | 0.96448 | 0.9242 | -0.040282 |  | 0.95 | 1.05 | 0.030557 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | STILWEL7 | 0.96448 | 0.9242 | -0.040282 |  | 0.95 | 1.05 | 0.067346 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | STILWEL7 | 0.96448 | 0.9242 | -0.040282 |  | 0.95 | 1.05 | 0.030557 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | STILWEL7 | 0.96448 | 0.9242 | -0.040282 |  | 0.95 | 1.05 | 0.030851 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | STILWEL7 | 0.96448 | 0.9242 | -0.040282 |  | 0.95 | 1.05 | 0.032161 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | STILWEL7 | 0.96448 | 0.9242 | -0.040282 |  | 0.95 | 1.05 | 0.04067 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | STILWEL7 | 0.96448 | 0.9242 | -0.040282 |  | 0.95 | 1.05 | 0.040569 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | STILWEL7 | 0.96448 | 0.9242 | -0.040282 |  | 0.95 | 1.05 | 0.03086 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | STILWEL7 | 0.96448 | 0.9242 | -0.040282 |  | 0.95 | 1.05 | 0.033223 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | STILWEL7 | 0.96448 | 0.9242 | -0.040282 |  | 0.95 | 1.05 | 0.033733 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | STK324 2 | 0.98252 | 0.90598 | -0.076548 |  | 0.925 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | STK324 2 | 0.98252 | 0.90598 | -0.076548 |  | 0.925 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | STK324 2 | 0.98252 | 0.90598 | -0.076548 |  | 0.925 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | STK324 2 | 0.98252 | 0.90598 | -0.076548 |  | 0.925 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | STK324 2 | 0.98252 | 0.90598 | -0.076548 |  | 0.925 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | STK324 2 | 0.98252 | 0.90598 | -0.076548 |  | 0.925 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | STK324 2 | 0.98252 | 0.90598 | -0.076548 |  | 0.925 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | STK324 2 | 0.98252 | 0.90598 | -0.076548 |  | 0.925 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | STK324 2 | 0.98252 | 0.90598 | -0.076548 |  | 0.925 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | STK324 2 | 0.98252 | 0.90598 | -0.076548 |  | 0.925 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | STK324 2 | 0.98252 | 0.90598 | -0.076548 |  | 0.925 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | STK324 2 | 0.98252 | 0.90598 | -0.076548 |  | 0.925 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | STK324 2 | 0.98252 | 0.90598 | -0.076548 |  | 0.925 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | STK324 2 | 0.98252 | 0.90598 | -0.076548 |  | 0.925 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | STK324 2 | 0.98252 | 0.90598 | -0.076548 |  | 0.925 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | STK324 2 | 0.98252 | 0.90598 | -0.076548 |  | 0.925 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | STK324 2 | 0.98252 | 0.90598 | -0.076548 |  | 0.925 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | STK324 2 | 0.98252 | 0.90598 | -0.076548 |  | 0.925 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | STK324 2 | 0.98252 | 0.90598 | -0.076548 |  | 0.925 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | STK324 2 | 0.98252 | 0.90598 | -0.076548 |  | 0.925 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | STK324 2 | 0.98252 | 0.90598 | -0.076548 |  | 0.925 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | STK324 2 | 0.98252 | 0.90598 | -0.076548 |  | 0.925 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | STK324 2 | 0.98252 | 0.90598 | -0.076548 |  | 0.925 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | STK324 2 | 0.98252 | 0.90598 | -0.076548 |  | 0.925 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | STK324 2 | 0.98252 | 0.90598 | -0.076548 |  | 0.925 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | STK324J2 | 0.98253 | 0.90598 | -0.076548 |  | 0.925 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | STK324J2 | 0.98253 | 0.90598 | -0.076548 |  | 0.925 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | STK324J2 | 0.98253 | 0.90598 | -0.076548 |  | 0.925 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | STK324J2 | 0.98253 | 0.90598 | -0.076548 |  | 0.925 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | STK324J2 | 0.98253 | 0.90598 | -0.076548 |  | 0.925 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | STK324J2 | 0.98253 | 0.90598 | -0.076548 |  | 0.925 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | STK324J2 | 0.98253 | 0.90598 | -0.076548 |  | 0.925 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | STK324J2 | 0.98253 | 0.90598 | -0.076548 |  | 0.925 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | STK324J2 | 0.98253 | 0.90598 | -0.076548 |  | 0.925 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | STK324J2 | 0.98253 | 0.90598 | -0.076548 |  | 0.925 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | STK324J2 | 0.98253 | 0.90598 | -0.076548 |  | 0.925 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | STK324J2 | 0.98253 | 0.90598 | -0.076548 |  | 0.925 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | STK324J2 | 0.98253 | 0.90598 | -0.076548 |  | 0.925 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | STK324J2 | 0.98253 | 0.90598 | -0.076548 |  | 0.925 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | STK324J2 | 0.98253 | 0.90598 | -0.076548 |  | 0.925 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | STK324J2 | 0.98253 | 0.90598 | -0.076548 |  | 0.925 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | STK324J2 | 0.98253 | 0.90598 | -0.076548 |  | 0.925 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | STK324J2 | 0.98253 | 0.90598 | -0.076548 |  | 0.925 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | STK324J2 | 0.98253 | 0.90598 | -0.076548 |  | 0.925 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | STK324J2 | 0.98253 | 0.90598 | -0.076548 |  | 0.925 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | STK324J2 | 0.98253 | 0.90598 | -0.076548 |  | 0.925 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | STK324J2 | 0.98253 | 0.90598 | -0.076548 |  | 0.925 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | STK324J2 | 0.98253 | 0.90598 | -0.076548 |  | 0.925 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | STK324J2 | 0.98253 | 0.90598 | -0.076548 |  | 0.925 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | STK324J2 | 0.98253 | 0.90598 | -0.076548 |  | 0.925 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | STK418 2 | 0.98333 | 0.92305 | -0.060281 |  | 0.925 | 1.05 | 0.03053 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | STK418 2 | 0.98333 | 0.92305 | -0.060281 |  | 0.925 | 1.05 | 0.044933 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | STK418 2 | 0.98333 | 0.92305 | -0.060281 |  | 0.925 | 1.05 | 0.047811 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | STK418 2 | 0.98333 | 0.92305 | -0.060281 |  | 0.925 | 1.05 | 0.09719 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | STK418 2 | 0.98333 | 0.92305 | -0.060281 |  | 0.925 | 1.05 | 0.069376 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | STK418 2 | 0.98333 | 0.92305 | -0.060281 |  | 0.925 | 1.05 | 0.04277 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | STK418 2 | 0.98333 | 0.92305 | -0.060281 |  | 0.925 | 1.05 | 0.071112 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | STK418 2 | 0.98333 | 0.92305 | -0.060281 |  | 0.925 | 1.05 | 0.039357 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | STK418 2 | 0.98333 | 0.92305 | -0.060281 |  | 0.925 | 1.05 | 0.04035 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | STK418 2 | 0.98333 | 0.92305 | -0.060281 |  | 0.925 | 1.05 | 0.052332 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | STK418 2 | 0.98333 | 0.92305 | -0.060281 |  | 0.925 | 1.05 | 0.045944 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | STK418 2 | 0.98333 | 0.92305 | -0.060281 |  | 0.925 | 1.05 | 0.038178 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | STK418 2 | 0.98333 | 0.92305 | -0.060281 |  | 0.925 | 1.05 | 0.13469 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | STK418 2 | 0.98333 | 0.92305 | -0.060281 |  | 0.925 | 1.05 | 0.03053 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | STK418 2 | 0.98333 | 0.92305 | -0.060281 |  | 0.925 | 1.05 | 0.038178 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | STK418 2 | 0.98333 | 0.92305 | -0.060281 |  | 0.925 | 1.05 | 0.037309 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | STK418 2 | 0.98333 | 0.92305 | -0.060281 |  | 0.925 | 1.05 | 0.040075 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | STK418 2 | 0.98333 | 0.92305 | -0.060281 |  | 0.925 | 1.05 | 0.053764 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | STK418 2 | 0.98333 | 0.92305 | -0.060281 |  | 0.925 | 1.05 | 0.071762 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | STK418 2 | 0.98333 | 0.92305 | -0.060281 |  | 0.925 | 1.05 | 0.047827 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | STK418 2 | 0.98333 | 0.92305 | -0.060281 |  | 0.925 | 1.05 | 0.047827 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | STK418 2 | 0.98333 | 0.92305 | -0.060281 |  | 0.925 | 1.05 | 0.070303 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | STK418 2 | 0.98333 | 0.92305 | -0.060281 |  | 0.925 | 1.05 | 0.040614 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | STK418 2 | 0.98333 | 0.92305 | -0.060281 |  | 0.925 | 1.05 | 0.039729 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | STK418 2 | 0.98333 | 0.92305 | -0.060281 |  | 0.925 | 1.05 | 0.049662 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | STK418 2 | 0.98333 | 0.92305 | -0.060281 |  | 0.925 | 1.05 | 0.042332 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | STK418 2 | 0.98333 | 0.92305 | -0.060281 |  | 0.925 | 1.05 | 0.048722 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | STK418 2 | 0.98333 | 0.92305 | -0.060281 |  | 0.925 | 1.05 | 0.038156 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | STK418 2 | 0.98333 | 0.92305 | -0.060281 |  | 0.925 | 1.05 | 0.036794 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | STK418 2 | 0.98063 | 0.92391 | -0.056725 |  | 0.925 | 1.05 | 0.036307 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | STK418 2 | 0.98063 | 0.92391 | -0.056725 |  | 0.925 | 1.05 | 0.052743 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | STK418 2 | 0.98063 | 0.92391 | -0.056725 |  | 0.925 | 1.05 | 0.039345 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | STK418 2 | 0.98063 | 0.92391 | -0.056725 |  | 0.925 | 1.05 | 0.031366 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | STK418 2 | 0.98063 | 0.92391 | -0.056725 |  | 0.925 | 1.05 | 0.041888 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | STK418 2 | 0.98063 | 0.92391 | -0.056725 |  | 0.925 | 1.05 | 0.038797 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | STK418 2 | 0.98063 | 0.92391 | -0.056725 |  | 0.925 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | STK418 2 | 0.98063 | 0.92391 | -0.056725 |  | 0.925 | 1.05 | 0.067346 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | STK418 2 | 0.98063 | 0.92391 | -0.056725 |  | 0.925 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | STK418 2 | 0.98063 | 0.92391 | -0.056725 |  | 0.925 | 1.05 | 0.030851 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | STK418 2 | 0.98063 | 0.92391 | -0.056725 |  | 0.925 | 1.05 | 0.032161 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | STK418 2 | 0.98063 | 0.92391 | -0.056725 |  | 0.925 | 1.05 | 0.04067 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | STK418 2 | 0.98063 | 0.92391 | -0.056725 |  | 0.925 | 1.05 | 0.040569 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | STK418 2 | 0.98063 | 0.92391 | -0.056725 |  | 0.925 | 1.05 | 0.03086 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | STK418 2 | 0.98063 | 0.92391 | -0.056725 |  | 0.925 | 1.05 | 0.033223 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | STK418 2 | 0.98063 | 0.92391 | -0.056725 |  | 0.925 | 1.05 | 0.033733 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Add 45 MVAR switched shunt at NEVADA 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | STK418 2 | 0.98116 | 0.90166 | -0.0795 |  | 0.925 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | STK418 2 | 0.98116 | 0.90166 | -0.0795 |  | 0.925 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | STK418 2 | 0.98116 | 0.90166 | -0.0795 |  | 0.925 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | STK418 2 | 0.98116 | 0.90166 | -0.0795 |  | 0.925 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | STK418 2 | 0.98116 | 0.90166 | -0.0795 |  | 0.925 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | STK418 2 | 0.98116 | 0.90166 | -0.0795 |  | 0.925 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | STK418 2 | 0.98116 | 0.90166 | -0.0795 |  | 0.925 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | STK418 2 | 0.98116 | 0.90166 | -0.0795 |  | 0.925 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | STK418 2 | 0.98116 | 0.90166 | -0.0795 |  | 0.925 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | STK418 2 | 0.98116 | 0.90166 | -0.0795 |  | 0.925 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | STK418 2 | 0.98116 | 0.90166 | -0.0795 |  | 0.925 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | STK418 2 | 0.98116 | 0.90166 | -0.0795 |  | 0.925 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | STK418 2 | 0.98116 | 0.90166 | -0.0795 |  | 0.925 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | STK418 2 | 0.98116 | 0.90166 | -0.0795 |  | 0.925 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | STK418 2 | 0.98116 | 0.90166 | -0.0795 |  | 0.925 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | STK418 2 | 0.98116 | 0.90166 | -0.0795 |  | 0.925 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | STK418 2 | 0.98116 | 0.90166 | -0.0795 |  | 0.925 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | STK418 2 | 0.98116 | 0.90166 | -0.0795 |  | 0.925 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | STK418 2 | 0.98116 | 0.90166 | -0.0795 |  | 0.925 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | STK418 2 | 0.98116 | 0.90166 | -0.0795 |  | 0.925 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | STK418 2 | 0.98116 | 0.90166 | -0.0795 |  | 0.925 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | STK418 2 | 0.98116 | 0.90166 | -0.0795 |  | 0.925 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | STK418 2 | 0.98116 | 0.90166 | -0.0795 |  | 0.925 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | STK418 2 | 0.98116 | 0.90166 | -0.0795 |  | 0.925 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | STK418 2 | 0.98116 | 0.90166 | -0.0795 |  | 0.925 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | SUMMIT 6 | 0.9969 | 0.94577 | -0.051129 |  | 0.95 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | SUMMIT 6 | 0.9969 | 0.94577 | -0.051129 |  | 0.95 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | SUMMIT 6 | 0.9969 | 0.94577 | -0.051129 |  | 0.95 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | SUMMIT 6 | 0.9969 | 0.94577 | -0.051129 |  | 0.95 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | SUMMIT 6 | 0.9969 | 0.94577 | -0.051129 |  | 0.95 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | SUMMIT 6 | 0.9969 | 0.94577 | -0.051129 |  | 0.95 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | SUMMIT 6 | 0.9969 | 0.94577 | -0.051129 |  | 0.95 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | SUMMIT 6 | 0.9969 | 0.94577 | -0.051129 |  | 0.95 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | SUMMIT 6 | 0.9969 | 0.94577 | -0.051129 |  | 0.95 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | SUMMIT 6 | 0.9969 | 0.94577 | -0.051129 |  | 0.95 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | SUMMIT 6 | 0.9969 | 0.94577 | -0.051129 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | SUMMIT 6 | 0.9969 | 0.94577 | -0.051129 |  | 0.95 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | SUMMIT 6 | 0.9969 | 0.94577 | -0.051129 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | SUMMIT 6 | 0.9969 | 0.94577 | -0.051129 |  | 0.95 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | SUMMIT 6 | 0.9969 | 0.94577 | -0.051129 |  | 0.95 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | SUMMIT 6 | 0.9969 | 0.94577 | -0.051129 |  | 0.95 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | SUMMIT 6 | 0.9969 | 0.94577 | -0.051129 |  | 0.95 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | SUMMIT 6 | 0.9969 | 0.94577 | -0.051129 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | SUMMIT 6 | 0.9969 | 0.94577 | -0.051129 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | SUMMIT 6 | 0.9969 | 0.94577 | -0.051129 |  | 0.95 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | SUMMIT 6 | 0.9969 | 0.94577 | -0.051129 |  | 0.95 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | SUMMIT 6 | 0.9969 | 0.94577 | -0.051129 |  | 0.95 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | SUMMIT 6 | 0.9969 | 0.94577 | -0.051129 |  | 0.95 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | SUMMIT 6 | 0.9969 | 0.94577 | -0.051129 |  | 0.95 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | SUMMIT 6 | 0.9969 | 0.94577 | -0.051129 |  | 0.95 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | SUMMIT 7 | 0.9942 | 0.92053 | -0.073668 |  | 0.95 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | SUMMIT 7 | 0.9942 | 0.92053 | -0.073668 |  | 0.95 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | SUMMIT 7 | 0.9942 | 0.92053 | -0.073668 |  | 0.95 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | SUMMIT 7 | 0.9942 | 0.92053 | -0.073668 |  | 0.95 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | SUMMIT 7 | 0.9942 | 0.92053 | -0.073668 |  | 0.95 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | SUMMIT 7 | 0.9942 | 0.92053 | -0.073668 |  | 0.95 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | SUMMIT 7 | 0.9942 | 0.92053 | -0.073668 |  | 0.95 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | SUMMIT 7 | 0.9942 | 0.92053 | -0.073668 |  | 0.95 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | SUMMIT 7 | 0.9942 | 0.92053 | -0.073668 |  | 0.95 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | SUMMIT 7 | 0.9942 | 0.92053 | -0.073668 |  | 0.95 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | SUMMIT 7 | 0.9942 | 0.92053 | -0.073668 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | SUMMIT 7 | 0.9942 | 0.92053 | -0.073668 |  | 0.95 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | SUMMIT 7 | 0.9942 | 0.92053 | -0.073668 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | SUMMIT 7 | 0.9942 | 0.92053 | -0.073668 |  | 0.95 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | SUMMIT 7 | 0.9942 | 0.92053 | -0.073668 |  | 0.95 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | SUMMIT 7 | 0.9942 | 0.92053 | -0.073668 |  | 0.95 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | SUMMIT 7 | 0.9942 | 0.92053 | -0.073668 |  | 0.95 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | SUMMIT 7 | 0.9942 | 0.92053 | -0.073668 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | SUMMIT 7 | 0.9942 | 0.92053 | -0.073668 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | SUMMIT 7 | 0.9942 | 0.92053 | -0.073668 |  | 0.95 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | SUMMIT 7 | 0.9942 | 0.92053 | -0.073668 |  | 0.95 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | SUMMIT 7 | 0.9942 | 0.92053 | -0.073668 |  | 0.95 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | SUMMIT 7 | 0.9942 | 0.92053 | -0.073668 |  | 0.95 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | SUMMIT 7 | 0.9942 | 0.92053 | -0.073668 |  | 0.95 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | SUMMIT 7 | 0.9942 | 0.92053 | -0.073668 |  | 0.95 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | SUNSHINE5 | 0.98921 | 0.91885 | -0.070357 |  | 0.92 | 1.05 | 0.033596 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | SUNSHINE5 | 0.98921 | 0.91885 | -0.070357 |  | 0.92 | 1.05 | 0.040193 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | SUNSHINE5 | 0.98921 | 0.91885 | -0.070357 |  | 0.92 | 1.05 | 0.088122 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | SUNSHINE5 | 0.98921 | 0.91885 | -0.070357 |  | 0.92 | 1.05 | 0.074664 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | SUNSHINE5 | 0.98921 | 0.91885 | -0.070357 |  | 0.92 | 1.05 | 0.068051 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | SUNSHINE5 | 0.98921 | 0.91885 | -0.070357 |  | 0.92 | 1.05 | 0.035565 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | SUNSHINE5 | 0.98921 | 0.91885 | -0.070357 |  | 0.92 | 1.05 | 0.033904 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | SUNSHINE5 | 0.98921 | 0.91885 | -0.070357 |  | 0.92 | 1.05 | 0.16366 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | SUNSHINE5 | 0.98921 | 0.91885 | -0.070357 |  | 0.92 | 1.05 | 0.045569 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | SUNSHINE5 | 0.98921 | 0.91885 | -0.070357 |  | 0.92 | 1.05 | 0.13458 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | SUNSHINE5 | 0.98921 | 0.91885 | -0.070357 |  | 0.92 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | SUNSHINE5 | 0.98921 | 0.91885 | -0.070357 |  | 0.92 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | SUNSHINE5 | 0.98921 | 0.91885 | -0.070357 |  | 0.92 | 1.05 | 0.068426 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | SUNSHINE5 | 0.98921 | 0.91885 | -0.070357 |  | 0.92 | 1.05 | 0.035223 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | SUNSHINE5 | 0.98921 | 0.91885 | -0.070357 |  | 0.92 | 1.05 | 0.034504 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | SUNSHINE5 | 0.98941 | 0.91977 | -0.069641 |  | 0.92 | 1.05 | 0.040193 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | SUNSHINE5 | 0.98941 | 0.91977 | -0.069641 |  | 0.92 | 1.05 | 0.088122 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | SUNSHINE5 | 0.98941 | 0.91977 | -0.069641 |  | 0.92 | 1.05 | 0.074664 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | SUNSHINE5 | 0.98941 | 0.91977 | -0.069641 |  | 0.92 | 1.05 | 0.068051 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | SUNSHINE5 | 0.98941 | 0.91977 | -0.069641 |  | 0.92 | 1.05 | 0.034774 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | SUNSHINE5 | 0.98941 | 0.91977 | -0.069641 |  | 0.92 | 1.05 | 0.033904 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | SUNSHINE5 | 0.98941 | 0.91977 | -0.069641 |  | 0.92 | 1.05 | 0.16366 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | SUNSHINE5 | 0.98941 | 0.91977 | -0.069641 |  | 0.92 | 1.05 | 0.045569 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | SUNSHINE5 | 0.98941 | 0.91977 | -0.069641 |  | 0.92 | 1.05 | 0.13458 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | SUNSHINE5 | 0.98941 | 0.91977 | -0.069641 |  | 0.92 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | SUNSHINE5 | 0.98941 | 0.91977 | -0.069641 |  | 0.92 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | SUNSHINE5 | 0.98941 | 0.91977 | -0.069641 |  | 0.92 | 1.05 | 0.068426 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | SUNSHINE5 | 0.98941 | 0.91977 | -0.069641 |  | 0.92 | 1.05 | 0.035223 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | SUNSHINE5 | 0.98941 | 0.91977 | -0.069641 |  | 0.92 | 1.05 | 0.034504 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | SWISVAL6 | 0.97939 | 0.93476 | -0.044627 |  | 0.95 | 1.05 | 0.039728 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | SWISVAL6 | 0.97939 | 0.93476 | -0.044627 |  | 0.95 | 1.05 | 0.040762 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | SWISVAL6 | 0.97939 | 0.93476 | -0.044627 |  | 0.95 | 1.05 | 0.030778 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | SWISVAL6 | 0.97939 | 0.93476 | -0.044627 |  | 0.95 | 1.05 | 0.034227 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | SWISVAL6 | 0.97939 | 0.93476 | -0.044627 |  | 0.95 | 1.05 | 0.037164 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | SWISVAL6 | 0.97939 | 0.93476 | -0.044627 |  | 0.95 | 1.05 | 0.031937 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | SWISVAL6 | 0.97939 | 0.93476 | -0.044627 |  | 0.95 | 1.05 | 0.03782 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | SWISVAL6 | 0.97939 | 0.93476 | -0.044627 |  | 0.95 | 1.05 | 0.036407 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | SWISVAL6 | 0.97939 | 0.93476 | -0.044627 |  | 0.95 | 1.05 | 0.053181 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | SWISVAL6 | 0.97939 | 0.93476 | -0.044627 |  | 0.95 | 1.05 | 0.036407 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | SWISVAL6 | 0.97939 | 0.93476 | -0.044627 |  | 0.95 | 1.05 | 0.037418 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | SWISVAL6 | 0.97939 | 0.93476 | -0.044627 |  | 0.95 | 1.05 | 0.037355 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | SWISVAL6 | 0.97939 | 0.93476 | -0.044627 |  | 0.95 | 1.05 | 0.032533 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | SWISVAL6 | 0.97939 | 0.93476 | -0.044627 |  | 0.95 | 1.05 | 0.031326 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | SWISVAL6 | 0.97939 | 0.93476 | -0.044627 |  | 0.95 | 1.05 | 0.035094 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | SWISVAL6 | 0.97939 | 0.93476 | -0.044627 |  | 0.95 | 1.05 | 0.031652 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | SWISVAL6 | 0.97939 | 0.93476 | -0.044627 |  | 0.95 | 1.05 | 0.031104 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | SWISVAL6 | 0.97939 | 0.93476 | -0.044627 |  | 0.95 | 1.05 | 0.033175 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | SWISVAL6 | 0.97939 | 0.93476 | -0.044627 |  | 0.95 | 1.05 | 0.034843 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | SWISVAL6 | 0.98521 | 0.93898 | -0.046235 |  | 0.95 | 1.05 | 0.03053 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | SWISVAL6 | 0.98521 | 0.93898 | -0.046235 |  | 0.95 | 1.05 | 0.044933 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | SWISVAL6 | 0.98521 | 0.93898 | -0.046235 |  | 0.95 | 1.05 | 0.047811 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | SWISVAL6 | 0.98521 | 0.93898 | -0.046235 |  | 0.95 | 1.05 | 0.09719 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | SWISVAL6 | 0.98521 | 0.93898 | -0.046235 |  | 0.95 | 1.05 | 0.069376 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | SWISVAL6 | 0.98521 | 0.93898 | -0.046235 |  | 0.95 | 1.05 | 0.04277 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | SWISVAL6 | 0.98521 | 0.93898 | -0.046235 |  | 0.95 | 1.05 | 0.071112 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | SWISVAL6 | 0.98521 | 0.93898 | -0.046235 |  | 0.95 | 1.05 | 0.039357 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | SWISVAL6 | 0.98521 | 0.93898 | -0.046235 |  | 0.95 | 1.05 | 0.04035 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | SWISVAL6 | 0.98521 | 0.93898 | -0.046235 |  | 0.95 | 1.05 | 0.052332 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | SWISVAL6 | 0.98521 | 0.93898 | -0.046235 |  | 0.95 | 1.05 | 0.045944 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | SWISVAL6 | 0.98521 | 0.93898 | -0.046235 |  | 0.95 | 1.05 | 0.038178 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | SWISVAL6 | 0.98521 | 0.93898 | -0.046235 |  | 0.95 | 1.05 | 0.13469 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | SWISVAL6 | 0.98521 | 0.93898 | -0.046235 |  | 0.95 | 1.05 | 0.03053 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | SWISVAL6 | 0.98521 | 0.93898 | -0.046235 |  | 0.95 | 1.05 | 0.038178 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | SWISVAL6 | 0.98521 | 0.93898 | -0.046235 |  | 0.95 | 1.05 | 0.037309 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | SWISVAL6 | 0.98521 | 0.93898 | -0.046235 |  | 0.95 | 1.05 | 0.040075 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | SWISVAL6 | 0.98521 | 0.93898 | -0.046235 |  | 0.95 | 1.05 | 0.053764 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | SWISVAL6 | 0.98521 | 0.93898 | -0.046235 |  | 0.95 | 1.05 | 0.071762 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | SWISVAL6 | 0.98521 | 0.93898 | -0.046235 |  | 0.95 | 1.05 | 0.047827 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | SWISVAL6 | 0.98521 | 0.93898 | -0.046235 |  | 0.95 | 1.05 | 0.047827 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | SWISVAL6 | 0.98521 | 0.93898 | -0.046235 |  | 0.95 | 1.05 | 0.070303 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | SWISVAL6 | 0.98521 | 0.93898 | -0.046235 |  | 0.95 | 1.05 | 0.040614 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | SWISVAL6 | 0.98521 | 0.93898 | -0.046235 |  | 0.95 | 1.05 | 0.039729 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | SWISVAL6 | 0.98521 | 0.93898 | -0.046235 |  | 0.95 | 1.05 | 0.049662 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | SWISVAL6 | 0.98521 | 0.93898 | -0.046235 |  | 0.95 | 1.05 | 0.042332 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | SWISVAL6 | 0.98521 | 0.93898 | -0.046235 |  | 0.95 | 1.05 | 0.048722 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | SWISVAL6 | 0.98521 | 0.93898 | -0.046235 |  | 0.95 | 1.05 | 0.038156 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | SWISVAL6 | 0.98521 | 0.93898 | -0.046235 |  | 0.95 | 1.05 | 0.036794 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | SWISVAL6 | 0.97648 | 0.93112 | -0.045359 |  | 0.95 | 1.05 | 0.036307 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | SWISVAL6 | 0.97648 | 0.93112 | -0.045359 |  | 0.95 | 1.05 | 0.052743 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | SWISVAL6 | 0.97648 | 0.93112 | -0.045359 |  | 0.95 | 1.05 | 0.039345 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | SWISVAL6 | 0.97648 | 0.93112 | -0.045359 |  | 0.95 | 1.05 | 0.031366 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | SWISVAL6 | 0.97648 | 0.93112 | -0.045359 |  | 0.95 | 1.05 | 0.041888 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | SWISVAL6 | 0.97648 | 0.93112 | -0.045359 |  | 0.95 | 1.05 | 0.038797 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | SWISVAL6 | 0.97648 | 0.93112 | -0.045359 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | SWISVAL6 | 0.97648 | 0.93112 | -0.045359 |  | 0.95 | 1.05 | 0.067346 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | SWISVAL6 | 0.97648 | 0.93112 | -0.045359 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | SWISVAL6 | 0.97648 | 0.93112 | -0.045359 |  | 0.95 | 1.05 | 0.030851 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | SWISVAL6 | 0.97648 | 0.93112 | -0.045359 |  | 0.95 | 1.05 | 0.032161 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | SWISVAL6 | 0.97648 | 0.93112 | -0.045359 |  | 0.95 | 1.05 | 0.04067 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | SWISVAL6 | 0.97648 | 0.93112 | -0.045359 |  | 0.95 | 1.05 | 0.040569 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | SWISVAL6 | 0.97648 | 0.93112 | -0.045359 |  | 0.95 | 1.05 | 0.03086 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | SWISVAL6 | 0.97648 | 0.93112 | -0.045359 |  | 0.95 | 1.05 | 0.033223 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | SWISVAL6 | 0.97648 | 0.93112 | -0.045359 |  | 0.95 | 1.05 | 0.033733 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | SWISVAL6 | 0.98113 | 0.92862 | -0.052511 |  | 0.95 | 1.05 | 0.036307 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | SWISVAL6 | 0.98113 | 0.92862 | -0.052511 |  | 0.95 | 1.05 | 0.052743 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | SWISVAL6 | 0.98113 | 0.92862 | -0.052511 |  | 0.95 | 1.05 | 0.039345 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | SWISVAL6 | 0.98113 | 0.92862 | -0.052511 |  | 0.95 | 1.05 | 0.031366 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | SWISVAL6 | 0.98113 | 0.92862 | -0.052511 |  | 0.95 | 1.05 | 0.041888 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | SWISVAL6 | 0.98113 | 0.92862 | -0.052511 |  | 0.95 | 1.05 | 0.038797 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | SWISVAL6 | 0.98113 | 0.92862 | -0.052511 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | SWISVAL6 | 0.98113 | 0.92862 | -0.052511 |  | 0.95 | 1.05 | 0.067346 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | SWISVAL6 | 0.98113 | 0.92862 | -0.052511 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | SWISVAL6 | 0.98113 | 0.92862 | -0.052511 |  | 0.95 | 1.05 | 0.030851 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | SWISVAL6 | 0.98113 | 0.92862 | -0.052511 |  | 0.95 | 1.05 | 0.032161 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | SWISVAL6 | 0.98113 | 0.92862 | -0.052511 |  | 0.95 | 1.05 | 0.04067 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | SWISVAL6 | 0.98113 | 0.92862 | -0.052511 |  | 0.95 | 1.05 | 0.040569 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | SWISVAL6 | 0.98113 | 0.92862 | -0.052511 |  | 0.95 | 1.05 | 0.03086 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | SWISVAL6 | 0.98113 | 0.92862 | -0.052511 |  | 0.95 | 1.05 | 0.033223 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | SWISVAL6 | 0.98113 | 0.92862 | -0.052511 |  | 0.95 | 1.05 | 0.033733 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | SWISVAL6 | 0.98488 | 0.93055 | -0.054325 |  | 0.95 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | SWISVAL6 | 0.98488 | 0.93055 | -0.054325 |  | 0.95 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | SWISVAL6 | 0.98488 | 0.93055 | -0.054325 |  | 0.95 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | SWISVAL6 | 0.98488 | 0.93055 | -0.054325 |  | 0.95 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | SWISVAL6 | 0.98488 | 0.93055 | -0.054325 |  | 0.95 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | SWISVAL6 | 0.98488 | 0.93055 | -0.054325 |  | 0.95 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | SWISVAL6 | 0.98488 | 0.93055 | -0.054325 |  | 0.95 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | SWISVAL6 | 0.98488 | 0.93055 | -0.054325 |  | 0.95 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | SWISVAL6 | 0.98488 | 0.93055 | -0.054325 |  | 0.95 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | SWISVAL6 | 0.98488 | 0.93055 | -0.054325 |  | 0.95 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | SWISVAL6 | 0.98488 | 0.93055 | -0.054325 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | SWISVAL6 | 0.98488 | 0.93055 | -0.054325 |  | 0.95 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | SWISVAL6 | 0.98488 | 0.93055 | -0.054325 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | SWISVAL6 | 0.98488 | 0.93055 | -0.054325 |  | 0.95 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | SWISVAL6 | 0.98488 | 0.93055 | -0.054325 |  | 0.95 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | SWISVAL6 | 0.98488 | 0.93055 | -0.054325 |  | 0.95 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | SWISVAL6 | 0.98488 | 0.93055 | -0.054325 |  | 0.95 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | SWISVAL6 | 0.98488 | 0.93055 | -0.054325 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | SWISVAL6 | 0.98488 | 0.93055 | -0.054325 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | SWISVAL6 | 0.98488 | 0.93055 | -0.054325 |  | 0.95 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | SWISVAL6 | 0.98488 | 0.93055 | -0.054325 |  | 0.95 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | SWISVAL6 | 0.98488 | 0.93055 | -0.054325 |  | 0.95 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | SWISVAL6 | 0.98488 | 0.93055 | -0.054325 |  | 0.95 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | SWISVAL6 | 0.98488 | 0.93055 | -0.054325 |  | 0.95 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | SWISVAL6 | 0.98488 | 0.93055 | -0.054325 |  | 0.95 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | SWISVAL7 | 0.97697 | 0.92318 | -0.053791 |  | 0.95 | 1.05 | 0.039728 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | SWISVAL7 | 0.97697 | 0.92318 | -0.053791 |  | 0.95 | 1.05 | 0.040762 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | SWISVAL7 | 0.97697 | 0.92318 | -0.053791 |  | 0.95 | 1.05 | 0.030778 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | SWISVAL7 | 0.97697 | 0.92318 | -0.053791 |  | 0.95 | 1.05 | 0.034227 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | SWISVAL7 | 0.97697 | 0.92318 | -0.053791 |  | 0.95 | 1.05 | 0.037164 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | SWISVAL7 | 0.97697 | 0.92318 | -0.053791 |  | 0.95 | 1.05 | 0.031937 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | SWISVAL7 | 0.97697 | 0.92318 | -0.053791 |  | 0.95 | 1.05 | 0.03782 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | SWISVAL7 | 0.97697 | 0.92318 | -0.053791 |  | 0.95 | 1.05 | 0.036407 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | SWISVAL7 | 0.97697 | 0.92318 | -0.053791 |  | 0.95 | 1.05 | 0.053181 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | SWISVAL7 | 0.97697 | 0.92318 | -0.053791 |  | 0.95 | 1.05 | 0.036407 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | SWISVAL7 | 0.97697 | 0.92318 | -0.053791 |  | 0.95 | 1.05 | 0.037418 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | SWISVAL7 | 0.97697 | 0.92318 | -0.053791 |  | 0.95 | 1.05 | 0.037355 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | SWISVAL7 | 0.97697 | 0.92318 | -0.053791 |  | 0.95 | 1.05 | 0.032533 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | SWISVAL7 | 0.97697 | 0.92318 | -0.053791 |  | 0.95 | 1.05 | 0.031326 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | SWISVAL7 | 0.97697 | 0.92318 | -0.053791 |  | 0.95 | 1.05 | 0.035094 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | SWISVAL7 | 0.97697 | 0.92318 | -0.053791 |  | 0.95 | 1.05 | 0.031652 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | SWISVAL7 | 0.97697 | 0.92318 | -0.053791 |  | 0.95 | 1.05 | 0.031104 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | SWISVAL7 | 0.97697 | 0.92318 | -0.053791 |  | 0.95 | 1.05 | 0.033175 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | SWISVAL7 | 0.97697 | 0.92318 | -0.053791 |  | 0.95 | 1.05 | 0.034843 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | SWISVAL7 | 0.98381 | 0.92727 | -0.056541 |  | 0.95 | 1.05 | 0.03053 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | SWISVAL7 | 0.98381 | 0.92727 | -0.056541 |  | 0.95 | 1.05 | 0.044933 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | SWISVAL7 | 0.98381 | 0.92727 | -0.056541 |  | 0.95 | 1.05 | 0.047811 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | SWISVAL7 | 0.98381 | 0.92727 | -0.056541 |  | 0.95 | 1.05 | 0.09719 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | SWISVAL7 | 0.98381 | 0.92727 | -0.056541 |  | 0.95 | 1.05 | 0.069376 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | SWISVAL7 | 0.98381 | 0.92727 | -0.056541 |  | 0.95 | 1.05 | 0.04277 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | SWISVAL7 | 0.98381 | 0.92727 | -0.056541 |  | 0.95 | 1.05 | 0.071112 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | SWISVAL7 | 0.98381 | 0.92727 | -0.056541 |  | 0.95 | 1.05 | 0.039357 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | SWISVAL7 | 0.98381 | 0.92727 | -0.056541 |  | 0.95 | 1.05 | 0.04035 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | SWISVAL7 | 0.98381 | 0.92727 | -0.056541 |  | 0.95 | 1.05 | 0.052332 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | SWISVAL7 | 0.98381 | 0.92727 | -0.056541 |  | 0.95 | 1.05 | 0.045944 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | SWISVAL7 | 0.98381 | 0.92727 | -0.056541 |  | 0.95 | 1.05 | 0.038178 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | SWISVAL7 | 0.98381 | 0.92727 | -0.056541 |  | 0.95 | 1.05 | 0.13469 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | SWISVAL7 | 0.98381 | 0.92727 | -0.056541 |  | 0.95 | 1.05 | 0.03053 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | SWISVAL7 | 0.98381 | 0.92727 | -0.056541 |  | 0.95 | 1.05 | 0.038178 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | SWISVAL7 | 0.98381 | 0.92727 | -0.056541 |  | 0.95 | 1.05 | 0.037309 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | SWISVAL7 | 0.98381 | 0.92727 | -0.056541 |  | 0.95 | 1.05 | 0.040075 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | SWISVAL7 | 0.98381 | 0.92727 | -0.056541 |  | 0.95 | 1.05 | 0.053764 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | SWISVAL7 | 0.98381 | 0.92727 | -0.056541 |  | 0.95 | 1.05 | 0.071762 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | SWISVAL7 | 0.98381 | 0.92727 | -0.056541 |  | 0.95 | 1.05 | 0.047827 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | SWISVAL7 | 0.98381 | 0.92727 | -0.056541 |  | 0.95 | 1.05 | 0.047827 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | SWISVAL7 | 0.98381 | 0.92727 | -0.056541 |  | 0.95 | 1.05 | 0.070303 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | SWISVAL7 | 0.98381 | 0.92727 | -0.056541 |  | 0.95 | 1.05 | 0.040614 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | SWISVAL7 | 0.98381 | 0.92727 | -0.056541 |  | 0.95 | 1.05 | 0.039729 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | SWISVAL7 | 0.98381 | 0.92727 | -0.056541 |  | 0.95 | 1.05 | 0.049662 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | SWISVAL7 | 0.98381 | 0.92727 | -0.056541 |  | 0.95 | 1.05 | 0.042332 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | SWISVAL7 | 0.98381 | 0.92727 | -0.056541 |  | 0.95 | 1.05 | 0.048722 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | SWISVAL7 | 0.98381 | 0.92727 | -0.056541 |  | 0.95 | 1.05 | 0.038156 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | SWISVAL7 | 0.98381 | 0.92727 | -0.056541 |  | 0.95 | 1.05 | 0.036794 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | SWISVAL7 | 0.97309 | 0.91915 | -0.053943 |  | 0.95 | 1.05 | 0.036307 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | SWISVAL7 | 0.97309 | 0.91915 | -0.053943 |  | 0.95 | 1.05 | 0.052743 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | SWISVAL7 | 0.97309 | 0.91915 | -0.053943 |  | 0.95 | 1.05 | 0.039345 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | SWISVAL7 | 0.97309 | 0.91915 | -0.053943 |  | 0.95 | 1.05 | 0.031366 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | SWISVAL7 | 0.97309 | 0.91915 | -0.053943 |  | 0.95 | 1.05 | 0.041888 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | SWISVAL7 | 0.97309 | 0.91915 | -0.053943 |  | 0.95 | 1.05 | 0.038797 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | SWISVAL7 | 0.97309 | 0.91915 | -0.053943 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | SWISVAL7 | 0.97309 | 0.91915 | -0.053943 |  | 0.95 | 1.05 | 0.067346 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | SWISVAL7 | 0.97309 | 0.91915 | -0.053943 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | SWISVAL7 | 0.97309 | 0.91915 | -0.053943 |  | 0.95 | 1.05 | 0.030851 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | SWISVAL7 | 0.97309 | 0.91915 | -0.053943 |  | 0.95 | 1.05 | 0.032161 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | SWISVAL7 | 0.97309 | 0.91915 | -0.053943 |  | 0.95 | 1.05 | 0.04067 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | SWISVAL7 | 0.97309 | 0.91915 | -0.053943 |  | 0.95 | 1.05 | 0.040569 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | SWISVAL7 | 0.97309 | 0.91915 | -0.053943 |  | 0.95 | 1.05 | 0.03086 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | SWISVAL7 | 0.97309 | 0.91915 | -0.053943 |  | 0.95 | 1.05 | 0.033223 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | SWISVAL7 | 0.97309 | 0.91915 | -0.053943 |  | 0.95 | 1.05 | 0.033733 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | SWISVAL7 | 0.97883 | 0.91571 | -0.06312 |  | 0.95 | 1.05 | 0.036307 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | SWISVAL7 | 0.97883 | 0.91571 | -0.06312 |  | 0.95 | 1.05 | 0.052743 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | SWISVAL7 | 0.97883 | 0.91571 | -0.06312 |  | 0.95 | 1.05 | 0.039345 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | SWISVAL7 | 0.97883 | 0.91571 | -0.06312 |  | 0.95 | 1.05 | 0.031366 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | SWISVAL7 | 0.97883 | 0.91571 | -0.06312 |  | 0.95 | 1.05 | 0.041888 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | SWISVAL7 | 0.97883 | 0.91571 | -0.06312 |  | 0.95 | 1.05 | 0.038797 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | SWISVAL7 | 0.97883 | 0.91571 | -0.06312 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | SWISVAL7 | 0.97883 | 0.91571 | -0.06312 |  | 0.95 | 1.05 | 0.067346 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | SWISVAL7 | 0.97883 | 0.91571 | -0.06312 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | SWISVAL7 | 0.97883 | 0.91571 | -0.06312 |  | 0.95 | 1.05 | 0.030851 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | SWISVAL7 | 0.97883 | 0.91571 | -0.06312 |  | 0.95 | 1.05 | 0.032161 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | SWISVAL7 | 0.97883 | 0.91571 | -0.06312 |  | 0.95 | 1.05 | 0.04067 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | SWISVAL7 | 0.97883 | 0.91571 | -0.06312 |  | 0.95 | 1.05 | 0.040569 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | SWISVAL7 | 0.97883 | 0.91571 | -0.06312 |  | 0.95 | 1.05 | 0.03086 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | SWISVAL7 | 0.97883 | 0.91571 | -0.06312 |  | 0.95 | 1.05 | 0.033223 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | SWISVAL7 | 0.97883 | 0.91571 | -0.06312 |  | 0.95 | 1.05 | 0.033733 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | SWISVAL7 | 0.98447 | 0.91741 | -0.067064 |  | 0.95 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | SWISVAL7 | 0.98447 | 0.91741 | -0.067064 |  | 0.95 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | SWISVAL7 | 0.98447 | 0.91741 | -0.067064 |  | 0.95 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | SWISVAL7 | 0.98447 | 0.91741 | -0.067064 |  | 0.95 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | SWISVAL7 | 0.98447 | 0.91741 | -0.067064 |  | 0.95 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | SWISVAL7 | 0.98447 | 0.91741 | -0.067064 |  | 0.95 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | SWISVAL7 | 0.98447 | 0.91741 | -0.067064 |  | 0.95 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | SWISVAL7 | 0.98447 | 0.91741 | -0.067064 |  | 0.95 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | SWISVAL7 | 0.98447 | 0.91741 | -0.067064 |  | 0.95 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | SWISVAL7 | 0.98447 | 0.91741 | -0.067064 |  | 0.95 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | SWISVAL7 | 0.98447 | 0.91741 | -0.067064 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | SWISVAL7 | 0.98447 | 0.91741 | -0.067064 |  | 0.95 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | SWISVAL7 | 0.98447 | 0.91741 | -0.067064 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | SWISVAL7 | 0.98447 | 0.91741 | -0.067064 |  | 0.95 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | SWISVAL7 | 0.98447 | 0.91741 | -0.067064 |  | 0.95 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | SWISVAL7 | 0.98447 | 0.91741 | -0.067064 |  | 0.95 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | SWISVAL7 | 0.98447 | 0.91741 | -0.067064 |  | 0.95 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | SWISVAL7 | 0.98447 | 0.91741 | -0.067064 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | SWISVAL7 | 0.98447 | 0.91741 | -0.067064 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | SWISVAL7 | 0.98447 | 0.91741 | -0.067064 |  | 0.95 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | SWISVAL7 | 0.98447 | 0.91741 | -0.067064 |  | 0.95 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | SWISVAL7 | 0.98447 | 0.91741 | -0.067064 |  | 0.95 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | SWISVAL7 | 0.98447 | 0.91741 | -0.067064 |  | 0.95 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | SWISVAL7 | 0.98447 | 0.91741 | -0.067064 |  | 0.95 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | SWISVAL7 | 0.98447 | 0.91741 | -0.067064 |  | 0.95 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | SWITZER5 | 0.96419 | 0.9241 | -0.040092 |  | 0.93 | 1.05 | 0.036307 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | SWITZER5 | 0.96419 | 0.9241 | -0.040092 |  | 0.93 | 1.05 | 0.052743 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | SWITZER5 | 0.96419 | 0.9241 | -0.040092 |  | 0.93 | 1.05 | 0.039345 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | SWITZER5 | 0.96419 | 0.9241 | -0.040092 |  | 0.93 | 1.05 | 0.031366 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | SWITZER5 | 0.96419 | 0.9241 | -0.040092 |  | 0.93 | 1.05 | 0.041888 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | SWITZER5 | 0.96419 | 0.9241 | -0.040092 |  | 0.93 | 1.05 | 0.038797 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | SWITZER5 | 0.96419 | 0.9241 | -0.040092 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | SWITZER5 | 0.96419 | 0.9241 | -0.040092 |  | 0.93 | 1.05 | 0.067346 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | SWITZER5 | 0.96419 | 0.9241 | -0.040092 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | SWITZER5 | 0.96419 | 0.9241 | -0.040092 |  | 0.93 | 1.05 | 0.030851 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | SWITZER5 | 0.96419 | 0.9241 | -0.040092 |  | 0.93 | 1.05 | 0.032161 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | SWITZER5 | 0.96419 | 0.9241 | -0.040092 |  | 0.93 | 1.05 | 0.04067 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | SWITZER5 | 0.96419 | 0.9241 | -0.040092 |  | 0.93 | 1.05 | 0.040569 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | SWITZER5 | 0.96419 | 0.9241 | -0.040092 |  | 0.93 | 1.05 | 0.03086 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | SWITZER5 | 0.96419 | 0.9241 | -0.040092 |  | 0.93 | 1.05 | 0.033223 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | SWITZER5 | 0.96419 | 0.9241 | -0.040092 |  | 0.93 | 1.05 | 0.033733 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | SWITZER5 | 0.9736 | 0.9264 | -0.047203 |  | 0.93 | 1.05 | 0.036307 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | SWITZER5 | 0.9736 | 0.9264 | -0.047203 |  | 0.93 | 1.05 | 0.052743 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | SWITZER5 | 0.9736 | 0.9264 | -0.047203 |  | 0.93 | 1.05 | 0.039345 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | SWITZER5 | 0.9736 | 0.9264 | -0.047203 |  | 0.93 | 1.05 | 0.031366 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | SWITZER5 | 0.9736 | 0.9264 | -0.047203 |  | 0.93 | 1.05 | 0.041888 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | SWITZER5 | 0.9736 | 0.9264 | -0.047203 |  | 0.93 | 1.05 | 0.038797 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | SWITZER5 | 0.9736 | 0.9264 | -0.047203 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | SWITZER5 | 0.9736 | 0.9264 | -0.047203 |  | 0.93 | 1.05 | 0.067346 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | SWITZER5 | 0.9736 | 0.9264 | -0.047203 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | SWITZER5 | 0.9736 | 0.9264 | -0.047203 |  | 0.93 | 1.05 | 0.030851 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | SWITZER5 | 0.9736 | 0.9264 | -0.047203 |  | 0.93 | 1.05 | 0.032161 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | SWITZER5 | 0.9736 | 0.9264 | -0.047203 |  | 0.93 | 1.05 | 0.04067 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | SWITZER5 | 0.9736 | 0.9264 | -0.047203 |  | 0.93 | 1.05 | 0.040569 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | SWITZER5 | 0.9736 | 0.9264 | -0.047203 |  | 0.93 | 1.05 | 0.03086 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | SWITZER5 | 0.9736 | 0.9264 | -0.047203 |  | 0.93 | 1.05 | 0.033223 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | SWITZER5 | 0.9736 | 0.9264 | -0.047203 |  | 0.93 | 1.05 | 0.033733 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | SWITZER5 | 0.97626 | 0.90724 | -0.06902 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | SWITZER5 | 0.97626 | 0.90724 | -0.06902 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | SWITZER5 | 0.97626 | 0.90724 | -0.06902 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | SWITZER5 | 0.97626 | 0.90724 | -0.06902 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | SWITZER5 | 0.97626 | 0.90724 | -0.06902 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | SWITZER5 | 0.97626 | 0.90724 | -0.06902 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | SWITZER5 | 0.97626 | 0.90724 | -0.06902 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | SWITZER5 | 0.97626 | 0.90724 | -0.06902 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | SWITZER5 | 0.97626 | 0.90724 | -0.06902 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | SWITZER5 | 0.97626 | 0.90724 | -0.06902 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | SWITZER5 | 0.97626 | 0.90724 | -0.06902 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | SWITZER5 | 0.97626 | 0.90724 | -0.06902 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | SWITZER5 | 0.97626 | 0.90724 | -0.06902 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | SWITZER5 | 0.97626 | 0.90724 | -0.06902 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | SWITZER5 | 0.97626 | 0.90724 | -0.06902 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | SWITZER5 | 0.97626 | 0.90724 | -0.06902 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | SWITZER5 | 0.97626 | 0.90724 | -0.06902 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | SWITZER5 | 0.97626 | 0.90724 | -0.06902 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | SWITZER5 | 0.97626 | 0.90724 | -0.06902 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | SWITZER5 | 0.97626 | 0.90724 | -0.06902 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | SWITZER5 | 0.97626 | 0.90724 | -0.06902 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | SWITZER5 | 0.97626 | 0.90724 | -0.06902 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | SWITZER5 | 0.97626 | 0.90724 | -0.06902 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | SWITZER5 | 0.97626 | 0.90724 | -0.06902 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | SWITZER5 | 0.97626 | 0.90724 | -0.06902 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | TAYLOR 4 | 0.96481 | 0.9191 | -0.045703 |  | 0.93 | 1.05 | 0.091967 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | TAYLOR 4 | 0.96481 | 0.9191 | -0.045703 |  | 0.93 | 1.05 | 0.033356 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | TAYLOR 4 | 0.96481 | 0.9191 | -0.045703 |  | 0.93 | 1.05 | 0.044346 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | TAYLOR 4 | 0.96481 | 0.9191 | -0.045703 |  | 0.93 | 1.05 | 0.058536 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | TAYLOR 4 | 0.96481 | 0.9191 | -0.045703 |  | 0.93 | 1.05 | 0.059327 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | TAYLOR 4 | 0.96481 | 0.9191 | -0.045703 |  | 0.93 | 1.05 | 0.041874 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | TAYLOR 4 | 0.96481 | 0.9191 | -0.045703 |  | 0.93 | 1.05 | 0.046192 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | TAYLOR 4 | 0.96481 | 0.9191 | -0.045703 |  | 0.93 | 1.05 | 0.12754 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | TAYLOR 4 | 0.96481 | 0.9191 | -0.045703 |  | 0.93 | 1.05 | 0.047018 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | TAYLOR 4 | 0.96481 | 0.9191 | -0.045703 |  | 0.93 | 1.05 | 0.056662 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | TAYLOR 4 | 0.96481 | 0.9191 | -0.045703 |  | 0.93 | 1.05 | 0.056662 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | TAYLOR 4 | 0.96481 | 0.9191 | -0.045703 |  | 0.93 | 1.05 | 0.056727 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | TAYLOR 4 | 0.96481 | 0.9191 | -0.045703 |  | 0.93 | 1.05 | 0.074186 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | TAYLOR 4 | 0.96481 | 0.9191 | -0.045703 |  | 0.93 | 1.05 | 0.040839 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | TAYLOR 4 | 0.96481 | 0.9191 | -0.045703 |  | 0.93 | 1.05 | 0.03863 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | TAYLOR 4 | 0.96481 | 0.9191 | -0.045703 |  | 0.93 | 1.05 | 0.042285 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | TAYLOR 4 | 0.96481 | 0.9191 | -0.045703 |  | 0.93 | 1.05 | 0.042285 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | TAYLOR 4 | 0.96481 | 0.9191 | -0.045703 |  | 0.93 | 1.05 | 0.050204 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | TAYLOR 4 | 0.96481 | 0.9191 | -0.045703 |  | 0.93 | 1.05 | 0.058005 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | TAYLOR 4 | 0.96481 | 0.9191 | -0.045703 |  | 0.93 | 1.05 | 0.041735 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | TAYLOR 4 | 0.96481 | 0.9191 | -0.045703 |  | 0.93 | 1.05 | 0.057076 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | TAYLOR 4 | 0.96481 | 0.9191 | -0.045703 |  | 0.93 | 1.05 | 0.050111 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | TAYLOR 4 | 0.96481 | 0.9191 | -0.045703 |  | 0.93 | 1.05 | 0.06491 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | TAYLOR 4 | 0.96481 | 0.9191 | -0.045703 |  | 0.93 | 1.05 | 0.051051 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | TAYLOR 4 | 0.96481 | 0.9191 | -0.045703 |  | 0.93 | 1.05 | 0.036279 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | TAYLOR 4 | 0.97327 | 0.92509 | -0.048174 |  | 0.93 | 1.05 | 0.035768 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | TAYLOR 4 | 0.97327 | 0.92509 | -0.048174 |  | 0.93 | 1.05 | 0.088718 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | TAYLOR 4 | 0.97327 | 0.92509 | -0.048174 |  | 0.93 | 1.05 | 0.031473 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | TAYLOR 4 | 0.97327 | 0.92509 | -0.048174 |  | 0.93 | 1.05 | 0.034941 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | TAYLOR 4 | 0.97327 | 0.92509 | -0.048174 |  | 0.93 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | TAYLOR 4 | 0.97327 | 0.92509 | -0.048174 |  | 0.93 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | TAYLOR 4 | 0.97327 | 0.92509 | -0.048174 |  | 0.93 | 1.05 | 0.049224 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | TAYLOR 4 | 0.97327 | 0.92509 | -0.048174 |  | 0.93 | 1.05 | 0.038981 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | TAYLOR 4 | 0.97327 | 0.92509 | -0.048174 |  | 0.93 | 1.05 | 0.040399 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | TAYLOR 4 | 0.97327 | 0.92509 | -0.048174 |  | 0.93 | 1.05 | 0.031912 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | TAYLOR 4 | 0.97327 | 0.92509 | -0.048174 |  | 0.93 | 1.05 | 0.034127 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | TAYLOR 4 | 0.97327 | 0.92509 | -0.048174 |  | 0.93 | 1.05 | 0.047318 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | TAYLOR 4 | 0.96678 | 0.91932 | -0.047468 |  | 0.93 | 1.05 | 0.040439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | TAYLOR 4 | 0.96678 | 0.91932 | -0.047468 |  | 0.93 | 1.05 | 0.034853 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | TAYLOR 4 | 0.96678 | 0.91932 | -0.047468 |  | 0.93 | 1.05 | 0.046783 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | TAYLOR 4 | 0.96678 | 0.91932 | -0.047468 |  | 0.93 | 1.05 | 0.047615 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | TAYLOR 4 | 0.96678 | 0.91932 | -0.047468 |  | 0.93 | 1.05 | 0.034938 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | TAYLOR 4 | 0.96678 | 0.91932 | -0.047468 |  | 0.93 | 1.05 | 0.037875 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | TAYLOR 4 | 0.96678 | 0.91932 | -0.047468 |  | 0.93 | 1.05 | 0.044022 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | TAYLOR 4 | 0.96678 | 0.91932 | -0.047468 |  | 0.93 | 1.05 | 0.030552 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | TAYLOR 4 | 0.96678 | 0.91932 | -0.047468 |  | 0.93 | 1.05 | 0.038531 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | TAYLOR 4 | 0.96678 | 0.91932 | -0.047468 |  | 0.93 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | TAYLOR 4 | 0.96678 | 0.91932 | -0.047468 |  | 0.93 | 1.05 | 0.062491 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | TAYLOR 4 | 0.96678 | 0.91932 | -0.047468 |  | 0.93 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | TAYLOR 4 | 0.96678 | 0.91932 | -0.047468 |  | 0.93 | 1.05 | 0.038129 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | TAYLOR 4 | 0.96678 | 0.91932 | -0.047468 |  | 0.93 | 1.05 | 0.038066 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | TAYLOR 4 | 0.96678 | 0.91932 | -0.047468 |  | 0.93 | 1.05 | 0.034955 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | TAYLOR 4 | 0.96678 | 0.91932 | -0.047468 |  | 0.93 | 1.05 | 0.06281 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | TAYLOR 4 | 0.96678 | 0.91932 | -0.047468 |  | 0.93 | 1.05 | 0.045309 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | TAYLOR 4 | 0.96678 | 0.91932 | -0.047468 |  | 0.93 | 1.05 | 0.035805 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | TAYLOR 4 | 0.96678 | 0.91932 | -0.047468 |  | 0.93 | 1.05 | 0.032364 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | TAYLOR 4 | 0.96678 | 0.91932 | -0.047468 |  | 0.93 | 1.05 | 0.031815 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | TAYLOR 4 | 0.96678 | 0.91932 | -0.047468 |  | 0.93 | 1.05 | 0.033886 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | TAYLOR 4 | 0.96678 | 0.91932 | -0.047468 |  | 0.93 | 1.05 | 0.035554 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | TAYLOR 4 | 0.97159 | 0.91257 | -0.059019 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | TAYLOR 4 | 0.97159 | 0.91257 | -0.059019 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | TAYLOR 4 | 0.97159 | 0.91257 | -0.059019 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | TAYLOR 4 | 0.97159 | 0.91257 | -0.059019 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | TAYLOR 4 | 0.97159 | 0.91257 | -0.059019 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | TAYLOR 4 | 0.97159 | 0.91257 | -0.059019 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | TAYLOR 4 | 0.97159 | 0.91257 | -0.059019 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | TAYLOR 4 | 0.97159 | 0.91257 | -0.059019 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | TAYLOR 4 | 0.97159 | 0.91257 | -0.059019 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | TAYLOR 4 | 0.97159 | 0.91257 | -0.059019 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | TAYLOR 4 | 0.97159 | 0.91257 | -0.059019 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | TAYLOR 4 | 0.97159 | 0.91257 | -0.059019 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | TAYLOR 4 | 0.97159 | 0.91257 | -0.059019 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | TAYLOR 4 | 0.97159 | 0.91257 | -0.059019 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | TAYLOR 4 | 0.97159 | 0.91257 | -0.059019 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | TAYLOR 4 | 0.97159 | 0.91257 | -0.059019 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | TAYLOR 4 | 0.97159 | 0.91257 | -0.059019 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | TAYLOR 4 | 0.97159 | 0.91257 | -0.059019 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | TAYLOR 4 | 0.97159 | 0.91257 | -0.059019 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | TAYLOR 4 | 0.97159 | 0.91257 | -0.059019 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | TAYLOR 4 | 0.97159 | 0.91257 | -0.059019 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | TAYLOR 4 | 0.97159 | 0.91257 | -0.059019 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | TAYLOR 4 | 0.97159 | 0.91257 | -0.059019 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | TAYLOR 4 | 0.97159 | 0.91257 | -0.059019 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | TAYLOR 4 | 0.97159 | 0.91257 | -0.059019 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | TECHILL6 | 0.97113 | 0.93541 | -0.035723 |  | 0.95 | 1.05 | 0.039728 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | TECHILL6 | 0.97113 | 0.93541 | -0.035723 |  | 0.95 | 1.05 | 0.040762 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | TECHILL6 | 0.97113 | 0.93541 | -0.035723 |  | 0.95 | 1.05 | 0.030778 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | TECHILL6 | 0.97113 | 0.93541 | -0.035723 |  | 0.95 | 1.05 | 0.034227 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | TECHILL6 | 0.97113 | 0.93541 | -0.035723 |  | 0.95 | 1.05 | 0.037164 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | TECHILL6 | 0.97113 | 0.93541 | -0.035723 |  | 0.95 | 1.05 | 0.031937 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | TECHILL6 | 0.97113 | 0.93541 | -0.035723 |  | 0.95 | 1.05 | 0.03782 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | TECHILL6 | 0.97113 | 0.93541 | -0.035723 |  | 0.95 | 1.05 | 0.036407 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | TECHILL6 | 0.97113 | 0.93541 | -0.035723 |  | 0.95 | 1.05 | 0.053181 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | TECHILL6 | 0.97113 | 0.93541 | -0.035723 |  | 0.95 | 1.05 | 0.036407 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | TECHILL6 | 0.97113 | 0.93541 | -0.035723 |  | 0.95 | 1.05 | 0.037418 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | TECHILL6 | 0.97113 | 0.93541 | -0.035723 |  | 0.95 | 1.05 | 0.037355 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | TECHILL6 | 0.97113 | 0.93541 | -0.035723 |  | 0.95 | 1.05 | 0.032533 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | TECHILL6 | 0.97113 | 0.93541 | -0.035723 |  | 0.95 | 1.05 | 0.031326 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | TECHILL6 | 0.97113 | 0.93541 | -0.035723 |  | 0.95 | 1.05 | 0.035094 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | TECHILL6 | 0.97113 | 0.93541 | -0.035723 |  | 0.95 | 1.05 | 0.031652 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | TECHILL6 | 0.97113 | 0.93541 | -0.035723 |  | 0.95 | 1.05 | 0.031104 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | TECHILL6 | 0.97113 | 0.93541 | -0.035723 |  | 0.95 | 1.05 | 0.033175 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | TECHILL6 | 0.97113 | 0.93541 | -0.035723 |  | 0.95 | 1.05 | 0.034843 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 30 MVAR switched shunt at G23-220-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | TECHILL6 | 0.9678 | 0.93068 | -0.037116 |  | 0.95 | 1.05 | 0.036307 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | TECHILL6 | 0.9678 | 0.93068 | -0.037116 |  | 0.95 | 1.05 | 0.052743 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | TECHILL6 | 0.9678 | 0.93068 | -0.037116 |  | 0.95 | 1.05 | 0.039345 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | TECHILL6 | 0.9678 | 0.93068 | -0.037116 |  | 0.95 | 1.05 | 0.031366 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | TECHILL6 | 0.9678 | 0.93068 | -0.037116 |  | 0.95 | 1.05 | 0.041888 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | TECHILL6 | 0.9678 | 0.93068 | -0.037116 |  | 0.95 | 1.05 | 0.038797 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | TECHILL6 | 0.9678 | 0.93068 | -0.037116 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | TECHILL6 | 0.9678 | 0.93068 | -0.037116 |  | 0.95 | 1.05 | 0.067346 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | TECHILL6 | 0.9678 | 0.93068 | -0.037116 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | TECHILL6 | 0.9678 | 0.93068 | -0.037116 |  | 0.95 | 1.05 | 0.030851 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | TECHILL6 | 0.9678 | 0.93068 | -0.037116 |  | 0.95 | 1.05 | 0.032161 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | TECHILL6 | 0.9678 | 0.93068 | -0.037116 |  | 0.95 | 1.05 | 0.04067 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | TECHILL6 | 0.9678 | 0.93068 | -0.037116 |  | 0.95 | 1.05 | 0.040569 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | TECHILL6 | 0.9678 | 0.93068 | -0.037116 |  | 0.95 | 1.05 | 0.03086 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | TECHILL6 | 0.9678 | 0.93068 | -0.037116 |  | 0.95 | 1.05 | 0.033223 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | TECHILL6 | 0.9678 | 0.93068 | -0.037116 |  | 0.95 | 1.05 | 0.033733 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | TECHILL6 | 0.97258 | 0.92969 | -0.042885 |  | 0.95 | 1.05 | 0.036307 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | TECHILL6 | 0.97258 | 0.92969 | -0.042885 |  | 0.95 | 1.05 | 0.052743 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | TECHILL6 | 0.97258 | 0.92969 | -0.042885 |  | 0.95 | 1.05 | 0.039345 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | TECHILL6 | 0.97258 | 0.92969 | -0.042885 |  | 0.95 | 1.05 | 0.031366 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | TECHILL6 | 0.97258 | 0.92969 | -0.042885 |  | 0.95 | 1.05 | 0.041888 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | TECHILL6 | 0.97258 | 0.92969 | -0.042885 |  | 0.95 | 1.05 | 0.038797 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | TECHILL6 | 0.97258 | 0.92969 | -0.042885 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | TECHILL6 | 0.97258 | 0.92969 | -0.042885 |  | 0.95 | 1.05 | 0.067346 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | TECHILL6 | 0.97258 | 0.92969 | -0.042885 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | TECHILL6 | 0.97258 | 0.92969 | -0.042885 |  | 0.95 | 1.05 | 0.030851 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | TECHILL6 | 0.97258 | 0.92969 | -0.042885 |  | 0.95 | 1.05 | 0.032161 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | TECHILL6 | 0.97258 | 0.92969 | -0.042885 |  | 0.95 | 1.05 | 0.04067 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | TECHILL6 | 0.97258 | 0.92969 | -0.042885 |  | 0.95 | 1.05 | 0.040569 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | TECHILL6 | 0.97258 | 0.92969 | -0.042885 |  | 0.95 | 1.05 | 0.03086 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | TECHILL6 | 0.97258 | 0.92969 | -0.042885 |  | 0.95 | 1.05 | 0.033223 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | TECHILL6 | 0.97258 | 0.92969 | -0.042885 |  | 0.95 | 1.05 | 0.033733 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | TECHILL6 | 0.9773 | 0.93342 | -0.043875 |  | 0.95 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | TECHILL6 | 0.9773 | 0.93342 | -0.043875 |  | 0.95 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | TECHILL6 | 0.9773 | 0.93342 | -0.043875 |  | 0.95 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | TECHILL6 | 0.9773 | 0.93342 | -0.043875 |  | 0.95 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | TECHILL6 | 0.9773 | 0.93342 | -0.043875 |  | 0.95 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | TECHILL6 | 0.9773 | 0.93342 | -0.043875 |  | 0.95 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | TECHILL6 | 0.9773 | 0.93342 | -0.043875 |  | 0.95 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | TECHILL6 | 0.9773 | 0.93342 | -0.043875 |  | 0.95 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | TECHILL6 | 0.9773 | 0.93342 | -0.043875 |  | 0.95 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | TECHILL6 | 0.9773 | 0.93342 | -0.043875 |  | 0.95 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | TECHILL6 | 0.9773 | 0.93342 | -0.043875 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | TECHILL6 | 0.9773 | 0.93342 | -0.043875 |  | 0.95 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | TECHILL6 | 0.9773 | 0.93342 | -0.043875 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | TECHILL6 | 0.9773 | 0.93342 | -0.043875 |  | 0.95 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | TECHILL6 | 0.9773 | 0.93342 | -0.043875 |  | 0.95 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | TECHILL6 | 0.9773 | 0.93342 | -0.043875 |  | 0.95 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | TECHILL6 | 0.9773 | 0.93342 | -0.043875 |  | 0.95 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | TECHILL6 | 0.9773 | 0.93342 | -0.043875 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | TECHILL6 | 0.9773 | 0.93342 | -0.043875 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | TECHILL6 | 0.9773 | 0.93342 | -0.043875 |  | 0.95 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | TECHILL6 | 0.9773 | 0.93342 | -0.043875 |  | 0.95 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | TECHILL6 | 0.9773 | 0.93342 | -0.043875 |  | 0.95 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | TECHILL6 | 0.9773 | 0.93342 | -0.043875 |  | 0.95 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | TECHILL6 | 0.9773 | 0.93342 | -0.043875 |  | 0.95 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | TECHILL6 | 0.9773 | 0.93342 | -0.043875 |  | 0.95 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | TECHILL6 | 0.96994 | 0.93824 | -0.031702 |  | 0.95 | 1.05 | 0.036307 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | TECHILL6 | 0.96994 | 0.93824 | -0.031702 |  | 0.95 | 1.05 | 0.052743 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | TECHILL6 | 0.96994 | 0.93824 | -0.031702 |  | 0.95 | 1.05 | 0.039345 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | TECHILL6 | 0.96994 | 0.93824 | -0.031702 |  | 0.95 | 1.05 | 0.031366 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | TECHILL6 | 0.96994 | 0.93824 | -0.031702 |  | 0.95 | 1.05 | 0.041888 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | TECHILL6 | 0.96994 | 0.93824 | -0.031702 |  | 0.95 | 1.05 | 0.038797 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | TECHILL6 | 0.96994 | 0.93824 | -0.031702 |  | 0.95 | 1.05 | 0.030557 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | TECHILL6 | 0.96994 | 0.93824 | -0.031702 |  | 0.95 | 1.05 | 0.067346 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | TECHILL6 | 0.96994 | 0.93824 | -0.031702 |  | 0.95 | 1.05 | 0.030557 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | TECHILL6 | 0.96994 | 0.93824 | -0.031702 |  | 0.95 | 1.05 | 0.030851 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | TECHILL6 | 0.96994 | 0.93824 | -0.031702 |  | 0.95 | 1.05 | 0.032161 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | TECHILL6 | 0.96994 | 0.93824 | -0.031702 |  | 0.95 | 1.05 | 0.04067 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | TECHILL6 | 0.96994 | 0.93824 | -0.031702 |  | 0.95 | 1.05 | 0.040569 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | TECHILL6 | 0.96994 | 0.93824 | -0.031702 |  | 0.95 | 1.05 | 0.03086 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | TECHILL6 | 0.96994 | 0.93824 | -0.031702 |  | 0.95 | 1.05 | 0.033223 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | TECHILL6 | 0.96994 | 0.93824 | -0.031702 |  | 0.95 | 1.05 | 0.033733 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | TIOGA 4 | 0.9616 | 0.91242 | -0.049181 |  | 0.93 | 1.05 | 0.040439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | TIOGA 4 | 0.9616 | 0.91242 | -0.049181 |  | 0.93 | 1.05 | 0.034853 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | TIOGA 4 | 0.9616 | 0.91242 | -0.049181 |  | 0.93 | 1.05 | 0.046783 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | TIOGA 4 | 0.9616 | 0.91242 | -0.049181 |  | 0.93 | 1.05 | 0.047615 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | TIOGA 4 | 0.9616 | 0.91242 | -0.049181 |  | 0.93 | 1.05 | 0.034938 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | TIOGA 4 | 0.9616 | 0.91242 | -0.049181 |  | 0.93 | 1.05 | 0.037875 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | TIOGA 4 | 0.9616 | 0.91242 | -0.049181 |  | 0.93 | 1.05 | 0.044022 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | TIOGA 4 | 0.9616 | 0.91242 | -0.049181 |  | 0.93 | 1.05 | 0.030552 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | TIOGA 4 | 0.9616 | 0.91242 | -0.049181 |  | 0.93 | 1.05 | 0.038531 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | TIOGA 4 | 0.9616 | 0.91242 | -0.049181 |  | 0.93 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | TIOGA 4 | 0.9616 | 0.91242 | -0.049181 |  | 0.93 | 1.05 | 0.062491 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | TIOGA 4 | 0.9616 | 0.91242 | -0.049181 |  | 0.93 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | TIOGA 4 | 0.9616 | 0.91242 | -0.049181 |  | 0.93 | 1.05 | 0.038129 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | TIOGA 4 | 0.9616 | 0.91242 | -0.049181 |  | 0.93 | 1.05 | 0.038066 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | TIOGA 4 | 0.9616 | 0.91242 | -0.049181 |  | 0.93 | 1.05 | 0.034955 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | TIOGA 4 | 0.9616 | 0.91242 | -0.049181 |  | 0.93 | 1.05 | 0.06281 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | TIOGA 4 | 0.9616 | 0.91242 | -0.049181 |  | 0.93 | 1.05 | 0.045309 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | TIOGA 4 | 0.9616 | 0.91242 | -0.049181 |  | 0.93 | 1.05 | 0.035805 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | TIOGA 4 | 0.9616 | 0.91242 | -0.049181 |  | 0.93 | 1.05 | 0.032364 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | TIOGA 4 | 0.9616 | 0.91242 | -0.049181 |  | 0.93 | 1.05 | 0.031815 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | TIOGA 4 | 0.9616 | 0.91242 | -0.049181 |  | 0.93 | 1.05 | 0.033886 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | TIOGA 4 | 0.9616 | 0.91242 | -0.049181 |  | 0.93 | 1.05 | 0.035554 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | TIOGA 4 | 0.97811 | 0.91207 | -0.066038 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | TIOGA 4 | 0.97811 | 0.91207 | -0.066038 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | TIOGA 4 | 0.97811 | 0.91207 | -0.066038 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | TIOGA 4 | 0.97811 | 0.91207 | -0.066038 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | TIOGA 4 | 0.97811 | 0.91207 | -0.066038 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | TIOGA 4 | 0.97811 | 0.91207 | -0.066038 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | TIOGA 4 | 0.97811 | 0.91207 | -0.066038 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | TIOGA 4 | 0.97811 | 0.91207 | -0.066038 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | TIOGA 4 | 0.97811 | 0.91207 | -0.066038 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | TIOGA 4 | 0.97811 | 0.91207 | -0.066038 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | TIOGA 4 | 0.97811 | 0.91207 | -0.066038 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | TIOGA 4 | 0.97811 | 0.91207 | -0.066038 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | TIOGA 4 | 0.97811 | 0.91207 | -0.066038 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | TIOGA 4 | 0.97811 | 0.91207 | -0.066038 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | TIOGA 4 | 0.97811 | 0.91207 | -0.066038 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | TIOGA 4 | 0.97811 | 0.91207 | -0.066038 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | TIOGA 4 | 0.97811 | 0.91207 | -0.066038 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | TIOGA 4 | 0.97811 | 0.91207 | -0.066038 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | TIOGA 4 | 0.97811 | 0.91207 | -0.066038 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | TIOGA 4 | 0.97811 | 0.91207 | -0.066038 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | TIOGA 4 | 0.97811 | 0.91207 | -0.066038 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | TIOGA 4 | 0.97811 | 0.91207 | -0.066038 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | TIOGA 4 | 0.97811 | 0.91207 | -0.066038 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | TIOGA 4 | 0.97811 | 0.91207 | -0.066038 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | TIOGA 4 | 0.97811 | 0.91207 | -0.066038 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | TIP292 5 | 0.97603 | 0.92434 | -0.051689 |  | 0.925 | 1.05 | 0.033596 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | TIP292 5 | 0.97603 | 0.92434 | -0.051689 |  | 0.925 | 1.05 | 0.040193 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | TIP292 5 | 0.97603 | 0.92434 | -0.051689 |  | 0.925 | 1.05 | 0.088122 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | TIP292 5 | 0.97603 | 0.92434 | -0.051689 |  | 0.925 | 1.05 | 0.074664 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | TIP292 5 | 0.97603 | 0.92434 | -0.051689 |  | 0.925 | 1.05 | 0.068051 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | TIP292 5 | 0.97603 | 0.92434 | -0.051689 |  | 0.925 | 1.05 | 0.035565 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | TIP292 5 | 0.97603 | 0.92434 | -0.051689 |  | 0.925 | 1.05 | 0.033904 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | TIP292 5 | 0.97603 | 0.92434 | -0.051689 |  | 0.925 | 1.05 | 0.16366 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | TIP292 5 | 0.97603 | 0.92434 | -0.051689 |  | 0.925 | 1.05 | 0.045569 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | TIP292 5 | 0.97603 | 0.92434 | -0.051689 |  | 0.925 | 1.05 | 0.13458 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | TIP292 5 | 0.97603 | 0.92434 | -0.051689 |  | 0.925 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | TIP292 5 | 0.97603 | 0.92434 | -0.051689 |  | 0.925 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | TIP292 5 | 0.97603 | 0.92434 | -0.051689 |  | 0.925 | 1.05 | 0.068426 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | TIP292 5 | 0.97603 | 0.92434 | -0.051689 |  | 0.925 | 1.05 | 0.035223 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | TIP292 5 | 0.97603 | 0.92434 | -0.051689 |  | 0.925 | 1.05 | 0.034504 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | TOMHAWK5 | 0.9826 | 0.91659 | -0.066007 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | TOMHAWK5 | 0.9826 | 0.91659 | -0.066007 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | TOMHAWK5 | 0.9826 | 0.91659 | -0.066007 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | TOMHAWK5 | 0.9826 | 0.91659 | -0.066007 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | TOMHAWK5 | 0.9826 | 0.91659 | -0.066007 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | TOMHAWK5 | 0.9826 | 0.91659 | -0.066007 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | TOMHAWK5 | 0.9826 | 0.91659 | -0.066007 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | TOMHAWK5 | 0.9826 | 0.91659 | -0.066007 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | TOMHAWK5 | 0.9826 | 0.91659 | -0.066007 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | TOMHAWK5 | 0.9826 | 0.91659 | -0.066007 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | TOMHAWK5 | 0.9826 | 0.91659 | -0.066007 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | TOMHAWK5 | 0.9826 | 0.91659 | -0.066007 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | TOMHAWK5 | 0.9826 | 0.91659 | -0.066007 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | TOMHAWK5 | 0.9826 | 0.91659 | -0.066007 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | TOMHAWK5 | 0.9826 | 0.91659 | -0.066007 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | TOMHAWK5 | 0.9826 | 0.91659 | -0.066007 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | TOMHAWK5 | 0.9826 | 0.91659 | -0.066007 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | TOMHAWK5 | 0.9826 | 0.91659 | -0.066007 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | TOMHAWK5 | 0.9826 | 0.91659 | -0.066007 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | TOMHAWK5 | 0.9826 | 0.91659 | -0.066007 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | TOMHAWK5 | 0.9826 | 0.91659 | -0.066007 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | TOMHAWK5 | 0.9826 | 0.91659 | -0.066007 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | TOMHAWK5 | 0.9826 | 0.91659 | -0.066007 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | TOMHAWK5 | 0.9826 | 0.91659 | -0.066007 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | TOMHAWK5 | 0.9826 | 0.91659 | -0.066007 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | TONTITN7 | 0.98623 | 0.91823 | -0.068003 |  | 0.92 | 1.05 | 0.035932 | P23:345:GRDA:TONNECE CB9580:::EHV: | Add 0.4 MVAR switched shunt at TONTITN7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | TONTITN7 | 0.98623 | 0.91823 | -0.068003 |  | 0.92 | 1.05 | 0.057432 | P23:345:GRDA:TONNECE CB9580:::EHV: | Add 0.4 MVAR switched shunt at TONTITN7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | TONTITN7 | 0.98623 | 0.91823 | -0.068003 |  | 0.92 | 1.05 | 0.068475 | P23:345:GRDA:TONNECE CB9580:::EHV: | Add 0.4 MVAR switched shunt at TONTITN7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | TONTITN7 | 0.98623 | 0.91823 | -0.068003 |  | 0.92 | 1.05 | 0.035744 | P23:345:GRDA:TONNECE CB9580:::EHV: | Add 0.4 MVAR switched shunt at TONTITN7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | TONTITN7 | 0.98623 | 0.91823 | -0.068003 |  | 0.92 | 1.05 | 0.1501 | P23:345:GRDA:TONNECE CB9580:::EHV: | Add 0.4 MVAR switched shunt at TONTITN7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | TONTITN7 | 0.98623 | 0.91823 | -0.068003 |  | 0.92 | 1.05 | 0.058419 | P23:345:GRDA:TONNECE CB9580:::EHV: | Add 0.4 MVAR switched shunt at TONTITN7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | TURNER_RD5 | 0.99516 | 0.91955 | -0.075609 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | TURNER_RD5 | 0.99516 | 0.91955 | -0.075609 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | TURNER_RD5 | 0.99516 | 0.91955 | -0.075609 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | TURNER_RD5 | 0.99516 | 0.91955 | -0.075609 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | TURNER_RD5 | 0.99516 | 0.91955 | -0.075609 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | TURNER_RD5 | 0.99516 | 0.91955 | -0.075609 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | TURNER_RD5 | 0.99516 | 0.91955 | -0.075609 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | TURNER_RD5 | 0.99516 | 0.91955 | -0.075609 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | TURNER_RD5 | 0.99516 | 0.91955 | -0.075609 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | TURNER_RD5 | 0.99516 | 0.91955 | -0.075609 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | TURNER_RD5 | 0.99516 | 0.91955 | -0.075609 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | TURNER_RD5 | 0.99516 | 0.91955 | -0.075609 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | TURNER_RD5 | 0.99516 | 0.91955 | -0.075609 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | TURNER_RD5 | 0.99516 | 0.91955 | -0.075609 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | TURNER_RD5 | 0.99516 | 0.91955 | -0.075609 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | TURNER_RD5 | 0.99516 | 0.91955 | -0.075609 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | TURNER_RD5 | 0.99516 | 0.91955 | -0.075609 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | TURNER_RD5 | 0.99516 | 0.91955 | -0.075609 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | TURNER_RD5 | 0.99516 | 0.91955 | -0.075609 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | TURNER_RD5 | 0.99516 | 0.91955 | -0.075609 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | TURNER_RD5 | 0.99516 | 0.91955 | -0.075609 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | TURNER_RD5 | 0.99516 | 0.91955 | -0.075609 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | TURNER_RD5 | 0.99516 | 0.91955 | -0.075609 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | TURNER_RD5 | 0.99516 | 0.91955 | -0.075609 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | TURNER_RD5 | 0.99516 | 0.91955 | -0.075609 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | TV1MNDV4 | 0.95763 | 0.91076 | -0.04687 |  | 0.93 | 1.05 | 0.091967 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | TV1MNDV4 | 0.95763 | 0.91076 | -0.04687 |  | 0.93 | 1.05 | 0.033356 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | TV1MNDV4 | 0.95763 | 0.91076 | -0.04687 |  | 0.93 | 1.05 | 0.044346 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | TV1MNDV4 | 0.95763 | 0.91076 | -0.04687 |  | 0.93 | 1.05 | 0.058536 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | TV1MNDV4 | 0.95763 | 0.91076 | -0.04687 |  | 0.93 | 1.05 | 0.059327 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | TV1MNDV4 | 0.95763 | 0.91076 | -0.04687 |  | 0.93 | 1.05 | 0.041874 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | TV1MNDV4 | 0.95763 | 0.91076 | -0.04687 |  | 0.93 | 1.05 | 0.046192 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | TV1MNDV4 | 0.95763 | 0.91076 | -0.04687 |  | 0.93 | 1.05 | 0.12754 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | TV1MNDV4 | 0.95763 | 0.91076 | -0.04687 |  | 0.93 | 1.05 | 0.047018 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | TV1MNDV4 | 0.95763 | 0.91076 | -0.04687 |  | 0.93 | 1.05 | 0.056662 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | TV1MNDV4 | 0.95763 | 0.91076 | -0.04687 |  | 0.93 | 1.05 | 0.056662 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | TV1MNDV4 | 0.95763 | 0.91076 | -0.04687 |  | 0.93 | 1.05 | 0.056727 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | TV1MNDV4 | 0.95763 | 0.91076 | -0.04687 |  | 0.93 | 1.05 | 0.074186 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | TV1MNDV4 | 0.95763 | 0.91076 | -0.04687 |  | 0.93 | 1.05 | 0.040839 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | TV1MNDV4 | 0.95763 | 0.91076 | -0.04687 |  | 0.93 | 1.05 | 0.03863 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | TV1MNDV4 | 0.95763 | 0.91076 | -0.04687 |  | 0.93 | 1.05 | 0.042285 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | TV1MNDV4 | 0.95763 | 0.91076 | -0.04687 |  | 0.93 | 1.05 | 0.042285 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | TV1MNDV4 | 0.95763 | 0.91076 | -0.04687 |  | 0.93 | 1.05 | 0.050204 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | TV1MNDV4 | 0.95763 | 0.91076 | -0.04687 |  | 0.93 | 1.05 | 0.058005 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | TV1MNDV4 | 0.95763 | 0.91076 | -0.04687 |  | 0.93 | 1.05 | 0.041735 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | TV1MNDV4 | 0.95763 | 0.91076 | -0.04687 |  | 0.93 | 1.05 | 0.057076 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | TV1MNDV4 | 0.95763 | 0.91076 | -0.04687 |  | 0.93 | 1.05 | 0.050111 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | TV1MNDV4 | 0.95763 | 0.91076 | -0.04687 |  | 0.93 | 1.05 | 0.06491 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | TV1MNDV4 | 0.95763 | 0.91076 | -0.04687 |  | 0.93 | 1.05 | 0.051051 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | TV1MNDV4 | 0.95763 | 0.91076 | -0.04687 |  | 0.93 | 1.05 | 0.036279 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 20 MVAR switched shunt at LIBERTY4 138 kV; Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | ASGI-2024-023 | TV1MNDV4 | 0.96448 | 0.91763 | -0.046846 |  | 0.93 | 1.05 | 0.079962 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | TV1MNDV4 | 0.96448 | 0.91763 | -0.046846 |  | 0.93 | 1.05 | 0.065323 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-068 | TV1MNDV4 | 0.96448 | 0.91763 | -0.046846 |  | 0.93 | 1.05 | 0.067422 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-071 | TV1MNDV4 | 0.96448 | 0.91763 | -0.046846 |  | 0.93 | 1.05 | 0.074668 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | TV1MNDV4 | 0.96448 | 0.91763 | -0.046846 |  | 0.93 | 1.05 | 0.053027 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-122 | TV1MNDV4 | 0.96448 | 0.91763 | -0.046846 |  | 0.93 | 1.05 | 0.082926 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-177 | TV1MNDV4 | 0.96448 | 0.91763 | -0.046846 |  | 0.93 | 1.05 | 0.084694 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-178 | TV1MNDV4 | 0.96448 | 0.91763 | -0.046846 |  | 0.93 | 1.05 | 0.078867 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | TV1MNDV4 | 0.96448 | 0.91763 | -0.046846 |  | 0.93 | 1.05 | 0.031571 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-220 | TV1MNDV4 | 0.96448 | 0.91763 | -0.046846 |  | 0.93 | 1.05 | 0.075331 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-232 | TV1MNDV4 | 0.96448 | 0.91763 | -0.046846 |  | 0.93 | 1.05 | 0.078906 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | TV1MNDV4 | 0.96448 | 0.91763 | -0.046846 |  | 0.93 | 1.05 | 0.065323 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | TV1MNDV4 | 0.96448 | 0.91763 | -0.046846 |  | 0.93 | 1.05 | 0.03431 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | TV1MNDV4 | 0.96448 | 0.91763 | -0.046846 |  | 0.93 | 1.05 | 0.031504 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | TV1MNDV4 | 0.96448 | 0.91763 | -0.046846 |  | 0.93 | 1.05 | 0.031504 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | TV1MNDV4 | 0.96448 | 0.91763 | -0.046846 |  | 0.93 | 1.05 | 0.030663 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | TV1MNDV4 | 0.96448 | 0.91763 | -0.046846 |  | 0.93 | 1.05 | 0.04269 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-376 | TV1MNDV4 | 0.96448 | 0.91763 | -0.046846 |  | 0.93 | 1.05 | 0.082476 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | TV1MNDV4 | 0.96966 | 0.94333 | -0.026338 |  | 0.95 | 1.05 | 0.149 | System Intact | Add 150 MVAR switched shunt at NEOSHO 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | TV1MNDV4 | 0.96492 | 0.91518 | -0.049741 |  | 0.93 | 1.05 | 0.035768 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | TV1MNDV4 | 0.96492 | 0.91518 | -0.049741 |  | 0.93 | 1.05 | 0.088718 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | TV1MNDV4 | 0.96492 | 0.91518 | -0.049741 |  | 0.93 | 1.05 | 0.031473 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | TV1MNDV4 | 0.96492 | 0.91518 | -0.049741 |  | 0.93 | 1.05 | 0.034941 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | TV1MNDV4 | 0.96492 | 0.91518 | -0.049741 |  | 0.93 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | TV1MNDV4 | 0.96492 | 0.91518 | -0.049741 |  | 0.93 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | TV1MNDV4 | 0.96492 | 0.91518 | -0.049741 |  | 0.93 | 1.05 | 0.049224 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | TV1MNDV4 | 0.96492 | 0.91518 | -0.049741 |  | 0.93 | 1.05 | 0.038981 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | TV1MNDV4 | 0.96492 | 0.91518 | -0.049741 |  | 0.93 | 1.05 | 0.040399 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | TV1MNDV4 | 0.96492 | 0.91518 | -0.049741 |  | 0.93 | 1.05 | 0.031912 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | TV1MNDV4 | 0.96492 | 0.91518 | -0.049741 |  | 0.93 | 1.05 | 0.034127 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | TV1MNDV4 | 0.96492 | 0.91518 | -0.049741 |  | 0.93 | 1.05 | 0.047318 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | TV1MNDV4 | 0.96059 | 0.91091 | -0.049675 |  | 0.93 | 1.05 | 0.040439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | TV1MNDV4 | 0.96059 | 0.91091 | -0.049675 |  | 0.93 | 1.05 | 0.034853 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | TV1MNDV4 | 0.96059 | 0.91091 | -0.049675 |  | 0.93 | 1.05 | 0.046783 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | TV1MNDV4 | 0.96059 | 0.91091 | -0.049675 |  | 0.93 | 1.05 | 0.047615 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | TV1MNDV4 | 0.96059 | 0.91091 | -0.049675 |  | 0.93 | 1.05 | 0.034938 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | TV1MNDV4 | 0.96059 | 0.91091 | -0.049675 |  | 0.93 | 1.05 | 0.037875 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | TV1MNDV4 | 0.96059 | 0.91091 | -0.049675 |  | 0.93 | 1.05 | 0.044022 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | TV1MNDV4 | 0.96059 | 0.91091 | -0.049675 |  | 0.93 | 1.05 | 0.030552 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | TV1MNDV4 | 0.96059 | 0.91091 | -0.049675 |  | 0.93 | 1.05 | 0.038531 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | TV1MNDV4 | 0.96059 | 0.91091 | -0.049675 |  | 0.93 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | TV1MNDV4 | 0.96059 | 0.91091 | -0.049675 |  | 0.93 | 1.05 | 0.062491 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | TV1MNDV4 | 0.96059 | 0.91091 | -0.049675 |  | 0.93 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | TV1MNDV4 | 0.96059 | 0.91091 | -0.049675 |  | 0.93 | 1.05 | 0.038129 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | TV1MNDV4 | 0.96059 | 0.91091 | -0.049675 |  | 0.93 | 1.05 | 0.038066 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | TV1MNDV4 | 0.96059 | 0.91091 | -0.049675 |  | 0.93 | 1.05 | 0.034955 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | TV1MNDV4 | 0.96059 | 0.91091 | -0.049675 |  | 0.93 | 1.05 | 0.06281 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | TV1MNDV4 | 0.96059 | 0.91091 | -0.049675 |  | 0.93 | 1.05 | 0.045309 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | TV1MNDV4 | 0.96059 | 0.91091 | -0.049675 |  | 0.93 | 1.05 | 0.035805 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | TV1MNDV4 | 0.96059 | 0.91091 | -0.049675 |  | 0.93 | 1.05 | 0.032364 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | TV1MNDV4 | 0.96059 | 0.91091 | -0.049675 |  | 0.93 | 1.05 | 0.031815 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | TV1MNDV4 | 0.96059 | 0.91091 | -0.049675 |  | 0.93 | 1.05 | 0.033886 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | TV1MNDV4 | 0.96059 | 0.91091 | -0.049675 |  | 0.93 | 1.05 | 0.035554 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | TV1MNDV4 | 0.96378 | 0.90237 | -0.061413 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | TV1MNDV4 | 0.96378 | 0.90237 | -0.061413 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | TV1MNDV4 | 0.96378 | 0.90237 | -0.061413 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | TV1MNDV4 | 0.96378 | 0.90237 | -0.061413 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | TV1MNDV4 | 0.96378 | 0.90237 | -0.061413 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | TV1MNDV4 | 0.96378 | 0.90237 | -0.061413 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | TV1MNDV4 | 0.96378 | 0.90237 | -0.061413 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | TV1MNDV4 | 0.96378 | 0.90237 | -0.061413 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | TV1MNDV4 | 0.96378 | 0.90237 | -0.061413 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | TV1MNDV4 | 0.96378 | 0.90237 | -0.061413 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | TV1MNDV4 | 0.96378 | 0.90237 | -0.061413 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | TV1MNDV4 | 0.96378 | 0.90237 | -0.061413 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | TV1MNDV4 | 0.96378 | 0.90237 | -0.061413 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | TV1MNDV4 | 0.96378 | 0.90237 | -0.061413 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | TV1MNDV4 | 0.96378 | 0.90237 | -0.061413 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | TV1MNDV4 | 0.96378 | 0.90237 | -0.061413 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | TV1MNDV4 | 0.96378 | 0.90237 | -0.061413 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | TV1MNDV4 | 0.96378 | 0.90237 | -0.061413 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | TV1MNDV4 | 0.96378 | 0.90237 | -0.061413 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | TV1MNDV4 | 0.96378 | 0.90237 | -0.061413 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | TV1MNDV4 | 0.96378 | 0.90237 | -0.061413 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | TV1MNDV4 | 0.96378 | 0.90237 | -0.061413 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | TV1MNDV4 | 0.96378 | 0.90237 | -0.061413 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | TV1MNDV4 | 0.96378 | 0.90237 | -0.061413 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | TV1MNDV4 | 0.96378 | 0.90237 | -0.061413 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | W.GRDNR7 | 0.9654 | 0.9201 | -0.045301 |  | 0.95 | 1.05 | 0.036307 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | W.GRDNR7 | 0.9654 | 0.9201 | -0.045301 |  | 0.95 | 1.05 | 0.052743 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | W.GRDNR7 | 0.9654 | 0.9201 | -0.045301 |  | 0.95 | 1.05 | 0.039345 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | W.GRDNR7 | 0.9654 | 0.9201 | -0.045301 |  | 0.95 | 1.05 | 0.031366 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | W.GRDNR7 | 0.9654 | 0.9201 | -0.045301 |  | 0.95 | 1.05 | 0.041888 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | W.GRDNR7 | 0.9654 | 0.9201 | -0.045301 |  | 0.95 | 1.05 | 0.038797 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | W.GRDNR7 | 0.9654 | 0.9201 | -0.045301 |  | 0.95 | 1.05 | 0.030557 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | W.GRDNR7 | 0.9654 | 0.9201 | -0.045301 |  | 0.95 | 1.05 | 0.067346 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | W.GRDNR7 | 0.9654 | 0.9201 | -0.045301 |  | 0.95 | 1.05 | 0.030557 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | W.GRDNR7 | 0.9654 | 0.9201 | -0.045301 |  | 0.95 | 1.05 | 0.030851 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | W.GRDNR7 | 0.9654 | 0.9201 | -0.045301 |  | 0.95 | 1.05 | 0.032161 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | W.GRDNR7 | 0.9654 | 0.9201 | -0.045301 |  | 0.95 | 1.05 | 0.04067 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | W.GRDNR7 | 0.9654 | 0.9201 | -0.045301 |  | 0.95 | 1.05 | 0.040569 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | W.GRDNR7 | 0.9654 | 0.9201 | -0.045301 |  | 0.95 | 1.05 | 0.03086 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | W.GRDNR7 | 0.9654 | 0.9201 | -0.045301 |  | 0.95 | 1.05 | 0.033223 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | W.GRDNR7 | 0.9654 | 0.9201 | -0.045301 |  | 0.95 | 1.05 | 0.033733 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 316 MVAR switched shunt at W.GRDNR7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | W.GRDNR7 | 0.95804 | 0.90477 | -0.053273 |  | 0.95 | 1.05 | 0.036307 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | W.GRDNR7 | 0.95804 | 0.90477 | -0.053273 |  | 0.95 | 1.05 | 0.052743 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | W.GRDNR7 | 0.95804 | 0.90477 | -0.053273 |  | 0.95 | 1.05 | 0.039345 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | W.GRDNR7 | 0.95804 | 0.90477 | -0.053273 |  | 0.95 | 1.05 | 0.031366 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | W.GRDNR7 | 0.95804 | 0.90477 | -0.053273 |  | 0.95 | 1.05 | 0.041888 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | W.GRDNR7 | 0.95804 | 0.90477 | -0.053273 |  | 0.95 | 1.05 | 0.038797 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | W.GRDNR7 | 0.95804 | 0.90477 | -0.053273 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | W.GRDNR7 | 0.95804 | 0.90477 | -0.053273 |  | 0.95 | 1.05 | 0.067346 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | W.GRDNR7 | 0.95804 | 0.90477 | -0.053273 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | W.GRDNR7 | 0.95804 | 0.90477 | -0.053273 |  | 0.95 | 1.05 | 0.030851 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | W.GRDNR7 | 0.95804 | 0.90477 | -0.053273 |  | 0.95 | 1.05 | 0.032161 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | W.GRDNR7 | 0.95804 | 0.90477 | -0.053273 |  | 0.95 | 1.05 | 0.04067 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | W.GRDNR7 | 0.95804 | 0.90477 | -0.053273 |  | 0.95 | 1.05 | 0.040569 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | W.GRDNR7 | 0.95804 | 0.90477 | -0.053273 |  | 0.95 | 1.05 | 0.03086 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | W.GRDNR7 | 0.95804 | 0.90477 | -0.053273 |  | 0.95 | 1.05 | 0.033223 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | W.GRDNR7 | 0.95804 | 0.90477 | -0.053273 |  | 0.95 | 1.05 | 0.033733 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | W.GRDNR7 | 0.97166 | 0.90762 | -0.064042 |  | 0.95 | 1.05 | 0.036307 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | W.GRDNR7 | 0.97166 | 0.90762 | -0.064042 |  | 0.95 | 1.05 | 0.052743 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | W.GRDNR7 | 0.97166 | 0.90762 | -0.064042 |  | 0.95 | 1.05 | 0.039345 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | W.GRDNR7 | 0.97166 | 0.90762 | -0.064042 |  | 0.95 | 1.05 | 0.031366 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | W.GRDNR7 | 0.97166 | 0.90762 | -0.064042 |  | 0.95 | 1.05 | 0.041888 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | W.GRDNR7 | 0.97166 | 0.90762 | -0.064042 |  | 0.95 | 1.05 | 0.038797 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | W.GRDNR7 | 0.97166 | 0.90762 | -0.064042 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | W.GRDNR7 | 0.97166 | 0.90762 | -0.064042 |  | 0.95 | 1.05 | 0.067346 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | W.GRDNR7 | 0.97166 | 0.90762 | -0.064042 |  | 0.95 | 1.05 | 0.030557 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | W.GRDNR7 | 0.97166 | 0.90762 | -0.064042 |  | 0.95 | 1.05 | 0.030851 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | W.GRDNR7 | 0.97166 | 0.90762 | -0.064042 |  | 0.95 | 1.05 | 0.032161 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | W.GRDNR7 | 0.97166 | 0.90762 | -0.064042 |  | 0.95 | 1.05 | 0.04067 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | W.GRDNR7 | 0.97166 | 0.90762 | -0.064042 |  | 0.95 | 1.05 | 0.040569 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | W.GRDNR7 | 0.97166 | 0.90762 | -0.064042 |  | 0.95 | 1.05 | 0.03086 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | W.GRDNR7 | 0.97166 | 0.90762 | -0.064042 |  | 0.95 | 1.05 | 0.033223 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | W.GRDNR7 | 0.97166 | 0.90762 | -0.064042 |  | 0.95 | 1.05 | 0.033733 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | W.GRDNR7 | 0.97927 | 0.89179 | -0.087477 |  | 0.95 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | W.GRDNR7 | 0.97927 | 0.89179 | -0.087477 |  | 0.95 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | W.GRDNR7 | 0.97927 | 0.89179 | -0.087477 |  | 0.95 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | W.GRDNR7 | 0.97927 | 0.89179 | -0.087477 |  | 0.95 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | W.GRDNR7 | 0.97927 | 0.89179 | -0.087477 |  | 0.95 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | W.GRDNR7 | 0.97927 | 0.89179 | -0.087477 |  | 0.95 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | W.GRDNR7 | 0.97927 | 0.89179 | -0.087477 |  | 0.95 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | W.GRDNR7 | 0.97927 | 0.89179 | -0.087477 |  | 0.95 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | W.GRDNR7 | 0.97927 | 0.89179 | -0.087477 |  | 0.95 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | W.GRDNR7 | 0.97927 | 0.89179 | -0.087477 |  | 0.95 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | W.GRDNR7 | 0.97927 | 0.89179 | -0.087477 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | W.GRDNR7 | 0.97927 | 0.89179 | -0.087477 |  | 0.95 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | W.GRDNR7 | 0.97927 | 0.89179 | -0.087477 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | W.GRDNR7 | 0.97927 | 0.89179 | -0.087477 |  | 0.95 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | W.GRDNR7 | 0.97927 | 0.89179 | -0.087477 |  | 0.95 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | W.GRDNR7 | 0.97927 | 0.89179 | -0.087477 |  | 0.95 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | W.GRDNR7 | 0.97927 | 0.89179 | -0.087477 |  | 0.95 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | W.GRDNR7 | 0.97927 | 0.89179 | -0.087477 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | W.GRDNR7 | 0.97927 | 0.89179 | -0.087477 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | W.GRDNR7 | 0.97927 | 0.89179 | -0.087477 |  | 0.95 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | W.GRDNR7 | 0.97927 | 0.89179 | -0.087477 |  | 0.95 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | W.GRDNR7 | 0.97927 | 0.89179 | -0.087477 |  | 0.95 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | W.GRDNR7 | 0.97927 | 0.89179 | -0.087477 |  | 0.95 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | W.GRDNR7 | 0.97927 | 0.89179 | -0.087477 |  | 0.95 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | W.GRDNR7 | 0.97927 | 0.89179 | -0.087477 |  | 0.95 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | W.GRDNR7 | 0.96445 | 0.91831 | -0.046147 |  | 0.95 | 1.05 | 0.036307 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | W.GRDNR7 | 0.96445 | 0.91831 | -0.046147 |  | 0.95 | 1.05 | 0.052743 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | W.GRDNR7 | 0.96445 | 0.91831 | -0.046147 |  | 0.95 | 1.05 | 0.039345 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | W.GRDNR7 | 0.96445 | 0.91831 | -0.046147 |  | 0.95 | 1.05 | 0.031366 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | W.GRDNR7 | 0.96445 | 0.91831 | -0.046147 |  | 0.95 | 1.05 | 0.041888 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | W.GRDNR7 | 0.96445 | 0.91831 | -0.046147 |  | 0.95 | 1.05 | 0.038797 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | W.GRDNR7 | 0.96445 | 0.91831 | -0.046147 |  | 0.95 | 1.05 | 0.030557 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | W.GRDNR7 | 0.96445 | 0.91831 | -0.046147 |  | 0.95 | 1.05 | 0.067346 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | W.GRDNR7 | 0.96445 | 0.91831 | -0.046147 |  | 0.95 | 1.05 | 0.030557 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | W.GRDNR7 | 0.96445 | 0.91831 | -0.046147 |  | 0.95 | 1.05 | 0.030851 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | W.GRDNR7 | 0.96445 | 0.91831 | -0.046147 |  | 0.95 | 1.05 | 0.032161 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | W.GRDNR7 | 0.96445 | 0.91831 | -0.046147 |  | 0.95 | 1.05 | 0.04067 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | W.GRDNR7 | 0.96445 | 0.91831 | -0.046147 |  | 0.95 | 1.05 | 0.040569 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | W.GRDNR7 | 0.96445 | 0.91831 | -0.046147 |  | 0.95 | 1.05 | 0.03086 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | W.GRDNR7 | 0.96445 | 0.91831 | -0.046147 |  | 0.95 | 1.05 | 0.033223 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | W.GRDNR7 | 0.96445 | 0.91831 | -0.046147 |  | 0.95 | 1.05 | 0.033733 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | WAGSTAF5 | 0.98236 | 0.92936 | -0.052999 |  | 0.93 | 1.05 | 0.036307 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | WAGSTAF5 | 0.98236 | 0.92936 | -0.052999 |  | 0.93 | 1.05 | 0.052743 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | WAGSTAF5 | 0.98236 | 0.92936 | -0.052999 |  | 0.93 | 1.05 | 0.039345 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | WAGSTAF5 | 0.98236 | 0.92936 | -0.052999 |  | 0.93 | 1.05 | 0.031366 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | WAGSTAF5 | 0.98236 | 0.92936 | -0.052999 |  | 0.93 | 1.05 | 0.041888 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | WAGSTAF5 | 0.98236 | 0.92936 | -0.052999 |  | 0.93 | 1.05 | 0.038797 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | WAGSTAF5 | 0.98236 | 0.92936 | -0.052999 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | WAGSTAF5 | 0.98236 | 0.92936 | -0.052999 |  | 0.93 | 1.05 | 0.067346 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | WAGSTAF5 | 0.98236 | 0.92936 | -0.052999 |  | 0.93 | 1.05 | 0.030557 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | WAGSTAF5 | 0.98236 | 0.92936 | -0.052999 |  | 0.93 | 1.05 | 0.030851 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | WAGSTAF5 | 0.98236 | 0.92936 | -0.052999 |  | 0.93 | 1.05 | 0.032161 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | WAGSTAF5 | 0.98236 | 0.92936 | -0.052999 |  | 0.93 | 1.05 | 0.04067 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | WAGSTAF5 | 0.98236 | 0.92936 | -0.052999 |  | 0.93 | 1.05 | 0.040569 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | WAGSTAF5 | 0.98236 | 0.92936 | -0.052999 |  | 0.93 | 1.05 | 0.03086 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | WAGSTAF5 | 0.98236 | 0.92936 | -0.052999 |  | 0.93 | 1.05 | 0.033223 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | WAGSTAF5 | 0.98236 | 0.92936 | -0.052999 |  | 0.93 | 1.05 | 0.033733 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | WAGSTAF5 | 0.99618 | 0.90674 | -0.089436 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | WAGSTAF5 | 0.99618 | 0.90674 | -0.089436 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | WAGSTAF5 | 0.99618 | 0.90674 | -0.089436 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | WAGSTAF5 | 0.99618 | 0.90674 | -0.089436 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | WAGSTAF5 | 0.99618 | 0.90674 | -0.089436 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | WAGSTAF5 | 0.99618 | 0.90674 | -0.089436 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | WAGSTAF5 | 0.99618 | 0.90674 | -0.089436 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | WAGSTAF5 | 0.99618 | 0.90674 | -0.089436 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | WAGSTAF5 | 0.99618 | 0.90674 | -0.089436 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | WAGSTAF5 | 0.99618 | 0.90674 | -0.089436 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | WAGSTAF5 | 0.99618 | 0.90674 | -0.089436 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | WAGSTAF5 | 0.99618 | 0.90674 | -0.089436 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | WAGSTAF5 | 0.99618 | 0.90674 | -0.089436 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | WAGSTAF5 | 0.99618 | 0.90674 | -0.089436 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | WAGSTAF5 | 0.99618 | 0.90674 | -0.089436 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | WAGSTAF5 | 0.99618 | 0.90674 | -0.089436 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | WAGSTAF5 | 0.99618 | 0.90674 | -0.089436 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | WAGSTAF5 | 0.99618 | 0.90674 | -0.089436 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | WAGSTAF5 | 0.99618 | 0.90674 | -0.089436 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | WAGSTAF5 | 0.99618 | 0.90674 | -0.089436 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | WAGSTAF5 | 0.99618 | 0.90674 | -0.089436 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | WAGSTAF5 | 0.99618 | 0.90674 | -0.089436 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | WAGSTAF5 | 0.99618 | 0.90674 | -0.089436 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | WAGSTAF5 | 0.99618 | 0.90674 | -0.089436 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | WAGSTAF5 | 0.99618 | 0.90674 | -0.089436 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | WAVERLY3 | 0.9877 | 0.92593 | -0.061776 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | WAVERLY3 | 0.9877 | 0.92593 | -0.061776 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | WAVERLY3 | 0.9877 | 0.92593 | -0.061776 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | WAVERLY3 | 0.9877 | 0.92593 | -0.061776 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | WAVERLY3 | 0.9877 | 0.92593 | -0.061776 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | WAVERLY3 | 0.9877 | 0.92593 | -0.061776 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | WAVERLY3 | 0.9877 | 0.92593 | -0.061776 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | WAVERLY3 | 0.9877 | 0.92593 | -0.061776 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | WAVERLY3 | 0.9877 | 0.92593 | -0.061776 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | WAVERLY3 | 0.9877 | 0.92593 | -0.061776 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | WAVERLY3 | 0.9877 | 0.92593 | -0.061776 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | WAVERLY3 | 0.9877 | 0.92593 | -0.061776 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | WAVERLY3 | 0.9877 | 0.92593 | -0.061776 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | WAVERLY3 | 0.9877 | 0.92593 | -0.061776 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | WAVERLY3 | 0.9877 | 0.92593 | -0.061776 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | WAVERLY3 | 0.9877 | 0.92593 | -0.061776 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | WAVERLY3 | 0.9877 | 0.92593 | -0.061776 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | WAVERLY3 | 0.9877 | 0.92593 | -0.061776 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | WAVERLY3 | 0.9877 | 0.92593 | -0.061776 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | WAVERLY3 | 0.9877 | 0.92593 | -0.061776 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | WAVERLY3 | 0.9877 | 0.92593 | -0.061776 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | WAVERLY3 | 0.9877 | 0.92593 | -0.061776 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | WAVERLY3 | 0.9877 | 0.92593 | -0.061776 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | WAVERLY3 | 0.9877 | 0.92593 | -0.061776 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | WAVERLY3 | 0.9877 | 0.92593 | -0.061776 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | WHARV4 | 0.97149 | 0.92639 | -0.045091 |  | 0.93 | 1.05 | 0.03053 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | WHARV4 | 0.97149 | 0.92639 | -0.045091 |  | 0.93 | 1.05 | 0.044933 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | WHARV4 | 0.97149 | 0.92639 | -0.045091 |  | 0.93 | 1.05 | 0.047811 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | WHARV4 | 0.97149 | 0.92639 | -0.045091 |  | 0.93 | 1.05 | 0.09719 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | WHARV4 | 0.97149 | 0.92639 | -0.045091 |  | 0.93 | 1.05 | 0.069376 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | WHARV4 | 0.97149 | 0.92639 | -0.045091 |  | 0.93 | 1.05 | 0.04277 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | WHARV4 | 0.97149 | 0.92639 | -0.045091 |  | 0.93 | 1.05 | 0.071112 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | WHARV4 | 0.97149 | 0.92639 | -0.045091 |  | 0.93 | 1.05 | 0.039357 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | WHARV4 | 0.97149 | 0.92639 | -0.045091 |  | 0.93 | 1.05 | 0.04035 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | WHARV4 | 0.97149 | 0.92639 | -0.045091 |  | 0.93 | 1.05 | 0.052332 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | WHARV4 | 0.97149 | 0.92639 | -0.045091 |  | 0.93 | 1.05 | 0.045944 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | WHARV4 | 0.97149 | 0.92639 | -0.045091 |  | 0.93 | 1.05 | 0.038178 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | WHARV4 | 0.97149 | 0.92639 | -0.045091 |  | 0.93 | 1.05 | 0.13469 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | WHARV4 | 0.97149 | 0.92639 | -0.045091 |  | 0.93 | 1.05 | 0.03053 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | WHARV4 | 0.97149 | 0.92639 | -0.045091 |  | 0.93 | 1.05 | 0.038178 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | WHARV4 | 0.97149 | 0.92639 | -0.045091 |  | 0.93 | 1.05 | 0.037309 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | WHARV4 | 0.97149 | 0.92639 | -0.045091 |  | 0.93 | 1.05 | 0.040075 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | WHARV4 | 0.97149 | 0.92639 | -0.045091 |  | 0.93 | 1.05 | 0.053764 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | WHARV4 | 0.97149 | 0.92639 | -0.045091 |  | 0.93 | 1.05 | 0.071762 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | WHARV4 | 0.97149 | 0.92639 | -0.045091 |  | 0.93 | 1.05 | 0.047827 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | WHARV4 | 0.97149 | 0.92639 | -0.045091 |  | 0.93 | 1.05 | 0.047827 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | WHARV4 | 0.97149 | 0.92639 | -0.045091 |  | 0.93 | 1.05 | 0.070303 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | WHARV4 | 0.97149 | 0.92639 | -0.045091 |  | 0.93 | 1.05 | 0.040614 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | WHARV4 | 0.97149 | 0.92639 | -0.045091 |  | 0.93 | 1.05 | 0.039729 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | WHARV4 | 0.97149 | 0.92639 | -0.045091 |  | 0.93 | 1.05 | 0.049662 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | WHARV4 | 0.97149 | 0.92639 | -0.045091 |  | 0.93 | 1.05 | 0.042332 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | WHARV4 | 0.97149 | 0.92639 | -0.045091 |  | 0.93 | 1.05 | 0.048722 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | WHARV4 | 0.97149 | 0.92639 | -0.045091 |  | 0.93 | 1.05 | 0.038156 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | WHARV4 | 0.97149 | 0.92639 | -0.045091 |  | 0.93 | 1.05 | 0.036794 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | WHARV4 | 0.94697 | 0.89525 | -0.051722 |  | 0.93 | 1.05 | 0.044747 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | WHARV4 | 0.94697 | 0.89525 | -0.051722 |  | 0.93 | 1.05 | 0.063323 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | WHARV4 | 0.94697 | 0.89525 | -0.051722 |  | 0.93 | 1.05 | 0.043143 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | WHARV4 | 0.94697 | 0.89525 | -0.051722 |  | 0.93 | 1.05 | 0.038771 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | WHARV4 | 0.94697 | 0.89525 | -0.051722 |  | 0.93 | 1.05 | 0.038438 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | WHARV4 | 0.94697 | 0.89525 | -0.051722 |  | 0.93 | 1.05 | 0.04552 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | WHARV4 | 0.94697 | 0.89525 | -0.051722 |  | 0.93 | 1.05 | 0.03158 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | WHARV4 | 0.94697 | 0.89525 | -0.051722 |  | 0.93 | 1.05 | 0.034131 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | WHARV4 | 0.94697 | 0.89525 | -0.051722 |  | 0.93 | 1.05 | 0.042547 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | WHARV4 | 0.94697 | 0.89525 | -0.051722 |  | 0.93 | 1.05 | 0.032964 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | WHARV4 | 0.94697 | 0.89525 | -0.051722 |  | 0.93 | 1.05 | 0.041072 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | WHARV4 | 0.94697 | 0.89525 | -0.051722 |  | 0.93 | 1.05 | 0.069811 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | WHARV4 | 0.94697 | 0.89525 | -0.051722 |  | 0.93 | 1.05 | 0.041072 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | WHARV4 | 0.94697 | 0.89525 | -0.051722 |  | 0.93 | 1.05 | 0.042352 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | WHARV4 | 0.94697 | 0.89525 | -0.051722 |  | 0.93 | 1.05 | 0.041773 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | WHARV4 | 0.94697 | 0.89525 | -0.051722 |  | 0.93 | 1.05 | 0.048747 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | WHARV4 | 0.94697 | 0.89525 | -0.051722 |  | 0.93 | 1.05 | 0.044283 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | WHARV4 | 0.94697 | 0.89525 | -0.051722 |  | 0.93 | 1.05 | 0.039667 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | WHARV4 | 0.94697 | 0.89525 | -0.051722 |  | 0.93 | 1.05 | 0.031705 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | WHARV4 | 0.94697 | 0.89525 | -0.051722 |  | 0.93 | 1.05 | 0.036041 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | WHARV4 | 0.94697 | 0.89525 | -0.051722 |  | 0.93 | 1.05 | 0.035457 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | WHARV4 | 0.94697 | 0.89525 | -0.051722 |  | 0.93 | 1.05 | 0.0376 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | WHARV4 | 0.94697 | 0.89525 | -0.051722 |  | 0.93 | 1.05 | 0.039043 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | WHARV4 | 0.94732 | 0.89629 | -0.051029 |  | 0.93 | 1.05 | 0.044747 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | WHARV4 | 0.94732 | 0.89629 | -0.051029 |  | 0.93 | 1.05 | 0.038771 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | WHARV4 | 0.94732 | 0.89629 | -0.051029 |  | 0.93 | 1.05 | 0.038438 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | WHARV4 | 0.94732 | 0.89629 | -0.051029 |  | 0.93 | 1.05 | 0.030968 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | WHARV4 | 0.94732 | 0.89629 | -0.051029 |  | 0.93 | 1.05 | 0.03158 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | WHARV4 | 0.94732 | 0.89629 | -0.051029 |  | 0.93 | 1.05 | 0.034131 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | WHARV4 | 0.94732 | 0.89629 | -0.051029 |  | 0.93 | 1.05 | 0.040933 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | WHARV4 | 0.94732 | 0.89629 | -0.051029 |  | 0.93 | 1.05 | 0.032964 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | WHARV4 | 0.94732 | 0.89629 | -0.051029 |  | 0.93 | 1.05 | 0.041072 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | WHARV4 | 0.94732 | 0.89629 | -0.051029 |  | 0.93 | 1.05 | 0.041072 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | WHARV4 | 0.94732 | 0.89629 | -0.051029 |  | 0.93 | 1.05 | 0.042352 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | WHARV4 | 0.94732 | 0.89629 | -0.051029 |  | 0.93 | 1.05 | 0.041773 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | WHARV4 | 0.94732 | 0.89629 | -0.051029 |  | 0.93 | 1.05 | 0.039667 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | WHARV4 | 0.94732 | 0.89629 | -0.051029 |  | 0.93 | 1.05 | 0.031705 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | WHARV4 | 0.94732 | 0.89629 | -0.051029 |  | 0.93 | 1.05 | 0.036041 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | WHARV4 | 0.94732 | 0.89629 | -0.051029 |  | 0.93 | 1.05 | 0.035457 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | WHARV4 | 0.94732 | 0.89629 | -0.051029 |  | 0.93 | 1.05 | 0.0376 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | WHARV4 | 0.94732 | 0.89629 | -0.051029 |  | 0.93 | 1.05 | 0.039043 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | WHARV4 | 0.97218 | 0.91542 | -0.056753 |  | 0.93 | 1.05 | 0.040439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | WHARV4 | 0.97218 | 0.91542 | -0.056753 |  | 0.93 | 1.05 | 0.034853 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | WHARV4 | 0.97218 | 0.91542 | -0.056753 |  | 0.93 | 1.05 | 0.046783 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | WHARV4 | 0.97218 | 0.91542 | -0.056753 |  | 0.93 | 1.05 | 0.047615 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | WHARV4 | 0.97218 | 0.91542 | -0.056753 |  | 0.93 | 1.05 | 0.034938 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | WHARV4 | 0.97218 | 0.91542 | -0.056753 |  | 0.93 | 1.05 | 0.037875 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | WHARV4 | 0.97218 | 0.91542 | -0.056753 |  | 0.93 | 1.05 | 0.044022 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | WHARV4 | 0.97218 | 0.91542 | -0.056753 |  | 0.93 | 1.05 | 0.030552 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | WHARV4 | 0.97218 | 0.91542 | -0.056753 |  | 0.93 | 1.05 | 0.038531 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | WHARV4 | 0.97218 | 0.91542 | -0.056753 |  | 0.93 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | WHARV4 | 0.97218 | 0.91542 | -0.056753 |  | 0.93 | 1.05 | 0.062491 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | WHARV4 | 0.97218 | 0.91542 | -0.056753 |  | 0.93 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | WHARV4 | 0.97218 | 0.91542 | -0.056753 |  | 0.93 | 1.05 | 0.038129 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | WHARV4 | 0.97218 | 0.91542 | -0.056753 |  | 0.93 | 1.05 | 0.038066 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | WHARV4 | 0.97218 | 0.91542 | -0.056753 |  | 0.93 | 1.05 | 0.034955 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | WHARV4 | 0.97218 | 0.91542 | -0.056753 |  | 0.93 | 1.05 | 0.06281 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | WHARV4 | 0.97218 | 0.91542 | -0.056753 |  | 0.93 | 1.05 | 0.045309 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | WHARV4 | 0.97218 | 0.91542 | -0.056753 |  | 0.93 | 1.05 | 0.035805 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | WHARV4 | 0.97218 | 0.91542 | -0.056753 |  | 0.93 | 1.05 | 0.032364 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | WHARV4 | 0.97218 | 0.91542 | -0.056753 |  | 0.93 | 1.05 | 0.031815 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | WHARV4 | 0.97218 | 0.91542 | -0.056753 |  | 0.93 | 1.05 | 0.033886 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | WHARV4 | 0.97218 | 0.91542 | -0.056753 |  | 0.93 | 1.05 | 0.035554 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | WHARV4 | 0.9599 | 0.87787 | -0.082033 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | WHARV4 | 0.9599 | 0.87787 | -0.082033 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | WHARV4 | 0.9599 | 0.87787 | -0.082033 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | WHARV4 | 0.9599 | 0.87787 | -0.082033 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | WHARV4 | 0.9599 | 0.87787 | -0.082033 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | WHARV4 | 0.9599 | 0.87787 | -0.082033 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | WHARV4 | 0.9599 | 0.87787 | -0.082033 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | WHARV4 | 0.9599 | 0.87787 | -0.082033 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | WHARV4 | 0.9599 | 0.87787 | -0.082033 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | WHARV4 | 0.9599 | 0.87787 | -0.082033 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | WHARV4 | 0.9599 | 0.87787 | -0.082033 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | WHARV4 | 0.9599 | 0.87787 | -0.082033 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | WHARV4 | 0.9599 | 0.87787 | -0.082033 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | WHARV4 | 0.9599 | 0.87787 | -0.082033 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | WHARV4 | 0.9599 | 0.87787 | -0.082033 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | WHARV4 | 0.9599 | 0.87787 | -0.082033 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | WHARV4 | 0.9599 | 0.87787 | -0.082033 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | WHARV4 | 0.9599 | 0.87787 | -0.082033 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | WHARV4 | 0.9599 | 0.87787 | -0.082033 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | WHARV4 | 0.9599 | 0.87787 | -0.082033 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | WHARV4 | 0.9599 | 0.87787 | -0.082033 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | WHARV4 | 0.9599 | 0.87787 | -0.082033 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | WHARV4 | 0.9599 | 0.87787 | -0.082033 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | WHARV4 | 0.9599 | 0.87787 | -0.082033 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | WHARV4 | 0.9599 | 0.87787 | -0.082033 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-025 | WICHITA7 | 0.98814 | 0.92749 | -0.060645 |  | 0.95 | 1.05 | 0.03053 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | WICHITA7 | 0.98814 | 0.92749 | -0.060645 |  | 0.95 | 1.05 | 0.044933 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | WICHITA7 | 0.98814 | 0.92749 | -0.060645 |  | 0.95 | 1.05 | 0.047811 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | WICHITA7 | 0.98814 | 0.92749 | -0.060645 |  | 0.95 | 1.05 | 0.09719 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | WICHITA7 | 0.98814 | 0.92749 | -0.060645 |  | 0.95 | 1.05 | 0.069376 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | WICHITA7 | 0.98814 | 0.92749 | -0.060645 |  | 0.95 | 1.05 | 0.04277 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | WICHITA7 | 0.98814 | 0.92749 | -0.060645 |  | 0.95 | 1.05 | 0.071112 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | WICHITA7 | 0.98814 | 0.92749 | -0.060645 |  | 0.95 | 1.05 | 0.039357 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | WICHITA7 | 0.98814 | 0.92749 | -0.060645 |  | 0.95 | 1.05 | 0.04035 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | WICHITA7 | 0.98814 | 0.92749 | -0.060645 |  | 0.95 | 1.05 | 0.052332 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | WICHITA7 | 0.98814 | 0.92749 | -0.060645 |  | 0.95 | 1.05 | 0.045944 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | WICHITA7 | 0.98814 | 0.92749 | -0.060645 |  | 0.95 | 1.05 | 0.038178 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | WICHITA7 | 0.98814 | 0.92749 | -0.060645 |  | 0.95 | 1.05 | 0.13469 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-241 | WICHITA7 | 0.98814 | 0.92749 | -0.060645 |  | 0.95 | 1.05 | 0.03053 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | WICHITA7 | 0.98814 | 0.92749 | -0.060645 |  | 0.95 | 1.05 | 0.038178 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | WICHITA7 | 0.98814 | 0.92749 | -0.060645 |  | 0.95 | 1.05 | 0.037309 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | WICHITA7 | 0.98814 | 0.92749 | -0.060645 |  | 0.95 | 1.05 | 0.040075 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | WICHITA7 | 0.98814 | 0.92749 | -0.060645 |  | 0.95 | 1.05 | 0.053764 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | WICHITA7 | 0.98814 | 0.92749 | -0.060645 |  | 0.95 | 1.05 | 0.071762 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | WICHITA7 | 0.98814 | 0.92749 | -0.060645 |  | 0.95 | 1.05 | 0.047827 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | WICHITA7 | 0.98814 | 0.92749 | -0.060645 |  | 0.95 | 1.05 | 0.047827 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | WICHITA7 | 0.98814 | 0.92749 | -0.060645 |  | 0.95 | 1.05 | 0.070303 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | WICHITA7 | 0.98814 | 0.92749 | -0.060645 |  | 0.95 | 1.05 | 0.040614 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | WICHITA7 | 0.98814 | 0.92749 | -0.060645 |  | 0.95 | 1.05 | 0.039729 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | WICHITA7 | 0.98814 | 0.92749 | -0.060645 |  | 0.95 | 1.05 | 0.049662 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | WICHITA7 | 0.98814 | 0.92749 | -0.060645 |  | 0.95 | 1.05 | 0.042332 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | WICHITA7 | 0.98814 | 0.92749 | -0.060645 |  | 0.95 | 1.05 | 0.048722 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | WICHITA7 | 0.98814 | 0.92749 | -0.060645 |  | 0.95 | 1.05 | 0.038156 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-373 | WICHITA7 | 0.98814 | 0.92749 | -0.060645 |  | 0.95 | 1.05 | 0.036794 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | WICHITA7 | 0.98785 | 0.92719 | -0.060658 |  | 0.95 | 1.05 | 0.075186 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | WICHITA7 | 0.98785 | 0.92719 | -0.060658 |  | 0.95 | 1.05 | 0.031338 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | WICHITA7 | 0.98785 | 0.92719 | -0.060658 |  | 0.95 | 1.05 | 0.031338 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | WICHITA7 | 0.98785 | 0.92719 | -0.060658 |  | 0.95 | 1.05 | 0.031391 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | WICHITA7 | 0.98785 | 0.92719 | -0.060658 |  | 0.95 | 1.05 | 0.034523 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 160 MVAR switched shunt at WICHITA7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | WICHITA7 | 0.98499 | 0.92248 | -0.062514 |  | 0.95 | 1.05 | 0.035768 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | WICHITA7 | 0.98499 | 0.92248 | -0.062514 |  | 0.95 | 1.05 | 0.088718 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | WICHITA7 | 0.98499 | 0.92248 | -0.062514 |  | 0.95 | 1.05 | 0.031473 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | WICHITA7 | 0.98499 | 0.92248 | -0.062514 |  | 0.95 | 1.05 | 0.034941 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | WICHITA7 | 0.98499 | 0.92248 | -0.062514 |  | 0.95 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | WICHITA7 | 0.98499 | 0.92248 | -0.062514 |  | 0.95 | 1.05 | 0.046801 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | WICHITA7 | 0.98499 | 0.92248 | -0.062514 |  | 0.95 | 1.05 | 0.049224 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | WICHITA7 | 0.98499 | 0.92248 | -0.062514 |  | 0.95 | 1.05 | 0.038981 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | WICHITA7 | 0.98499 | 0.92248 | -0.062514 |  | 0.95 | 1.05 | 0.040399 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | WICHITA7 | 0.98499 | 0.92248 | -0.062514 |  | 0.95 | 1.05 | 0.031912 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | WICHITA7 | 0.98499 | 0.92248 | -0.062514 |  | 0.95 | 1.05 | 0.034127 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | WICHITA7 | 0.98499 | 0.92248 | -0.062514 |  | 0.95 | 1.05 | 0.047318 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | WICHITA7 | 0.98446 | 0.90901 | -0.075443 |  | 0.95 | 1.05 | 0.040439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | WICHITA7 | 0.98446 | 0.90901 | -0.075443 |  | 0.95 | 1.05 | 0.034853 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | WICHITA7 | 0.98446 | 0.90901 | -0.075443 |  | 0.95 | 1.05 | 0.046783 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | WICHITA7 | 0.98446 | 0.90901 | -0.075443 |  | 0.95 | 1.05 | 0.047615 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | WICHITA7 | 0.98446 | 0.90901 | -0.075443 |  | 0.95 | 1.05 | 0.034938 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | WICHITA7 | 0.98446 | 0.90901 | -0.075443 |  | 0.95 | 1.05 | 0.037875 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | WICHITA7 | 0.98446 | 0.90901 | -0.075443 |  | 0.95 | 1.05 | 0.044022 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | WICHITA7 | 0.98446 | 0.90901 | -0.075443 |  | 0.95 | 1.05 | 0.030552 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | WICHITA7 | 0.98446 | 0.90901 | -0.075443 |  | 0.95 | 1.05 | 0.038531 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | WICHITA7 | 0.98446 | 0.90901 | -0.075443 |  | 0.95 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | WICHITA7 | 0.98446 | 0.90901 | -0.075443 |  | 0.95 | 1.05 | 0.062491 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | WICHITA7 | 0.98446 | 0.90901 | -0.075443 |  | 0.95 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | WICHITA7 | 0.98446 | 0.90901 | -0.075443 |  | 0.95 | 1.05 | 0.038129 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | WICHITA7 | 0.98446 | 0.90901 | -0.075443 |  | 0.95 | 1.05 | 0.038066 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | WICHITA7 | 0.98446 | 0.90901 | -0.075443 |  | 0.95 | 1.05 | 0.034955 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | WICHITA7 | 0.98446 | 0.90901 | -0.075443 |  | 0.95 | 1.05 | 0.06281 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | WICHITA7 | 0.98446 | 0.90901 | -0.075443 |  | 0.95 | 1.05 | 0.045309 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | WICHITA7 | 0.98446 | 0.90901 | -0.075443 |  | 0.95 | 1.05 | 0.035805 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | WICHITA7 | 0.98446 | 0.90901 | -0.075443 |  | 0.95 | 1.05 | 0.032364 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | WICHITA7 | 0.98446 | 0.90901 | -0.075443 |  | 0.95 | 1.05 | 0.031815 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | WICHITA7 | 0.98446 | 0.90901 | -0.075443 |  | 0.95 | 1.05 | 0.033886 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | WICHITA7 | 0.98446 | 0.90901 | -0.075443 |  | 0.95 | 1.05 | 0.035554 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | WICHITA7 | 0.98493 | 0.91013 | -0.074802 |  | 0.95 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | WICHITA7 | 0.98493 | 0.91013 | -0.074802 |  | 0.95 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | WICHITA7 | 0.98493 | 0.91013 | -0.074802 |  | 0.95 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | WICHITA7 | 0.98493 | 0.91013 | -0.074802 |  | 0.95 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | WICHITA7 | 0.98493 | 0.91013 | -0.074802 |  | 0.95 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | WICHITA7 | 0.98493 | 0.91013 | -0.074802 |  | 0.95 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | WICHITA7 | 0.98493 | 0.91013 | -0.074802 |  | 0.95 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | WICHITA7 | 0.98493 | 0.91013 | -0.074802 |  | 0.95 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | WICHITA7 | 0.98493 | 0.91013 | -0.074802 |  | 0.95 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | WICHITA7 | 0.98493 | 0.91013 | -0.074802 |  | 0.95 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | WICHITA7 | 0.98493 | 0.91013 | -0.074802 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | WICHITA7 | 0.98493 | 0.91013 | -0.074802 |  | 0.95 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | WICHITA7 | 0.98493 | 0.91013 | -0.074802 |  | 0.95 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | WICHITA7 | 0.98493 | 0.91013 | -0.074802 |  | 0.95 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | WICHITA7 | 0.98493 | 0.91013 | -0.074802 |  | 0.95 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | WICHITA7 | 0.98493 | 0.91013 | -0.074802 |  | 0.95 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | WICHITA7 | 0.98493 | 0.91013 | -0.074802 |  | 0.95 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | WICHITA7 | 0.98493 | 0.91013 | -0.074802 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | WICHITA7 | 0.98493 | 0.91013 | -0.074802 |  | 0.95 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | WICHITA7 | 0.98493 | 0.91013 | -0.074802 |  | 0.95 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | WICHITA7 | 0.98493 | 0.91013 | -0.074802 |  | 0.95 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | WICHITA7 | 0.98493 | 0.91013 | -0.074802 |  | 0.95 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | WICHITA7 | 0.98493 | 0.91013 | -0.074802 |  | 0.95 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | WICHITA7 | 0.98493 | 0.91013 | -0.074802 |  | 0.95 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | WICHITA7 | 0.98493 | 0.91013 | -0.074802 |  | 0.95 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | WINDSR 5 | 0.99353 | 0.92552 | -0.068005 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | WINDSR 5 | 0.99353 | 0.92552 | -0.068005 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | WINDSR 5 | 0.99353 | 0.92552 | -0.068005 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | WINDSR 5 | 0.99353 | 0.92552 | -0.068005 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | WINDSR 5 | 0.99353 | 0.92552 | -0.068005 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | WINDSR 5 | 0.99353 | 0.92552 | -0.068005 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | WINDSR 5 | 0.99353 | 0.92552 | -0.068005 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | WINDSR 5 | 0.99353 | 0.92552 | -0.068005 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | WINDSR 5 | 0.99353 | 0.92552 | -0.068005 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | WINDSR 5 | 0.99353 | 0.92552 | -0.068005 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | WINDSR 5 | 0.99353 | 0.92552 | -0.068005 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | WINDSR 5 | 0.99353 | 0.92552 | -0.068005 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | WINDSR 5 | 0.99353 | 0.92552 | -0.068005 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | WINDSR 5 | 0.99353 | 0.92552 | -0.068005 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | WINDSR 5 | 0.99353 | 0.92552 | -0.068005 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | WINDSR 5 | 0.99353 | 0.92552 | -0.068005 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | WINDSR 5 | 0.99353 | 0.92552 | -0.068005 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | WINDSR 5 | 0.99353 | 0.92552 | -0.068005 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | WINDSR 5 | 0.99353 | 0.92552 | -0.068005 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | WINDSR 5 | 0.99353 | 0.92552 | -0.068005 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | WINDSR 5 | 0.99353 | 0.92552 | -0.068005 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | WINDSR 5 | 0.99353 | 0.92552 | -0.068005 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | WINDSR 5 | 0.99353 | 0.92552 | -0.068005 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | WINDSR 5 | 0.99353 | 0.92552 | -0.068005 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | WINDSR 5 | 0.99353 | 0.92552 | -0.068005 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | WMBROS 3 | 0.96842 | 0.87096 | -0.097462 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | WMBROS 3 | 0.96842 | 0.87096 | -0.097462 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | WMBROS 3 | 0.96842 | 0.87096 | -0.097462 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | WMBROS 3 | 0.96842 | 0.87096 | -0.097462 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | WMBROS 3 | 0.96842 | 0.87096 | -0.097462 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | WMBROS 3 | 0.96842 | 0.87096 | -0.097462 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | WMBROS 3 | 0.96842 | 0.87096 | -0.097462 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | WMBROS 3 | 0.96842 | 0.87096 | -0.097462 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | WMBROS 3 | 0.96842 | 0.87096 | -0.097462 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | WMBROS 3 | 0.96842 | 0.87096 | -0.097462 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | WMBROS 3 | 0.96842 | 0.87096 | -0.097462 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | WMBROS 3 | 0.96842 | 0.87096 | -0.097462 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | WMBROS 3 | 0.96842 | 0.87096 | -0.097462 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | WMBROS 3 | 0.96842 | 0.87096 | -0.097462 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | WMBROS 3 | 0.96842 | 0.87096 | -0.097462 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | WMBROS 3 | 0.96842 | 0.87096 | -0.097462 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | WMBROS 3 | 0.96842 | 0.87096 | -0.097462 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | WMBROS 3 | 0.96842 | 0.87096 | -0.097462 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | WMBROS 3 | 0.96842 | 0.87096 | -0.097462 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | WMBROS 3 | 0.96842 | 0.87096 | -0.097462 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | WMBROS 3 | 0.96842 | 0.87096 | -0.097462 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | WMBROS 3 | 0.96842 | 0.87096 | -0.097462 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | WMBROS 3 | 0.96842 | 0.87096 | -0.097462 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | WMBROS 3 | 0.96842 | 0.87096 | -0.097462 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | WMBROS 3 | 0.96842 | 0.87096 | -0.097462 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | WMBROSJ3 | 0.96842 | 0.87096 | -0.097462 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | WMBROSJ3 | 0.96842 | 0.87096 | -0.097462 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | WMBROSJ3 | 0.96842 | 0.87096 | -0.097462 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | WMBROSJ3 | 0.96842 | 0.87096 | -0.097462 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | WMBROSJ3 | 0.96842 | 0.87096 | -0.097462 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | WMBROSJ3 | 0.96842 | 0.87096 | -0.097462 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | WMBROSJ3 | 0.96842 | 0.87096 | -0.097462 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | WMBROSJ3 | 0.96842 | 0.87096 | -0.097462 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | WMBROSJ3 | 0.96842 | 0.87096 | -0.097462 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | WMBROSJ3 | 0.96842 | 0.87096 | -0.097462 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | WMBROSJ3 | 0.96842 | 0.87096 | -0.097462 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | WMBROSJ3 | 0.96842 | 0.87096 | -0.097462 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | WMBROSJ3 | 0.96842 | 0.87096 | -0.097462 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | WMBROSJ3 | 0.96842 | 0.87096 | -0.097462 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | WMBROSJ3 | 0.96842 | 0.87096 | -0.097462 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | WMBROSJ3 | 0.96842 | 0.87096 | -0.097462 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | WMBROSJ3 | 0.96842 | 0.87096 | -0.097462 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | WMBROSJ3 | 0.96842 | 0.87096 | -0.097462 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | WMBROSJ3 | 0.96842 | 0.87096 | -0.097462 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | WMBROSJ3 | 0.96842 | 0.87096 | -0.097462 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | WMBROSJ3 | 0.96842 | 0.87096 | -0.097462 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | WMBROSJ3 | 0.96842 | 0.87096 | -0.097462 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | WMBROSJ3 | 0.96842 | 0.87096 | -0.097462 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | WMBROSJ3 | 0.96842 | 0.87096 | -0.097462 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | WMBROSJ3 | 0.96842 | 0.87096 | -0.097462 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | WOODLND5 | 0.98674 | 0.92303 | -0.063713 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | WOODLND5 | 0.98674 | 0.92303 | -0.063713 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | WOODLND5 | 0.98674 | 0.92303 | -0.063713 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | WOODLND5 | 0.98674 | 0.92303 | -0.063713 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | WOODLND5 | 0.98674 | 0.92303 | -0.063713 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | WOODLND5 | 0.98674 | 0.92303 | -0.063713 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | WOODLND5 | 0.98674 | 0.92303 | -0.063713 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | WOODLND5 | 0.98674 | 0.92303 | -0.063713 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | WOODLND5 | 0.98674 | 0.92303 | -0.063713 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | WOODLND5 | 0.98674 | 0.92303 | -0.063713 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | WOODLND5 | 0.98674 | 0.92303 | -0.063713 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | WOODLND5 | 0.98674 | 0.92303 | -0.063713 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | WOODLND5 | 0.98674 | 0.92303 | -0.063713 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | WOODLND5 | 0.98674 | 0.92303 | -0.063713 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | WOODLND5 | 0.98674 | 0.92303 | -0.063713 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | WOODLND5 | 0.98674 | 0.92303 | -0.063713 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | WOODLND5 | 0.98674 | 0.92303 | -0.063713 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | WOODLND5 | 0.98674 | 0.92303 | -0.063713 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | WOODLND5 | 0.98674 | 0.92303 | -0.063713 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | WOODLND5 | 0.98674 | 0.92303 | -0.063713 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | WOODLND5 | 0.98674 | 0.92303 | -0.063713 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | WOODLND5 | 0.98674 | 0.92303 | -0.063713 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | WOODLND5 | 0.98674 | 0.92303 | -0.063713 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | WOODLND5 | 0.98674 | 0.92303 | -0.063713 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | WOODLND5 | 0.98674 | 0.92303 | -0.063713 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | WROGERS 5 | 0.98933 | 0.91883 | -0.070507 |  | 0.92 | 1.05 | 0.033596 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | WROGERS 5 | 0.98933 | 0.91883 | -0.070507 |  | 0.92 | 1.05 | 0.040193 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | WROGERS 5 | 0.98933 | 0.91883 | -0.070507 |  | 0.92 | 1.05 | 0.088122 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | WROGERS 5 | 0.98933 | 0.91883 | -0.070507 |  | 0.92 | 1.05 | 0.074664 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | WROGERS 5 | 0.98933 | 0.91883 | -0.070507 |  | 0.92 | 1.05 | 0.068051 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | WROGERS 5 | 0.98933 | 0.91883 | -0.070507 |  | 0.92 | 1.05 | 0.035565 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | WROGERS 5 | 0.98933 | 0.91883 | -0.070507 |  | 0.92 | 1.05 | 0.033904 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | WROGERS 5 | 0.98933 | 0.91883 | -0.070507 |  | 0.92 | 1.05 | 0.16366 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | WROGERS 5 | 0.98933 | 0.91883 | -0.070507 |  | 0.92 | 1.05 | 0.045569 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | WROGERS 5 | 0.98933 | 0.91883 | -0.070507 |  | 0.92 | 1.05 | 0.13458 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | WROGERS 5 | 0.98933 | 0.91883 | -0.070507 |  | 0.92 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | WROGERS 5 | 0.98933 | 0.91883 | -0.070507 |  | 0.92 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | WROGERS 5 | 0.98933 | 0.91883 | -0.070507 |  | 0.92 | 1.05 | 0.068426 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | WROGERS 5 | 0.98933 | 0.91883 | -0.070507 |  | 0.92 | 1.05 | 0.035223 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | WROGERS 5 | 0.98933 | 0.91883 | -0.070507 |  | 0.92 | 1.05 | 0.034504 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | WROGERS 5 | 0.98953 | 0.91975 | -0.069783 |  | 0.92 | 1.05 | 0.040193 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | WROGERS 5 | 0.98953 | 0.91975 | -0.069783 |  | 0.92 | 1.05 | 0.088122 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | WROGERS 5 | 0.98953 | 0.91975 | -0.069783 |  | 0.92 | 1.05 | 0.074664 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | WROGERS 5 | 0.98953 | 0.91975 | -0.069783 |  | 0.92 | 1.05 | 0.068051 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | WROGERS 5 | 0.98953 | 0.91975 | -0.069783 |  | 0.92 | 1.05 | 0.034774 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | WROGERS 5 | 0.98953 | 0.91975 | -0.069783 |  | 0.92 | 1.05 | 0.033904 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | WROGERS 5 | 0.98953 | 0.91975 | -0.069783 |  | 0.92 | 1.05 | 0.16366 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | WROGERS 5 | 0.98953 | 0.91975 | -0.069783 |  | 0.92 | 1.05 | 0.045569 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | WROGERS 5 | 0.98953 | 0.91975 | -0.069783 |  | 0.92 | 1.05 | 0.13458 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | WROGERS 5 | 0.98953 | 0.91975 | -0.069783 |  | 0.92 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | WROGERS 5 | 0.98953 | 0.91975 | -0.069783 |  | 0.92 | 1.05 | 0.037476 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | WROGERS 5 | 0.98953 | 0.91975 | -0.069783 |  | 0.92 | 1.05 | 0.068426 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | WROGERS 5 | 0.98953 | 0.91975 | -0.069783 |  | 0.92 | 1.05 | 0.035223 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | WROGERS 5 | 0.98953 | 0.91975 | -0.069783 |  | 0.92 | 1.05 | 0.034504 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | WWUPLNT4 | 0.97118 | 0.92294 | -0.04824 |  | 0.93 | 1.05 | 0.044747 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | WWUPLNT4 | 0.97118 | 0.92294 | -0.04824 |  | 0.93 | 1.05 | 0.063323 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | WWUPLNT4 | 0.97118 | 0.92294 | -0.04824 |  | 0.93 | 1.05 | 0.043143 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | WWUPLNT4 | 0.97118 | 0.92294 | -0.04824 |  | 0.93 | 1.05 | 0.038771 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | WWUPLNT4 | 0.97118 | 0.92294 | -0.04824 |  | 0.93 | 1.05 | 0.038438 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | WWUPLNT4 | 0.97118 | 0.92294 | -0.04824 |  | 0.93 | 1.05 | 0.04552 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | WWUPLNT4 | 0.97118 | 0.92294 | -0.04824 |  | 0.93 | 1.05 | 0.03158 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | WWUPLNT4 | 0.97118 | 0.92294 | -0.04824 |  | 0.93 | 1.05 | 0.034131 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | WWUPLNT4 | 0.97118 | 0.92294 | -0.04824 |  | 0.93 | 1.05 | 0.042547 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | WWUPLNT4 | 0.97118 | 0.92294 | -0.04824 |  | 0.93 | 1.05 | 0.032964 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | WWUPLNT4 | 0.97118 | 0.92294 | -0.04824 |  | 0.93 | 1.05 | 0.041072 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | WWUPLNT4 | 0.97118 | 0.92294 | -0.04824 |  | 0.93 | 1.05 | 0.069811 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | WWUPLNT4 | 0.97118 | 0.92294 | -0.04824 |  | 0.93 | 1.05 | 0.041072 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | WWUPLNT4 | 0.97118 | 0.92294 | -0.04824 |  | 0.93 | 1.05 | 0.042352 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | WWUPLNT4 | 0.97118 | 0.92294 | -0.04824 |  | 0.93 | 1.05 | 0.041773 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | WWUPLNT4 | 0.97118 | 0.92294 | -0.04824 |  | 0.93 | 1.05 | 0.048747 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | WWUPLNT4 | 0.97118 | 0.92294 | -0.04824 |  | 0.93 | 1.05 | 0.044283 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | WWUPLNT4 | 0.97118 | 0.92294 | -0.04824 |  | 0.93 | 1.05 | 0.039667 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | WWUPLNT4 | 0.97118 | 0.92294 | -0.04824 |  | 0.93 | 1.05 | 0.031705 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | WWUPLNT4 | 0.97118 | 0.92294 | -0.04824 |  | 0.93 | 1.05 | 0.036041 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | WWUPLNT4 | 0.97118 | 0.92294 | -0.04824 |  | 0.93 | 1.05 | 0.035457 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | WWUPLNT4 | 0.97118 | 0.92294 | -0.04824 |  | 0.93 | 1.05 | 0.0376 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | WWUPLNT4 | 0.97118 | 0.92294 | -0.04824 |  | 0.93 | 1.05 | 0.039043 | P23:345:WERE:WICH-345-50:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | WWUPLNT4 | 0.97145 | 0.92373 | -0.047721 |  | 0.93 | 1.05 | 0.044747 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | WWUPLNT4 | 0.97145 | 0.92373 | -0.047721 |  | 0.93 | 1.05 | 0.038771 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | WWUPLNT4 | 0.97145 | 0.92373 | -0.047721 |  | 0.93 | 1.05 | 0.038438 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | WWUPLNT4 | 0.97145 | 0.92373 | -0.047721 |  | 0.93 | 1.05 | 0.030968 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-204 | WWUPLNT4 | 0.97145 | 0.92373 | -0.047721 |  | 0.93 | 1.05 | 0.03158 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | WWUPLNT4 | 0.97145 | 0.92373 | -0.047721 |  | 0.93 | 1.05 | 0.034131 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | WWUPLNT4 | 0.97145 | 0.92373 | -0.047721 |  | 0.93 | 1.05 | 0.040933 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | WWUPLNT4 | 0.97145 | 0.92373 | -0.047721 |  | 0.93 | 1.05 | 0.032964 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | WWUPLNT4 | 0.97145 | 0.92373 | -0.047721 |  | 0.93 | 1.05 | 0.041072 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | WWUPLNT4 | 0.97145 | 0.92373 | -0.047721 |  | 0.93 | 1.05 | 0.041072 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | WWUPLNT4 | 0.97145 | 0.92373 | -0.047721 |  | 0.93 | 1.05 | 0.042352 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | WWUPLNT4 | 0.97145 | 0.92373 | -0.047721 |  | 0.93 | 1.05 | 0.041773 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | WWUPLNT4 | 0.97145 | 0.92373 | -0.047721 |  | 0.93 | 1.05 | 0.039667 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-338 | WWUPLNT4 | 0.97145 | 0.92373 | -0.047721 |  | 0.93 | 1.05 | 0.031705 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | WWUPLNT4 | 0.97145 | 0.92373 | -0.047721 |  | 0.93 | 1.05 | 0.036041 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | WWUPLNT4 | 0.97145 | 0.92373 | -0.047721 |  | 0.93 | 1.05 | 0.035457 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | WWUPLNT4 | 0.97145 | 0.92373 | -0.047721 |  | 0.93 | 1.05 | 0.0376 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | WWUPLNT4 | 0.97145 | 0.92373 | -0.047721 |  | 0.93 | 1.05 | 0.039043 | P12:345:WERE:RENO-WICH-345:EHV: | Add 0.02 MVAR switched shunt at MOUND 4 138 kV; Add 56 MVAR switched shunt at WHARV4 138 kV
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | WWUPLNT4 | 0.98739 | 0.92822 | -0.059164 |  | 0.93 | 1.05 | 0.040439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | WWUPLNT4 | 0.98739 | 0.92822 | -0.059164 |  | 0.93 | 1.05 | 0.034853 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | WWUPLNT4 | 0.98739 | 0.92822 | -0.059164 |  | 0.93 | 1.05 | 0.046783 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | WWUPLNT4 | 0.98739 | 0.92822 | -0.059164 |  | 0.93 | 1.05 | 0.047615 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | WWUPLNT4 | 0.98739 | 0.92822 | -0.059164 |  | 0.93 | 1.05 | 0.034938 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | WWUPLNT4 | 0.98739 | 0.92822 | -0.059164 |  | 0.93 | 1.05 | 0.037875 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | WWUPLNT4 | 0.98739 | 0.92822 | -0.059164 |  | 0.93 | 1.05 | 0.044022 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | WWUPLNT4 | 0.98739 | 0.92822 | -0.059164 |  | 0.93 | 1.05 | 0.030552 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | WWUPLNT4 | 0.98739 | 0.92822 | -0.059164 |  | 0.93 | 1.05 | 0.038531 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | WWUPLNT4 | 0.98739 | 0.92822 | -0.059164 |  | 0.93 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | WWUPLNT4 | 0.98739 | 0.92822 | -0.059164 |  | 0.93 | 1.05 | 0.062491 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | WWUPLNT4 | 0.98739 | 0.92822 | -0.059164 |  | 0.93 | 1.05 | 0.037118 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | WWUPLNT4 | 0.98739 | 0.92822 | -0.059164 |  | 0.93 | 1.05 | 0.038129 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | WWUPLNT4 | 0.98739 | 0.92822 | -0.059164 |  | 0.93 | 1.05 | 0.038066 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | WWUPLNT4 | 0.98739 | 0.92822 | -0.059164 |  | 0.93 | 1.05 | 0.034955 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | WWUPLNT4 | 0.98739 | 0.92822 | -0.059164 |  | 0.93 | 1.05 | 0.06281 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | WWUPLNT4 | 0.98739 | 0.92822 | -0.059164 |  | 0.93 | 1.05 | 0.045309 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | WWUPLNT4 | 0.98739 | 0.92822 | -0.059164 |  | 0.93 | 1.05 | 0.035805 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | WWUPLNT4 | 0.98739 | 0.92822 | -0.059164 |  | 0.93 | 1.05 | 0.032364 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | WWUPLNT4 | 0.98739 | 0.92822 | -0.059164 |  | 0.93 | 1.05 | 0.031815 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | WWUPLNT4 | 0.98739 | 0.92822 | -0.059164 |  | 0.93 | 1.05 | 0.033886 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | WWUPLNT4 | 0.98739 | 0.92822 | -0.059164 |  | 0.93 | 1.05 | 0.035554 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | WWUPLNT4 | 0.97982 | 0.90514 | -0.074685 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | WWUPLNT4 | 0.97982 | 0.90514 | -0.074685 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | WWUPLNT4 | 0.97982 | 0.90514 | -0.074685 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | WWUPLNT4 | 0.97982 | 0.90514 | -0.074685 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | WWUPLNT4 | 0.97982 | 0.90514 | -0.074685 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | WWUPLNT4 | 0.97982 | 0.90514 | -0.074685 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | WWUPLNT4 | 0.97982 | 0.90514 | -0.074685 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | WWUPLNT4 | 0.97982 | 0.90514 | -0.074685 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | WWUPLNT4 | 0.97982 | 0.90514 | -0.074685 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | WWUPLNT4 | 0.97982 | 0.90514 | -0.074685 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | WWUPLNT4 | 0.97982 | 0.90514 | -0.074685 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | WWUPLNT4 | 0.97982 | 0.90514 | -0.074685 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | WWUPLNT4 | 0.97982 | 0.90514 | -0.074685 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | WWUPLNT4 | 0.97982 | 0.90514 | -0.074685 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | WWUPLNT4 | 0.97982 | 0.90514 | -0.074685 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | WWUPLNT4 | 0.97982 | 0.90514 | -0.074685 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | WWUPLNT4 | 0.97982 | 0.90514 | -0.074685 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | WWUPLNT4 | 0.97982 | 0.90514 | -0.074685 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | WWUPLNT4 | 0.97982 | 0.90514 | -0.074685 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | WWUPLNT4 | 0.97982 | 0.90514 | -0.074685 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | WWUPLNT4 | 0.97982 | 0.90514 | -0.074685 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | WWUPLNT4 | 0.97982 | 0.90514 | -0.074685 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | WWUPLNT4 | 0.97982 | 0.90514 | -0.074685 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | WWUPLNT4 | 0.97982 | 0.90514 | -0.074685 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | WWUPLNT4 | 0.97982 | 0.90514 | -0.074685 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | YOST 2 | 0.98732 | 0.92043 | -0.066887 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | YOST 2 | 0.98732 | 0.92043 | -0.066887 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | YOST 2 | 0.98732 | 0.92043 | -0.066887 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | YOST 2 | 0.98732 | 0.92043 | -0.066887 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | YOST 2 | 0.98732 | 0.92043 | -0.066887 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | YOST 2 | 0.98732 | 0.92043 | -0.066887 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | YOST 2 | 0.98732 | 0.92043 | -0.066887 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | YOST 2 | 0.98732 | 0.92043 | -0.066887 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | YOST 2 | 0.98732 | 0.92043 | -0.066887 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | YOST 2 | 0.98732 | 0.92043 | -0.066887 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | YOST 2 | 0.98732 | 0.92043 | -0.066887 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | YOST 2 | 0.98732 | 0.92043 | -0.066887 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | YOST 2 | 0.98732 | 0.92043 | -0.066887 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | YOST 2 | 0.98732 | 0.92043 | -0.066887 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | YOST 2 | 0.98732 | 0.92043 | -0.066887 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | YOST 2 | 0.98732 | 0.92043 | -0.066887 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | YOST 2 | 0.98732 | 0.92043 | -0.066887 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | YOST 2 | 0.98732 | 0.92043 | -0.066887 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | YOST 2 | 0.98732 | 0.92043 | -0.066887 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | YOST 2 | 0.98732 | 0.92043 | -0.066887 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | YOST 2 | 0.98732 | 0.92043 | -0.066887 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | YOST 2 | 0.98732 | 0.92043 | -0.066887 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | YOST 2 | 0.98732 | 0.92043 | -0.066887 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | YOST 2 | 0.98732 | 0.92043 | -0.066887 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | YOST 2 | 0.98732 | 0.92043 | -0.066887 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-056 | ZOO 4 | 0.99395 | 0.92873 | -0.065214 |  | 0.93 | 1.05 | 0.037863 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-113 | ZOO 4 | 0.99395 | 0.92873 | -0.065214 |  | 0.93 | 1.05 | 0.033344 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-117 | ZOO 4 | 0.99395 | 0.92873 | -0.065214 |  | 0.93 | 1.05 | 0.0479 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-118 | ZOO 4 | 0.99395 | 0.92873 | -0.065214 |  | 0.93 | 1.05 | 0.044409 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-120 | ZOO 4 | 0.99395 | 0.92873 | -0.065214 |  | 0.93 | 1.05 | 0.03318 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-154 | ZOO 4 | 0.99395 | 0.92873 | -0.065214 |  | 0.93 | 1.05 | 0.045085 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-171 | ZOO 4 | 0.99395 | 0.92873 | -0.065214 |  | 0.93 | 1.05 | 0.045408 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-219 | ZOO 4 | 0.99395 | 0.92873 | -0.065214 |  | 0.93 | 1.05 | 0.030355 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-235 | ZOO 4 | 0.99395 | 0.92873 | -0.065214 |  | 0.93 | 1.05 | 0.042596 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-236 | ZOO 4 | 0.99395 | 0.92873 | -0.065214 |  | 0.93 | 1.05 | 0.033171 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-239 | ZOO 4 | 0.99395 | 0.92873 | -0.065214 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-240 | ZOO 4 | 0.99395 | 0.92873 | -0.065214 |  | 0.93 | 1.05 | 0.054253 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-252 | ZOO 4 | 0.99395 | 0.92873 | -0.065214 |  | 0.93 | 1.05 | 0.03801 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-254 | ZOO 4 | 0.99395 | 0.92873 | -0.065214 |  | 0.93 | 1.05 | 0.039771 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-255 | ZOO 4 | 0.99395 | 0.92873 | -0.065214 |  | 0.93 | 1.05 | 0.037144 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-268 | ZOO 4 | 0.99395 | 0.92873 | -0.065214 |  | 0.93 | 1.05 | 0.036491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-294 | ZOO 4 | 0.99395 | 0.92873 | -0.065214 |  | 0.93 | 1.05 | 0.048452 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-296 | ZOO 4 | 0.99395 | 0.92873 | -0.065214 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-297 | ZOO 4 | 0.99395 | 0.92873 | -0.065214 |  | 0.93 | 1.05 | 0.033729 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-318 | ZOO 4 | 0.99395 | 0.92873 | -0.065214 |  | 0.93 | 1.05 | 0.044721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-333 | ZOO 4 | 0.99395 | 0.92873 | -0.065214 |  | 0.93 | 1.05 | 0.035175 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-344 | ZOO 4 | 0.99395 | 0.92873 | -0.065214 |  | 0.93 | 1.05 | 0.03548 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-360 | ZOO 4 | 0.99395 | 0.92873 | -0.065214 |  | 0.93 | 1.05 | 0.031662 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-361 | ZOO 4 | 0.99395 | 0.92873 | -0.065214 |  | 0.93 | 1.05 | 0.036227 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 26SP | V | GEN-2024-362 | ZOO 4 | 0.99395 | 0.92873 | -0.065214 |  | 0.93 | 1.05 | 0.036216 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | CLARREC2 | 0.96717 | 0.91286 | -0.05431 |  | 0.92 | 1.05 | 0.081174 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 3.6 MVAR switched shunt at HEDLEY 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | CLARREC2 | 0.96717 | 0.91286 | -0.05431 |  | 0.92 | 1.05 | 0.19645 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 3.6 MVAR switched shunt at HEDLEY 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | CLARREC2 | 0.96717 | 0.91286 | -0.05431 |  | 0.92 | 1.05 | 0.23843 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 3.6 MVAR switched shunt at HEDLEY 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | CLARREC2 | 0.96717 | 0.91286 | -0.05431 |  | 0.92 | 1.05 | 0.23843 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 3.6 MVAR switched shunt at HEDLEY 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | CLARREC2 | 0.96717 | 0.91286 | -0.05431 |  | 0.92 | 1.05 | 0.17969 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 3.6 MVAR switched shunt at HEDLEY 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | CLARREC2 | 0.96717 | 0.91286 | -0.05431 |  | 0.92 | 1.05 | 0.17406 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 3.6 MVAR switched shunt at HEDLEY 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | CLARREC2 | 0.96717 | 0.91286 | -0.05431 |  | 0.92 | 1.05 | 0.17754 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 3.6 MVAR switched shunt at HEDLEY 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | CLARREC2 | 0.96717 | 0.91286 | -0.05431 |  | 0.92 | 1.05 | 0.1303 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 3.6 MVAR switched shunt at HEDLEY 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | CLARREC2 | 0.96717 | 0.91286 | -0.05431 |  | 0.92 | 1.05 | 0.1303 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 3.6 MVAR switched shunt at HEDLEY 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | CLARREC2 | 0.96717 | 0.91286 | -0.05431 |  | 0.92 | 1.05 | 0.18174 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 3.6 MVAR switched shunt at HEDLEY 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | CLARREC2 | 0.96717 | 0.91286 | -0.05431 |  | 0.92 | 1.05 | 0.18244 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 3.6 MVAR switched shunt at HEDLEY 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | CLARREC2 | 0.96717 | 0.91286 | -0.05431 |  | 0.92 | 1.05 | 0.19275 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 3.6 MVAR switched shunt at HEDLEY 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | CLARREC2 | 0.96717 | 0.91286 | -0.05431 |  | 0.92 | 1.05 | 0.19304 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 3.6 MVAR switched shunt at HEDLEY 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | CLARREC2 | 0.96717 | 0.91286 | -0.05431 |  | 0.92 | 1.05 | 0.19068 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 3.6 MVAR switched shunt at HEDLEY 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | CLARREC2 | 0.96717 | 0.91286 | -0.05431 |  | 0.92 | 1.05 | 0.19114 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 3.6 MVAR switched shunt at HEDLEY 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | CLARREC2 | 0.96717 | 0.91286 | -0.05431 |  | 0.92 | 1.05 | 0.19232 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 3.6 MVAR switched shunt at HEDLEY 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | CLARREC2 | 0.96717 | 0.91286 | -0.05431 |  | 0.92 | 1.05 | 0.17996 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 3.6 MVAR switched shunt at HEDLEY 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | CLARREC2 | 0.96717 | 0.91286 | -0.05431 |  | 0.92 | 1.05 | 0.17996 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 3.6 MVAR switched shunt at HEDLEY 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | CLARREC2 | 0.96717 | 0.91286 | -0.05431 |  | 0.92 | 1.05 | 0.18769 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 3.6 MVAR switched shunt at HEDLEY 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | CLARREC2 | 0.96717 | 0.91286 | -0.05431 |  | 0.92 | 1.05 | 0.18769 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 3.6 MVAR switched shunt at HEDLEY 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | CLARREC2 | 0.96717 | 0.91286 | -0.05431 |  | 0.92 | 1.05 | 0.4918 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 3.6 MVAR switched shunt at HEDLEY 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | CLARREC2 | 0.96717 | 0.91286 | -0.05431 |  | 0.92 | 1.05 | 0.1947 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 3.6 MVAR switched shunt at HEDLEY 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | G23-015-TAP | 1.0304 | 1.0552 | 0.024825 |  | 0.9 | 1.05 | 0.15536 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | G23-015-TAP | 1.0304 | 1.0552 | 0.024825 |  | 0.9 | 1.05 | 0.1089 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | G23-015-TAP | 1.0304 | 1.0552 | 0.024825 |  | 0.9 | 1.05 | 0.10092 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | G23-015-TAP | 1.0304 | 1.0552 | 0.024825 |  | 0.9 | 1.05 | 0.10092 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | G23-015-TAP | 1.0304 | 1.0552 | 0.024825 |  | 0.9 | 1.05 | 0.11212 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | G23-015-TAP | 1.0304 | 1.0552 | 0.024825 |  | 0.9 | 1.05 | 0.11308 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | G23-015-TAP | 1.0304 | 1.0552 | 0.024825 |  | 0.9 | 1.05 | 0.11252 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | G23-015-TAP | 1.0304 | 1.0552 | 0.024825 |  | 0.9 | 1.05 | 0.12756 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | G23-015-TAP | 1.0304 | 1.0552 | 0.024825 |  | 0.9 | 1.05 | 0.12756 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | G23-015-TAP | 1.0304 | 1.0552 | 0.024825 |  | 0.9 | 1.05 | 0.11169 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | G23-015-TAP | 1.0304 | 1.0552 | 0.024825 |  | 0.9 | 1.05 | 0.1116 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | G23-015-TAP | 1.0304 | 1.0552 | 0.024825 |  | 0.9 | 1.05 | 0.10962 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | G23-015-TAP | 1.0304 | 1.0552 | 0.024825 |  | 0.9 | 1.05 | 0.10956 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | G23-015-TAP | 1.0304 | 1.0552 | 0.024825 |  | 0.9 | 1.05 | 0.11002 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | G23-015-TAP | 1.0304 | 1.0552 | 0.024825 |  | 0.9 | 1.05 | 0.10993 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | G23-015-TAP | 1.0304 | 1.0552 | 0.024825 |  | 0.9 | 1.05 | 0.10972 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | G23-015-TAP | 1.0304 | 1.0552 | 0.024825 |  | 0.9 | 1.05 | 0.11208 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | G23-015-TAP | 1.0304 | 1.0552 | 0.024825 |  | 0.9 | 1.05 | 0.11208 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | G23-015-TAP | 1.0304 | 1.0552 | 0.024825 |  | 0.9 | 1.05 | 0.11059 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | G23-015-TAP | 1.0304 | 1.0552 | 0.024825 |  | 0.9 | 1.05 | 0.11059 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | G23-015-TAP | 1.0304 | 1.0552 | 0.024825 |  | 0.9 | 1.05 | 0.080245 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | G23-015-TAP | 1.0304 | 1.0552 | 0.024825 |  | 0.9 | 1.05 | 0.10924 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | GB-SHAMROCK | 0.91809 | 0.86644 | -0.051651 |  | 0.92 | 1.05 | 0.081174 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | GB-SHAMROCK | 0.91809 | 0.86644 | -0.051651 |  | 0.92 | 1.05 | 0.19645 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | GB-SHAMROCK | 0.91809 | 0.86644 | -0.051651 |  | 0.92 | 1.05 | 0.23843 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | GB-SHAMROCK | 0.91809 | 0.86644 | -0.051651 |  | 0.92 | 1.05 | 0.23843 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | GB-SHAMROCK | 0.91809 | 0.86644 | -0.051651 |  | 0.92 | 1.05 | 0.17969 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | GB-SHAMROCK | 0.91809 | 0.86644 | -0.051651 |  | 0.92 | 1.05 | 0.17406 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | GB-SHAMROCK | 0.91809 | 0.86644 | -0.051651 |  | 0.92 | 1.05 | 0.17754 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | GB-SHAMROCK | 0.91809 | 0.86644 | -0.051651 |  | 0.92 | 1.05 | 0.1303 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | GB-SHAMROCK | 0.91809 | 0.86644 | -0.051651 |  | 0.92 | 1.05 | 0.1303 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | GB-SHAMROCK | 0.91809 | 0.86644 | -0.051651 |  | 0.92 | 1.05 | 0.18174 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | GB-SHAMROCK | 0.91809 | 0.86644 | -0.051651 |  | 0.92 | 1.05 | 0.18244 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | GB-SHAMROCK | 0.91809 | 0.86644 | -0.051651 |  | 0.92 | 1.05 | 0.19275 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | GB-SHAMROCK | 0.91809 | 0.86644 | -0.051651 |  | 0.92 | 1.05 | 0.19304 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | GB-SHAMROCK | 0.91809 | 0.86644 | -0.051651 |  | 0.92 | 1.05 | 0.19068 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | GB-SHAMROCK | 0.91809 | 0.86644 | -0.051651 |  | 0.92 | 1.05 | 0.19114 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | GB-SHAMROCK | 0.91809 | 0.86644 | -0.051651 |  | 0.92 | 1.05 | 0.19232 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | GB-SHAMROCK | 0.91809 | 0.86644 | -0.051651 |  | 0.92 | 1.05 | 0.17996 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | GB-SHAMROCK | 0.91809 | 0.86644 | -0.051651 |  | 0.92 | 1.05 | 0.17996 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | GB-SHAMROCK | 0.91809 | 0.86644 | -0.051651 |  | 0.92 | 1.05 | 0.18769 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | GB-SHAMROCK | 0.91809 | 0.86644 | -0.051651 |  | 0.92 | 1.05 | 0.18769 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | GB-SHAMROCK | 0.91809 | 0.86644 | -0.051651 |  | 0.92 | 1.05 | 0.4918 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | GB-SHAMROCK | 0.91809 | 0.86644 | -0.051651 |  | 0.92 | 1.05 | 0.1947 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | GB-SHAMROCK | 0.92258 | 0.8767 | -0.045878 |  | 0.92 | 1.05 | 0.081174 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | GB-SHAMROCK | 0.92258 | 0.8767 | -0.045878 |  | 0.92 | 1.05 | 0.19645 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | GB-SHAMROCK | 0.92258 | 0.8767 | -0.045878 |  | 0.92 | 1.05 | 0.23843 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | GB-SHAMROCK | 0.92258 | 0.8767 | -0.045878 |  | 0.92 | 1.05 | 0.23843 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | GB-SHAMROCK | 0.92258 | 0.8767 | -0.045878 |  | 0.92 | 1.05 | 0.17969 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | GB-SHAMROCK | 0.92258 | 0.8767 | -0.045878 |  | 0.92 | 1.05 | 0.17406 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | GB-SHAMROCK | 0.92258 | 0.8767 | -0.045878 |  | 0.92 | 1.05 | 0.17754 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | GB-SHAMROCK | 0.92258 | 0.8767 | -0.045878 |  | 0.92 | 1.05 | 0.1303 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | GB-SHAMROCK | 0.92258 | 0.8767 | -0.045878 |  | 0.92 | 1.05 | 0.1303 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | GB-SHAMROCK | 0.92258 | 0.8767 | -0.045878 |  | 0.92 | 1.05 | 0.18174 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | GB-SHAMROCK | 0.92258 | 0.8767 | -0.045878 |  | 0.92 | 1.05 | 0.18244 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | GB-SHAMROCK | 0.92258 | 0.8767 | -0.045878 |  | 0.92 | 1.05 | 0.19275 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | GB-SHAMROCK | 0.92258 | 0.8767 | -0.045878 |  | 0.92 | 1.05 | 0.19304 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | GB-SHAMROCK | 0.92258 | 0.8767 | -0.045878 |  | 0.92 | 1.05 | 0.19068 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | GB-SHAMROCK | 0.92258 | 0.8767 | -0.045878 |  | 0.92 | 1.05 | 0.19114 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | GB-SHAMROCK | 0.92258 | 0.8767 | -0.045878 |  | 0.92 | 1.05 | 0.19232 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | GB-SHAMROCK | 0.92258 | 0.8767 | -0.045878 |  | 0.92 | 1.05 | 0.17996 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | GB-SHAMROCK | 0.92258 | 0.8767 | -0.045878 |  | 0.92 | 1.05 | 0.17996 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | GB-SHAMROCK | 0.92258 | 0.8767 | -0.045878 |  | 0.92 | 1.05 | 0.18769 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | GB-SHAMROCK | 0.92258 | 0.8767 | -0.045878 |  | 0.92 | 1.05 | 0.18769 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | GB-SHAMROCK | 0.92258 | 0.8767 | -0.045878 |  | 0.92 | 1.05 | 0.4918 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | GB-SHAMROCK | 0.92258 | 0.8767 | -0.045878 |  | 0.92 | 1.05 | 0.1947 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | GB-SHAMROCK | 0.92339 | 0.87892 | -0.04447 |  | 0.92 | 1.05 | 0.081174 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | GB-SHAMROCK | 0.92339 | 0.87892 | -0.04447 |  | 0.92 | 1.05 | 0.19645 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | GB-SHAMROCK | 0.92339 | 0.87892 | -0.04447 |  | 0.92 | 1.05 | 0.23843 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | GB-SHAMROCK | 0.92339 | 0.87892 | -0.04447 |  | 0.92 | 1.05 | 0.23843 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | GB-SHAMROCK | 0.92339 | 0.87892 | -0.04447 |  | 0.92 | 1.05 | 0.17969 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | GB-SHAMROCK | 0.92339 | 0.87892 | -0.04447 |  | 0.92 | 1.05 | 0.17406 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | GB-SHAMROCK | 0.92339 | 0.87892 | -0.04447 |  | 0.92 | 1.05 | 0.17754 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | GB-SHAMROCK | 0.92339 | 0.87892 | -0.04447 |  | 0.92 | 1.05 | 0.1303 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | GB-SHAMROCK | 0.92339 | 0.87892 | -0.04447 |  | 0.92 | 1.05 | 0.1303 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | GB-SHAMROCK | 0.92339 | 0.87892 | -0.04447 |  | 0.92 | 1.05 | 0.18174 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | GB-SHAMROCK | 0.92339 | 0.87892 | -0.04447 |  | 0.92 | 1.05 | 0.18244 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | GB-SHAMROCK | 0.92339 | 0.87892 | -0.04447 |  | 0.92 | 1.05 | 0.19275 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | GB-SHAMROCK | 0.92339 | 0.87892 | -0.04447 |  | 0.92 | 1.05 | 0.19304 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | GB-SHAMROCK | 0.92339 | 0.87892 | -0.04447 |  | 0.92 | 1.05 | 0.19068 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | GB-SHAMROCK | 0.92339 | 0.87892 | -0.04447 |  | 0.92 | 1.05 | 0.19114 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | GB-SHAMROCK | 0.92339 | 0.87892 | -0.04447 |  | 0.92 | 1.05 | 0.19232 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | GB-SHAMROCK | 0.92339 | 0.87892 | -0.04447 |  | 0.92 | 1.05 | 0.17996 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | GB-SHAMROCK | 0.92339 | 0.87892 | -0.04447 |  | 0.92 | 1.05 | 0.17996 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | GB-SHAMROCK | 0.92339 | 0.87892 | -0.04447 |  | 0.92 | 1.05 | 0.18769 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | GB-SHAMROCK | 0.92339 | 0.87892 | -0.04447 |  | 0.92 | 1.05 | 0.18769 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | GB-SHAMROCK | 0.92339 | 0.87892 | -0.04447 |  | 0.92 | 1.05 | 0.4918 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | GB-SHAMROCK | 0.92339 | 0.87892 | -0.04447 |  | 0.92 | 1.05 | 0.1947 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | GB-SHAMROCK | 0.92524 | 0.88001 | -0.045233 |  | 0.92 | 1.05 | 0.081174 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | GB-SHAMROCK | 0.92524 | 0.88001 | -0.045233 |  | 0.92 | 1.05 | 0.19645 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | GB-SHAMROCK | 0.92524 | 0.88001 | -0.045233 |  | 0.92 | 1.05 | 0.23843 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | GB-SHAMROCK | 0.92524 | 0.88001 | -0.045233 |  | 0.92 | 1.05 | 0.23843 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | GB-SHAMROCK | 0.92524 | 0.88001 | -0.045233 |  | 0.92 | 1.05 | 0.17969 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | GB-SHAMROCK | 0.92524 | 0.88001 | -0.045233 |  | 0.92 | 1.05 | 0.17406 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | GB-SHAMROCK | 0.92524 | 0.88001 | -0.045233 |  | 0.92 | 1.05 | 0.17754 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | GB-SHAMROCK | 0.92524 | 0.88001 | -0.045233 |  | 0.92 | 1.05 | 0.1303 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | GB-SHAMROCK | 0.92524 | 0.88001 | -0.045233 |  | 0.92 | 1.05 | 0.1303 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | GB-SHAMROCK | 0.92524 | 0.88001 | -0.045233 |  | 0.92 | 1.05 | 0.18174 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | GB-SHAMROCK | 0.92524 | 0.88001 | -0.045233 |  | 0.92 | 1.05 | 0.18244 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | GB-SHAMROCK | 0.92524 | 0.88001 | -0.045233 |  | 0.92 | 1.05 | 0.19275 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | GB-SHAMROCK | 0.92524 | 0.88001 | -0.045233 |  | 0.92 | 1.05 | 0.19304 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | GB-SHAMROCK | 0.92524 | 0.88001 | -0.045233 |  | 0.92 | 1.05 | 0.19068 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | GB-SHAMROCK | 0.92524 | 0.88001 | -0.045233 |  | 0.92 | 1.05 | 0.19114 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | GB-SHAMROCK | 0.92524 | 0.88001 | -0.045233 |  | 0.92 | 1.05 | 0.19232 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | GB-SHAMROCK | 0.92524 | 0.88001 | -0.045233 |  | 0.92 | 1.05 | 0.17996 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | GB-SHAMROCK | 0.92524 | 0.88001 | -0.045233 |  | 0.92 | 1.05 | 0.17996 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | GB-SHAMROCK | 0.92524 | 0.88001 | -0.045233 |  | 0.92 | 1.05 | 0.18769 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | GB-SHAMROCK | 0.92524 | 0.88001 | -0.045233 |  | 0.92 | 1.05 | 0.18769 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | GB-SHAMROCK | 0.92524 | 0.88001 | -0.045233 |  | 0.92 | 1.05 | 0.4918 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | GB-SHAMROCK | 0.92524 | 0.88001 | -0.045233 |  | 0.92 | 1.05 | 0.1947 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | GB-SHAMROCK | 0.92532 | 0.88002 | -0.0453 |  | 0.92 | 1.05 | 0.081174 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | GB-SHAMROCK | 0.92532 | 0.88002 | -0.0453 |  | 0.92 | 1.05 | 0.19645 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | GB-SHAMROCK | 0.92532 | 0.88002 | -0.0453 |  | 0.92 | 1.05 | 0.23843 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | GB-SHAMROCK | 0.92532 | 0.88002 | -0.0453 |  | 0.92 | 1.05 | 0.23843 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | GB-SHAMROCK | 0.92532 | 0.88002 | -0.0453 |  | 0.92 | 1.05 | 0.17969 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | GB-SHAMROCK | 0.92532 | 0.88002 | -0.0453 |  | 0.92 | 1.05 | 0.17406 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | GB-SHAMROCK | 0.92532 | 0.88002 | -0.0453 |  | 0.92 | 1.05 | 0.17754 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | GB-SHAMROCK | 0.92532 | 0.88002 | -0.0453 |  | 0.92 | 1.05 | 0.1303 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | GB-SHAMROCK | 0.92532 | 0.88002 | -0.0453 |  | 0.92 | 1.05 | 0.1303 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | GB-SHAMROCK | 0.92532 | 0.88002 | -0.0453 |  | 0.92 | 1.05 | 0.18174 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | GB-SHAMROCK | 0.92532 | 0.88002 | -0.0453 |  | 0.92 | 1.05 | 0.18244 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | GB-SHAMROCK | 0.92532 | 0.88002 | -0.0453 |  | 0.92 | 1.05 | 0.19275 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | GB-SHAMROCK | 0.92532 | 0.88002 | -0.0453 |  | 0.92 | 1.05 | 0.19304 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | GB-SHAMROCK | 0.92532 | 0.88002 | -0.0453 |  | 0.92 | 1.05 | 0.19068 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | GB-SHAMROCK | 0.92532 | 0.88002 | -0.0453 |  | 0.92 | 1.05 | 0.19114 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | GB-SHAMROCK | 0.92532 | 0.88002 | -0.0453 |  | 0.92 | 1.05 | 0.19232 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | GB-SHAMROCK | 0.92532 | 0.88002 | -0.0453 |  | 0.92 | 1.05 | 0.17996 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | GB-SHAMROCK | 0.92532 | 0.88002 | -0.0453 |  | 0.92 | 1.05 | 0.17996 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | GB-SHAMROCK | 0.92532 | 0.88002 | -0.0453 |  | 0.92 | 1.05 | 0.18769 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | GB-SHAMROCK | 0.92532 | 0.88002 | -0.0453 |  | 0.92 | 1.05 | 0.18769 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | GB-SHAMROCK | 0.92532 | 0.88002 | -0.0453 |  | 0.92 | 1.05 | 0.4918 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | GB-SHAMROCK | 0.92532 | 0.88002 | -0.0453 |  | 0.92 | 1.05 | 0.1947 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | GEN-2023-015 | 1.0304 | 1.0552 | 0.024825 |  | 0.9 | 1.05 | 0.15536 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | GEN-2023-015 | 1.0304 | 1.0552 | 0.024825 |  | 0.9 | 1.05 | 0.1089 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | GEN-2023-015 | 1.0304 | 1.0552 | 0.024825 |  | 0.9 | 1.05 | 0.10092 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | GEN-2023-015 | 1.0304 | 1.0552 | 0.024825 |  | 0.9 | 1.05 | 0.10092 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | GEN-2023-015 | 1.0304 | 1.0552 | 0.024825 |  | 0.9 | 1.05 | 0.11212 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | GEN-2023-015 | 1.0304 | 1.0552 | 0.024825 |  | 0.9 | 1.05 | 0.11308 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | GEN-2023-015 | 1.0304 | 1.0552 | 0.024825 |  | 0.9 | 1.05 | 0.11252 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | GEN-2023-015 | 1.0304 | 1.0552 | 0.024825 |  | 0.9 | 1.05 | 0.12756 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | GEN-2023-015 | 1.0304 | 1.0552 | 0.024825 |  | 0.9 | 1.05 | 0.12756 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | GEN-2023-015 | 1.0304 | 1.0552 | 0.024825 |  | 0.9 | 1.05 | 0.11169 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | GEN-2023-015 | 1.0304 | 1.0552 | 0.024825 |  | 0.9 | 1.05 | 0.1116 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | GEN-2023-015 | 1.0304 | 1.0552 | 0.024825 |  | 0.9 | 1.05 | 0.10962 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | GEN-2023-015 | 1.0304 | 1.0552 | 0.024825 |  | 0.9 | 1.05 | 0.10956 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | GEN-2023-015 | 1.0304 | 1.0552 | 0.024825 |  | 0.9 | 1.05 | 0.11002 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | GEN-2023-015 | 1.0304 | 1.0552 | 0.024825 |  | 0.9 | 1.05 | 0.10993 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | GEN-2023-015 | 1.0304 | 1.0552 | 0.024825 |  | 0.9 | 1.05 | 0.10972 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | GEN-2023-015 | 1.0304 | 1.0552 | 0.024825 |  | 0.9 | 1.05 | 0.11208 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | GEN-2023-015 | 1.0304 | 1.0552 | 0.024825 |  | 0.9 | 1.05 | 0.11208 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | GEN-2023-015 | 1.0304 | 1.0552 | 0.024825 |  | 0.9 | 1.05 | 0.11059 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | GEN-2023-015 | 1.0304 | 1.0552 | 0.024825 |  | 0.9 | 1.05 | 0.11059 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | GEN-2023-015 | 1.0304 | 1.0552 | 0.024825 |  | 0.9 | 1.05 | 0.080245 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | GEN-2023-015 | 1.0304 | 1.0552 | 0.024825 |  | 0.9 | 1.05 | 0.10924 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | HEDLEY 2 | 0.97422 | 0.91964 | -0.054577 |  | 0.92 | 1.05 | 0.081174 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 3.6 MVAR switched shunt at HEDLEY 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | HEDLEY 2 | 0.97422 | 0.91964 | -0.054577 |  | 0.92 | 1.05 | 0.19645 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 3.6 MVAR switched shunt at HEDLEY 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | HEDLEY 2 | 0.97422 | 0.91964 | -0.054577 |  | 0.92 | 1.05 | 0.23843 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 3.6 MVAR switched shunt at HEDLEY 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | HEDLEY 2 | 0.97422 | 0.91964 | -0.054577 |  | 0.92 | 1.05 | 0.23843 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 3.6 MVAR switched shunt at HEDLEY 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | HEDLEY 2 | 0.97422 | 0.91964 | -0.054577 |  | 0.92 | 1.05 | 0.17969 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 3.6 MVAR switched shunt at HEDLEY 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | HEDLEY 2 | 0.97422 | 0.91964 | -0.054577 |  | 0.92 | 1.05 | 0.17406 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 3.6 MVAR switched shunt at HEDLEY 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | HEDLEY 2 | 0.97422 | 0.91964 | -0.054577 |  | 0.92 | 1.05 | 0.17754 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 3.6 MVAR switched shunt at HEDLEY 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | HEDLEY 2 | 0.97422 | 0.91964 | -0.054577 |  | 0.92 | 1.05 | 0.1303 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 3.6 MVAR switched shunt at HEDLEY 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | HEDLEY 2 | 0.97422 | 0.91964 | -0.054577 |  | 0.92 | 1.05 | 0.1303 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 3.6 MVAR switched shunt at HEDLEY 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | HEDLEY 2 | 0.97422 | 0.91964 | -0.054577 |  | 0.92 | 1.05 | 0.18174 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 3.6 MVAR switched shunt at HEDLEY 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | HEDLEY 2 | 0.97422 | 0.91964 | -0.054577 |  | 0.92 | 1.05 | 0.18244 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 3.6 MVAR switched shunt at HEDLEY 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | HEDLEY 2 | 0.97422 | 0.91964 | -0.054577 |  | 0.92 | 1.05 | 0.19275 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 3.6 MVAR switched shunt at HEDLEY 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | HEDLEY 2 | 0.97422 | 0.91964 | -0.054577 |  | 0.92 | 1.05 | 0.19304 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 3.6 MVAR switched shunt at HEDLEY 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | HEDLEY 2 | 0.97422 | 0.91964 | -0.054577 |  | 0.92 | 1.05 | 0.19068 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 3.6 MVAR switched shunt at HEDLEY 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | HEDLEY 2 | 0.97422 | 0.91964 | -0.054577 |  | 0.92 | 1.05 | 0.19114 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 3.6 MVAR switched shunt at HEDLEY 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | HEDLEY 2 | 0.97422 | 0.91964 | -0.054577 |  | 0.92 | 1.05 | 0.19232 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 3.6 MVAR switched shunt at HEDLEY 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | HEDLEY 2 | 0.97422 | 0.91964 | -0.054577 |  | 0.92 | 1.05 | 0.17996 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 3.6 MVAR switched shunt at HEDLEY 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | HEDLEY 2 | 0.97422 | 0.91964 | -0.054577 |  | 0.92 | 1.05 | 0.17996 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 3.6 MVAR switched shunt at HEDLEY 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | HEDLEY 2 | 0.97422 | 0.91964 | -0.054577 |  | 0.92 | 1.05 | 0.18769 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 3.6 MVAR switched shunt at HEDLEY 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | HEDLEY 2 | 0.97422 | 0.91964 | -0.054577 |  | 0.92 | 1.05 | 0.18769 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 3.6 MVAR switched shunt at HEDLEY 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | HEDLEY 2 | 0.97422 | 0.91964 | -0.054577 |  | 0.92 | 1.05 | 0.4918 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 3.6 MVAR switched shunt at HEDLEY 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | HEDLEY 2 | 0.97422 | 0.91964 | -0.054577 |  | 0.92 | 1.05 | 0.1947 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 3.6 MVAR switched shunt at HEDLEY 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | HI_BNKS1_WF7 | 1.0459 | 1.0712 | 0.025278 |  | 0.95 | 1.05 | 0.07555 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | HI_BNKS1_WF7 | 1.0459 | 1.0712 | 0.025278 |  | 0.95 | 1.05 | 0.086927 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | HI_BNKS1_WF7 | 1.0459 | 1.0712 | 0.025278 |  | 0.95 | 1.05 | 0.085847 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | HI_BNKS1_WF7 | 1.0459 | 1.0712 | 0.025278 |  | 0.95 | 1.05 | 0.085847 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | HI_BNKS1_WF7 | 1.0459 | 1.0712 | 0.025278 |  | 0.95 | 1.05 | 0.08745 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | HI_BNKS1_WF7 | 1.0459 | 1.0712 | 0.025278 |  | 0.95 | 1.05 | 0.087244 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | HI_BNKS1_WF7 | 1.0459 | 1.0712 | 0.025278 |  | 0.95 | 1.05 | 0.087456 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | HI_BNKS1_WF7 | 1.0459 | 1.0712 | 0.025278 |  | 0.95 | 1.05 | 0.087184 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | HI_BNKS1_WF7 | 1.0459 | 1.0712 | 0.025278 |  | 0.95 | 1.05 | 0.087184 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | HI_BNKS1_WF7 | 1.0459 | 1.0712 | 0.025278 |  | 0.95 | 1.05 | 0.087259 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | HI_BNKS1_WF7 | 1.0459 | 1.0712 | 0.025278 |  | 0.95 | 1.05 | 0.087378 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | HI_BNKS1_WF7 | 1.0459 | 1.0712 | 0.025278 |  | 0.95 | 1.05 | 0.087068 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | HI_BNKS1_WF7 | 1.0459 | 1.0712 | 0.025278 |  | 0.95 | 1.05 | 0.087057 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | HI_BNKS1_WF7 | 1.0459 | 1.0712 | 0.025278 |  | 0.95 | 1.05 | 0.087143 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | HI_BNKS1_WF7 | 1.0459 | 1.0712 | 0.025278 |  | 0.95 | 1.05 | 0.08713 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | HI_BNKS1_WF7 | 1.0459 | 1.0712 | 0.025278 |  | 0.95 | 1.05 | 0.087113 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | HI_BNKS1_WF7 | 1.0459 | 1.0712 | 0.025278 |  | 0.95 | 1.05 | 0.087449 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | HI_BNKS1_WF7 | 1.0459 | 1.0712 | 0.025278 |  | 0.95 | 1.05 | 0.087449 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | HI_BNKS1_WF7 | 1.0459 | 1.0712 | 0.025278 |  | 0.95 | 1.05 | 0.087196 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | HI_BNKS1_WF7 | 1.0459 | 1.0712 | 0.025278 |  | 0.95 | 1.05 | 0.087196 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | HI_BNKS1_WF7 | 1.0459 | 1.0712 | 0.025278 |  | 0.95 | 1.05 | 0.075997 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | HI_BNKS1_WF7 | 1.0459 | 1.0712 | 0.025278 |  | 0.95 | 1.05 | 0.087001 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | HI_BNKS1_WF7 | 1.046 | 1.0712 | 0.025234 |  | 0.95 | 1.05 | 0.083222 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | HI_BNKS1_WF7 | 1.046 | 1.0712 | 0.025234 |  | 0.95 | 1.05 | 0.090954 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | HI_BNKS1_WF7 | 1.046 | 1.0712 | 0.025234 |  | 0.95 | 1.05 | 0.089327 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | HI_BNKS1_WF7 | 1.046 | 1.0712 | 0.025234 |  | 0.95 | 1.05 | 0.089327 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | HI_BNKS1_WF7 | 1.046 | 1.0712 | 0.025234 |  | 0.95 | 1.05 | 0.091714 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | HI_BNKS1_WF7 | 1.046 | 1.0712 | 0.025234 |  | 0.95 | 1.05 | 0.091515 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | HI_BNKS1_WF7 | 1.046 | 1.0712 | 0.025234 |  | 0.95 | 1.05 | 0.091739 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | HI_BNKS1_WF7 | 1.046 | 1.0712 | 0.025234 |  | 0.95 | 1.05 | 0.092385 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | HI_BNKS1_WF7 | 1.046 | 1.0712 | 0.025234 |  | 0.95 | 1.05 | 0.092385 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | HI_BNKS1_WF7 | 1.046 | 1.0712 | 0.025234 |  | 0.95 | 1.05 | 0.091471 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | HI_BNKS1_WF7 | 1.046 | 1.0712 | 0.025234 |  | 0.95 | 1.05 | 0.091606 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | HI_BNKS1_WF7 | 1.046 | 1.0712 | 0.025234 |  | 0.95 | 1.05 | 0.091153 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | HI_BNKS1_WF7 | 1.046 | 1.0712 | 0.025234 |  | 0.95 | 1.05 | 0.091138 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | HI_BNKS1_WF7 | 1.046 | 1.0712 | 0.025234 |  | 0.95 | 1.05 | 0.091259 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | HI_BNKS1_WF7 | 1.046 | 1.0712 | 0.025234 |  | 0.95 | 1.05 | 0.09124 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | HI_BNKS1_WF7 | 1.046 | 1.0712 | 0.025234 |  | 0.95 | 1.05 | 0.09121 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | HI_BNKS1_WF7 | 1.046 | 1.0712 | 0.025234 |  | 0.95 | 1.05 | 0.091711 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | HI_BNKS1_WF7 | 1.046 | 1.0712 | 0.025234 |  | 0.95 | 1.05 | 0.091711 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | HI_BNKS1_WF7 | 1.046 | 1.0712 | 0.025234 |  | 0.95 | 1.05 | 0.091347 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | HI_BNKS1_WF7 | 1.046 | 1.0712 | 0.025234 |  | 0.95 | 1.05 | 0.091347 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | HI_BNKS1_WF7 | 1.046 | 1.0712 | 0.025234 |  | 0.95 | 1.05 | 0.077443 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | HI_BNKS1_WF7 | 1.046 | 1.0712 | 0.025234 |  | 0.95 | 1.05 | 0.091057 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | HI_BNKS1_WF7 | 1.0459 | 1.0711 | 0.025223 |  | 0.95 | 1.05 | 0.040848 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | HI_BNKS1_WF7 | 1.0459 | 1.0711 | 0.025223 |  | 0.95 | 1.05 | 0.041168 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | HI_BNKS1_WF7 | 1.0459 | 1.0711 | 0.025223 |  | 0.95 | 1.05 | 0.041015 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | HI_BNKS1_WF7 | 1.0459 | 1.0711 | 0.025223 |  | 0.95 | 1.05 | 0.041015 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | HI_BNKS1_WF7 | 1.0459 | 1.0711 | 0.025223 |  | 0.95 | 1.05 | 0.041235 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | HI_BNKS1_WF7 | 1.0459 | 1.0711 | 0.025223 |  | 0.95 | 1.05 | 0.041233 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | HI_BNKS1_WF7 | 1.0459 | 1.0711 | 0.025223 |  | 0.95 | 1.05 | 0.041239 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | HI_BNKS1_WF7 | 1.0459 | 1.0711 | 0.025223 |  | 0.95 | 1.05 | 0.041327 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | HI_BNKS1_WF7 | 1.0459 | 1.0711 | 0.025223 |  | 0.95 | 1.05 | 0.041327 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | HI_BNKS1_WF7 | 1.0459 | 1.0711 | 0.025223 |  | 0.95 | 1.05 | 0.041219 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | HI_BNKS1_WF7 | 1.0459 | 1.0711 | 0.025223 |  | 0.95 | 1.05 | 0.041225 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | HI_BNKS1_WF7 | 1.0459 | 1.0711 | 0.025223 |  | 0.95 | 1.05 | 0.041184 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | HI_BNKS1_WF7 | 1.0459 | 1.0711 | 0.025223 |  | 0.95 | 1.05 | 0.041183 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | HI_BNKS1_WF7 | 1.0459 | 1.0711 | 0.025223 |  | 0.95 | 1.05 | 0.041193 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | HI_BNKS1_WF7 | 1.0459 | 1.0711 | 0.025223 |  | 0.95 | 1.05 | 0.041191 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | HI_BNKS1_WF7 | 1.0459 | 1.0711 | 0.025223 |  | 0.95 | 1.05 | 0.041188 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | HI_BNKS1_WF7 | 1.0459 | 1.0711 | 0.025223 |  | 0.95 | 1.05 | 0.041234 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | HI_BNKS1_WF7 | 1.0459 | 1.0711 | 0.025223 |  | 0.95 | 1.05 | 0.041234 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | HI_BNKS1_WF7 | 1.0459 | 1.0711 | 0.025223 |  | 0.95 | 1.05 | 0.041203 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | HI_BNKS1_WF7 | 1.0459 | 1.0711 | 0.025223 |  | 0.95 | 1.05 | 0.041203 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | HI_BNKS1_WF7 | 1.0459 | 1.0711 | 0.025223 |  | 0.95 | 1.05 | 0.039885 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | HI_BNKS1_WF7 | 1.0459 | 1.0711 | 0.025223 |  | 0.95 | 1.05 | 0.041176 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | HI_BNKS1_WF7 | 1.0458 | 1.0712 | 0.025439 |  | 0.95 | 1.05 | 0.051941 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | HI_BNKS1_WF7 | 1.0458 | 1.0712 | 0.025439 |  | 0.95 | 1.05 | 0.049557 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | HI_BNKS1_WF7 | 1.0458 | 1.0712 | 0.025439 |  | 0.95 | 1.05 | 0.048901 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | HI_BNKS1_WF7 | 1.0458 | 1.0712 | 0.025439 |  | 0.95 | 1.05 | 0.048901 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | HI_BNKS1_WF7 | 1.0458 | 1.0712 | 0.025439 |  | 0.95 | 1.05 | 0.049829 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | HI_BNKS1_WF7 | 1.0458 | 1.0712 | 0.025439 |  | 0.95 | 1.05 | 0.049876 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | HI_BNKS1_WF7 | 1.0458 | 1.0712 | 0.025439 |  | 0.95 | 1.05 | 0.049857 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | HI_BNKS1_WF7 | 1.0458 | 1.0712 | 0.025439 |  | 0.95 | 1.05 | 0.05072 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | HI_BNKS1_WF7 | 1.0458 | 1.0712 | 0.025439 |  | 0.95 | 1.05 | 0.05072 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | HI_BNKS1_WF7 | 1.0458 | 1.0712 | 0.025439 |  | 0.95 | 1.05 | 0.049781 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | HI_BNKS1_WF7 | 1.0458 | 1.0712 | 0.025439 |  | 0.95 | 1.05 | 0.049786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | HI_BNKS1_WF7 | 1.0458 | 1.0712 | 0.025439 |  | 0.95 | 1.05 | 0.04962 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | HI_BNKS1_WF7 | 1.0458 | 1.0712 | 0.025439 |  | 0.95 | 1.05 | 0.049615 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | HI_BNKS1_WF7 | 1.0458 | 1.0712 | 0.025439 |  | 0.95 | 1.05 | 0.049655 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | HI_BNKS1_WF7 | 1.0458 | 1.0712 | 0.025439 |  | 0.95 | 1.05 | 0.049648 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | HI_BNKS1_WF7 | 1.0458 | 1.0712 | 0.025439 |  | 0.95 | 1.05 | 0.049631 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | HI_BNKS1_WF7 | 1.0458 | 1.0712 | 0.025439 |  | 0.95 | 1.05 | 0.049826 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | HI_BNKS1_WF7 | 1.0458 | 1.0712 | 0.025439 |  | 0.95 | 1.05 | 0.049826 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | HI_BNKS1_WF7 | 1.0458 | 1.0712 | 0.025439 |  | 0.95 | 1.05 | 0.049699 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | HI_BNKS1_WF7 | 1.0458 | 1.0712 | 0.025439 |  | 0.95 | 1.05 | 0.049699 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | HI_BNKS1_WF7 | 1.0458 | 1.0712 | 0.025439 |  | 0.95 | 1.05 | 0.045602 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | HI_BNKS1_WF7 | 1.0458 | 1.0712 | 0.025439 |  | 0.95 | 1.05 | 0.049587 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | HI_BNKS1_WF7 | 1.046 | 1.0711 | 0.025153 |  | 0.95 | 1.05 | 0.03623 | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | HI_BNKS1_WF7 | 1.046 | 1.0711 | 0.025153 |  | 0.95 | 1.05 | 0.038105 | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | HI_BNKS1_WF7 | 1.046 | 1.0711 | 0.025153 |  | 0.95 | 1.05 | 0.038044 | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | HI_BNKS1_WF7 | 1.046 | 1.0711 | 0.025153 |  | 0.95 | 1.05 | 0.038044 | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | HI_BNKS1_WF7 | 1.046 | 1.0711 | 0.025153 |  | 0.95 | 1.05 | 0.038139 | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | HI_BNKS1_WF7 | 1.046 | 1.0711 | 0.025153 |  | 0.95 | 1.05 | 0.038109 | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | HI_BNKS1_WF7 | 1.046 | 1.0711 | 0.025153 |  | 0.95 | 1.05 | 0.038136 | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | HI_BNKS1_WF7 | 1.046 | 1.0711 | 0.025153 |  | 0.95 | 1.05 | 0.037958 | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | HI_BNKS1_WF7 | 1.046 | 1.0711 | 0.025153 |  | 0.95 | 1.05 | 0.037958 | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | HI_BNKS1_WF7 | 1.046 | 1.0711 | 0.025153 |  | 0.95 | 1.05 | 0.038121 | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | HI_BNKS1_WF7 | 1.046 | 1.0711 | 0.025153 |  | 0.95 | 1.05 | 0.038134 | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | HI_BNKS1_WF7 | 1.046 | 1.0711 | 0.025153 |  | 0.95 | 1.05 | 0.038115 | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | HI_BNKS1_WF7 | 1.046 | 1.0711 | 0.025153 |  | 0.95 | 1.05 | 0.038114 | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | HI_BNKS1_WF7 | 1.046 | 1.0711 | 0.025153 |  | 0.95 | 1.05 | 0.03812 | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | HI_BNKS1_WF7 | 1.046 | 1.0711 | 0.025153 |  | 0.95 | 1.05 | 0.038119 | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | HI_BNKS1_WF7 | 1.046 | 1.0711 | 0.025153 |  | 0.95 | 1.05 | 0.038119 | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | HI_BNKS1_WF7 | 1.046 | 1.0711 | 0.025153 |  | 0.95 | 1.05 | 0.038139 | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | HI_BNKS1_WF7 | 1.046 | 1.0711 | 0.025153 |  | 0.95 | 1.05 | 0.038139 | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | HI_BNKS1_WF7 | 1.046 | 1.0711 | 0.025153 |  | 0.95 | 1.05 | 0.038122 | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | HI_BNKS1_WF7 | 1.046 | 1.0711 | 0.025153 |  | 0.95 | 1.05 | 0.038122 | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | HI_BNKS1_WF7 | 1.046 | 1.0711 | 0.025153 |  | 0.95 | 1.05 | 0.036973 | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | HI_BNKS1_WF7 | 1.046 | 1.0711 | 0.025153 |  | 0.95 | 1.05 | 0.03811 | Single 532771 RENO7 345 532998 G16-111-TAP 345 1 | None
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | HI_BNKS2_WF7 | 1.0507 | 1.076 | 0.025332 |  | 0.95 | 1.05 | 0.07555 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | HI_BNKS2_WF7 | 1.0507 | 1.076 | 0.025332 |  | 0.95 | 1.05 | 0.086927 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | HI_BNKS2_WF7 | 1.0507 | 1.076 | 0.025332 |  | 0.95 | 1.05 | 0.085847 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | HI_BNKS2_WF7 | 1.0507 | 1.076 | 0.025332 |  | 0.95 | 1.05 | 0.085847 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | HI_BNKS2_WF7 | 1.0507 | 1.076 | 0.025332 |  | 0.95 | 1.05 | 0.08745 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | HI_BNKS2_WF7 | 1.0507 | 1.076 | 0.025332 |  | 0.95 | 1.05 | 0.087244 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | HI_BNKS2_WF7 | 1.0507 | 1.076 | 0.025332 |  | 0.95 | 1.05 | 0.087456 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | HI_BNKS2_WF7 | 1.0507 | 1.076 | 0.025332 |  | 0.95 | 1.05 | 0.087184 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | HI_BNKS2_WF7 | 1.0507 | 1.076 | 0.025332 |  | 0.95 | 1.05 | 0.087184 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | HI_BNKS2_WF7 | 1.0507 | 1.076 | 0.025332 |  | 0.95 | 1.05 | 0.087259 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | HI_BNKS2_WF7 | 1.0507 | 1.076 | 0.025332 |  | 0.95 | 1.05 | 0.087378 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | HI_BNKS2_WF7 | 1.0507 | 1.076 | 0.025332 |  | 0.95 | 1.05 | 0.087068 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | HI_BNKS2_WF7 | 1.0507 | 1.076 | 0.025332 |  | 0.95 | 1.05 | 0.087057 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | HI_BNKS2_WF7 | 1.0507 | 1.076 | 0.025332 |  | 0.95 | 1.05 | 0.087143 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | HI_BNKS2_WF7 | 1.0507 | 1.076 | 0.025332 |  | 0.95 | 1.05 | 0.08713 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | HI_BNKS2_WF7 | 1.0507 | 1.076 | 0.025332 |  | 0.95 | 1.05 | 0.087113 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | HI_BNKS2_WF7 | 1.0507 | 1.076 | 0.025332 |  | 0.95 | 1.05 | 0.087449 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | HI_BNKS2_WF7 | 1.0507 | 1.076 | 0.025332 |  | 0.95 | 1.05 | 0.087449 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | HI_BNKS2_WF7 | 1.0507 | 1.076 | 0.025332 |  | 0.95 | 1.05 | 0.087196 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | HI_BNKS2_WF7 | 1.0507 | 1.076 | 0.025332 |  | 0.95 | 1.05 | 0.087196 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | HI_BNKS2_WF7 | 1.0507 | 1.076 | 0.025332 |  | 0.95 | 1.05 | 0.075997 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | HI_BNKS2_WF7 | 1.0507 | 1.076 | 0.025332 |  | 0.95 | 1.05 | 0.087001 | P42:345:OKGE:SB_DGSE7313:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | HI_BNKS2_WF7 | 1.0507 | 1.076 | 0.025289 |  | 0.95 | 1.05 | 0.083222 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | HI_BNKS2_WF7 | 1.0507 | 1.076 | 0.025289 |  | 0.95 | 1.05 | 0.090954 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | HI_BNKS2_WF7 | 1.0507 | 1.076 | 0.025289 |  | 0.95 | 1.05 | 0.089327 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | HI_BNKS2_WF7 | 1.0507 | 1.076 | 0.025289 |  | 0.95 | 1.05 | 0.089327 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | HI_BNKS2_WF7 | 1.0507 | 1.076 | 0.025289 |  | 0.95 | 1.05 | 0.091714 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | HI_BNKS2_WF7 | 1.0507 | 1.076 | 0.025289 |  | 0.95 | 1.05 | 0.091515 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | HI_BNKS2_WF7 | 1.0507 | 1.076 | 0.025289 |  | 0.95 | 1.05 | 0.091739 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | HI_BNKS2_WF7 | 1.0507 | 1.076 | 0.025289 |  | 0.95 | 1.05 | 0.092385 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | HI_BNKS2_WF7 | 1.0507 | 1.076 | 0.025289 |  | 0.95 | 1.05 | 0.092385 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | HI_BNKS2_WF7 | 1.0507 | 1.076 | 0.025289 |  | 0.95 | 1.05 | 0.091471 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | HI_BNKS2_WF7 | 1.0507 | 1.076 | 0.025289 |  | 0.95 | 1.05 | 0.091606 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | HI_BNKS2_WF7 | 1.0507 | 1.076 | 0.025289 |  | 0.95 | 1.05 | 0.091153 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | HI_BNKS2_WF7 | 1.0507 | 1.076 | 0.025289 |  | 0.95 | 1.05 | 0.091138 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | HI_BNKS2_WF7 | 1.0507 | 1.076 | 0.025289 |  | 0.95 | 1.05 | 0.091259 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | HI_BNKS2_WF7 | 1.0507 | 1.076 | 0.025289 |  | 0.95 | 1.05 | 0.09124 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | HI_BNKS2_WF7 | 1.0507 | 1.076 | 0.025289 |  | 0.95 | 1.05 | 0.09121 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | HI_BNKS2_WF7 | 1.0507 | 1.076 | 0.025289 |  | 0.95 | 1.05 | 0.091711 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | HI_BNKS2_WF7 | 1.0507 | 1.076 | 0.025289 |  | 0.95 | 1.05 | 0.091711 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | HI_BNKS2_WF7 | 1.0507 | 1.076 | 0.025289 |  | 0.95 | 1.05 | 0.091347 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | HI_BNKS2_WF7 | 1.0507 | 1.076 | 0.025289 |  | 0.95 | 1.05 | 0.091347 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | HI_BNKS2_WF7 | 1.0507 | 1.076 | 0.025289 |  | 0.95 | 1.05 | 0.077443 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | HI_BNKS2_WF7 | 1.0507 | 1.076 | 0.025289 |  | 0.95 | 1.05 | 0.091057 | P42:345:OKGE:SB_DGSE7385:::EHV: | None
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | HI_BNKS2_WF7 | 1.0507 | 1.0759 | 0.02528 |  | 0.95 | 1.05 | 0.031137 | P12:345:WERE:RENO-WICH-345:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | HI_BNKS2_WF7 | 1.0507 | 1.0759 | 0.02528 |  | 0.95 | 1.05 | 0.039717 | P12:345:WERE:RENO-WICH-345:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | HI_BNKS2_WF7 | 1.0507 | 1.0759 | 0.02528 |  | 0.95 | 1.05 | 0.04029 | P12:345:WERE:RENO-WICH-345:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | HI_BNKS2_WF7 | 1.0507 | 1.0759 | 0.02528 |  | 0.95 | 1.05 | 0.04029 | P12:345:WERE:RENO-WICH-345:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | HI_BNKS2_WF7 | 1.0507 | 1.0759 | 0.02528 |  | 0.95 | 1.05 | 0.039505 | P12:345:WERE:RENO-WICH-345:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | HI_BNKS2_WF7 | 1.0507 | 1.0759 | 0.02528 |  | 0.95 | 1.05 | 0.039361 | P12:345:WERE:RENO-WICH-345:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | HI_BNKS2_WF7 | 1.0507 | 1.0759 | 0.02528 |  | 0.95 | 1.05 | 0.039466 | P12:345:WERE:RENO-WICH-345:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | HI_BNKS2_WF7 | 1.0507 | 1.0759 | 0.02528 |  | 0.95 | 1.05 | 0.03794 | P12:345:WERE:RENO-WICH-345:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | HI_BNKS2_WF7 | 1.0507 | 1.0759 | 0.02528 |  | 0.95 | 1.05 | 0.03794 | P12:345:WERE:RENO-WICH-345:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | HI_BNKS2_WF7 | 1.0507 | 1.0759 | 0.02528 |  | 0.95 | 1.05 | 0.039507 | P12:345:WERE:RENO-WICH-345:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | HI_BNKS2_WF7 | 1.0507 | 1.0759 | 0.02528 |  | 0.95 | 1.05 | 0.039542 | P12:345:WERE:RENO-WICH-345:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | HI_BNKS2_WF7 | 1.0507 | 1.0759 | 0.02528 |  | 0.95 | 1.05 | 0.039675 | P12:345:WERE:RENO-WICH-345:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | HI_BNKS2_WF7 | 1.0507 | 1.0759 | 0.02528 |  | 0.95 | 1.05 | 0.039678 | P12:345:WERE:RENO-WICH-345:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | HI_BNKS2_WF7 | 1.0507 | 1.0759 | 0.02528 |  | 0.95 | 1.05 | 0.039651 | P12:345:WERE:RENO-WICH-345:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | HI_BNKS2_WF7 | 1.0507 | 1.0759 | 0.02528 |  | 0.95 | 1.05 | 0.039657 | P12:345:WERE:RENO-WICH-345:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | HI_BNKS2_WF7 | 1.0507 | 1.0759 | 0.02528 |  | 0.95 | 1.05 | 0.039675 | P12:345:WERE:RENO-WICH-345:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | HI_BNKS2_WF7 | 1.0507 | 1.0759 | 0.02528 |  | 0.95 | 1.05 | 0.03951 | P12:345:WERE:RENO-WICH-345:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | HI_BNKS2_WF7 | 1.0507 | 1.0759 | 0.02528 |  | 0.95 | 1.05 | 0.03951 | P12:345:WERE:RENO-WICH-345:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | HI_BNKS2_WF7 | 1.0507 | 1.0759 | 0.02528 |  | 0.95 | 1.05 | 0.039605 | P12:345:WERE:RENO-WICH-345:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | HI_BNKS2_WF7 | 1.0507 | 1.0759 | 0.02528 |  | 0.95 | 1.05 | 0.039605 | P12:345:WERE:RENO-WICH-345:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | HI_BNKS2_WF7 | 1.0507 | 1.0759 | 0.02528 |  | 0.95 | 1.05 | 0.040961 | P12:345:WERE:RENO-WICH-345:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | HI_BNKS2_WF7 | 1.0507 | 1.0759 | 0.02528 |  | 0.95 | 1.05 | 0.039699 | P12:345:WERE:RENO-WICH-345:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | HI_BNKS2_WF7 | 1.0506 | 1.0759 | 0.025278 |  | 0.95 | 1.05 | 0.069339 | P23:345:WERE:WICH-345-50:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | HI_BNKS2_WF7 | 1.0506 | 1.0759 | 0.025278 |  | 0.95 | 1.05 | 0.051285 | P23:345:WERE:WICH-345-50:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | HI_BNKS2_WF7 | 1.0506 | 1.0759 | 0.025278 |  | 0.95 | 1.05 | 0.048375 | P23:345:WERE:WICH-345-50:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | HI_BNKS2_WF7 | 1.0506 | 1.0759 | 0.025278 |  | 0.95 | 1.05 | 0.048375 | P23:345:WERE:WICH-345-50:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | HI_BNKS2_WF7 | 1.0506 | 1.0759 | 0.025278 |  | 0.95 | 1.05 | 0.052469 | P23:345:WERE:WICH-345-50:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | HI_BNKS2_WF7 | 1.0506 | 1.0759 | 0.025278 |  | 0.95 | 1.05 | 0.052785 | P23:345:WERE:WICH-345-50:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | HI_BNKS2_WF7 | 1.0506 | 1.0759 | 0.025278 |  | 0.95 | 1.05 | 0.052608 | P23:345:WERE:WICH-345-50:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | HI_BNKS2_WF7 | 1.0506 | 1.0759 | 0.025278 |  | 0.95 | 1.05 | 0.057372 | P23:345:WERE:WICH-345-50:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | HI_BNKS2_WF7 | 1.0506 | 1.0759 | 0.025278 |  | 0.95 | 1.05 | 0.057372 | P23:345:WERE:WICH-345-50:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | HI_BNKS2_WF7 | 1.0506 | 1.0759 | 0.025278 |  | 0.95 | 1.05 | 0.052297 | P23:345:WERE:WICH-345-50:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | HI_BNKS2_WF7 | 1.0506 | 1.0759 | 0.025278 |  | 0.95 | 1.05 | 0.052278 | P23:345:WERE:WICH-345-50:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | HI_BNKS2_WF7 | 1.0506 | 1.0759 | 0.025278 |  | 0.95 | 1.05 | 0.051552 | P23:345:WERE:WICH-345-50:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | HI_BNKS2_WF7 | 1.0506 | 1.0759 | 0.025278 |  | 0.95 | 1.05 | 0.051531 | P23:345:WERE:WICH-345-50:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | HI_BNKS2_WF7 | 1.0506 | 1.0759 | 0.025278 |  | 0.95 | 1.05 | 0.051701 | P23:345:WERE:WICH-345-50:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | HI_BNKS2_WF7 | 1.0506 | 1.0759 | 0.025278 |  | 0.95 | 1.05 | 0.051669 | P23:345:WERE:WICH-345-50:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | HI_BNKS2_WF7 | 1.0506 | 1.0759 | 0.025278 |  | 0.95 | 1.05 | 0.05159 | P23:345:WERE:WICH-345-50:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | HI_BNKS2_WF7 | 1.0506 | 1.0759 | 0.025278 |  | 0.95 | 1.05 | 0.052452 | P23:345:WERE:WICH-345-50:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | HI_BNKS2_WF7 | 1.0506 | 1.0759 | 0.025278 |  | 0.95 | 1.05 | 0.052452 | P23:345:WERE:WICH-345-50:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | HI_BNKS2_WF7 | 1.0506 | 1.0759 | 0.025278 |  | 0.95 | 1.05 | 0.051904 | P23:345:WERE:WICH-345-50:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | HI_BNKS2_WF7 | 1.0506 | 1.0759 | 0.025278 |  | 0.95 | 1.05 | 0.051904 | P23:345:WERE:WICH-345-50:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | HI_BNKS2_WF7 | 1.0506 | 1.0759 | 0.025278 |  | 0.95 | 1.05 | 0.040961 | P23:345:WERE:WICH-345-50:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | HI_BNKS2_WF7 | 1.0506 | 1.0759 | 0.025278 |  | 0.95 | 1.05 | 0.051413 | P23:345:WERE:WICH-345-50:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | HI_BNKS2_WF7 | 1.0505 | 1.076 | 0.025494 |  | 0.95 | 1.05 | 0.051941 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | HI_BNKS2_WF7 | 1.0505 | 1.076 | 0.025494 |  | 0.95 | 1.05 | 0.049557 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | HI_BNKS2_WF7 | 1.0505 | 1.076 | 0.025494 |  | 0.95 | 1.05 | 0.048901 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | HI_BNKS2_WF7 | 1.0505 | 1.076 | 0.025494 |  | 0.95 | 1.05 | 0.048901 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | HI_BNKS2_WF7 | 1.0505 | 1.076 | 0.025494 |  | 0.95 | 1.05 | 0.049829 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | HI_BNKS2_WF7 | 1.0505 | 1.076 | 0.025494 |  | 0.95 | 1.05 | 0.049876 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | HI_BNKS2_WF7 | 1.0505 | 1.076 | 0.025494 |  | 0.95 | 1.05 | 0.049857 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | HI_BNKS2_WF7 | 1.0505 | 1.076 | 0.025494 |  | 0.95 | 1.05 | 0.05072 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | HI_BNKS2_WF7 | 1.0505 | 1.076 | 0.025494 |  | 0.95 | 1.05 | 0.05072 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | HI_BNKS2_WF7 | 1.0505 | 1.076 | 0.025494 |  | 0.95 | 1.05 | 0.049781 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | HI_BNKS2_WF7 | 1.0505 | 1.076 | 0.025494 |  | 0.95 | 1.05 | 0.049786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | HI_BNKS2_WF7 | 1.0505 | 1.076 | 0.025494 |  | 0.95 | 1.05 | 0.04962 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | HI_BNKS2_WF7 | 1.0505 | 1.076 | 0.025494 |  | 0.95 | 1.05 | 0.049615 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | HI_BNKS2_WF7 | 1.0505 | 1.076 | 0.025494 |  | 0.95 | 1.05 | 0.049655 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | HI_BNKS2_WF7 | 1.0505 | 1.076 | 0.025494 |  | 0.95 | 1.05 | 0.049648 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | HI_BNKS2_WF7 | 1.0505 | 1.076 | 0.025494 |  | 0.95 | 1.05 | 0.049631 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | HI_BNKS2_WF7 | 1.0505 | 1.076 | 0.025494 |  | 0.95 | 1.05 | 0.049826 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | HI_BNKS2_WF7 | 1.0505 | 1.076 | 0.025494 |  | 0.95 | 1.05 | 0.049826 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | HI_BNKS2_WF7 | 1.0505 | 1.076 | 0.025494 |  | 0.95 | 1.05 | 0.049699 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | HI_BNKS2_WF7 | 1.0505 | 1.076 | 0.025494 |  | 0.95 | 1.05 | 0.049699 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | HI_BNKS2_WF7 | 1.0505 | 1.076 | 0.025494 |  | 0.95 | 1.05 | 0.045602 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | HI_BNKS2_WF7 | 1.0505 | 1.076 | 0.025494 |  | 0.95 | 1.05 | 0.049587 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | HOLLIS 4 | 0.96064 | 0.91629 | -0.044358 |  | 0.92 | 1.05 | 0.081174 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | HOLLIS 4 | 0.96064 | 0.91629 | -0.044358 |  | 0.92 | 1.05 | 0.19645 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | HOLLIS 4 | 0.96064 | 0.91629 | -0.044358 |  | 0.92 | 1.05 | 0.23843 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | HOLLIS 4 | 0.96064 | 0.91629 | -0.044358 |  | 0.92 | 1.05 | 0.23843 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | HOLLIS 4 | 0.96064 | 0.91629 | -0.044358 |  | 0.92 | 1.05 | 0.17969 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | HOLLIS 4 | 0.96064 | 0.91629 | -0.044358 |  | 0.92 | 1.05 | 0.17406 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | HOLLIS 4 | 0.96064 | 0.91629 | -0.044358 |  | 0.92 | 1.05 | 0.17754 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | HOLLIS 4 | 0.96064 | 0.91629 | -0.044358 |  | 0.92 | 1.05 | 0.1303 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | HOLLIS 4 | 0.96064 | 0.91629 | -0.044358 |  | 0.92 | 1.05 | 0.1303 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | HOLLIS 4 | 0.96064 | 0.91629 | -0.044358 |  | 0.92 | 1.05 | 0.18174 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | HOLLIS 4 | 0.96064 | 0.91629 | -0.044358 |  | 0.92 | 1.05 | 0.18244 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | HOLLIS 4 | 0.96064 | 0.91629 | -0.044358 |  | 0.92 | 1.05 | 0.19275 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | HOLLIS 4 | 0.96064 | 0.91629 | -0.044358 |  | 0.92 | 1.05 | 0.19304 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | HOLLIS 4 | 0.96064 | 0.91629 | -0.044358 |  | 0.92 | 1.05 | 0.19068 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | HOLLIS 4 | 0.96064 | 0.91629 | -0.044358 |  | 0.92 | 1.05 | 0.19114 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | HOLLIS 4 | 0.96064 | 0.91629 | -0.044358 |  | 0.92 | 1.05 | 0.19232 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | HOLLIS 4 | 0.96064 | 0.91629 | -0.044358 |  | 0.92 | 1.05 | 0.17996 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | HOLLIS 4 | 0.96064 | 0.91629 | -0.044358 |  | 0.92 | 1.05 | 0.17996 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | HOLLIS 4 | 0.96064 | 0.91629 | -0.044358 |  | 0.92 | 1.05 | 0.18769 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | HOLLIS 4 | 0.96064 | 0.91629 | -0.044358 |  | 0.92 | 1.05 | 0.18769 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | HOLLIS 4 | 0.96064 | 0.91629 | -0.044358 |  | 0.92 | 1.05 | 0.4918 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | HOLLIS 4 | 0.96064 | 0.91629 | -0.044358 |  | 0.92 | 1.05 | 0.1947 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | HOLTP4WT | 0.96146 | 0.9172 | -0.044261 |  | 0.92 | 1.05 | 0.081174 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | HOLTP4WT | 0.96146 | 0.9172 | -0.044261 |  | 0.92 | 1.05 | 0.19645 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | HOLTP4WT | 0.96146 | 0.9172 | -0.044261 |  | 0.92 | 1.05 | 0.23843 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | HOLTP4WT | 0.96146 | 0.9172 | -0.044261 |  | 0.92 | 1.05 | 0.23843 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | HOLTP4WT | 0.96146 | 0.9172 | -0.044261 |  | 0.92 | 1.05 | 0.17969 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | HOLTP4WT | 0.96146 | 0.9172 | -0.044261 |  | 0.92 | 1.05 | 0.17406 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | HOLTP4WT | 0.96146 | 0.9172 | -0.044261 |  | 0.92 | 1.05 | 0.17754 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | HOLTP4WT | 0.96146 | 0.9172 | -0.044261 |  | 0.92 | 1.05 | 0.1303 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | HOLTP4WT | 0.96146 | 0.9172 | -0.044261 |  | 0.92 | 1.05 | 0.1303 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | HOLTP4WT | 0.96146 | 0.9172 | -0.044261 |  | 0.92 | 1.05 | 0.18174 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | HOLTP4WT | 0.96146 | 0.9172 | -0.044261 |  | 0.92 | 1.05 | 0.18244 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | HOLTP4WT | 0.96146 | 0.9172 | -0.044261 |  | 0.92 | 1.05 | 0.19275 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | HOLTP4WT | 0.96146 | 0.9172 | -0.044261 |  | 0.92 | 1.05 | 0.19304 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | HOLTP4WT | 0.96146 | 0.9172 | -0.044261 |  | 0.92 | 1.05 | 0.19068 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | HOLTP4WT | 0.96146 | 0.9172 | -0.044261 |  | 0.92 | 1.05 | 0.19114 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | HOLTP4WT | 0.96146 | 0.9172 | -0.044261 |  | 0.92 | 1.05 | 0.19232 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | HOLTP4WT | 0.96146 | 0.9172 | -0.044261 |  | 0.92 | 1.05 | 0.17996 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | HOLTP4WT | 0.96146 | 0.9172 | -0.044261 |  | 0.92 | 1.05 | 0.17996 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | HOLTP4WT | 0.96146 | 0.9172 | -0.044261 |  | 0.92 | 1.05 | 0.18769 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | HOLTP4WT | 0.96146 | 0.9172 | -0.044261 |  | 0.92 | 1.05 | 0.18769 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | HOLTP4WT | 0.96146 | 0.9172 | -0.044261 |  | 0.92 | 1.05 | 0.4918 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | HOLTP4WT | 0.96146 | 0.9172 | -0.044261 |  | 0.92 | 1.05 | 0.1947 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | NP-GLAZIR_G2 | 0.69341 | 0.67079 | -0.022615 |  | 0.9 | 1.05 | 0.081174 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | NP-GLAZIR_G2 | 0.69341 | 0.67079 | -0.022615 |  | 0.9 | 1.05 | 0.19645 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | NP-GLAZIR_G2 | 0.69341 | 0.67079 | -0.022615 |  | 0.9 | 1.05 | 0.23843 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | NP-GLAZIR_G2 | 0.69341 | 0.67079 | -0.022615 |  | 0.9 | 1.05 | 0.23843 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | NP-GLAZIR_G2 | 0.69341 | 0.67079 | -0.022615 |  | 0.9 | 1.05 | 0.17969 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | NP-GLAZIR_G2 | 0.69341 | 0.67079 | -0.022615 |  | 0.9 | 1.05 | 0.17406 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | NP-GLAZIR_G2 | 0.69341 | 0.67079 | -0.022615 |  | 0.9 | 1.05 | 0.17754 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | NP-GLAZIR_G2 | 0.69341 | 0.67079 | -0.022615 |  | 0.9 | 1.05 | 0.1303 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | NP-GLAZIR_G2 | 0.69341 | 0.67079 | -0.022615 |  | 0.9 | 1.05 | 0.1303 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | NP-GLAZIR_G2 | 0.69341 | 0.67079 | -0.022615 |  | 0.9 | 1.05 | 0.18174 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | NP-GLAZIR_G2 | 0.69341 | 0.67079 | -0.022615 |  | 0.9 | 1.05 | 0.18244 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | NP-GLAZIR_G2 | 0.69341 | 0.67079 | -0.022615 |  | 0.9 | 1.05 | 0.19275 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | NP-GLAZIR_G2 | 0.69341 | 0.67079 | -0.022615 |  | 0.9 | 1.05 | 0.19304 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | NP-GLAZIR_G2 | 0.69341 | 0.67079 | -0.022615 |  | 0.9 | 1.05 | 0.19068 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | NP-GLAZIR_G2 | 0.69341 | 0.67079 | -0.022615 |  | 0.9 | 1.05 | 0.19114 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | NP-GLAZIR_G2 | 0.69341 | 0.67079 | -0.022615 |  | 0.9 | 1.05 | 0.19232 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | NP-GLAZIR_G2 | 0.69341 | 0.67079 | -0.022615 |  | 0.9 | 1.05 | 0.17996 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | NP-GLAZIR_G2 | 0.69341 | 0.67079 | -0.022615 |  | 0.9 | 1.05 | 0.17996 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | NP-GLAZIR_G2 | 0.69341 | 0.67079 | -0.022615 |  | 0.9 | 1.05 | 0.18769 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | NP-GLAZIR_G2 | 0.69341 | 0.67079 | -0.022615 |  | 0.9 | 1.05 | 0.18769 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | NP-GLAZIR_G2 | 0.69341 | 0.67079 | -0.022615 |  | 0.9 | 1.05 | 0.4918 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | NP-GLAZIR_G2 | 0.69341 | 0.67079 | -0.022615 |  | 0.9 | 1.05 | 0.1947 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | NP-GLAZIR_G2 | 0.69338 | 0.67084 | -0.022534 |  | 0.9 | 1.05 | 0.081174 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | NP-GLAZIR_G2 | 0.69338 | 0.67084 | -0.022534 |  | 0.9 | 1.05 | 0.19645 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | NP-GLAZIR_G2 | 0.69338 | 0.67084 | -0.022534 |  | 0.9 | 1.05 | 0.23843 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | NP-GLAZIR_G2 | 0.69338 | 0.67084 | -0.022534 |  | 0.9 | 1.05 | 0.23843 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | NP-GLAZIR_G2 | 0.69338 | 0.67084 | -0.022534 |  | 0.9 | 1.05 | 0.17969 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | NP-GLAZIR_G2 | 0.69338 | 0.67084 | -0.022534 |  | 0.9 | 1.05 | 0.17406 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | NP-GLAZIR_G2 | 0.69338 | 0.67084 | -0.022534 |  | 0.9 | 1.05 | 0.17754 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | NP-GLAZIR_G2 | 0.69338 | 0.67084 | -0.022534 |  | 0.9 | 1.05 | 0.1303 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | NP-GLAZIR_G2 | 0.69338 | 0.67084 | -0.022534 |  | 0.9 | 1.05 | 0.1303 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | NP-GLAZIR_G2 | 0.69338 | 0.67084 | -0.022534 |  | 0.9 | 1.05 | 0.18174 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | NP-GLAZIR_G2 | 0.69338 | 0.67084 | -0.022534 |  | 0.9 | 1.05 | 0.18244 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | NP-GLAZIR_G2 | 0.69338 | 0.67084 | -0.022534 |  | 0.9 | 1.05 | 0.19275 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | NP-GLAZIR_G2 | 0.69338 | 0.67084 | -0.022534 |  | 0.9 | 1.05 | 0.19304 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | NP-GLAZIR_G2 | 0.69338 | 0.67084 | -0.022534 |  | 0.9 | 1.05 | 0.19068 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | NP-GLAZIR_G2 | 0.69338 | 0.67084 | -0.022534 |  | 0.9 | 1.05 | 0.19114 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | NP-GLAZIR_G2 | 0.69338 | 0.67084 | -0.022534 |  | 0.9 | 1.05 | 0.19232 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | NP-GLAZIR_G2 | 0.69338 | 0.67084 | -0.022534 |  | 0.9 | 1.05 | 0.17996 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | NP-GLAZIR_G2 | 0.69338 | 0.67084 | -0.022534 |  | 0.9 | 1.05 | 0.17996 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | NP-GLAZIR_G2 | 0.69338 | 0.67084 | -0.022534 |  | 0.9 | 1.05 | 0.18769 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | NP-GLAZIR_G2 | 0.69338 | 0.67084 | -0.022534 |  | 0.9 | 1.05 | 0.18769 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | NP-GLAZIR_G2 | 0.69338 | 0.67084 | -0.022534 |  | 0.9 | 1.05 | 0.4918 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | NP-GLAZIR_G2 | 0.69338 | 0.67084 | -0.022534 |  | 0.9 | 1.05 | 0.1947 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | NP-GLAZIR_G2 | 0.69365 | 0.67129 | -0.022354 |  | 0.9 | 1.05 | 0.081174 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | NP-GLAZIR_G2 | 0.69365 | 0.67129 | -0.022354 |  | 0.9 | 1.05 | 0.19645 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | NP-GLAZIR_G2 | 0.69365 | 0.67129 | -0.022354 |  | 0.9 | 1.05 | 0.23843 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | NP-GLAZIR_G2 | 0.69365 | 0.67129 | -0.022354 |  | 0.9 | 1.05 | 0.23843 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | NP-GLAZIR_G2 | 0.69365 | 0.67129 | -0.022354 |  | 0.9 | 1.05 | 0.17969 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | NP-GLAZIR_G2 | 0.69365 | 0.67129 | -0.022354 |  | 0.9 | 1.05 | 0.17406 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | NP-GLAZIR_G2 | 0.69365 | 0.67129 | -0.022354 |  | 0.9 | 1.05 | 0.17754 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | NP-GLAZIR_G2 | 0.69365 | 0.67129 | -0.022354 |  | 0.9 | 1.05 | 0.1303 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | NP-GLAZIR_G2 | 0.69365 | 0.67129 | -0.022354 |  | 0.9 | 1.05 | 0.1303 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | NP-GLAZIR_G2 | 0.69365 | 0.67129 | -0.022354 |  | 0.9 | 1.05 | 0.18174 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | NP-GLAZIR_G2 | 0.69365 | 0.67129 | -0.022354 |  | 0.9 | 1.05 | 0.18244 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | NP-GLAZIR_G2 | 0.69365 | 0.67129 | -0.022354 |  | 0.9 | 1.05 | 0.19275 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | NP-GLAZIR_G2 | 0.69365 | 0.67129 | -0.022354 |  | 0.9 | 1.05 | 0.19304 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | NP-GLAZIR_G2 | 0.69365 | 0.67129 | -0.022354 |  | 0.9 | 1.05 | 0.19068 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | NP-GLAZIR_G2 | 0.69365 | 0.67129 | -0.022354 |  | 0.9 | 1.05 | 0.19114 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | NP-GLAZIR_G2 | 0.69365 | 0.67129 | -0.022354 |  | 0.9 | 1.05 | 0.19232 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | NP-GLAZIR_G2 | 0.69365 | 0.67129 | -0.022354 |  | 0.9 | 1.05 | 0.17996 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | NP-GLAZIR_G2 | 0.69365 | 0.67129 | -0.022354 |  | 0.9 | 1.05 | 0.17996 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | NP-GLAZIR_G2 | 0.69365 | 0.67129 | -0.022354 |  | 0.9 | 1.05 | 0.18769 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | NP-GLAZIR_G2 | 0.69365 | 0.67129 | -0.022354 |  | 0.9 | 1.05 | 0.18769 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | NP-GLAZIR_G2 | 0.69365 | 0.67129 | -0.022354 |  | 0.9 | 1.05 | 0.4918 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | NP-GLAZIR_G2 | 0.69365 | 0.67129 | -0.022354 |  | 0.9 | 1.05 | 0.1947 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | NP-GLAZIR_G2 | 0.69165 | 0.66169 | -0.029963 |  | 0.9 | 1.05 | 0.081174 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | NP-GLAZIR_G2 | 0.69165 | 0.66169 | -0.029963 |  | 0.9 | 1.05 | 0.19645 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | NP-GLAZIR_G2 | 0.69165 | 0.66169 | -0.029963 |  | 0.9 | 1.05 | 0.23843 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | NP-GLAZIR_G2 | 0.69165 | 0.66169 | -0.029963 |  | 0.9 | 1.05 | 0.23843 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | NP-GLAZIR_G2 | 0.69165 | 0.66169 | -0.029963 |  | 0.9 | 1.05 | 0.17969 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | NP-GLAZIR_G2 | 0.69165 | 0.66169 | -0.029963 |  | 0.9 | 1.05 | 0.17406 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | NP-GLAZIR_G2 | 0.69165 | 0.66169 | -0.029963 |  | 0.9 | 1.05 | 0.17754 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | NP-GLAZIR_G2 | 0.69165 | 0.66169 | -0.029963 |  | 0.9 | 1.05 | 0.1303 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | NP-GLAZIR_G2 | 0.69165 | 0.66169 | -0.029963 |  | 0.9 | 1.05 | 0.1303 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | NP-GLAZIR_G2 | 0.69165 | 0.66169 | -0.029963 |  | 0.9 | 1.05 | 0.18174 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | NP-GLAZIR_G2 | 0.69165 | 0.66169 | -0.029963 |  | 0.9 | 1.05 | 0.18244 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | NP-GLAZIR_G2 | 0.69165 | 0.66169 | -0.029963 |  | 0.9 | 1.05 | 0.19275 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | NP-GLAZIR_G2 | 0.69165 | 0.66169 | -0.029963 |  | 0.9 | 1.05 | 0.19304 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | NP-GLAZIR_G2 | 0.69165 | 0.66169 | -0.029963 |  | 0.9 | 1.05 | 0.19068 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | NP-GLAZIR_G2 | 0.69165 | 0.66169 | -0.029963 |  | 0.9 | 1.05 | 0.19114 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | NP-GLAZIR_G2 | 0.69165 | 0.66169 | -0.029963 |  | 0.9 | 1.05 | 0.19232 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | NP-GLAZIR_G2 | 0.69165 | 0.66169 | -0.029963 |  | 0.9 | 1.05 | 0.17996 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | NP-GLAZIR_G2 | 0.69165 | 0.66169 | -0.029963 |  | 0.9 | 1.05 | 0.17996 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | NP-GLAZIR_G2 | 0.69165 | 0.66169 | -0.029963 |  | 0.9 | 1.05 | 0.18769 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | NP-GLAZIR_G2 | 0.69165 | 0.66169 | -0.029963 |  | 0.9 | 1.05 | 0.18769 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | NP-GLAZIR_G2 | 0.69165 | 0.66169 | -0.029963 |  | 0.9 | 1.05 | 0.4918 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | NP-GLAZIR_G2 | 0.69165 | 0.66169 | -0.029963 |  | 0.9 | 1.05 | 0.1947 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | NP-GLAZIR_G2 | 0.69335 | 0.67078 | -0.022568 |  | 0.9 | 1.05 | 0.081174 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | NP-GLAZIR_G2 | 0.69335 | 0.67078 | -0.022568 |  | 0.9 | 1.05 | 0.19645 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | NP-GLAZIR_G2 | 0.69335 | 0.67078 | -0.022568 |  | 0.9 | 1.05 | 0.23843 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | NP-GLAZIR_G2 | 0.69335 | 0.67078 | -0.022568 |  | 0.9 | 1.05 | 0.23843 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | NP-GLAZIR_G2 | 0.69335 | 0.67078 | -0.022568 |  | 0.9 | 1.05 | 0.17969 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | NP-GLAZIR_G2 | 0.69335 | 0.67078 | -0.022568 |  | 0.9 | 1.05 | 0.17406 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | NP-GLAZIR_G2 | 0.69335 | 0.67078 | -0.022568 |  | 0.9 | 1.05 | 0.17754 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | NP-GLAZIR_G2 | 0.69335 | 0.67078 | -0.022568 |  | 0.9 | 1.05 | 0.1303 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | NP-GLAZIR_G2 | 0.69335 | 0.67078 | -0.022568 |  | 0.9 | 1.05 | 0.1303 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | NP-GLAZIR_G2 | 0.69335 | 0.67078 | -0.022568 |  | 0.9 | 1.05 | 0.18174 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | NP-GLAZIR_G2 | 0.69335 | 0.67078 | -0.022568 |  | 0.9 | 1.05 | 0.18244 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | NP-GLAZIR_G2 | 0.69335 | 0.67078 | -0.022568 |  | 0.9 | 1.05 | 0.19275 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | NP-GLAZIR_G2 | 0.69335 | 0.67078 | -0.022568 |  | 0.9 | 1.05 | 0.19304 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | NP-GLAZIR_G2 | 0.69335 | 0.67078 | -0.022568 |  | 0.9 | 1.05 | 0.19068 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | NP-GLAZIR_G2 | 0.69335 | 0.67078 | -0.022568 |  | 0.9 | 1.05 | 0.19114 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | NP-GLAZIR_G2 | 0.69335 | 0.67078 | -0.022568 |  | 0.9 | 1.05 | 0.19232 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | NP-GLAZIR_G2 | 0.69335 | 0.67078 | -0.022568 |  | 0.9 | 1.05 | 0.17996 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | NP-GLAZIR_G2 | 0.69335 | 0.67078 | -0.022568 |  | 0.9 | 1.05 | 0.17996 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | NP-GLAZIR_G2 | 0.69335 | 0.67078 | -0.022568 |  | 0.9 | 1.05 | 0.18769 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | NP-GLAZIR_G2 | 0.69335 | 0.67078 | -0.022568 |  | 0.9 | 1.05 | 0.18769 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | NP-GLAZIR_G2 | 0.69335 | 0.67078 | -0.022568 |  | 0.9 | 1.05 | 0.4918 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | NP-GLAZIR_G2 | 0.69335 | 0.67078 | -0.022568 |  | 0.9 | 1.05 | 0.1947 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | NP-LIPSCOMB2 | 0.6561 | 0.6326 | -0.023503 |  | 0.9 | 1.05 | 0.081174 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | NP-LIPSCOMB2 | 0.6561 | 0.6326 | -0.023503 |  | 0.9 | 1.05 | 0.19645 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | NP-LIPSCOMB2 | 0.6561 | 0.6326 | -0.023503 |  | 0.9 | 1.05 | 0.23843 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | NP-LIPSCOMB2 | 0.6561 | 0.6326 | -0.023503 |  | 0.9 | 1.05 | 0.23843 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | NP-LIPSCOMB2 | 0.6561 | 0.6326 | -0.023503 |  | 0.9 | 1.05 | 0.17969 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | NP-LIPSCOMB2 | 0.6561 | 0.6326 | -0.023503 |  | 0.9 | 1.05 | 0.17406 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | NP-LIPSCOMB2 | 0.6561 | 0.6326 | -0.023503 |  | 0.9 | 1.05 | 0.17754 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | NP-LIPSCOMB2 | 0.6561 | 0.6326 | -0.023503 |  | 0.9 | 1.05 | 0.1303 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | NP-LIPSCOMB2 | 0.6561 | 0.6326 | -0.023503 |  | 0.9 | 1.05 | 0.1303 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | NP-LIPSCOMB2 | 0.6561 | 0.6326 | -0.023503 |  | 0.9 | 1.05 | 0.18174 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | NP-LIPSCOMB2 | 0.6561 | 0.6326 | -0.023503 |  | 0.9 | 1.05 | 0.18244 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | NP-LIPSCOMB2 | 0.6561 | 0.6326 | -0.023503 |  | 0.9 | 1.05 | 0.19275 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | NP-LIPSCOMB2 | 0.6561 | 0.6326 | -0.023503 |  | 0.9 | 1.05 | 0.19304 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | NP-LIPSCOMB2 | 0.6561 | 0.6326 | -0.023503 |  | 0.9 | 1.05 | 0.19068 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | NP-LIPSCOMB2 | 0.6561 | 0.6326 | -0.023503 |  | 0.9 | 1.05 | 0.19114 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | NP-LIPSCOMB2 | 0.6561 | 0.6326 | -0.023503 |  | 0.9 | 1.05 | 0.19232 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | NP-LIPSCOMB2 | 0.6561 | 0.6326 | -0.023503 |  | 0.9 | 1.05 | 0.17996 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | NP-LIPSCOMB2 | 0.6561 | 0.6326 | -0.023503 |  | 0.9 | 1.05 | 0.17996 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | NP-LIPSCOMB2 | 0.6561 | 0.6326 | -0.023503 |  | 0.9 | 1.05 | 0.18769 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | NP-LIPSCOMB2 | 0.6561 | 0.6326 | -0.023503 |  | 0.9 | 1.05 | 0.18769 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | NP-LIPSCOMB2 | 0.6561 | 0.6326 | -0.023503 |  | 0.9 | 1.05 | 0.4918 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | NP-LIPSCOMB2 | 0.6561 | 0.6326 | -0.023503 |  | 0.9 | 1.05 | 0.1947 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | NP-LIPSCOMB2 | 0.65607 | 0.63265 | -0.023419 |  | 0.9 | 1.05 | 0.081174 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | NP-LIPSCOMB2 | 0.65607 | 0.63265 | -0.023419 |  | 0.9 | 1.05 | 0.19645 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | NP-LIPSCOMB2 | 0.65607 | 0.63265 | -0.023419 |  | 0.9 | 1.05 | 0.23843 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | NP-LIPSCOMB2 | 0.65607 | 0.63265 | -0.023419 |  | 0.9 | 1.05 | 0.23843 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | NP-LIPSCOMB2 | 0.65607 | 0.63265 | -0.023419 |  | 0.9 | 1.05 | 0.17969 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | NP-LIPSCOMB2 | 0.65607 | 0.63265 | -0.023419 |  | 0.9 | 1.05 | 0.17406 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | NP-LIPSCOMB2 | 0.65607 | 0.63265 | -0.023419 |  | 0.9 | 1.05 | 0.17754 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | NP-LIPSCOMB2 | 0.65607 | 0.63265 | -0.023419 |  | 0.9 | 1.05 | 0.1303 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | NP-LIPSCOMB2 | 0.65607 | 0.63265 | -0.023419 |  | 0.9 | 1.05 | 0.1303 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | NP-LIPSCOMB2 | 0.65607 | 0.63265 | -0.023419 |  | 0.9 | 1.05 | 0.18174 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | NP-LIPSCOMB2 | 0.65607 | 0.63265 | -0.023419 |  | 0.9 | 1.05 | 0.18244 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | NP-LIPSCOMB2 | 0.65607 | 0.63265 | -0.023419 |  | 0.9 | 1.05 | 0.19275 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | NP-LIPSCOMB2 | 0.65607 | 0.63265 | -0.023419 |  | 0.9 | 1.05 | 0.19304 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | NP-LIPSCOMB2 | 0.65607 | 0.63265 | -0.023419 |  | 0.9 | 1.05 | 0.19068 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | NP-LIPSCOMB2 | 0.65607 | 0.63265 | -0.023419 |  | 0.9 | 1.05 | 0.19114 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | NP-LIPSCOMB2 | 0.65607 | 0.63265 | -0.023419 |  | 0.9 | 1.05 | 0.19232 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | NP-LIPSCOMB2 | 0.65607 | 0.63265 | -0.023419 |  | 0.9 | 1.05 | 0.17996 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | NP-LIPSCOMB2 | 0.65607 | 0.63265 | -0.023419 |  | 0.9 | 1.05 | 0.17996 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | NP-LIPSCOMB2 | 0.65607 | 0.63265 | -0.023419 |  | 0.9 | 1.05 | 0.18769 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | NP-LIPSCOMB2 | 0.65607 | 0.63265 | -0.023419 |  | 0.9 | 1.05 | 0.18769 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | NP-LIPSCOMB2 | 0.65607 | 0.63265 | -0.023419 |  | 0.9 | 1.05 | 0.4918 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | NP-LIPSCOMB2 | 0.65607 | 0.63265 | -0.023419 |  | 0.9 | 1.05 | 0.1947 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | NP-LIPSCOMB2 | 0.65636 | 0.63312 | -0.023234 |  | 0.9 | 1.05 | 0.081174 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | NP-LIPSCOMB2 | 0.65636 | 0.63312 | -0.023234 |  | 0.9 | 1.05 | 0.19645 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | NP-LIPSCOMB2 | 0.65636 | 0.63312 | -0.023234 |  | 0.9 | 1.05 | 0.23843 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | NP-LIPSCOMB2 | 0.65636 | 0.63312 | -0.023234 |  | 0.9 | 1.05 | 0.23843 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | NP-LIPSCOMB2 | 0.65636 | 0.63312 | -0.023234 |  | 0.9 | 1.05 | 0.17969 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | NP-LIPSCOMB2 | 0.65636 | 0.63312 | -0.023234 |  | 0.9 | 1.05 | 0.17406 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | NP-LIPSCOMB2 | 0.65636 | 0.63312 | -0.023234 |  | 0.9 | 1.05 | 0.17754 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | NP-LIPSCOMB2 | 0.65636 | 0.63312 | -0.023234 |  | 0.9 | 1.05 | 0.1303 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | NP-LIPSCOMB2 | 0.65636 | 0.63312 | -0.023234 |  | 0.9 | 1.05 | 0.1303 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | NP-LIPSCOMB2 | 0.65636 | 0.63312 | -0.023234 |  | 0.9 | 1.05 | 0.18174 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | NP-LIPSCOMB2 | 0.65636 | 0.63312 | -0.023234 |  | 0.9 | 1.05 | 0.18244 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | NP-LIPSCOMB2 | 0.65636 | 0.63312 | -0.023234 |  | 0.9 | 1.05 | 0.19275 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | NP-LIPSCOMB2 | 0.65636 | 0.63312 | -0.023234 |  | 0.9 | 1.05 | 0.19304 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | NP-LIPSCOMB2 | 0.65636 | 0.63312 | -0.023234 |  | 0.9 | 1.05 | 0.19068 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | NP-LIPSCOMB2 | 0.65636 | 0.63312 | -0.023234 |  | 0.9 | 1.05 | 0.19114 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | NP-LIPSCOMB2 | 0.65636 | 0.63312 | -0.023234 |  | 0.9 | 1.05 | 0.19232 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | NP-LIPSCOMB2 | 0.65636 | 0.63312 | -0.023234 |  | 0.9 | 1.05 | 0.17996 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | NP-LIPSCOMB2 | 0.65636 | 0.63312 | -0.023234 |  | 0.9 | 1.05 | 0.17996 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | NP-LIPSCOMB2 | 0.65636 | 0.63312 | -0.023234 |  | 0.9 | 1.05 | 0.18769 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | NP-LIPSCOMB2 | 0.65636 | 0.63312 | -0.023234 |  | 0.9 | 1.05 | 0.18769 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | NP-LIPSCOMB2 | 0.65636 | 0.63312 | -0.023234 |  | 0.9 | 1.05 | 0.4918 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | NP-LIPSCOMB2 | 0.65636 | 0.63312 | -0.023234 |  | 0.9 | 1.05 | 0.1947 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | NP-LIPSCOMB2 | 0.65427 | 0.62318 | -0.03109 |  | 0.9 | 1.05 | 0.081174 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | NP-LIPSCOMB2 | 0.65427 | 0.62318 | -0.03109 |  | 0.9 | 1.05 | 0.19645 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | NP-LIPSCOMB2 | 0.65427 | 0.62318 | -0.03109 |  | 0.9 | 1.05 | 0.23843 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | NP-LIPSCOMB2 | 0.65427 | 0.62318 | -0.03109 |  | 0.9 | 1.05 | 0.23843 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | NP-LIPSCOMB2 | 0.65427 | 0.62318 | -0.03109 |  | 0.9 | 1.05 | 0.17969 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | NP-LIPSCOMB2 | 0.65427 | 0.62318 | -0.03109 |  | 0.9 | 1.05 | 0.17406 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | NP-LIPSCOMB2 | 0.65427 | 0.62318 | -0.03109 |  | 0.9 | 1.05 | 0.17754 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | NP-LIPSCOMB2 | 0.65427 | 0.62318 | -0.03109 |  | 0.9 | 1.05 | 0.1303 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | NP-LIPSCOMB2 | 0.65427 | 0.62318 | -0.03109 |  | 0.9 | 1.05 | 0.1303 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | NP-LIPSCOMB2 | 0.65427 | 0.62318 | -0.03109 |  | 0.9 | 1.05 | 0.18174 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | NP-LIPSCOMB2 | 0.65427 | 0.62318 | -0.03109 |  | 0.9 | 1.05 | 0.18244 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | NP-LIPSCOMB2 | 0.65427 | 0.62318 | -0.03109 |  | 0.9 | 1.05 | 0.19275 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | NP-LIPSCOMB2 | 0.65427 | 0.62318 | -0.03109 |  | 0.9 | 1.05 | 0.19304 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | NP-LIPSCOMB2 | 0.65427 | 0.62318 | -0.03109 |  | 0.9 | 1.05 | 0.19068 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | NP-LIPSCOMB2 | 0.65427 | 0.62318 | -0.03109 |  | 0.9 | 1.05 | 0.19114 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | NP-LIPSCOMB2 | 0.65427 | 0.62318 | -0.03109 |  | 0.9 | 1.05 | 0.19232 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | NP-LIPSCOMB2 | 0.65427 | 0.62318 | -0.03109 |  | 0.9 | 1.05 | 0.17996 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | NP-LIPSCOMB2 | 0.65427 | 0.62318 | -0.03109 |  | 0.9 | 1.05 | 0.17996 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | NP-LIPSCOMB2 | 0.65427 | 0.62318 | -0.03109 |  | 0.9 | 1.05 | 0.18769 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | NP-LIPSCOMB2 | 0.65427 | 0.62318 | -0.03109 |  | 0.9 | 1.05 | 0.18769 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | NP-LIPSCOMB2 | 0.65427 | 0.62318 | -0.03109 |  | 0.9 | 1.05 | 0.4918 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | NP-LIPSCOMB2 | 0.65427 | 0.62318 | -0.03109 |  | 0.9 | 1.05 | 0.1947 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | NP-LIPSCOMB2 | 0.65605 | 0.63259 | -0.023454 |  | 0.9 | 1.05 | 0.081174 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | NP-LIPSCOMB2 | 0.65605 | 0.63259 | -0.023454 |  | 0.9 | 1.05 | 0.19645 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | NP-LIPSCOMB2 | 0.65605 | 0.63259 | -0.023454 |  | 0.9 | 1.05 | 0.23843 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | NP-LIPSCOMB2 | 0.65605 | 0.63259 | -0.023454 |  | 0.9 | 1.05 | 0.23843 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | NP-LIPSCOMB2 | 0.65605 | 0.63259 | -0.023454 |  | 0.9 | 1.05 | 0.17969 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | NP-LIPSCOMB2 | 0.65605 | 0.63259 | -0.023454 |  | 0.9 | 1.05 | 0.17406 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | NP-LIPSCOMB2 | 0.65605 | 0.63259 | -0.023454 |  | 0.9 | 1.05 | 0.17754 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | NP-LIPSCOMB2 | 0.65605 | 0.63259 | -0.023454 |  | 0.9 | 1.05 | 0.1303 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | NP-LIPSCOMB2 | 0.65605 | 0.63259 | -0.023454 |  | 0.9 | 1.05 | 0.1303 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | NP-LIPSCOMB2 | 0.65605 | 0.63259 | -0.023454 |  | 0.9 | 1.05 | 0.18174 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | NP-LIPSCOMB2 | 0.65605 | 0.63259 | -0.023454 |  | 0.9 | 1.05 | 0.18244 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | NP-LIPSCOMB2 | 0.65605 | 0.63259 | -0.023454 |  | 0.9 | 1.05 | 0.19275 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | NP-LIPSCOMB2 | 0.65605 | 0.63259 | -0.023454 |  | 0.9 | 1.05 | 0.19304 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | NP-LIPSCOMB2 | 0.65605 | 0.63259 | -0.023454 |  | 0.9 | 1.05 | 0.19068 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | NP-LIPSCOMB2 | 0.65605 | 0.63259 | -0.023454 |  | 0.9 | 1.05 | 0.19114 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | NP-LIPSCOMB2 | 0.65605 | 0.63259 | -0.023454 |  | 0.9 | 1.05 | 0.19232 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | NP-LIPSCOMB2 | 0.65605 | 0.63259 | -0.023454 |  | 0.9 | 1.05 | 0.17996 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | NP-LIPSCOMB2 | 0.65605 | 0.63259 | -0.023454 |  | 0.9 | 1.05 | 0.17996 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | NP-LIPSCOMB2 | 0.65605 | 0.63259 | -0.023454 |  | 0.9 | 1.05 | 0.18769 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | NP-LIPSCOMB2 | 0.65605 | 0.63259 | -0.023454 |  | 0.9 | 1.05 | 0.18769 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | NP-LIPSCOMB2 | 0.65605 | 0.63259 | -0.023454 |  | 0.9 | 1.05 | 0.4918 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | NP-LIPSCOMB2 | 0.65605 | 0.63259 | -0.023454 |  | 0.9 | 1.05 | 0.1947 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | NP-LIPS_SHA2 | 0.6561 | 0.6326 | -0.023503 |  | 0.9 | 1.05 | 0.081174 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | NP-LIPS_SHA2 | 0.6561 | 0.6326 | -0.023503 |  | 0.9 | 1.05 | 0.19645 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | NP-LIPS_SHA2 | 0.6561 | 0.6326 | -0.023503 |  | 0.9 | 1.05 | 0.23843 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | NP-LIPS_SHA2 | 0.6561 | 0.6326 | -0.023503 |  | 0.9 | 1.05 | 0.23843 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | NP-LIPS_SHA2 | 0.6561 | 0.6326 | -0.023503 |  | 0.9 | 1.05 | 0.17969 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | NP-LIPS_SHA2 | 0.6561 | 0.6326 | -0.023503 |  | 0.9 | 1.05 | 0.17406 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | NP-LIPS_SHA2 | 0.6561 | 0.6326 | -0.023503 |  | 0.9 | 1.05 | 0.17754 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | NP-LIPS_SHA2 | 0.6561 | 0.6326 | -0.023503 |  | 0.9 | 1.05 | 0.1303 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | NP-LIPS_SHA2 | 0.6561 | 0.6326 | -0.023503 |  | 0.9 | 1.05 | 0.1303 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | NP-LIPS_SHA2 | 0.6561 | 0.6326 | -0.023503 |  | 0.9 | 1.05 | 0.18174 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | NP-LIPS_SHA2 | 0.6561 | 0.6326 | -0.023503 |  | 0.9 | 1.05 | 0.18244 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | NP-LIPS_SHA2 | 0.6561 | 0.6326 | -0.023503 |  | 0.9 | 1.05 | 0.19275 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | NP-LIPS_SHA2 | 0.6561 | 0.6326 | -0.023503 |  | 0.9 | 1.05 | 0.19304 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | NP-LIPS_SHA2 | 0.6561 | 0.6326 | -0.023503 |  | 0.9 | 1.05 | 0.19068 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | NP-LIPS_SHA2 | 0.6561 | 0.6326 | -0.023503 |  | 0.9 | 1.05 | 0.19114 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | NP-LIPS_SHA2 | 0.6561 | 0.6326 | -0.023503 |  | 0.9 | 1.05 | 0.19232 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | NP-LIPS_SHA2 | 0.6561 | 0.6326 | -0.023503 |  | 0.9 | 1.05 | 0.17996 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | NP-LIPS_SHA2 | 0.6561 | 0.6326 | -0.023503 |  | 0.9 | 1.05 | 0.17996 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | NP-LIPS_SHA2 | 0.6561 | 0.6326 | -0.023503 |  | 0.9 | 1.05 | 0.18769 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | NP-LIPS_SHA2 | 0.6561 | 0.6326 | -0.023503 |  | 0.9 | 1.05 | 0.18769 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | NP-LIPS_SHA2 | 0.6561 | 0.6326 | -0.023503 |  | 0.9 | 1.05 | 0.4918 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | NP-LIPS_SHA2 | 0.6561 | 0.6326 | -0.023503 |  | 0.9 | 1.05 | 0.1947 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | NP-LIPS_SHA2 | 0.65607 | 0.63265 | -0.023419 |  | 0.9 | 1.05 | 0.081174 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | NP-LIPS_SHA2 | 0.65607 | 0.63265 | -0.023419 |  | 0.9 | 1.05 | 0.19645 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | NP-LIPS_SHA2 | 0.65607 | 0.63265 | -0.023419 |  | 0.9 | 1.05 | 0.23843 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | NP-LIPS_SHA2 | 0.65607 | 0.63265 | -0.023419 |  | 0.9 | 1.05 | 0.23843 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | NP-LIPS_SHA2 | 0.65607 | 0.63265 | -0.023419 |  | 0.9 | 1.05 | 0.17969 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | NP-LIPS_SHA2 | 0.65607 | 0.63265 | -0.023419 |  | 0.9 | 1.05 | 0.17406 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | NP-LIPS_SHA2 | 0.65607 | 0.63265 | -0.023419 |  | 0.9 | 1.05 | 0.17754 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | NP-LIPS_SHA2 | 0.65607 | 0.63265 | -0.023419 |  | 0.9 | 1.05 | 0.1303 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | NP-LIPS_SHA2 | 0.65607 | 0.63265 | -0.023419 |  | 0.9 | 1.05 | 0.1303 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | NP-LIPS_SHA2 | 0.65607 | 0.63265 | -0.023419 |  | 0.9 | 1.05 | 0.18174 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | NP-LIPS_SHA2 | 0.65607 | 0.63265 | -0.023419 |  | 0.9 | 1.05 | 0.18244 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | NP-LIPS_SHA2 | 0.65607 | 0.63265 | -0.023419 |  | 0.9 | 1.05 | 0.19275 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | NP-LIPS_SHA2 | 0.65607 | 0.63265 | -0.023419 |  | 0.9 | 1.05 | 0.19304 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | NP-LIPS_SHA2 | 0.65607 | 0.63265 | -0.023419 |  | 0.9 | 1.05 | 0.19068 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | NP-LIPS_SHA2 | 0.65607 | 0.63265 | -0.023419 |  | 0.9 | 1.05 | 0.19114 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | NP-LIPS_SHA2 | 0.65607 | 0.63265 | -0.023419 |  | 0.9 | 1.05 | 0.19232 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | NP-LIPS_SHA2 | 0.65607 | 0.63265 | -0.023419 |  | 0.9 | 1.05 | 0.17996 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | NP-LIPS_SHA2 | 0.65607 | 0.63265 | -0.023419 |  | 0.9 | 1.05 | 0.17996 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | NP-LIPS_SHA2 | 0.65607 | 0.63265 | -0.023419 |  | 0.9 | 1.05 | 0.18769 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | NP-LIPS_SHA2 | 0.65607 | 0.63265 | -0.023419 |  | 0.9 | 1.05 | 0.18769 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | NP-LIPS_SHA2 | 0.65607 | 0.63265 | -0.023419 |  | 0.9 | 1.05 | 0.4918 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | NP-LIPS_SHA2 | 0.65607 | 0.63265 | -0.023419 |  | 0.9 | 1.05 | 0.1947 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | NP-LIPS_SHA2 | 0.65636 | 0.63312 | -0.023234 |  | 0.9 | 1.05 | 0.081174 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | NP-LIPS_SHA2 | 0.65636 | 0.63312 | -0.023234 |  | 0.9 | 1.05 | 0.19645 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | NP-LIPS_SHA2 | 0.65636 | 0.63312 | -0.023234 |  | 0.9 | 1.05 | 0.23843 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | NP-LIPS_SHA2 | 0.65636 | 0.63312 | -0.023234 |  | 0.9 | 1.05 | 0.23843 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | NP-LIPS_SHA2 | 0.65636 | 0.63312 | -0.023234 |  | 0.9 | 1.05 | 0.17969 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | NP-LIPS_SHA2 | 0.65636 | 0.63312 | -0.023234 |  | 0.9 | 1.05 | 0.17406 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | NP-LIPS_SHA2 | 0.65636 | 0.63312 | -0.023234 |  | 0.9 | 1.05 | 0.17754 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | NP-LIPS_SHA2 | 0.65636 | 0.63312 | -0.023234 |  | 0.9 | 1.05 | 0.1303 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | NP-LIPS_SHA2 | 0.65636 | 0.63312 | -0.023234 |  | 0.9 | 1.05 | 0.1303 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | NP-LIPS_SHA2 | 0.65636 | 0.63312 | -0.023234 |  | 0.9 | 1.05 | 0.18174 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | NP-LIPS_SHA2 | 0.65636 | 0.63312 | -0.023234 |  | 0.9 | 1.05 | 0.18244 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | NP-LIPS_SHA2 | 0.65636 | 0.63312 | -0.023234 |  | 0.9 | 1.05 | 0.19275 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | NP-LIPS_SHA2 | 0.65636 | 0.63312 | -0.023234 |  | 0.9 | 1.05 | 0.19304 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | NP-LIPS_SHA2 | 0.65636 | 0.63312 | -0.023234 |  | 0.9 | 1.05 | 0.19068 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | NP-LIPS_SHA2 | 0.65636 | 0.63312 | -0.023234 |  | 0.9 | 1.05 | 0.19114 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | NP-LIPS_SHA2 | 0.65636 | 0.63312 | -0.023234 |  | 0.9 | 1.05 | 0.19232 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | NP-LIPS_SHA2 | 0.65636 | 0.63312 | -0.023234 |  | 0.9 | 1.05 | 0.17996 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | NP-LIPS_SHA2 | 0.65636 | 0.63312 | -0.023234 |  | 0.9 | 1.05 | 0.17996 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | NP-LIPS_SHA2 | 0.65636 | 0.63312 | -0.023234 |  | 0.9 | 1.05 | 0.18769 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | NP-LIPS_SHA2 | 0.65636 | 0.63312 | -0.023234 |  | 0.9 | 1.05 | 0.18769 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | NP-LIPS_SHA2 | 0.65636 | 0.63312 | -0.023234 |  | 0.9 | 1.05 | 0.4918 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | NP-LIPS_SHA2 | 0.65636 | 0.63312 | -0.023234 |  | 0.9 | 1.05 | 0.1947 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | NP-LIPS_SHA2 | 0.65427 | 0.62318 | -0.03109 |  | 0.9 | 1.05 | 0.081174 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | NP-LIPS_SHA2 | 0.65427 | 0.62318 | -0.03109 |  | 0.9 | 1.05 | 0.19645 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | NP-LIPS_SHA2 | 0.65427 | 0.62318 | -0.03109 |  | 0.9 | 1.05 | 0.23843 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | NP-LIPS_SHA2 | 0.65427 | 0.62318 | -0.03109 |  | 0.9 | 1.05 | 0.23843 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | NP-LIPS_SHA2 | 0.65427 | 0.62318 | -0.03109 |  | 0.9 | 1.05 | 0.17969 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | NP-LIPS_SHA2 | 0.65427 | 0.62318 | -0.03109 |  | 0.9 | 1.05 | 0.17406 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | NP-LIPS_SHA2 | 0.65427 | 0.62318 | -0.03109 |  | 0.9 | 1.05 | 0.17754 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | NP-LIPS_SHA2 | 0.65427 | 0.62318 | -0.03109 |  | 0.9 | 1.05 | 0.1303 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | NP-LIPS_SHA2 | 0.65427 | 0.62318 | -0.03109 |  | 0.9 | 1.05 | 0.1303 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | NP-LIPS_SHA2 | 0.65427 | 0.62318 | -0.03109 |  | 0.9 | 1.05 | 0.18174 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | NP-LIPS_SHA2 | 0.65427 | 0.62318 | -0.03109 |  | 0.9 | 1.05 | 0.18244 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | NP-LIPS_SHA2 | 0.65427 | 0.62318 | -0.03109 |  | 0.9 | 1.05 | 0.19275 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | NP-LIPS_SHA2 | 0.65427 | 0.62318 | -0.03109 |  | 0.9 | 1.05 | 0.19304 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | NP-LIPS_SHA2 | 0.65427 | 0.62318 | -0.03109 |  | 0.9 | 1.05 | 0.19068 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | NP-LIPS_SHA2 | 0.65427 | 0.62318 | -0.03109 |  | 0.9 | 1.05 | 0.19114 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | NP-LIPS_SHA2 | 0.65427 | 0.62318 | -0.03109 |  | 0.9 | 1.05 | 0.19232 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | NP-LIPS_SHA2 | 0.65427 | 0.62318 | -0.03109 |  | 0.9 | 1.05 | 0.17996 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | NP-LIPS_SHA2 | 0.65427 | 0.62318 | -0.03109 |  | 0.9 | 1.05 | 0.17996 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | NP-LIPS_SHA2 | 0.65427 | 0.62318 | -0.03109 |  | 0.9 | 1.05 | 0.18769 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | NP-LIPS_SHA2 | 0.65427 | 0.62318 | -0.03109 |  | 0.9 | 1.05 | 0.18769 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | NP-LIPS_SHA2 | 0.65427 | 0.62318 | -0.03109 |  | 0.9 | 1.05 | 0.4918 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | NP-LIPS_SHA2 | 0.65427 | 0.62318 | -0.03109 |  | 0.9 | 1.05 | 0.1947 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | NP-LIPS_SHA2 | 0.65605 | 0.63259 | -0.023454 |  | 0.9 | 1.05 | 0.081174 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | NP-LIPS_SHA2 | 0.65605 | 0.63259 | -0.023454 |  | 0.9 | 1.05 | 0.19645 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | NP-LIPS_SHA2 | 0.65605 | 0.63259 | -0.023454 |  | 0.9 | 1.05 | 0.23843 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | NP-LIPS_SHA2 | 0.65605 | 0.63259 | -0.023454 |  | 0.9 | 1.05 | 0.23843 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | NP-LIPS_SHA2 | 0.65605 | 0.63259 | -0.023454 |  | 0.9 | 1.05 | 0.17969 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | NP-LIPS_SHA2 | 0.65605 | 0.63259 | -0.023454 |  | 0.9 | 1.05 | 0.17406 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | NP-LIPS_SHA2 | 0.65605 | 0.63259 | -0.023454 |  | 0.9 | 1.05 | 0.17754 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | NP-LIPS_SHA2 | 0.65605 | 0.63259 | -0.023454 |  | 0.9 | 1.05 | 0.1303 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | NP-LIPS_SHA2 | 0.65605 | 0.63259 | -0.023454 |  | 0.9 | 1.05 | 0.1303 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | NP-LIPS_SHA2 | 0.65605 | 0.63259 | -0.023454 |  | 0.9 | 1.05 | 0.18174 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | NP-LIPS_SHA2 | 0.65605 | 0.63259 | -0.023454 |  | 0.9 | 1.05 | 0.18244 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | NP-LIPS_SHA2 | 0.65605 | 0.63259 | -0.023454 |  | 0.9 | 1.05 | 0.19275 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | NP-LIPS_SHA2 | 0.65605 | 0.63259 | -0.023454 |  | 0.9 | 1.05 | 0.19304 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | NP-LIPS_SHA2 | 0.65605 | 0.63259 | -0.023454 |  | 0.9 | 1.05 | 0.19068 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | NP-LIPS_SHA2 | 0.65605 | 0.63259 | -0.023454 |  | 0.9 | 1.05 | 0.19114 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | NP-LIPS_SHA2 | 0.65605 | 0.63259 | -0.023454 |  | 0.9 | 1.05 | 0.19232 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | NP-LIPS_SHA2 | 0.65605 | 0.63259 | -0.023454 |  | 0.9 | 1.05 | 0.17996 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | NP-LIPS_SHA2 | 0.65605 | 0.63259 | -0.023454 |  | 0.9 | 1.05 | 0.17996 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | NP-LIPS_SHA2 | 0.65605 | 0.63259 | -0.023454 |  | 0.9 | 1.05 | 0.18769 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | NP-LIPS_SHA2 | 0.65605 | 0.63259 | -0.023454 |  | 0.9 | 1.05 | 0.18769 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | NP-LIPS_SHA2 | 0.65605 | 0.63259 | -0.023454 |  | 0.9 | 1.05 | 0.4918 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | NP-LIPS_SHA2 | 0.65605 | 0.63259 | -0.023454 |  | 0.9 | 1.05 | 0.1947 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | NP-LUCKY_CR2 | 0.78019 | 0.75995 | -0.020241 |  | 0.9 | 1.05 | 0.081174 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | NP-LUCKY_CR2 | 0.78019 | 0.75995 | -0.020241 |  | 0.9 | 1.05 | 0.19645 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | NP-LUCKY_CR2 | 0.78019 | 0.75995 | -0.020241 |  | 0.9 | 1.05 | 0.23843 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | NP-LUCKY_CR2 | 0.78019 | 0.75995 | -0.020241 |  | 0.9 | 1.05 | 0.23843 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | NP-LUCKY_CR2 | 0.78019 | 0.75995 | -0.020241 |  | 0.9 | 1.05 | 0.17969 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | NP-LUCKY_CR2 | 0.78019 | 0.75995 | -0.020241 |  | 0.9 | 1.05 | 0.17406 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | NP-LUCKY_CR2 | 0.78019 | 0.75995 | -0.020241 |  | 0.9 | 1.05 | 0.17754 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | NP-LUCKY_CR2 | 0.78019 | 0.75995 | -0.020241 |  | 0.9 | 1.05 | 0.1303 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | NP-LUCKY_CR2 | 0.78019 | 0.75995 | -0.020241 |  | 0.9 | 1.05 | 0.1303 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | NP-LUCKY_CR2 | 0.78019 | 0.75995 | -0.020241 |  | 0.9 | 1.05 | 0.18174 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | NP-LUCKY_CR2 | 0.78019 | 0.75995 | -0.020241 |  | 0.9 | 1.05 | 0.18244 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | NP-LUCKY_CR2 | 0.78019 | 0.75995 | -0.020241 |  | 0.9 | 1.05 | 0.19275 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | NP-LUCKY_CR2 | 0.78019 | 0.75995 | -0.020241 |  | 0.9 | 1.05 | 0.19304 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | NP-LUCKY_CR2 | 0.78019 | 0.75995 | -0.020241 |  | 0.9 | 1.05 | 0.19068 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | NP-LUCKY_CR2 | 0.78019 | 0.75995 | -0.020241 |  | 0.9 | 1.05 | 0.19114 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | NP-LUCKY_CR2 | 0.78019 | 0.75995 | -0.020241 |  | 0.9 | 1.05 | 0.19232 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | NP-LUCKY_CR2 | 0.78019 | 0.75995 | -0.020241 |  | 0.9 | 1.05 | 0.17996 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | NP-LUCKY_CR2 | 0.78019 | 0.75995 | -0.020241 |  | 0.9 | 1.05 | 0.17996 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | NP-LUCKY_CR2 | 0.78019 | 0.75995 | -0.020241 |  | 0.9 | 1.05 | 0.18769 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | NP-LUCKY_CR2 | 0.78019 | 0.75995 | -0.020241 |  | 0.9 | 1.05 | 0.18769 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | NP-LUCKY_CR2 | 0.78019 | 0.75995 | -0.020241 |  | 0.9 | 1.05 | 0.4918 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | NP-LUCKY_CR2 | 0.78019 | 0.75995 | -0.020241 |  | 0.9 | 1.05 | 0.1947 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | NP-LUCKY_CR2 | 0.78017 | 0.76 | -0.020168 |  | 0.9 | 1.05 | 0.081174 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | NP-LUCKY_CR2 | 0.78017 | 0.76 | -0.020168 |  | 0.9 | 1.05 | 0.19645 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | NP-LUCKY_CR2 | 0.78017 | 0.76 | -0.020168 |  | 0.9 | 1.05 | 0.23843 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | NP-LUCKY_CR2 | 0.78017 | 0.76 | -0.020168 |  | 0.9 | 1.05 | 0.23843 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | NP-LUCKY_CR2 | 0.78017 | 0.76 | -0.020168 |  | 0.9 | 1.05 | 0.17969 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | NP-LUCKY_CR2 | 0.78017 | 0.76 | -0.020168 |  | 0.9 | 1.05 | 0.17406 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | NP-LUCKY_CR2 | 0.78017 | 0.76 | -0.020168 |  | 0.9 | 1.05 | 0.17754 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | NP-LUCKY_CR2 | 0.78017 | 0.76 | -0.020168 |  | 0.9 | 1.05 | 0.1303 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | NP-LUCKY_CR2 | 0.78017 | 0.76 | -0.020168 |  | 0.9 | 1.05 | 0.1303 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | NP-LUCKY_CR2 | 0.78017 | 0.76 | -0.020168 |  | 0.9 | 1.05 | 0.18174 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | NP-LUCKY_CR2 | 0.78017 | 0.76 | -0.020168 |  | 0.9 | 1.05 | 0.18244 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | NP-LUCKY_CR2 | 0.78017 | 0.76 | -0.020168 |  | 0.9 | 1.05 | 0.19275 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | NP-LUCKY_CR2 | 0.78017 | 0.76 | -0.020168 |  | 0.9 | 1.05 | 0.19304 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | NP-LUCKY_CR2 | 0.78017 | 0.76 | -0.020168 |  | 0.9 | 1.05 | 0.19068 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | NP-LUCKY_CR2 | 0.78017 | 0.76 | -0.020168 |  | 0.9 | 1.05 | 0.19114 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | NP-LUCKY_CR2 | 0.78017 | 0.76 | -0.020168 |  | 0.9 | 1.05 | 0.19232 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | NP-LUCKY_CR2 | 0.78017 | 0.76 | -0.020168 |  | 0.9 | 1.05 | 0.17996 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | NP-LUCKY_CR2 | 0.78017 | 0.76 | -0.020168 |  | 0.9 | 1.05 | 0.17996 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | NP-LUCKY_CR2 | 0.78017 | 0.76 | -0.020168 |  | 0.9 | 1.05 | 0.18769 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | NP-LUCKY_CR2 | 0.78017 | 0.76 | -0.020168 |  | 0.9 | 1.05 | 0.18769 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | NP-LUCKY_CR2 | 0.78017 | 0.76 | -0.020168 |  | 0.9 | 1.05 | 0.4918 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | NP-LUCKY_CR2 | 0.78017 | 0.76 | -0.020168 |  | 0.9 | 1.05 | 0.1947 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | NP-LUCKY_CR2 | 0.78041 | 0.76041 | -0.020001 |  | 0.9 | 1.05 | 0.081174 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | NP-LUCKY_CR2 | 0.78041 | 0.76041 | -0.020001 |  | 0.9 | 1.05 | 0.19645 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | NP-LUCKY_CR2 | 0.78041 | 0.76041 | -0.020001 |  | 0.9 | 1.05 | 0.23843 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | NP-LUCKY_CR2 | 0.78041 | 0.76041 | -0.020001 |  | 0.9 | 1.05 | 0.23843 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | NP-LUCKY_CR2 | 0.78041 | 0.76041 | -0.020001 |  | 0.9 | 1.05 | 0.17969 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | NP-LUCKY_CR2 | 0.78041 | 0.76041 | -0.020001 |  | 0.9 | 1.05 | 0.17406 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | NP-LUCKY_CR2 | 0.78041 | 0.76041 | -0.020001 |  | 0.9 | 1.05 | 0.17754 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | NP-LUCKY_CR2 | 0.78041 | 0.76041 | -0.020001 |  | 0.9 | 1.05 | 0.1303 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | NP-LUCKY_CR2 | 0.78041 | 0.76041 | -0.020001 |  | 0.9 | 1.05 | 0.1303 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | NP-LUCKY_CR2 | 0.78041 | 0.76041 | -0.020001 |  | 0.9 | 1.05 | 0.18174 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | NP-LUCKY_CR2 | 0.78041 | 0.76041 | -0.020001 |  | 0.9 | 1.05 | 0.18244 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | NP-LUCKY_CR2 | 0.78041 | 0.76041 | -0.020001 |  | 0.9 | 1.05 | 0.19275 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | NP-LUCKY_CR2 | 0.78041 | 0.76041 | -0.020001 |  | 0.9 | 1.05 | 0.19304 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | NP-LUCKY_CR2 | 0.78041 | 0.76041 | -0.020001 |  | 0.9 | 1.05 | 0.19068 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | NP-LUCKY_CR2 | 0.78041 | 0.76041 | -0.020001 |  | 0.9 | 1.05 | 0.19114 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | NP-LUCKY_CR2 | 0.78041 | 0.76041 | -0.020001 |  | 0.9 | 1.05 | 0.19232 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | NP-LUCKY_CR2 | 0.78041 | 0.76041 | -0.020001 |  | 0.9 | 1.05 | 0.17996 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | NP-LUCKY_CR2 | 0.78041 | 0.76041 | -0.020001 |  | 0.9 | 1.05 | 0.17996 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | NP-LUCKY_CR2 | 0.78041 | 0.76041 | -0.020001 |  | 0.9 | 1.05 | 0.18769 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | NP-LUCKY_CR2 | 0.78041 | 0.76041 | -0.020001 |  | 0.9 | 1.05 | 0.18769 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | NP-LUCKY_CR2 | 0.78041 | 0.76041 | -0.020001 |  | 0.9 | 1.05 | 0.4918 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | NP-LUCKY_CR2 | 0.78041 | 0.76041 | -0.020001 |  | 0.9 | 1.05 | 0.1947 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | NP-LUCKY_CR2 | 0.77863 | 0.7517 | -0.026938 |  | 0.9 | 1.05 | 0.081174 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | NP-LUCKY_CR2 | 0.77863 | 0.7517 | -0.026938 |  | 0.9 | 1.05 | 0.19645 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | NP-LUCKY_CR2 | 0.77863 | 0.7517 | -0.026938 |  | 0.9 | 1.05 | 0.23843 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | NP-LUCKY_CR2 | 0.77863 | 0.7517 | -0.026938 |  | 0.9 | 1.05 | 0.23843 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | NP-LUCKY_CR2 | 0.77863 | 0.7517 | -0.026938 |  | 0.9 | 1.05 | 0.17969 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | NP-LUCKY_CR2 | 0.77863 | 0.7517 | -0.026938 |  | 0.9 | 1.05 | 0.17406 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | NP-LUCKY_CR2 | 0.77863 | 0.7517 | -0.026938 |  | 0.9 | 1.05 | 0.17754 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | NP-LUCKY_CR2 | 0.77863 | 0.7517 | -0.026938 |  | 0.9 | 1.05 | 0.1303 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | NP-LUCKY_CR2 | 0.77863 | 0.7517 | -0.026938 |  | 0.9 | 1.05 | 0.1303 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | NP-LUCKY_CR2 | 0.77863 | 0.7517 | -0.026938 |  | 0.9 | 1.05 | 0.18174 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | NP-LUCKY_CR2 | 0.77863 | 0.7517 | -0.026938 |  | 0.9 | 1.05 | 0.18244 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | NP-LUCKY_CR2 | 0.77863 | 0.7517 | -0.026938 |  | 0.9 | 1.05 | 0.19275 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | NP-LUCKY_CR2 | 0.77863 | 0.7517 | -0.026938 |  | 0.9 | 1.05 | 0.19304 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | NP-LUCKY_CR2 | 0.77863 | 0.7517 | -0.026938 |  | 0.9 | 1.05 | 0.19068 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | NP-LUCKY_CR2 | 0.77863 | 0.7517 | -0.026938 |  | 0.9 | 1.05 | 0.19114 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | NP-LUCKY_CR2 | 0.77863 | 0.7517 | -0.026938 |  | 0.9 | 1.05 | 0.19232 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | NP-LUCKY_CR2 | 0.77863 | 0.7517 | -0.026938 |  | 0.9 | 1.05 | 0.17996 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | NP-LUCKY_CR2 | 0.77863 | 0.7517 | -0.026938 |  | 0.9 | 1.05 | 0.17996 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | NP-LUCKY_CR2 | 0.77863 | 0.7517 | -0.026938 |  | 0.9 | 1.05 | 0.18769 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | NP-LUCKY_CR2 | 0.77863 | 0.7517 | -0.026938 |  | 0.9 | 1.05 | 0.18769 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | NP-LUCKY_CR2 | 0.77863 | 0.7517 | -0.026938 |  | 0.9 | 1.05 | 0.4918 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | NP-LUCKY_CR2 | 0.77863 | 0.7517 | -0.026938 |  | 0.9 | 1.05 | 0.1947 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | NP-LUCKY_CR2 | 0.78014 | 0.75994 | -0.020199 |  | 0.9 | 1.05 | 0.081174 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | NP-LUCKY_CR2 | 0.78014 | 0.75994 | -0.020199 |  | 0.9 | 1.05 | 0.19645 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | NP-LUCKY_CR2 | 0.78014 | 0.75994 | -0.020199 |  | 0.9 | 1.05 | 0.23843 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | NP-LUCKY_CR2 | 0.78014 | 0.75994 | -0.020199 |  | 0.9 | 1.05 | 0.23843 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | NP-LUCKY_CR2 | 0.78014 | 0.75994 | -0.020199 |  | 0.9 | 1.05 | 0.17969 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | NP-LUCKY_CR2 | 0.78014 | 0.75994 | -0.020199 |  | 0.9 | 1.05 | 0.17406 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | NP-LUCKY_CR2 | 0.78014 | 0.75994 | -0.020199 |  | 0.9 | 1.05 | 0.17754 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | NP-LUCKY_CR2 | 0.78014 | 0.75994 | -0.020199 |  | 0.9 | 1.05 | 0.1303 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | NP-LUCKY_CR2 | 0.78014 | 0.75994 | -0.020199 |  | 0.9 | 1.05 | 0.1303 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | NP-LUCKY_CR2 | 0.78014 | 0.75994 | -0.020199 |  | 0.9 | 1.05 | 0.18174 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | NP-LUCKY_CR2 | 0.78014 | 0.75994 | -0.020199 |  | 0.9 | 1.05 | 0.18244 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | NP-LUCKY_CR2 | 0.78014 | 0.75994 | -0.020199 |  | 0.9 | 1.05 | 0.19275 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | NP-LUCKY_CR2 | 0.78014 | 0.75994 | -0.020199 |  | 0.9 | 1.05 | 0.19304 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | NP-LUCKY_CR2 | 0.78014 | 0.75994 | -0.020199 |  | 0.9 | 1.05 | 0.19068 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | NP-LUCKY_CR2 | 0.78014 | 0.75994 | -0.020199 |  | 0.9 | 1.05 | 0.19114 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | NP-LUCKY_CR2 | 0.78014 | 0.75994 | -0.020199 |  | 0.9 | 1.05 | 0.19232 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | NP-LUCKY_CR2 | 0.78014 | 0.75994 | -0.020199 |  | 0.9 | 1.05 | 0.17996 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | NP-LUCKY_CR2 | 0.78014 | 0.75994 | -0.020199 |  | 0.9 | 1.05 | 0.17996 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | NP-LUCKY_CR2 | 0.78014 | 0.75994 | -0.020199 |  | 0.9 | 1.05 | 0.18769 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | NP-LUCKY_CR2 | 0.78014 | 0.75994 | -0.020199 |  | 0.9 | 1.05 | 0.18769 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | NP-LUCKY_CR2 | 0.78014 | 0.75994 | -0.020199 |  | 0.9 | 1.05 | 0.4918 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | NP-LUCKY_CR2 | 0.78014 | 0.75994 | -0.020199 |  | 0.9 | 1.05 | 0.1947 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | NP-LUCKY_G 2 | 0.78033 | 0.7601 | -0.020237 |  | 0.9 | 1.05 | 0.081174 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | NP-LUCKY_G 2 | 0.78033 | 0.7601 | -0.020237 |  | 0.9 | 1.05 | 0.19645 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | NP-LUCKY_G 2 | 0.78033 | 0.7601 | -0.020237 |  | 0.9 | 1.05 | 0.23843 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | NP-LUCKY_G 2 | 0.78033 | 0.7601 | -0.020237 |  | 0.9 | 1.05 | 0.23843 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | NP-LUCKY_G 2 | 0.78033 | 0.7601 | -0.020237 |  | 0.9 | 1.05 | 0.17969 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | NP-LUCKY_G 2 | 0.78033 | 0.7601 | -0.020237 |  | 0.9 | 1.05 | 0.17406 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | NP-LUCKY_G 2 | 0.78033 | 0.7601 | -0.020237 |  | 0.9 | 1.05 | 0.17754 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | NP-LUCKY_G 2 | 0.78033 | 0.7601 | -0.020237 |  | 0.9 | 1.05 | 0.1303 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | NP-LUCKY_G 2 | 0.78033 | 0.7601 | -0.020237 |  | 0.9 | 1.05 | 0.1303 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | NP-LUCKY_G 2 | 0.78033 | 0.7601 | -0.020237 |  | 0.9 | 1.05 | 0.18174 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | NP-LUCKY_G 2 | 0.78033 | 0.7601 | -0.020237 |  | 0.9 | 1.05 | 0.18244 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | NP-LUCKY_G 2 | 0.78033 | 0.7601 | -0.020237 |  | 0.9 | 1.05 | 0.19275 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | NP-LUCKY_G 2 | 0.78033 | 0.7601 | -0.020237 |  | 0.9 | 1.05 | 0.19304 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | NP-LUCKY_G 2 | 0.78033 | 0.7601 | -0.020237 |  | 0.9 | 1.05 | 0.19068 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | NP-LUCKY_G 2 | 0.78033 | 0.7601 | -0.020237 |  | 0.9 | 1.05 | 0.19114 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | NP-LUCKY_G 2 | 0.78033 | 0.7601 | -0.020237 |  | 0.9 | 1.05 | 0.19232 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | NP-LUCKY_G 2 | 0.78033 | 0.7601 | -0.020237 |  | 0.9 | 1.05 | 0.17996 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | NP-LUCKY_G 2 | 0.78033 | 0.7601 | -0.020237 |  | 0.9 | 1.05 | 0.17996 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | NP-LUCKY_G 2 | 0.78033 | 0.7601 | -0.020237 |  | 0.9 | 1.05 | 0.18769 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | NP-LUCKY_G 2 | 0.78033 | 0.7601 | -0.020237 |  | 0.9 | 1.05 | 0.18769 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | NP-LUCKY_G 2 | 0.78033 | 0.7601 | -0.020237 |  | 0.9 | 1.05 | 0.4918 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | NP-LUCKY_G 2 | 0.78033 | 0.7601 | -0.020237 |  | 0.9 | 1.05 | 0.1947 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | NP-LUCKY_G 2 | 0.78031 | 0.76014 | -0.020164 |  | 0.9 | 1.05 | 0.081174 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | NP-LUCKY_G 2 | 0.78031 | 0.76014 | -0.020164 |  | 0.9 | 1.05 | 0.19645 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | NP-LUCKY_G 2 | 0.78031 | 0.76014 | -0.020164 |  | 0.9 | 1.05 | 0.23843 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | NP-LUCKY_G 2 | 0.78031 | 0.76014 | -0.020164 |  | 0.9 | 1.05 | 0.23843 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | NP-LUCKY_G 2 | 0.78031 | 0.76014 | -0.020164 |  | 0.9 | 1.05 | 0.17969 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | NP-LUCKY_G 2 | 0.78031 | 0.76014 | -0.020164 |  | 0.9 | 1.05 | 0.17406 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | NP-LUCKY_G 2 | 0.78031 | 0.76014 | -0.020164 |  | 0.9 | 1.05 | 0.17754 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | NP-LUCKY_G 2 | 0.78031 | 0.76014 | -0.020164 |  | 0.9 | 1.05 | 0.1303 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | NP-LUCKY_G 2 | 0.78031 | 0.76014 | -0.020164 |  | 0.9 | 1.05 | 0.1303 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | NP-LUCKY_G 2 | 0.78031 | 0.76014 | -0.020164 |  | 0.9 | 1.05 | 0.18174 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | NP-LUCKY_G 2 | 0.78031 | 0.76014 | -0.020164 |  | 0.9 | 1.05 | 0.18244 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | NP-LUCKY_G 2 | 0.78031 | 0.76014 | -0.020164 |  | 0.9 | 1.05 | 0.19275 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | NP-LUCKY_G 2 | 0.78031 | 0.76014 | -0.020164 |  | 0.9 | 1.05 | 0.19304 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | NP-LUCKY_G 2 | 0.78031 | 0.76014 | -0.020164 |  | 0.9 | 1.05 | 0.19068 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | NP-LUCKY_G 2 | 0.78031 | 0.76014 | -0.020164 |  | 0.9 | 1.05 | 0.19114 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | NP-LUCKY_G 2 | 0.78031 | 0.76014 | -0.020164 |  | 0.9 | 1.05 | 0.19232 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | NP-LUCKY_G 2 | 0.78031 | 0.76014 | -0.020164 |  | 0.9 | 1.05 | 0.17996 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | NP-LUCKY_G 2 | 0.78031 | 0.76014 | -0.020164 |  | 0.9 | 1.05 | 0.17996 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | NP-LUCKY_G 2 | 0.78031 | 0.76014 | -0.020164 |  | 0.9 | 1.05 | 0.18769 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | NP-LUCKY_G 2 | 0.78031 | 0.76014 | -0.020164 |  | 0.9 | 1.05 | 0.18769 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | NP-LUCKY_G 2 | 0.78031 | 0.76014 | -0.020164 |  | 0.9 | 1.05 | 0.4918 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | NP-LUCKY_G 2 | 0.78031 | 0.76014 | -0.020164 |  | 0.9 | 1.05 | 0.1947 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | NP-LUCKY_G 2 | 0.78055 | 0.76055 | -0.019997 |  | 0.9 | 1.05 | 0.081174 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | NP-LUCKY_G 2 | 0.78055 | 0.76055 | -0.019997 |  | 0.9 | 1.05 | 0.19645 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | NP-LUCKY_G 2 | 0.78055 | 0.76055 | -0.019997 |  | 0.9 | 1.05 | 0.23843 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | NP-LUCKY_G 2 | 0.78055 | 0.76055 | -0.019997 |  | 0.9 | 1.05 | 0.23843 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | NP-LUCKY_G 2 | 0.78055 | 0.76055 | -0.019997 |  | 0.9 | 1.05 | 0.17969 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | NP-LUCKY_G 2 | 0.78055 | 0.76055 | -0.019997 |  | 0.9 | 1.05 | 0.17406 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | NP-LUCKY_G 2 | 0.78055 | 0.76055 | -0.019997 |  | 0.9 | 1.05 | 0.17754 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | NP-LUCKY_G 2 | 0.78055 | 0.76055 | -0.019997 |  | 0.9 | 1.05 | 0.1303 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | NP-LUCKY_G 2 | 0.78055 | 0.76055 | -0.019997 |  | 0.9 | 1.05 | 0.1303 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | NP-LUCKY_G 2 | 0.78055 | 0.76055 | -0.019997 |  | 0.9 | 1.05 | 0.18174 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | NP-LUCKY_G 2 | 0.78055 | 0.76055 | -0.019997 |  | 0.9 | 1.05 | 0.18244 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | NP-LUCKY_G 2 | 0.78055 | 0.76055 | -0.019997 |  | 0.9 | 1.05 | 0.19275 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | NP-LUCKY_G 2 | 0.78055 | 0.76055 | -0.019997 |  | 0.9 | 1.05 | 0.19304 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | NP-LUCKY_G 2 | 0.78055 | 0.76055 | -0.019997 |  | 0.9 | 1.05 | 0.19068 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | NP-LUCKY_G 2 | 0.78055 | 0.76055 | -0.019997 |  | 0.9 | 1.05 | 0.19114 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | NP-LUCKY_G 2 | 0.78055 | 0.76055 | -0.019997 |  | 0.9 | 1.05 | 0.19232 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | NP-LUCKY_G 2 | 0.78055 | 0.76055 | -0.019997 |  | 0.9 | 1.05 | 0.17996 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | NP-LUCKY_G 2 | 0.78055 | 0.76055 | -0.019997 |  | 0.9 | 1.05 | 0.17996 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | NP-LUCKY_G 2 | 0.78055 | 0.76055 | -0.019997 |  | 0.9 | 1.05 | 0.18769 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | NP-LUCKY_G 2 | 0.78055 | 0.76055 | -0.019997 |  | 0.9 | 1.05 | 0.18769 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | NP-LUCKY_G 2 | 0.78055 | 0.76055 | -0.019997 |  | 0.9 | 1.05 | 0.4918 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | NP-LUCKY_G 2 | 0.78055 | 0.76055 | -0.019997 |  | 0.9 | 1.05 | 0.1947 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | NP-LUCKY_G 2 | 0.77877 | 0.75184 | -0.026932 |  | 0.9 | 1.05 | 0.081174 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | NP-LUCKY_G 2 | 0.77877 | 0.75184 | -0.026932 |  | 0.9 | 1.05 | 0.19645 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | NP-LUCKY_G 2 | 0.77877 | 0.75184 | -0.026932 |  | 0.9 | 1.05 | 0.23843 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | NP-LUCKY_G 2 | 0.77877 | 0.75184 | -0.026932 |  | 0.9 | 1.05 | 0.23843 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | NP-LUCKY_G 2 | 0.77877 | 0.75184 | -0.026932 |  | 0.9 | 1.05 | 0.17969 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | NP-LUCKY_G 2 | 0.77877 | 0.75184 | -0.026932 |  | 0.9 | 1.05 | 0.17406 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | NP-LUCKY_G 2 | 0.77877 | 0.75184 | -0.026932 |  | 0.9 | 1.05 | 0.17754 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | NP-LUCKY_G 2 | 0.77877 | 0.75184 | -0.026932 |  | 0.9 | 1.05 | 0.1303 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | NP-LUCKY_G 2 | 0.77877 | 0.75184 | -0.026932 |  | 0.9 | 1.05 | 0.1303 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | NP-LUCKY_G 2 | 0.77877 | 0.75184 | -0.026932 |  | 0.9 | 1.05 | 0.18174 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | NP-LUCKY_G 2 | 0.77877 | 0.75184 | -0.026932 |  | 0.9 | 1.05 | 0.18244 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | NP-LUCKY_G 2 | 0.77877 | 0.75184 | -0.026932 |  | 0.9 | 1.05 | 0.19275 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | NP-LUCKY_G 2 | 0.77877 | 0.75184 | -0.026932 |  | 0.9 | 1.05 | 0.19304 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | NP-LUCKY_G 2 | 0.77877 | 0.75184 | -0.026932 |  | 0.9 | 1.05 | 0.19068 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | NP-LUCKY_G 2 | 0.77877 | 0.75184 | -0.026932 |  | 0.9 | 1.05 | 0.19114 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | NP-LUCKY_G 2 | 0.77877 | 0.75184 | -0.026932 |  | 0.9 | 1.05 | 0.19232 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | NP-LUCKY_G 2 | 0.77877 | 0.75184 | -0.026932 |  | 0.9 | 1.05 | 0.17996 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | NP-LUCKY_G 2 | 0.77877 | 0.75184 | -0.026932 |  | 0.9 | 1.05 | 0.17996 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | NP-LUCKY_G 2 | 0.77877 | 0.75184 | -0.026932 |  | 0.9 | 1.05 | 0.18769 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | NP-LUCKY_G 2 | 0.77877 | 0.75184 | -0.026932 |  | 0.9 | 1.05 | 0.18769 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | NP-LUCKY_G 2 | 0.77877 | 0.75184 | -0.026932 |  | 0.9 | 1.05 | 0.4918 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | NP-LUCKY_G 2 | 0.77877 | 0.75184 | -0.026932 |  | 0.9 | 1.05 | 0.1947 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | NP-LUCKY_G 2 | 0.78028 | 0.76009 | -0.020195 |  | 0.9 | 1.05 | 0.081174 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | NP-LUCKY_G 2 | 0.78028 | 0.76009 | -0.020195 |  | 0.9 | 1.05 | 0.19645 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | NP-LUCKY_G 2 | 0.78028 | 0.76009 | -0.020195 |  | 0.9 | 1.05 | 0.23843 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | NP-LUCKY_G 2 | 0.78028 | 0.76009 | -0.020195 |  | 0.9 | 1.05 | 0.23843 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | NP-LUCKY_G 2 | 0.78028 | 0.76009 | -0.020195 |  | 0.9 | 1.05 | 0.17969 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | NP-LUCKY_G 2 | 0.78028 | 0.76009 | -0.020195 |  | 0.9 | 1.05 | 0.17406 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | NP-LUCKY_G 2 | 0.78028 | 0.76009 | -0.020195 |  | 0.9 | 1.05 | 0.17754 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | NP-LUCKY_G 2 | 0.78028 | 0.76009 | -0.020195 |  | 0.9 | 1.05 | 0.1303 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | NP-LUCKY_G 2 | 0.78028 | 0.76009 | -0.020195 |  | 0.9 | 1.05 | 0.1303 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | NP-LUCKY_G 2 | 0.78028 | 0.76009 | -0.020195 |  | 0.9 | 1.05 | 0.18174 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | NP-LUCKY_G 2 | 0.78028 | 0.76009 | -0.020195 |  | 0.9 | 1.05 | 0.18244 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | NP-LUCKY_G 2 | 0.78028 | 0.76009 | -0.020195 |  | 0.9 | 1.05 | 0.19275 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | NP-LUCKY_G 2 | 0.78028 | 0.76009 | -0.020195 |  | 0.9 | 1.05 | 0.19304 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | NP-LUCKY_G 2 | 0.78028 | 0.76009 | -0.020195 |  | 0.9 | 1.05 | 0.19068 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | NP-LUCKY_G 2 | 0.78028 | 0.76009 | -0.020195 |  | 0.9 | 1.05 | 0.19114 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | NP-LUCKY_G 2 | 0.78028 | 0.76009 | -0.020195 |  | 0.9 | 1.05 | 0.19232 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | NP-LUCKY_G 2 | 0.78028 | 0.76009 | -0.020195 |  | 0.9 | 1.05 | 0.17996 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | NP-LUCKY_G 2 | 0.78028 | 0.76009 | -0.020195 |  | 0.9 | 1.05 | 0.17996 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | NP-LUCKY_G 2 | 0.78028 | 0.76009 | -0.020195 |  | 0.9 | 1.05 | 0.18769 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | NP-LUCKY_G 2 | 0.78028 | 0.76009 | -0.020195 |  | 0.9 | 1.05 | 0.18769 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | NP-LUCKY_G 2 | 0.78028 | 0.76009 | -0.020195 |  | 0.9 | 1.05 | 0.4918 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | NP-LUCKY_G 2 | 0.78028 | 0.76009 | -0.020195 |  | 0.9 | 1.05 | 0.1947 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | NP-SHATTUCK2 | 0.63525 | 0.61131 | -0.023945 |  | 0.9 | 1.05 | 0.081174 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | NP-SHATTUCK2 | 0.63525 | 0.61131 | -0.023945 |  | 0.9 | 1.05 | 0.19645 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | NP-SHATTUCK2 | 0.63525 | 0.61131 | -0.023945 |  | 0.9 | 1.05 | 0.23843 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | NP-SHATTUCK2 | 0.63525 | 0.61131 | -0.023945 |  | 0.9 | 1.05 | 0.23843 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | NP-SHATTUCK2 | 0.63525 | 0.61131 | -0.023945 |  | 0.9 | 1.05 | 0.17969 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | NP-SHATTUCK2 | 0.63525 | 0.61131 | -0.023945 |  | 0.9 | 1.05 | 0.17406 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | NP-SHATTUCK2 | 0.63525 | 0.61131 | -0.023945 |  | 0.9 | 1.05 | 0.17754 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | NP-SHATTUCK2 | 0.63525 | 0.61131 | -0.023945 |  | 0.9 | 1.05 | 0.1303 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | NP-SHATTUCK2 | 0.63525 | 0.61131 | -0.023945 |  | 0.9 | 1.05 | 0.1303 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | NP-SHATTUCK2 | 0.63525 | 0.61131 | -0.023945 |  | 0.9 | 1.05 | 0.18174 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | NP-SHATTUCK2 | 0.63525 | 0.61131 | -0.023945 |  | 0.9 | 1.05 | 0.18244 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | NP-SHATTUCK2 | 0.63525 | 0.61131 | -0.023945 |  | 0.9 | 1.05 | 0.19275 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | NP-SHATTUCK2 | 0.63525 | 0.61131 | -0.023945 |  | 0.9 | 1.05 | 0.19304 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | NP-SHATTUCK2 | 0.63525 | 0.61131 | -0.023945 |  | 0.9 | 1.05 | 0.19068 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | NP-SHATTUCK2 | 0.63525 | 0.61131 | -0.023945 |  | 0.9 | 1.05 | 0.19114 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | NP-SHATTUCK2 | 0.63525 | 0.61131 | -0.023945 |  | 0.9 | 1.05 | 0.19232 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | NP-SHATTUCK2 | 0.63525 | 0.61131 | -0.023945 |  | 0.9 | 1.05 | 0.17996 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | NP-SHATTUCK2 | 0.63525 | 0.61131 | -0.023945 |  | 0.9 | 1.05 | 0.17996 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | NP-SHATTUCK2 | 0.63525 | 0.61131 | -0.023945 |  | 0.9 | 1.05 | 0.18769 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | NP-SHATTUCK2 | 0.63525 | 0.61131 | -0.023945 |  | 0.9 | 1.05 | 0.18769 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | NP-SHATTUCK2 | 0.63525 | 0.61131 | -0.023945 |  | 0.9 | 1.05 | 0.4918 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | NP-SHATTUCK2 | 0.63525 | 0.61131 | -0.023945 |  | 0.9 | 1.05 | 0.1947 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | NP-SHATTUCK2 | 0.63522 | 0.61136 | -0.023859 |  | 0.9 | 1.05 | 0.081174 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | NP-SHATTUCK2 | 0.63522 | 0.61136 | -0.023859 |  | 0.9 | 1.05 | 0.19645 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | NP-SHATTUCK2 | 0.63522 | 0.61136 | -0.023859 |  | 0.9 | 1.05 | 0.23843 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | NP-SHATTUCK2 | 0.63522 | 0.61136 | -0.023859 |  | 0.9 | 1.05 | 0.23843 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | NP-SHATTUCK2 | 0.63522 | 0.61136 | -0.023859 |  | 0.9 | 1.05 | 0.17969 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | NP-SHATTUCK2 | 0.63522 | 0.61136 | -0.023859 |  | 0.9 | 1.05 | 0.17406 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | NP-SHATTUCK2 | 0.63522 | 0.61136 | -0.023859 |  | 0.9 | 1.05 | 0.17754 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | NP-SHATTUCK2 | 0.63522 | 0.61136 | -0.023859 |  | 0.9 | 1.05 | 0.1303 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | NP-SHATTUCK2 | 0.63522 | 0.61136 | -0.023859 |  | 0.9 | 1.05 | 0.1303 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | NP-SHATTUCK2 | 0.63522 | 0.61136 | -0.023859 |  | 0.9 | 1.05 | 0.18174 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | NP-SHATTUCK2 | 0.63522 | 0.61136 | -0.023859 |  | 0.9 | 1.05 | 0.18244 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | NP-SHATTUCK2 | 0.63522 | 0.61136 | -0.023859 |  | 0.9 | 1.05 | 0.19275 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | NP-SHATTUCK2 | 0.63522 | 0.61136 | -0.023859 |  | 0.9 | 1.05 | 0.19304 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | NP-SHATTUCK2 | 0.63522 | 0.61136 | -0.023859 |  | 0.9 | 1.05 | 0.19068 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | NP-SHATTUCK2 | 0.63522 | 0.61136 | -0.023859 |  | 0.9 | 1.05 | 0.19114 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | NP-SHATTUCK2 | 0.63522 | 0.61136 | -0.023859 |  | 0.9 | 1.05 | 0.19232 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | NP-SHATTUCK2 | 0.63522 | 0.61136 | -0.023859 |  | 0.9 | 1.05 | 0.17996 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | NP-SHATTUCK2 | 0.63522 | 0.61136 | -0.023859 |  | 0.9 | 1.05 | 0.17996 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | NP-SHATTUCK2 | 0.63522 | 0.61136 | -0.023859 |  | 0.9 | 1.05 | 0.18769 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | NP-SHATTUCK2 | 0.63522 | 0.61136 | -0.023859 |  | 0.9 | 1.05 | 0.18769 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | NP-SHATTUCK2 | 0.63522 | 0.61136 | -0.023859 |  | 0.9 | 1.05 | 0.4918 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | NP-SHATTUCK2 | 0.63522 | 0.61136 | -0.023859 |  | 0.9 | 1.05 | 0.1947 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | NP-SHATTUCK2 | 0.63551 | 0.61183 | -0.023673 |  | 0.9 | 1.05 | 0.081174 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | NP-SHATTUCK2 | 0.63551 | 0.61183 | -0.023673 |  | 0.9 | 1.05 | 0.19645 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | NP-SHATTUCK2 | 0.63551 | 0.61183 | -0.023673 |  | 0.9 | 1.05 | 0.23843 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | NP-SHATTUCK2 | 0.63551 | 0.61183 | -0.023673 |  | 0.9 | 1.05 | 0.23843 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | NP-SHATTUCK2 | 0.63551 | 0.61183 | -0.023673 |  | 0.9 | 1.05 | 0.17969 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | NP-SHATTUCK2 | 0.63551 | 0.61183 | -0.023673 |  | 0.9 | 1.05 | 0.17406 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | NP-SHATTUCK2 | 0.63551 | 0.61183 | -0.023673 |  | 0.9 | 1.05 | 0.17754 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | NP-SHATTUCK2 | 0.63551 | 0.61183 | -0.023673 |  | 0.9 | 1.05 | 0.1303 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | NP-SHATTUCK2 | 0.63551 | 0.61183 | -0.023673 |  | 0.9 | 1.05 | 0.1303 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | NP-SHATTUCK2 | 0.63551 | 0.61183 | -0.023673 |  | 0.9 | 1.05 | 0.18174 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | NP-SHATTUCK2 | 0.63551 | 0.61183 | -0.023673 |  | 0.9 | 1.05 | 0.18244 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | NP-SHATTUCK2 | 0.63551 | 0.61183 | -0.023673 |  | 0.9 | 1.05 | 0.19275 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | NP-SHATTUCK2 | 0.63551 | 0.61183 | -0.023673 |  | 0.9 | 1.05 | 0.19304 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | NP-SHATTUCK2 | 0.63551 | 0.61183 | -0.023673 |  | 0.9 | 1.05 | 0.19068 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | NP-SHATTUCK2 | 0.63551 | 0.61183 | -0.023673 |  | 0.9 | 1.05 | 0.19114 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | NP-SHATTUCK2 | 0.63551 | 0.61183 | -0.023673 |  | 0.9 | 1.05 | 0.19232 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | NP-SHATTUCK2 | 0.63551 | 0.61183 | -0.023673 |  | 0.9 | 1.05 | 0.17996 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | NP-SHATTUCK2 | 0.63551 | 0.61183 | -0.023673 |  | 0.9 | 1.05 | 0.17996 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | NP-SHATTUCK2 | 0.63551 | 0.61183 | -0.023673 |  | 0.9 | 1.05 | 0.18769 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | NP-SHATTUCK2 | 0.63551 | 0.61183 | -0.023673 |  | 0.9 | 1.05 | 0.18769 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | NP-SHATTUCK2 | 0.63551 | 0.61183 | -0.023673 |  | 0.9 | 1.05 | 0.4918 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | NP-SHATTUCK2 | 0.63551 | 0.61183 | -0.023673 |  | 0.9 | 1.05 | 0.1947 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | NP-SHATTUCK2 | 0.63338 | 0.60173 | -0.031648 |  | 0.9 | 1.05 | 0.081174 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | NP-SHATTUCK2 | 0.63338 | 0.60173 | -0.031648 |  | 0.9 | 1.05 | 0.19645 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | NP-SHATTUCK2 | 0.63338 | 0.60173 | -0.031648 |  | 0.9 | 1.05 | 0.23843 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | NP-SHATTUCK2 | 0.63338 | 0.60173 | -0.031648 |  | 0.9 | 1.05 | 0.23843 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | NP-SHATTUCK2 | 0.63338 | 0.60173 | -0.031648 |  | 0.9 | 1.05 | 0.17969 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | NP-SHATTUCK2 | 0.63338 | 0.60173 | -0.031648 |  | 0.9 | 1.05 | 0.17406 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | NP-SHATTUCK2 | 0.63338 | 0.60173 | -0.031648 |  | 0.9 | 1.05 | 0.17754 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | NP-SHATTUCK2 | 0.63338 | 0.60173 | -0.031648 |  | 0.9 | 1.05 | 0.1303 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | NP-SHATTUCK2 | 0.63338 | 0.60173 | -0.031648 |  | 0.9 | 1.05 | 0.1303 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | NP-SHATTUCK2 | 0.63338 | 0.60173 | -0.031648 |  | 0.9 | 1.05 | 0.18174 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | NP-SHATTUCK2 | 0.63338 | 0.60173 | -0.031648 |  | 0.9 | 1.05 | 0.18244 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | NP-SHATTUCK2 | 0.63338 | 0.60173 | -0.031648 |  | 0.9 | 1.05 | 0.19275 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | NP-SHATTUCK2 | 0.63338 | 0.60173 | -0.031648 |  | 0.9 | 1.05 | 0.19304 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | NP-SHATTUCK2 | 0.63338 | 0.60173 | -0.031648 |  | 0.9 | 1.05 | 0.19068 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | NP-SHATTUCK2 | 0.63338 | 0.60173 | -0.031648 |  | 0.9 | 1.05 | 0.19114 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | NP-SHATTUCK2 | 0.63338 | 0.60173 | -0.031648 |  | 0.9 | 1.05 | 0.19232 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | NP-SHATTUCK2 | 0.63338 | 0.60173 | -0.031648 |  | 0.9 | 1.05 | 0.17996 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | NP-SHATTUCK2 | 0.63338 | 0.60173 | -0.031648 |  | 0.9 | 1.05 | 0.17996 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | NP-SHATTUCK2 | 0.63338 | 0.60173 | -0.031648 |  | 0.9 | 1.05 | 0.18769 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | NP-SHATTUCK2 | 0.63338 | 0.60173 | -0.031648 |  | 0.9 | 1.05 | 0.18769 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | NP-SHATTUCK2 | 0.63338 | 0.60173 | -0.031648 |  | 0.9 | 1.05 | 0.4918 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | NP-SHATTUCK2 | 0.63338 | 0.60173 | -0.031648 |  | 0.9 | 1.05 | 0.1947 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | NP-SHATTUCK2 | 0.63519 | 0.6113 | -0.023895 |  | 0.9 | 1.05 | 0.081174 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | NP-SHATTUCK2 | 0.63519 | 0.6113 | -0.023895 |  | 0.9 | 1.05 | 0.19645 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | NP-SHATTUCK2 | 0.63519 | 0.6113 | -0.023895 |  | 0.9 | 1.05 | 0.23843 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | NP-SHATTUCK2 | 0.63519 | 0.6113 | -0.023895 |  | 0.9 | 1.05 | 0.23843 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | NP-SHATTUCK2 | 0.63519 | 0.6113 | -0.023895 |  | 0.9 | 1.05 | 0.17969 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | NP-SHATTUCK2 | 0.63519 | 0.6113 | -0.023895 |  | 0.9 | 1.05 | 0.17406 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | NP-SHATTUCK2 | 0.63519 | 0.6113 | -0.023895 |  | 0.9 | 1.05 | 0.17754 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | NP-SHATTUCK2 | 0.63519 | 0.6113 | -0.023895 |  | 0.9 | 1.05 | 0.1303 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | NP-SHATTUCK2 | 0.63519 | 0.6113 | -0.023895 |  | 0.9 | 1.05 | 0.1303 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | NP-SHATTUCK2 | 0.63519 | 0.6113 | -0.023895 |  | 0.9 | 1.05 | 0.18174 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | NP-SHATTUCK2 | 0.63519 | 0.6113 | -0.023895 |  | 0.9 | 1.05 | 0.18244 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | NP-SHATTUCK2 | 0.63519 | 0.6113 | -0.023895 |  | 0.9 | 1.05 | 0.19275 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | NP-SHATTUCK2 | 0.63519 | 0.6113 | -0.023895 |  | 0.9 | 1.05 | 0.19304 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | NP-SHATTUCK2 | 0.63519 | 0.6113 | -0.023895 |  | 0.9 | 1.05 | 0.19068 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | NP-SHATTUCK2 | 0.63519 | 0.6113 | -0.023895 |  | 0.9 | 1.05 | 0.19114 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | NP-SHATTUCK2 | 0.63519 | 0.6113 | -0.023895 |  | 0.9 | 1.05 | 0.19232 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | NP-SHATTUCK2 | 0.63519 | 0.6113 | -0.023895 |  | 0.9 | 1.05 | 0.17996 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | NP-SHATTUCK2 | 0.63519 | 0.6113 | -0.023895 |  | 0.9 | 1.05 | 0.17996 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | NP-SHATTUCK2 | 0.63519 | 0.6113 | -0.023895 |  | 0.9 | 1.05 | 0.18769 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | NP-SHATTUCK2 | 0.63519 | 0.6113 | -0.023895 |  | 0.9 | 1.05 | 0.18769 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | NP-SHATTUCK2 | 0.63519 | 0.6113 | -0.023895 |  | 0.9 | 1.05 | 0.4918 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | NP-SHATTUCK2 | 0.63519 | 0.6113 | -0.023895 |  | 0.9 | 1.05 | 0.1947 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | NP-SUB_A 2 | 0.84361 | 0.82522 | -0.018398 |  | 0.9 | 1.05 | 0.081174 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | NP-SUB_A 2 | 0.84361 | 0.82522 | -0.018398 |  | 0.9 | 1.05 | 0.19645 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | NP-SUB_A 2 | 0.84361 | 0.82522 | -0.018398 |  | 0.9 | 1.05 | 0.23843 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | NP-SUB_A 2 | 0.84361 | 0.82522 | -0.018398 |  | 0.9 | 1.05 | 0.23843 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | NP-SUB_A 2 | 0.84361 | 0.82522 | -0.018398 |  | 0.9 | 1.05 | 0.17969 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | NP-SUB_A 2 | 0.84361 | 0.82522 | -0.018398 |  | 0.9 | 1.05 | 0.17406 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | NP-SUB_A 2 | 0.84361 | 0.82522 | -0.018398 |  | 0.9 | 1.05 | 0.17754 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | NP-SUB_A 2 | 0.84361 | 0.82522 | -0.018398 |  | 0.9 | 1.05 | 0.1303 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | NP-SUB_A 2 | 0.84361 | 0.82522 | -0.018398 |  | 0.9 | 1.05 | 0.1303 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | NP-SUB_A 2 | 0.84361 | 0.82522 | -0.018398 |  | 0.9 | 1.05 | 0.18174 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | NP-SUB_A 2 | 0.84361 | 0.82522 | -0.018398 |  | 0.9 | 1.05 | 0.18244 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | NP-SUB_A 2 | 0.84361 | 0.82522 | -0.018398 |  | 0.9 | 1.05 | 0.19275 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | NP-SUB_A 2 | 0.84361 | 0.82522 | -0.018398 |  | 0.9 | 1.05 | 0.19304 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | NP-SUB_A 2 | 0.84361 | 0.82522 | -0.018398 |  | 0.9 | 1.05 | 0.19068 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | NP-SUB_A 2 | 0.84361 | 0.82522 | -0.018398 |  | 0.9 | 1.05 | 0.19114 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | NP-SUB_A 2 | 0.84361 | 0.82522 | -0.018398 |  | 0.9 | 1.05 | 0.19232 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | NP-SUB_A 2 | 0.84361 | 0.82522 | -0.018398 |  | 0.9 | 1.05 | 0.17996 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | NP-SUB_A 2 | 0.84361 | 0.82522 | -0.018398 |  | 0.9 | 1.05 | 0.17996 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | NP-SUB_A 2 | 0.84361 | 0.82522 | -0.018398 |  | 0.9 | 1.05 | 0.18769 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | NP-SUB_A 2 | 0.84361 | 0.82522 | -0.018398 |  | 0.9 | 1.05 | 0.18769 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | NP-SUB_A 2 | 0.84361 | 0.82522 | -0.018398 |  | 0.9 | 1.05 | 0.4918 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | NP-SUB_A 2 | 0.84361 | 0.82522 | -0.018398 |  | 0.9 | 1.05 | 0.1947 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | NP-SUB_A 2 | 0.84359 | 0.82526 | -0.018332 |  | 0.9 | 1.05 | 0.081174 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | NP-SUB_A 2 | 0.84359 | 0.82526 | -0.018332 |  | 0.9 | 1.05 | 0.19645 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | NP-SUB_A 2 | 0.84359 | 0.82526 | -0.018332 |  | 0.9 | 1.05 | 0.23843 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | NP-SUB_A 2 | 0.84359 | 0.82526 | -0.018332 |  | 0.9 | 1.05 | 0.23843 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | NP-SUB_A 2 | 0.84359 | 0.82526 | -0.018332 |  | 0.9 | 1.05 | 0.17969 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | NP-SUB_A 2 | 0.84359 | 0.82526 | -0.018332 |  | 0.9 | 1.05 | 0.17406 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | NP-SUB_A 2 | 0.84359 | 0.82526 | -0.018332 |  | 0.9 | 1.05 | 0.17754 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | NP-SUB_A 2 | 0.84359 | 0.82526 | -0.018332 |  | 0.9 | 1.05 | 0.1303 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | NP-SUB_A 2 | 0.84359 | 0.82526 | -0.018332 |  | 0.9 | 1.05 | 0.1303 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | NP-SUB_A 2 | 0.84359 | 0.82526 | -0.018332 |  | 0.9 | 1.05 | 0.18174 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | NP-SUB_A 2 | 0.84359 | 0.82526 | -0.018332 |  | 0.9 | 1.05 | 0.18244 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | NP-SUB_A 2 | 0.84359 | 0.82526 | -0.018332 |  | 0.9 | 1.05 | 0.19275 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | NP-SUB_A 2 | 0.84359 | 0.82526 | -0.018332 |  | 0.9 | 1.05 | 0.19304 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | NP-SUB_A 2 | 0.84359 | 0.82526 | -0.018332 |  | 0.9 | 1.05 | 0.19068 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | NP-SUB_A 2 | 0.84359 | 0.82526 | -0.018332 |  | 0.9 | 1.05 | 0.19114 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | NP-SUB_A 2 | 0.84359 | 0.82526 | -0.018332 |  | 0.9 | 1.05 | 0.19232 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | NP-SUB_A 2 | 0.84359 | 0.82526 | -0.018332 |  | 0.9 | 1.05 | 0.17996 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | NP-SUB_A 2 | 0.84359 | 0.82526 | -0.018332 |  | 0.9 | 1.05 | 0.17996 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | NP-SUB_A 2 | 0.84359 | 0.82526 | -0.018332 |  | 0.9 | 1.05 | 0.18769 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | NP-SUB_A 2 | 0.84359 | 0.82526 | -0.018332 |  | 0.9 | 1.05 | 0.18769 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | NP-SUB_A 2 | 0.84359 | 0.82526 | -0.018332 |  | 0.9 | 1.05 | 0.4918 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | NP-SUB_A 2 | 0.84359 | 0.82526 | -0.018332 |  | 0.9 | 1.05 | 0.1947 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | NP-SUB_A 2 | 0.84381 | 0.82563 | -0.018178 |  | 0.9 | 1.05 | 0.081174 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | NP-SUB_A 2 | 0.84381 | 0.82563 | -0.018178 |  | 0.9 | 1.05 | 0.19645 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | NP-SUB_A 2 | 0.84381 | 0.82563 | -0.018178 |  | 0.9 | 1.05 | 0.23843 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | NP-SUB_A 2 | 0.84381 | 0.82563 | -0.018178 |  | 0.9 | 1.05 | 0.23843 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | NP-SUB_A 2 | 0.84381 | 0.82563 | -0.018178 |  | 0.9 | 1.05 | 0.17969 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | NP-SUB_A 2 | 0.84381 | 0.82563 | -0.018178 |  | 0.9 | 1.05 | 0.17406 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | NP-SUB_A 2 | 0.84381 | 0.82563 | -0.018178 |  | 0.9 | 1.05 | 0.17754 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | NP-SUB_A 2 | 0.84381 | 0.82563 | -0.018178 |  | 0.9 | 1.05 | 0.1303 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | NP-SUB_A 2 | 0.84381 | 0.82563 | -0.018178 |  | 0.9 | 1.05 | 0.1303 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | NP-SUB_A 2 | 0.84381 | 0.82563 | -0.018178 |  | 0.9 | 1.05 | 0.18174 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | NP-SUB_A 2 | 0.84381 | 0.82563 | -0.018178 |  | 0.9 | 1.05 | 0.18244 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | NP-SUB_A 2 | 0.84381 | 0.82563 | -0.018178 |  | 0.9 | 1.05 | 0.19275 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | NP-SUB_A 2 | 0.84381 | 0.82563 | -0.018178 |  | 0.9 | 1.05 | 0.19304 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | NP-SUB_A 2 | 0.84381 | 0.82563 | -0.018178 |  | 0.9 | 1.05 | 0.19068 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | NP-SUB_A 2 | 0.84381 | 0.82563 | -0.018178 |  | 0.9 | 1.05 | 0.19114 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | NP-SUB_A 2 | 0.84381 | 0.82563 | -0.018178 |  | 0.9 | 1.05 | 0.19232 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | NP-SUB_A 2 | 0.84381 | 0.82563 | -0.018178 |  | 0.9 | 1.05 | 0.17996 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | NP-SUB_A 2 | 0.84381 | 0.82563 | -0.018178 |  | 0.9 | 1.05 | 0.17996 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | NP-SUB_A 2 | 0.84381 | 0.82563 | -0.018178 |  | 0.9 | 1.05 | 0.18769 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | NP-SUB_A 2 | 0.84381 | 0.82563 | -0.018178 |  | 0.9 | 1.05 | 0.18769 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | NP-SUB_A 2 | 0.84381 | 0.82563 | -0.018178 |  | 0.9 | 1.05 | 0.4918 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | NP-SUB_A 2 | 0.84381 | 0.82563 | -0.018178 |  | 0.9 | 1.05 | 0.1947 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | NP-SUB_A 2 | 0.8422 | 0.81767 | -0.024534 |  | 0.9 | 1.05 | 0.081174 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | NP-SUB_A 2 | 0.8422 | 0.81767 | -0.024534 |  | 0.9 | 1.05 | 0.19645 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | NP-SUB_A 2 | 0.8422 | 0.81767 | -0.024534 |  | 0.9 | 1.05 | 0.23843 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | NP-SUB_A 2 | 0.8422 | 0.81767 | -0.024534 |  | 0.9 | 1.05 | 0.23843 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | NP-SUB_A 2 | 0.8422 | 0.81767 | -0.024534 |  | 0.9 | 1.05 | 0.17969 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | NP-SUB_A 2 | 0.8422 | 0.81767 | -0.024534 |  | 0.9 | 1.05 | 0.17406 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | NP-SUB_A 2 | 0.8422 | 0.81767 | -0.024534 |  | 0.9 | 1.05 | 0.17754 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | NP-SUB_A 2 | 0.8422 | 0.81767 | -0.024534 |  | 0.9 | 1.05 | 0.1303 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | NP-SUB_A 2 | 0.8422 | 0.81767 | -0.024534 |  | 0.9 | 1.05 | 0.1303 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | NP-SUB_A 2 | 0.8422 | 0.81767 | -0.024534 |  | 0.9 | 1.05 | 0.18174 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | NP-SUB_A 2 | 0.8422 | 0.81767 | -0.024534 |  | 0.9 | 1.05 | 0.18244 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | NP-SUB_A 2 | 0.8422 | 0.81767 | -0.024534 |  | 0.9 | 1.05 | 0.19275 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | NP-SUB_A 2 | 0.8422 | 0.81767 | -0.024534 |  | 0.9 | 1.05 | 0.19304 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | NP-SUB_A 2 | 0.8422 | 0.81767 | -0.024534 |  | 0.9 | 1.05 | 0.19068 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | NP-SUB_A 2 | 0.8422 | 0.81767 | -0.024534 |  | 0.9 | 1.05 | 0.19114 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | NP-SUB_A 2 | 0.8422 | 0.81767 | -0.024534 |  | 0.9 | 1.05 | 0.19232 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | NP-SUB_A 2 | 0.8422 | 0.81767 | -0.024534 |  | 0.9 | 1.05 | 0.17996 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | NP-SUB_A 2 | 0.8422 | 0.81767 | -0.024534 |  | 0.9 | 1.05 | 0.17996 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | NP-SUB_A 2 | 0.8422 | 0.81767 | -0.024534 |  | 0.9 | 1.05 | 0.18769 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | NP-SUB_A 2 | 0.8422 | 0.81767 | -0.024534 |  | 0.9 | 1.05 | 0.18769 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | NP-SUB_A 2 | 0.8422 | 0.81767 | -0.024534 |  | 0.9 | 1.05 | 0.4918 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | NP-SUB_A 2 | 0.8422 | 0.81767 | -0.024534 |  | 0.9 | 1.05 | 0.1947 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | NP-SUB_A 2 | 0.84357 | 0.82521 | -0.01836 |  | 0.9 | 1.05 | 0.081174 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | NP-SUB_A 2 | 0.84357 | 0.82521 | -0.01836 |  | 0.9 | 1.05 | 0.19645 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | NP-SUB_A 2 | 0.84357 | 0.82521 | -0.01836 |  | 0.9 | 1.05 | 0.23843 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | NP-SUB_A 2 | 0.84357 | 0.82521 | -0.01836 |  | 0.9 | 1.05 | 0.23843 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | NP-SUB_A 2 | 0.84357 | 0.82521 | -0.01836 |  | 0.9 | 1.05 | 0.17969 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | NP-SUB_A 2 | 0.84357 | 0.82521 | -0.01836 |  | 0.9 | 1.05 | 0.17406 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | NP-SUB_A 2 | 0.84357 | 0.82521 | -0.01836 |  | 0.9 | 1.05 | 0.17754 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | NP-SUB_A 2 | 0.84357 | 0.82521 | -0.01836 |  | 0.9 | 1.05 | 0.1303 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | NP-SUB_A 2 | 0.84357 | 0.82521 | -0.01836 |  | 0.9 | 1.05 | 0.1303 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | NP-SUB_A 2 | 0.84357 | 0.82521 | -0.01836 |  | 0.9 | 1.05 | 0.18174 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | NP-SUB_A 2 | 0.84357 | 0.82521 | -0.01836 |  | 0.9 | 1.05 | 0.18244 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | NP-SUB_A 2 | 0.84357 | 0.82521 | -0.01836 |  | 0.9 | 1.05 | 0.19275 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | NP-SUB_A 2 | 0.84357 | 0.82521 | -0.01836 |  | 0.9 | 1.05 | 0.19304 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | NP-SUB_A 2 | 0.84357 | 0.82521 | -0.01836 |  | 0.9 | 1.05 | 0.19068 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | NP-SUB_A 2 | 0.84357 | 0.82521 | -0.01836 |  | 0.9 | 1.05 | 0.19114 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | NP-SUB_A 2 | 0.84357 | 0.82521 | -0.01836 |  | 0.9 | 1.05 | 0.19232 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | NP-SUB_A 2 | 0.84357 | 0.82521 | -0.01836 |  | 0.9 | 1.05 | 0.17996 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | NP-SUB_A 2 | 0.84357 | 0.82521 | -0.01836 |  | 0.9 | 1.05 | 0.17996 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | NP-SUB_A 2 | 0.84357 | 0.82521 | -0.01836 |  | 0.9 | 1.05 | 0.18769 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | NP-SUB_A 2 | 0.84357 | 0.82521 | -0.01836 |  | 0.9 | 1.05 | 0.18769 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | NP-SUB_A 2 | 0.84357 | 0.82521 | -0.01836 |  | 0.9 | 1.05 | 0.4918 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | NP-SUB_A 2 | 0.84357 | 0.82521 | -0.01836 |  | 0.9 | 1.05 | 0.1947 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | NP-VALERO_P2 | 0.66395 | 0.64062 | -0.023326 |  | 0.9 | 1.05 | 0.081174 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | NP-VALERO_P2 | 0.66395 | 0.64062 | -0.023326 |  | 0.9 | 1.05 | 0.19645 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | NP-VALERO_P2 | 0.66395 | 0.64062 | -0.023326 |  | 0.9 | 1.05 | 0.23843 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | NP-VALERO_P2 | 0.66395 | 0.64062 | -0.023326 |  | 0.9 | 1.05 | 0.23843 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | NP-VALERO_P2 | 0.66395 | 0.64062 | -0.023326 |  | 0.9 | 1.05 | 0.17969 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | NP-VALERO_P2 | 0.66395 | 0.64062 | -0.023326 |  | 0.9 | 1.05 | 0.17406 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | NP-VALERO_P2 | 0.66395 | 0.64062 | -0.023326 |  | 0.9 | 1.05 | 0.17754 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | NP-VALERO_P2 | 0.66395 | 0.64062 | -0.023326 |  | 0.9 | 1.05 | 0.1303 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | NP-VALERO_P2 | 0.66395 | 0.64062 | -0.023326 |  | 0.9 | 1.05 | 0.1303 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | NP-VALERO_P2 | 0.66395 | 0.64062 | -0.023326 |  | 0.9 | 1.05 | 0.18174 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | NP-VALERO_P2 | 0.66395 | 0.64062 | -0.023326 |  | 0.9 | 1.05 | 0.18244 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | NP-VALERO_P2 | 0.66395 | 0.64062 | -0.023326 |  | 0.9 | 1.05 | 0.19275 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | NP-VALERO_P2 | 0.66395 | 0.64062 | -0.023326 |  | 0.9 | 1.05 | 0.19304 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | NP-VALERO_P2 | 0.66395 | 0.64062 | -0.023326 |  | 0.9 | 1.05 | 0.19068 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | NP-VALERO_P2 | 0.66395 | 0.64062 | -0.023326 |  | 0.9 | 1.05 | 0.19114 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | NP-VALERO_P2 | 0.66395 | 0.64062 | -0.023326 |  | 0.9 | 1.05 | 0.19232 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | NP-VALERO_P2 | 0.66395 | 0.64062 | -0.023326 |  | 0.9 | 1.05 | 0.17996 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | NP-VALERO_P2 | 0.66395 | 0.64062 | -0.023326 |  | 0.9 | 1.05 | 0.17996 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | NP-VALERO_P2 | 0.66395 | 0.64062 | -0.023326 |  | 0.9 | 1.05 | 0.18769 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | NP-VALERO_P2 | 0.66395 | 0.64062 | -0.023326 |  | 0.9 | 1.05 | 0.18769 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | NP-VALERO_P2 | 0.66395 | 0.64062 | -0.023326 |  | 0.9 | 1.05 | 0.4918 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | NP-VALERO_P2 | 0.66395 | 0.64062 | -0.023326 |  | 0.9 | 1.05 | 0.1947 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | NP-VALERO_P2 | 0.66392 | 0.64068 | -0.023242 |  | 0.9 | 1.05 | 0.081174 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | NP-VALERO_P2 | 0.66392 | 0.64068 | -0.023242 |  | 0.9 | 1.05 | 0.19645 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | NP-VALERO_P2 | 0.66392 | 0.64068 | -0.023242 |  | 0.9 | 1.05 | 0.23843 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | NP-VALERO_P2 | 0.66392 | 0.64068 | -0.023242 |  | 0.9 | 1.05 | 0.23843 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | NP-VALERO_P2 | 0.66392 | 0.64068 | -0.023242 |  | 0.9 | 1.05 | 0.17969 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | NP-VALERO_P2 | 0.66392 | 0.64068 | -0.023242 |  | 0.9 | 1.05 | 0.17406 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | NP-VALERO_P2 | 0.66392 | 0.64068 | -0.023242 |  | 0.9 | 1.05 | 0.17754 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | NP-VALERO_P2 | 0.66392 | 0.64068 | -0.023242 |  | 0.9 | 1.05 | 0.1303 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | NP-VALERO_P2 | 0.66392 | 0.64068 | -0.023242 |  | 0.9 | 1.05 | 0.1303 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | NP-VALERO_P2 | 0.66392 | 0.64068 | -0.023242 |  | 0.9 | 1.05 | 0.18174 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | NP-VALERO_P2 | 0.66392 | 0.64068 | -0.023242 |  | 0.9 | 1.05 | 0.18244 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | NP-VALERO_P2 | 0.66392 | 0.64068 | -0.023242 |  | 0.9 | 1.05 | 0.19275 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | NP-VALERO_P2 | 0.66392 | 0.64068 | -0.023242 |  | 0.9 | 1.05 | 0.19304 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | NP-VALERO_P2 | 0.66392 | 0.64068 | -0.023242 |  | 0.9 | 1.05 | 0.19068 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | NP-VALERO_P2 | 0.66392 | 0.64068 | -0.023242 |  | 0.9 | 1.05 | 0.19114 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | NP-VALERO_P2 | 0.66392 | 0.64068 | -0.023242 |  | 0.9 | 1.05 | 0.19232 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | NP-VALERO_P2 | 0.66392 | 0.64068 | -0.023242 |  | 0.9 | 1.05 | 0.17996 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | NP-VALERO_P2 | 0.66392 | 0.64068 | -0.023242 |  | 0.9 | 1.05 | 0.17996 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | NP-VALERO_P2 | 0.66392 | 0.64068 | -0.023242 |  | 0.9 | 1.05 | 0.18769 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | NP-VALERO_P2 | 0.66392 | 0.64068 | -0.023242 |  | 0.9 | 1.05 | 0.18769 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | NP-VALERO_P2 | 0.66392 | 0.64068 | -0.023242 |  | 0.9 | 1.05 | 0.4918 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | NP-VALERO_P2 | 0.66392 | 0.64068 | -0.023242 |  | 0.9 | 1.05 | 0.1947 | Single 511584 O.K.U.2-7 345 762467 G18-015-TAP 345 1 | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | NP-VALERO_P2 | 0.6642 | 0.64114 | -0.023058 |  | 0.9 | 1.05 | 0.081174 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | NP-VALERO_P2 | 0.6642 | 0.64114 | -0.023058 |  | 0.9 | 1.05 | 0.19645 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | NP-VALERO_P2 | 0.6642 | 0.64114 | -0.023058 |  | 0.9 | 1.05 | 0.23843 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | NP-VALERO_P2 | 0.6642 | 0.64114 | -0.023058 |  | 0.9 | 1.05 | 0.23843 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | NP-VALERO_P2 | 0.6642 | 0.64114 | -0.023058 |  | 0.9 | 1.05 | 0.17969 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | NP-VALERO_P2 | 0.6642 | 0.64114 | -0.023058 |  | 0.9 | 1.05 | 0.17406 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | NP-VALERO_P2 | 0.6642 | 0.64114 | -0.023058 |  | 0.9 | 1.05 | 0.17754 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | NP-VALERO_P2 | 0.6642 | 0.64114 | -0.023058 |  | 0.9 | 1.05 | 0.1303 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | NP-VALERO_P2 | 0.6642 | 0.64114 | -0.023058 |  | 0.9 | 1.05 | 0.1303 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | NP-VALERO_P2 | 0.6642 | 0.64114 | -0.023058 |  | 0.9 | 1.05 | 0.18174 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | NP-VALERO_P2 | 0.6642 | 0.64114 | -0.023058 |  | 0.9 | 1.05 | 0.18244 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | NP-VALERO_P2 | 0.6642 | 0.64114 | -0.023058 |  | 0.9 | 1.05 | 0.19275 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | NP-VALERO_P2 | 0.6642 | 0.64114 | -0.023058 |  | 0.9 | 1.05 | 0.19304 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | NP-VALERO_P2 | 0.6642 | 0.64114 | -0.023058 |  | 0.9 | 1.05 | 0.19068 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | NP-VALERO_P2 | 0.6642 | 0.64114 | -0.023058 |  | 0.9 | 1.05 | 0.19114 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | NP-VALERO_P2 | 0.6642 | 0.64114 | -0.023058 |  | 0.9 | 1.05 | 0.19232 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | NP-VALERO_P2 | 0.6642 | 0.64114 | -0.023058 |  | 0.9 | 1.05 | 0.17996 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | NP-VALERO_P2 | 0.6642 | 0.64114 | -0.023058 |  | 0.9 | 1.05 | 0.17996 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | NP-VALERO_P2 | 0.6642 | 0.64114 | -0.023058 |  | 0.9 | 1.05 | 0.18769 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | NP-VALERO_P2 | 0.6642 | 0.64114 | -0.023058 |  | 0.9 | 1.05 | 0.18769 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | NP-VALERO_P2 | 0.6642 | 0.64114 | -0.023058 |  | 0.9 | 1.05 | 0.4918 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | NP-VALERO_P2 | 0.6642 | 0.64114 | -0.023058 |  | 0.9 | 1.05 | 0.1947 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 2.4 MVAR switched shunt at NP-SUB_A 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | NP-VALERO_P2 | 0.66213 | 0.63127 | -0.030865 |  | 0.9 | 1.05 | 0.081174 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | NP-VALERO_P2 | 0.66213 | 0.63127 | -0.030865 |  | 0.9 | 1.05 | 0.19645 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | NP-VALERO_P2 | 0.66213 | 0.63127 | -0.030865 |  | 0.9 | 1.05 | 0.23843 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | NP-VALERO_P2 | 0.66213 | 0.63127 | -0.030865 |  | 0.9 | 1.05 | 0.23843 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | NP-VALERO_P2 | 0.66213 | 0.63127 | -0.030865 |  | 0.9 | 1.05 | 0.17969 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | NP-VALERO_P2 | 0.66213 | 0.63127 | -0.030865 |  | 0.9 | 1.05 | 0.17406 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | NP-VALERO_P2 | 0.66213 | 0.63127 | -0.030865 |  | 0.9 | 1.05 | 0.17754 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | NP-VALERO_P2 | 0.66213 | 0.63127 | -0.030865 |  | 0.9 | 1.05 | 0.1303 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | NP-VALERO_P2 | 0.66213 | 0.63127 | -0.030865 |  | 0.9 | 1.05 | 0.1303 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | NP-VALERO_P2 | 0.66213 | 0.63127 | -0.030865 |  | 0.9 | 1.05 | 0.18174 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | NP-VALERO_P2 | 0.66213 | 0.63127 | -0.030865 |  | 0.9 | 1.05 | 0.18244 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | NP-VALERO_P2 | 0.66213 | 0.63127 | -0.030865 |  | 0.9 | 1.05 | 0.19275 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | NP-VALERO_P2 | 0.66213 | 0.63127 | -0.030865 |  | 0.9 | 1.05 | 0.19304 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | NP-VALERO_P2 | 0.66213 | 0.63127 | -0.030865 |  | 0.9 | 1.05 | 0.19068 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | NP-VALERO_P2 | 0.66213 | 0.63127 | -0.030865 |  | 0.9 | 1.05 | 0.19114 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | NP-VALERO_P2 | 0.66213 | 0.63127 | -0.030865 |  | 0.9 | 1.05 | 0.19232 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | NP-VALERO_P2 | 0.66213 | 0.63127 | -0.030865 |  | 0.9 | 1.05 | 0.17996 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | NP-VALERO_P2 | 0.66213 | 0.63127 | -0.030865 |  | 0.9 | 1.05 | 0.17996 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | NP-VALERO_P2 | 0.66213 | 0.63127 | -0.030865 |  | 0.9 | 1.05 | 0.18769 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | NP-VALERO_P2 | 0.66213 | 0.63127 | -0.030865 |  | 0.9 | 1.05 | 0.18769 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | NP-VALERO_P2 | 0.66213 | 0.63127 | -0.030865 |  | 0.9 | 1.05 | 0.4918 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | NP-VALERO_P2 | 0.66213 | 0.63127 | -0.030865 |  | 0.9 | 1.05 | 0.1947 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 0.1 MVAR switched shunt at NP-SHATTUCK2 69 kV
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | NP-VALERO_P2 | 0.66389 | 0.64061 | -0.023277 |  | 0.9 | 1.05 | 0.081174 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | NP-VALERO_P2 | 0.66389 | 0.64061 | -0.023277 |  | 0.9 | 1.05 | 0.19645 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | NP-VALERO_P2 | 0.66389 | 0.64061 | -0.023277 |  | 0.9 | 1.05 | 0.23843 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | NP-VALERO_P2 | 0.66389 | 0.64061 | -0.023277 |  | 0.9 | 1.05 | 0.23843 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | NP-VALERO_P2 | 0.66389 | 0.64061 | -0.023277 |  | 0.9 | 1.05 | 0.17969 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | NP-VALERO_P2 | 0.66389 | 0.64061 | -0.023277 |  | 0.9 | 1.05 | 0.17406 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | NP-VALERO_P2 | 0.66389 | 0.64061 | -0.023277 |  | 0.9 | 1.05 | 0.17754 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | NP-VALERO_P2 | 0.66389 | 0.64061 | -0.023277 |  | 0.9 | 1.05 | 0.1303 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | NP-VALERO_P2 | 0.66389 | 0.64061 | -0.023277 |  | 0.9 | 1.05 | 0.1303 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | NP-VALERO_P2 | 0.66389 | 0.64061 | -0.023277 |  | 0.9 | 1.05 | 0.18174 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | NP-VALERO_P2 | 0.66389 | 0.64061 | -0.023277 |  | 0.9 | 1.05 | 0.18244 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | NP-VALERO_P2 | 0.66389 | 0.64061 | -0.023277 |  | 0.9 | 1.05 | 0.19275 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | NP-VALERO_P2 | 0.66389 | 0.64061 | -0.023277 |  | 0.9 | 1.05 | 0.19304 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | NP-VALERO_P2 | 0.66389 | 0.64061 | -0.023277 |  | 0.9 | 1.05 | 0.19068 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | NP-VALERO_P2 | 0.66389 | 0.64061 | -0.023277 |  | 0.9 | 1.05 | 0.19114 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | NP-VALERO_P2 | 0.66389 | 0.64061 | -0.023277 |  | 0.9 | 1.05 | 0.19232 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | NP-VALERO_P2 | 0.66389 | 0.64061 | -0.023277 |  | 0.9 | 1.05 | 0.17996 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | NP-VALERO_P2 | 0.66389 | 0.64061 | -0.023277 |  | 0.9 | 1.05 | 0.17996 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | NP-VALERO_P2 | 0.66389 | 0.64061 | -0.023277 |  | 0.9 | 1.05 | 0.18769 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | NP-VALERO_P2 | 0.66389 | 0.64061 | -0.023277 |  | 0.9 | 1.05 | 0.18769 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | NP-VALERO_P2 | 0.66389 | 0.64061 | -0.023277 |  | 0.9 | 1.05 | 0.4918 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | NP-VALERO_P2 | 0.66389 | 0.64061 | -0.023277 |  | 0.9 | 1.05 | 0.1947 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | None
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | RB-477_TP 2 | 0.91175 | 0.89029 | -0.021457 |  | 0.9 | 1.05 | 0.37235 | Single 523220 XIT_INTG3 115 523228 DALLAM3 115 1 | Add 8 MVAR switched shunt at RB-N_SEDAN 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | RB-477_TP 2 | 0.91175 | 0.89029 | -0.021457 |  | 0.9 | 1.05 | 0.37235 | Single 523220 XIT_INTG3 115 523228 DALLAM3 115 1 | Add 8 MVAR switched shunt at RB-N_SEDAN 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | RB-477_TP 2 | 0.91175 | 0.89029 | -0.021457 |  | 0.9 | 1.05 | 0.37235 | P12:115:SPS:W80.1.XIT.DALM:::HV: | Add 8 MVAR switched shunt at RB-N_SEDAN 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | RB-477_TP 2 | 0.91175 | 0.89029 | -0.021457 |  | 0.9 | 1.05 | 0.37235 | P12:115:SPS:W80.1.XIT.DALM:::HV: | Add 8 MVAR switched shunt at RB-N_SEDAN 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | RB-DALHART 2 | 0.91401 | 0.89264 | -0.021368 |  | 0.9 | 1.05 | 0.37235 | Single 523220 XIT_INTG3 115 523228 DALLAM3 115 1 | Add 8 MVAR switched shunt at RB-N_SEDAN 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | RB-DALHART 2 | 0.91401 | 0.89264 | -0.021368 |  | 0.9 | 1.05 | 0.37235 | Single 523220 XIT_INTG3 115 523228 DALLAM3 115 1 | Add 8 MVAR switched shunt at RB-N_SEDAN 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | RB-DALHART 2 | 0.91401 | 0.89264 | -0.021368 |  | 0.9 | 1.05 | 0.37235 | P12:115:SPS:W80.1.XIT.DALM:::HV: | Add 8 MVAR switched shunt at RB-N_SEDAN 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | RB-DALHART 2 | 0.91401 | 0.89264 | -0.021368 |  | 0.9 | 1.05 | 0.37235 | P12:115:SPS:W80.1.XIT.DALM:::HV: | Add 8 MVAR switched shunt at RB-N_SEDAN 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | RB-DALLAM 2 | 0.91622 | 0.89491 | -0.021303 |  | 0.9 | 1.05 | 0.37235 | Single 523220 XIT_INTG3 115 523228 DALLAM3 115 1 | Add 8 MVAR switched shunt at RB-N_SEDAN 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | RB-DALLAM 2 | 0.91622 | 0.89491 | -0.021303 |  | 0.9 | 1.05 | 0.37235 | Single 523220 XIT_INTG3 115 523228 DALLAM3 115 1 | Add 8 MVAR switched shunt at RB-N_SEDAN 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | RB-DALLAM 2 | 0.91622 | 0.89491 | -0.021303 |  | 0.9 | 1.05 | 0.37235 | P12:115:SPS:W80.1.XIT.DALM:::HV: | Add 8 MVAR switched shunt at RB-N_SEDAN 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | RB-DALLAM 2 | 0.91622 | 0.89491 | -0.021303 |  | 0.9 | 1.05 | 0.37235 | P12:115:SPS:W80.1.XIT.DALM:::HV: | Add 8 MVAR switched shunt at RB-N_SEDAN 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | RB-NMO1_SW 2 | 0.82758 | 0.80331 | -0.024274 |  | 0.9 | 1.05 | 0.37235 | Single 523220 XIT_INTG3 115 523228 DALLAM3 115 1 | Add 8 MVAR switched shunt at RB-N_SEDAN 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | RB-NMO1_SW 2 | 0.82758 | 0.80331 | -0.024274 |  | 0.9 | 1.05 | 0.37235 | Single 523220 XIT_INTG3 115 523228 DALLAM3 115 1 | Add 8 MVAR switched shunt at RB-N_SEDAN 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | RB-NMO1_SW 2 | 0.82758 | 0.80331 | -0.024274 |  | 0.9 | 1.05 | 0.37235 | P12:115:SPS:W80.1.XIT.DALM:::HV: | Add 8 MVAR switched shunt at RB-N_SEDAN 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | RB-NMO1_SW 2 | 0.82758 | 0.80331 | -0.024274 |  | 0.9 | 1.05 | 0.37235 | P12:115:SPS:W80.1.XIT.DALM:::HV: | Add 8 MVAR switched shunt at RB-N_SEDAN 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | RB-N_SEDAN 2 | 0.83914 | 0.8153 | -0.023848 |  | 0.9 | 1.05 | 0.37235 | Single 523220 XIT_INTG3 115 523228 DALLAM3 115 1 | Add 8 MVAR switched shunt at RB-N_SEDAN 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | RB-N_SEDAN 2 | 0.83914 | 0.8153 | -0.023848 |  | 0.9 | 1.05 | 0.37235 | Single 523220 XIT_INTG3 115 523228 DALLAM3 115 1 | Add 8 MVAR switched shunt at RB-N_SEDAN 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | RB-N_SEDAN 2 | 0.83914 | 0.8153 | -0.023848 |  | 0.9 | 1.05 | 0.37235 | P12:115:SPS:W80.1.XIT.DALM:::HV: | Add 8 MVAR switched shunt at RB-N_SEDAN 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | RB-N_SEDAN 2 | 0.83914 | 0.8153 | -0.023848 |  | 0.9 | 1.05 | 0.37235 | P12:115:SPS:W80.1.XIT.DALM:::HV: | Add 8 MVAR switched shunt at RB-N_SEDAN 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | RB-TEXLINE 2 | 0.82758 | 0.80331 | -0.024274 |  | 0.9 | 1.05 | 0.37235 | Single 523220 XIT_INTG3 115 523228 DALLAM3 115 1 | Add 8 MVAR switched shunt at RB-N_SEDAN 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | RB-TEXLINE 2 | 0.82758 | 0.80331 | -0.024274 |  | 0.9 | 1.05 | 0.37235 | Single 523220 XIT_INTG3 115 523228 DALLAM3 115 1 | Add 8 MVAR switched shunt at RB-N_SEDAN 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | RB-TEXLINE 2 | 0.82758 | 0.80331 | -0.024274 |  | 0.9 | 1.05 | 0.37235 | P12:115:SPS:W80.1.XIT.DALM:::HV: | Add 8 MVAR switched shunt at RB-N_SEDAN 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | RB-TEXLINE 2 | 0.82758 | 0.80331 | -0.024274 |  | 0.9 | 1.05 | 0.37235 | P12:115:SPS:W80.1.XIT.DALM:::HV: | Add 8 MVAR switched shunt at RB-N_SEDAN 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | RB-TEXLN_SW2 | 0.83046 | 0.80628 | -0.024177 |  | 0.9 | 1.05 | 0.37235 | Single 523220 XIT_INTG3 115 523228 DALLAM3 115 1 | Add 8 MVAR switched shunt at RB-N_SEDAN 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | RB-TEXLN_SW2 | 0.83046 | 0.80628 | -0.024177 |  | 0.9 | 1.05 | 0.37235 | Single 523220 XIT_INTG3 115 523228 DALLAM3 115 1 | Add 8 MVAR switched shunt at RB-N_SEDAN 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | RB-TEXLN_SW2 | 0.83046 | 0.80628 | -0.024177 |  | 0.9 | 1.05 | 0.37235 | P12:115:SPS:W80.1.XIT.DALM:::HV: | Add 8 MVAR switched shunt at RB-N_SEDAN 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | RB-TEXLN_SW2 | 0.83046 | 0.80628 | -0.024177 |  | 0.9 | 1.05 | 0.37235 | P12:115:SPS:W80.1.XIT.DALM:::HV: | Add 8 MVAR switched shunt at RB-N_SEDAN 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | RB-TEXRURAL2 | 0.82931 | 0.8051 | -0.024213 |  | 0.9 | 1.05 | 0.37235 | Single 523220 XIT_INTG3 115 523228 DALLAM3 115 1 | Add 8 MVAR switched shunt at RB-N_SEDAN 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | RB-TEXRURAL2 | 0.82931 | 0.8051 | -0.024213 |  | 0.9 | 1.05 | 0.37235 | Single 523220 XIT_INTG3 115 523228 DALLAM3 115 1 | Add 8 MVAR switched shunt at RB-N_SEDAN 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | RB-TEXRURAL2 | 0.82931 | 0.8051 | -0.024213 |  | 0.9 | 1.05 | 0.37235 | P12:115:SPS:W80.1.XIT.DALM:::HV: | Add 8 MVAR switched shunt at RB-N_SEDAN 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | RB-TEXRURAL2 | 0.82931 | 0.8051 | -0.024213 |  | 0.9 | 1.05 | 0.37235 | P12:115:SPS:W80.1.XIT.DALM:::HV: | Add 8 MVAR switched shunt at RB-N_SEDAN 2 69 kV
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | SHAM 3WT | 0.94704 | 0.89172 | -0.055318 |  | 0.92 | 1.05 | 0.081174 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | SHAM 3WT | 0.94704 | 0.89172 | -0.055318 |  | 0.92 | 1.05 | 0.19645 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | SHAM 3WT | 0.94704 | 0.89172 | -0.055318 |  | 0.92 | 1.05 | 0.23843 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | SHAM 3WT | 0.94704 | 0.89172 | -0.055318 |  | 0.92 | 1.05 | 0.23843 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | SHAM 3WT | 0.94704 | 0.89172 | -0.055318 |  | 0.92 | 1.05 | 0.17969 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | SHAM 3WT | 0.94704 | 0.89172 | -0.055318 |  | 0.92 | 1.05 | 0.17406 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | SHAM 3WT | 0.94704 | 0.89172 | -0.055318 |  | 0.92 | 1.05 | 0.17754 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | SHAM 3WT | 0.94704 | 0.89172 | -0.055318 |  | 0.92 | 1.05 | 0.1303 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | SHAM 3WT | 0.94704 | 0.89172 | -0.055318 |  | 0.92 | 1.05 | 0.1303 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | SHAM 3WT | 0.94704 | 0.89172 | -0.055318 |  | 0.92 | 1.05 | 0.18174 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | SHAM 3WT | 0.94704 | 0.89172 | -0.055318 |  | 0.92 | 1.05 | 0.18244 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | SHAM 3WT | 0.94704 | 0.89172 | -0.055318 |  | 0.92 | 1.05 | 0.19275 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | SHAM 3WT | 0.94704 | 0.89172 | -0.055318 |  | 0.92 | 1.05 | 0.19304 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | SHAM 3WT | 0.94704 | 0.89172 | -0.055318 |  | 0.92 | 1.05 | 0.19068 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | SHAM 3WT | 0.94704 | 0.89172 | -0.055318 |  | 0.92 | 1.05 | 0.19114 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | SHAM 3WT | 0.94704 | 0.89172 | -0.055318 |  | 0.92 | 1.05 | 0.19232 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | SHAM 3WT | 0.94704 | 0.89172 | -0.055318 |  | 0.92 | 1.05 | 0.17996 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | SHAM 3WT | 0.94704 | 0.89172 | -0.055318 |  | 0.92 | 1.05 | 0.17996 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | SHAM 3WT | 0.94704 | 0.89172 | -0.055318 |  | 0.92 | 1.05 | 0.18769 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | SHAM 3WT | 0.94704 | 0.89172 | -0.055318 |  | 0.92 | 1.05 | 0.18769 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | SHAM 3WT | 0.94704 | 0.89172 | -0.055318 |  | 0.92 | 1.05 | 0.4918 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | SHAM 3WT | 0.94704 | 0.89172 | -0.055318 |  | 0.92 | 1.05 | 0.1947 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | SHAM 3WT | 0.95194 | 0.90251 | -0.049433 |  | 0.92 | 1.05 | 0.081174 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | SHAM 3WT | 0.95194 | 0.90251 | -0.049433 |  | 0.92 | 1.05 | 0.19645 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | SHAM 3WT | 0.95194 | 0.90251 | -0.049433 |  | 0.92 | 1.05 | 0.23843 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | SHAM 3WT | 0.95194 | 0.90251 | -0.049433 |  | 0.92 | 1.05 | 0.23843 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | SHAM 3WT | 0.95194 | 0.90251 | -0.049433 |  | 0.92 | 1.05 | 0.17969 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | SHAM 3WT | 0.95194 | 0.90251 | -0.049433 |  | 0.92 | 1.05 | 0.17406 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | SHAM 3WT | 0.95194 | 0.90251 | -0.049433 |  | 0.92 | 1.05 | 0.17754 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | SHAM 3WT | 0.95194 | 0.90251 | -0.049433 |  | 0.92 | 1.05 | 0.1303 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | SHAM 3WT | 0.95194 | 0.90251 | -0.049433 |  | 0.92 | 1.05 | 0.1303 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | SHAM 3WT | 0.95194 | 0.90251 | -0.049433 |  | 0.92 | 1.05 | 0.18174 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | SHAM 3WT | 0.95194 | 0.90251 | -0.049433 |  | 0.92 | 1.05 | 0.18244 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | SHAM 3WT | 0.95194 | 0.90251 | -0.049433 |  | 0.92 | 1.05 | 0.19275 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | SHAM 3WT | 0.95194 | 0.90251 | -0.049433 |  | 0.92 | 1.05 | 0.19304 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | SHAM 3WT | 0.95194 | 0.90251 | -0.049433 |  | 0.92 | 1.05 | 0.19068 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | SHAM 3WT | 0.95194 | 0.90251 | -0.049433 |  | 0.92 | 1.05 | 0.19114 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | SHAM 3WT | 0.95194 | 0.90251 | -0.049433 |  | 0.92 | 1.05 | 0.19232 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | SHAM 3WT | 0.95194 | 0.90251 | -0.049433 |  | 0.92 | 1.05 | 0.17996 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | SHAM 3WT | 0.95194 | 0.90251 | -0.049433 |  | 0.92 | 1.05 | 0.17996 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | SHAM 3WT | 0.95194 | 0.90251 | -0.049433 |  | 0.92 | 1.05 | 0.18769 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | SHAM 3WT | 0.95194 | 0.90251 | -0.049433 |  | 0.92 | 1.05 | 0.18769 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | SHAM 3WT | 0.95194 | 0.90251 | -0.049433 |  | 0.92 | 1.05 | 0.4918 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | SHAM 3WT | 0.95194 | 0.90251 | -0.049433 |  | 0.92 | 1.05 | 0.1947 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | SHAM 3WT | 0.95284 | 0.90487 | -0.047964 |  | 0.92 | 1.05 | 0.081174 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | SHAM 3WT | 0.95284 | 0.90487 | -0.047964 |  | 0.92 | 1.05 | 0.19645 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | SHAM 3WT | 0.95284 | 0.90487 | -0.047964 |  | 0.92 | 1.05 | 0.23843 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | SHAM 3WT | 0.95284 | 0.90487 | -0.047964 |  | 0.92 | 1.05 | 0.23843 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | SHAM 3WT | 0.95284 | 0.90487 | -0.047964 |  | 0.92 | 1.05 | 0.17969 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | SHAM 3WT | 0.95284 | 0.90487 | -0.047964 |  | 0.92 | 1.05 | 0.17406 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | SHAM 3WT | 0.95284 | 0.90487 | -0.047964 |  | 0.92 | 1.05 | 0.17754 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | SHAM 3WT | 0.95284 | 0.90487 | -0.047964 |  | 0.92 | 1.05 | 0.1303 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | SHAM 3WT | 0.95284 | 0.90487 | -0.047964 |  | 0.92 | 1.05 | 0.1303 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | SHAM 3WT | 0.95284 | 0.90487 | -0.047964 |  | 0.92 | 1.05 | 0.18174 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | SHAM 3WT | 0.95284 | 0.90487 | -0.047964 |  | 0.92 | 1.05 | 0.18244 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | SHAM 3WT | 0.95284 | 0.90487 | -0.047964 |  | 0.92 | 1.05 | 0.19275 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | SHAM 3WT | 0.95284 | 0.90487 | -0.047964 |  | 0.92 | 1.05 | 0.19304 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | SHAM 3WT | 0.95284 | 0.90487 | -0.047964 |  | 0.92 | 1.05 | 0.19068 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | SHAM 3WT | 0.95284 | 0.90487 | -0.047964 |  | 0.92 | 1.05 | 0.19114 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | SHAM 3WT | 0.95284 | 0.90487 | -0.047964 |  | 0.92 | 1.05 | 0.19232 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | SHAM 3WT | 0.95284 | 0.90487 | -0.047964 |  | 0.92 | 1.05 | 0.17996 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | SHAM 3WT | 0.95284 | 0.90487 | -0.047964 |  | 0.92 | 1.05 | 0.17996 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | SHAM 3WT | 0.95284 | 0.90487 | -0.047964 |  | 0.92 | 1.05 | 0.18769 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | SHAM 3WT | 0.95284 | 0.90487 | -0.047964 |  | 0.92 | 1.05 | 0.18769 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | SHAM 3WT | 0.95284 | 0.90487 | -0.047964 |  | 0.92 | 1.05 | 0.4918 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | SHAM 3WT | 0.95284 | 0.90487 | -0.047964 |  | 0.92 | 1.05 | 0.1947 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | SHAM 3WT | 0.95489 | 0.90588 | -0.049009 |  | 0.92 | 1.05 | 0.081174 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | SHAM 3WT | 0.95489 | 0.90588 | -0.049009 |  | 0.92 | 1.05 | 0.19645 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | SHAM 3WT | 0.95489 | 0.90588 | -0.049009 |  | 0.92 | 1.05 | 0.23843 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | SHAM 3WT | 0.95489 | 0.90588 | -0.049009 |  | 0.92 | 1.05 | 0.23843 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | SHAM 3WT | 0.95489 | 0.90588 | -0.049009 |  | 0.92 | 1.05 | 0.17969 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | SHAM 3WT | 0.95489 | 0.90588 | -0.049009 |  | 0.92 | 1.05 | 0.17406 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | SHAM 3WT | 0.95489 | 0.90588 | -0.049009 |  | 0.92 | 1.05 | 0.17754 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | SHAM 3WT | 0.95489 | 0.90588 | -0.049009 |  | 0.92 | 1.05 | 0.1303 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | SHAM 3WT | 0.95489 | 0.90588 | -0.049009 |  | 0.92 | 1.05 | 0.1303 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | SHAM 3WT | 0.95489 | 0.90588 | -0.049009 |  | 0.92 | 1.05 | 0.18174 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | SHAM 3WT | 0.95489 | 0.90588 | -0.049009 |  | 0.92 | 1.05 | 0.18244 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | SHAM 3WT | 0.95489 | 0.90588 | -0.049009 |  | 0.92 | 1.05 | 0.19275 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | SHAM 3WT | 0.95489 | 0.90588 | -0.049009 |  | 0.92 | 1.05 | 0.19304 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | SHAM 3WT | 0.95489 | 0.90588 | -0.049009 |  | 0.92 | 1.05 | 0.19068 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | SHAM 3WT | 0.95489 | 0.90588 | -0.049009 |  | 0.92 | 1.05 | 0.19114 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | SHAM 3WT | 0.95489 | 0.90588 | -0.049009 |  | 0.92 | 1.05 | 0.19232 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | SHAM 3WT | 0.95489 | 0.90588 | -0.049009 |  | 0.92 | 1.05 | 0.17996 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | SHAM 3WT | 0.95489 | 0.90588 | -0.049009 |  | 0.92 | 1.05 | 0.17996 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | SHAM 3WT | 0.95489 | 0.90588 | -0.049009 |  | 0.92 | 1.05 | 0.18769 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | SHAM 3WT | 0.95489 | 0.90588 | -0.049009 |  | 0.92 | 1.05 | 0.18769 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | SHAM 3WT | 0.95489 | 0.90588 | -0.049009 |  | 0.92 | 1.05 | 0.4918 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | SHAM 3WT | 0.95489 | 0.90588 | -0.049009 |  | 0.92 | 1.05 | 0.1947 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | SHAM 3WT | 0.95498 | 0.9059 | -0.049081 |  | 0.92 | 1.05 | 0.081174 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | SHAM 3WT | 0.95498 | 0.9059 | -0.049081 |  | 0.92 | 1.05 | 0.19645 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | SHAM 3WT | 0.95498 | 0.9059 | -0.049081 |  | 0.92 | 1.05 | 0.23843 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | SHAM 3WT | 0.95498 | 0.9059 | -0.049081 |  | 0.92 | 1.05 | 0.23843 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | SHAM 3WT | 0.95498 | 0.9059 | -0.049081 |  | 0.92 | 1.05 | 0.17969 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | SHAM 3WT | 0.95498 | 0.9059 | -0.049081 |  | 0.92 | 1.05 | 0.17406 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | SHAM 3WT | 0.95498 | 0.9059 | -0.049081 |  | 0.92 | 1.05 | 0.17754 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | SHAM 3WT | 0.95498 | 0.9059 | -0.049081 |  | 0.92 | 1.05 | 0.1303 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | SHAM 3WT | 0.95498 | 0.9059 | -0.049081 |  | 0.92 | 1.05 | 0.1303 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | SHAM 3WT | 0.95498 | 0.9059 | -0.049081 |  | 0.92 | 1.05 | 0.18174 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | SHAM 3WT | 0.95498 | 0.9059 | -0.049081 |  | 0.92 | 1.05 | 0.18244 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | SHAM 3WT | 0.95498 | 0.9059 | -0.049081 |  | 0.92 | 1.05 | 0.19275 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | SHAM 3WT | 0.95498 | 0.9059 | -0.049081 |  | 0.92 | 1.05 | 0.19304 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | SHAM 3WT | 0.95498 | 0.9059 | -0.049081 |  | 0.92 | 1.05 | 0.19068 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | SHAM 3WT | 0.95498 | 0.9059 | -0.049081 |  | 0.92 | 1.05 | 0.19114 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | SHAM 3WT | 0.95498 | 0.9059 | -0.049081 |  | 0.92 | 1.05 | 0.19232 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | SHAM 3WT | 0.95498 | 0.9059 | -0.049081 |  | 0.92 | 1.05 | 0.17996 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | SHAM 3WT | 0.95498 | 0.9059 | -0.049081 |  | 0.92 | 1.05 | 0.17996 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | SHAM 3WT | 0.95498 | 0.9059 | -0.049081 |  | 0.92 | 1.05 | 0.18769 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | SHAM 3WT | 0.95498 | 0.9059 | -0.049081 |  | 0.92 | 1.05 | 0.18769 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | SHAM 3WT | 0.95498 | 0.9059 | -0.049081 |  | 0.92 | 1.05 | 0.4918 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | SHAM 3WT | 0.95498 | 0.9059 | -0.049081 |  | 0.92 | 1.05 | 0.1947 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | SHAM 4WT | 0.95421 | 0.90581 | -0.048401 |  | 0.92 | 1.05 | 0.081174 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | SHAM 4WT | 0.95421 | 0.90581 | -0.048401 |  | 0.92 | 1.05 | 0.19645 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | SHAM 4WT | 0.95421 | 0.90581 | -0.048401 |  | 0.92 | 1.05 | 0.23843 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | SHAM 4WT | 0.95421 | 0.90581 | -0.048401 |  | 0.92 | 1.05 | 0.23843 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | SHAM 4WT | 0.95421 | 0.90581 | -0.048401 |  | 0.92 | 1.05 | 0.17969 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | SHAM 4WT | 0.95421 | 0.90581 | -0.048401 |  | 0.92 | 1.05 | 0.17406 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | SHAM 4WT | 0.95421 | 0.90581 | -0.048401 |  | 0.92 | 1.05 | 0.17754 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | SHAM 4WT | 0.95421 | 0.90581 | -0.048401 |  | 0.92 | 1.05 | 0.1303 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | SHAM 4WT | 0.95421 | 0.90581 | -0.048401 |  | 0.92 | 1.05 | 0.1303 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | SHAM 4WT | 0.95421 | 0.90581 | -0.048401 |  | 0.92 | 1.05 | 0.18174 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | SHAM 4WT | 0.95421 | 0.90581 | -0.048401 |  | 0.92 | 1.05 | 0.18244 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | SHAM 4WT | 0.95421 | 0.90581 | -0.048401 |  | 0.92 | 1.05 | 0.19275 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | SHAM 4WT | 0.95421 | 0.90581 | -0.048401 |  | 0.92 | 1.05 | 0.19304 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | SHAM 4WT | 0.95421 | 0.90581 | -0.048401 |  | 0.92 | 1.05 | 0.19068 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | SHAM 4WT | 0.95421 | 0.90581 | -0.048401 |  | 0.92 | 1.05 | 0.19114 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | SHAM 4WT | 0.95421 | 0.90581 | -0.048401 |  | 0.92 | 1.05 | 0.19232 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | SHAM 4WT | 0.95421 | 0.90581 | -0.048401 |  | 0.92 | 1.05 | 0.17996 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | SHAM 4WT | 0.95421 | 0.90581 | -0.048401 |  | 0.92 | 1.05 | 0.17996 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | SHAM 4WT | 0.95421 | 0.90581 | -0.048401 |  | 0.92 | 1.05 | 0.18769 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | SHAM 4WT | 0.95421 | 0.90581 | -0.048401 |  | 0.92 | 1.05 | 0.18769 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | SHAM 4WT | 0.95421 | 0.90581 | -0.048401 |  | 0.92 | 1.05 | 0.4918 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | SHAM 4WT | 0.95421 | 0.90581 | -0.048401 |  | 0.92 | 1.05 | 0.1947 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | SHAM 4WT | 0.95832 | 0.91568 | -0.042635 |  | 0.92 | 1.05 | 0.081174 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | SHAM 4WT | 0.95832 | 0.91568 | -0.042635 |  | 0.92 | 1.05 | 0.19645 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | SHAM 4WT | 0.95832 | 0.91568 | -0.042635 |  | 0.92 | 1.05 | 0.23843 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | SHAM 4WT | 0.95832 | 0.91568 | -0.042635 |  | 0.92 | 1.05 | 0.23843 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | SHAM 4WT | 0.95832 | 0.91568 | -0.042635 |  | 0.92 | 1.05 | 0.17969 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | SHAM 4WT | 0.95832 | 0.91568 | -0.042635 |  | 0.92 | 1.05 | 0.17406 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | SHAM 4WT | 0.95832 | 0.91568 | -0.042635 |  | 0.92 | 1.05 | 0.17754 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | SHAM 4WT | 0.95832 | 0.91568 | -0.042635 |  | 0.92 | 1.05 | 0.1303 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | SHAM 4WT | 0.95832 | 0.91568 | -0.042635 |  | 0.92 | 1.05 | 0.1303 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | SHAM 4WT | 0.95832 | 0.91568 | -0.042635 |  | 0.92 | 1.05 | 0.18174 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | SHAM 4WT | 0.95832 | 0.91568 | -0.042635 |  | 0.92 | 1.05 | 0.18244 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | SHAM 4WT | 0.95832 | 0.91568 | -0.042635 |  | 0.92 | 1.05 | 0.19275 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | SHAM 4WT | 0.95832 | 0.91568 | -0.042635 |  | 0.92 | 1.05 | 0.19304 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | SHAM 4WT | 0.95832 | 0.91568 | -0.042635 |  | 0.92 | 1.05 | 0.19068 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | SHAM 4WT | 0.95832 | 0.91568 | -0.042635 |  | 0.92 | 1.05 | 0.19114 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | SHAM 4WT | 0.95832 | 0.91568 | -0.042635 |  | 0.92 | 1.05 | 0.19232 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | SHAM 4WT | 0.95832 | 0.91568 | -0.042635 |  | 0.92 | 1.05 | 0.17996 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | SHAM 4WT | 0.95832 | 0.91568 | -0.042635 |  | 0.92 | 1.05 | 0.17996 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | SHAM 4WT | 0.95832 | 0.91568 | -0.042635 |  | 0.92 | 1.05 | 0.18769 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | SHAM 4WT | 0.95832 | 0.91568 | -0.042635 |  | 0.92 | 1.05 | 0.18769 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | SHAM 4WT | 0.95832 | 0.91568 | -0.042635 |  | 0.92 | 1.05 | 0.4918 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | SHAM 4WT | 0.95832 | 0.91568 | -0.042635 |  | 0.92 | 1.05 | 0.1947 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | SHAM 4WT | 0.95907 | 0.91781 | -0.041258 |  | 0.92 | 1.05 | 0.081174 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | SHAM 4WT | 0.95907 | 0.91781 | -0.041258 |  | 0.92 | 1.05 | 0.19645 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | SHAM 4WT | 0.95907 | 0.91781 | -0.041258 |  | 0.92 | 1.05 | 0.23843 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | SHAM 4WT | 0.95907 | 0.91781 | -0.041258 |  | 0.92 | 1.05 | 0.23843 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | SHAM 4WT | 0.95907 | 0.91781 | -0.041258 |  | 0.92 | 1.05 | 0.17969 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | SHAM 4WT | 0.95907 | 0.91781 | -0.041258 |  | 0.92 | 1.05 | 0.17406 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | SHAM 4WT | 0.95907 | 0.91781 | -0.041258 |  | 0.92 | 1.05 | 0.17754 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | SHAM 4WT | 0.95907 | 0.91781 | -0.041258 |  | 0.92 | 1.05 | 0.1303 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | SHAM 4WT | 0.95907 | 0.91781 | -0.041258 |  | 0.92 | 1.05 | 0.1303 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | SHAM 4WT | 0.95907 | 0.91781 | -0.041258 |  | 0.92 | 1.05 | 0.18174 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | SHAM 4WT | 0.95907 | 0.91781 | -0.041258 |  | 0.92 | 1.05 | 0.18244 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | SHAM 4WT | 0.95907 | 0.91781 | -0.041258 |  | 0.92 | 1.05 | 0.19275 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | SHAM 4WT | 0.95907 | 0.91781 | -0.041258 |  | 0.92 | 1.05 | 0.19304 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | SHAM 4WT | 0.95907 | 0.91781 | -0.041258 |  | 0.92 | 1.05 | 0.19068 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | SHAM 4WT | 0.95907 | 0.91781 | -0.041258 |  | 0.92 | 1.05 | 0.19114 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | SHAM 4WT | 0.95907 | 0.91781 | -0.041258 |  | 0.92 | 1.05 | 0.19232 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | SHAM 4WT | 0.95907 | 0.91781 | -0.041258 |  | 0.92 | 1.05 | 0.17996 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | SHAM 4WT | 0.95907 | 0.91781 | -0.041258 |  | 0.92 | 1.05 | 0.17996 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | SHAM 4WT | 0.95907 | 0.91781 | -0.041258 |  | 0.92 | 1.05 | 0.18769 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | SHAM 4WT | 0.95907 | 0.91781 | -0.041258 |  | 0.92 | 1.05 | 0.18769 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | SHAM 4WT | 0.95907 | 0.91781 | -0.041258 |  | 0.92 | 1.05 | 0.4918 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | SHAM 4WT | 0.95907 | 0.91781 | -0.041258 |  | 0.92 | 1.05 | 0.1947 | P52:138:AEPW:NR5O.K.U:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | SHAM 4WT | 0.96071 | 0.91891 | -0.041799 |  | 0.92 | 1.05 | 0.081174 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | SHAM 4WT | 0.96071 | 0.91891 | -0.041799 |  | 0.92 | 1.05 | 0.19645 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | SHAM 4WT | 0.96071 | 0.91891 | -0.041799 |  | 0.92 | 1.05 | 0.23843 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | SHAM 4WT | 0.96071 | 0.91891 | -0.041799 |  | 0.92 | 1.05 | 0.23843 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | SHAM 4WT | 0.96071 | 0.91891 | -0.041799 |  | 0.92 | 1.05 | 0.17969 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | SHAM 4WT | 0.96071 | 0.91891 | -0.041799 |  | 0.92 | 1.05 | 0.17406 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | SHAM 4WT | 0.96071 | 0.91891 | -0.041799 |  | 0.92 | 1.05 | 0.17754 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | SHAM 4WT | 0.96071 | 0.91891 | -0.041799 |  | 0.92 | 1.05 | 0.1303 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | SHAM 4WT | 0.96071 | 0.91891 | -0.041799 |  | 0.92 | 1.05 | 0.1303 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | SHAM 4WT | 0.96071 | 0.91891 | -0.041799 |  | 0.92 | 1.05 | 0.18174 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | SHAM 4WT | 0.96071 | 0.91891 | -0.041799 |  | 0.92 | 1.05 | 0.18244 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | SHAM 4WT | 0.96071 | 0.91891 | -0.041799 |  | 0.92 | 1.05 | 0.19275 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | SHAM 4WT | 0.96071 | 0.91891 | -0.041799 |  | 0.92 | 1.05 | 0.19304 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | SHAM 4WT | 0.96071 | 0.91891 | -0.041799 |  | 0.92 | 1.05 | 0.19068 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | SHAM 4WT | 0.96071 | 0.91891 | -0.041799 |  | 0.92 | 1.05 | 0.19114 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | SHAM 4WT | 0.96071 | 0.91891 | -0.041799 |  | 0.92 | 1.05 | 0.19232 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | SHAM 4WT | 0.96071 | 0.91891 | -0.041799 |  | 0.92 | 1.05 | 0.17996 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | SHAM 4WT | 0.96071 | 0.91891 | -0.041799 |  | 0.92 | 1.05 | 0.17996 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | SHAM 4WT | 0.96071 | 0.91891 | -0.041799 |  | 0.92 | 1.05 | 0.18769 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | SHAM 4WT | 0.96071 | 0.91891 | -0.041799 |  | 0.92 | 1.05 | 0.18769 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | SHAM 4WT | 0.96071 | 0.91891 | -0.041799 |  | 0.92 | 1.05 | 0.4918 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | SHAM 4WT | 0.96071 | 0.91891 | -0.041799 |  | 0.92 | 1.05 | 0.1947 | Single 511456 O.K.U.-7 345 511584 O.K.U.2-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | SHAM 4WT | 0.96078 | 0.91892 | -0.041862 |  | 0.92 | 1.05 | 0.081174 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | SHAM 4WT | 0.96078 | 0.91892 | -0.041862 |  | 0.92 | 1.05 | 0.19645 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | SHAM 4WT | 0.96078 | 0.91892 | -0.041862 |  | 0.92 | 1.05 | 0.23843 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | SHAM 4WT | 0.96078 | 0.91892 | -0.041862 |  | 0.92 | 1.05 | 0.23843 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | SHAM 4WT | 0.96078 | 0.91892 | -0.041862 |  | 0.92 | 1.05 | 0.17969 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | SHAM 4WT | 0.96078 | 0.91892 | -0.041862 |  | 0.92 | 1.05 | 0.17406 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | SHAM 4WT | 0.96078 | 0.91892 | -0.041862 |  | 0.92 | 1.05 | 0.17754 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | SHAM 4WT | 0.96078 | 0.91892 | -0.041862 |  | 0.92 | 1.05 | 0.1303 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | SHAM 4WT | 0.96078 | 0.91892 | -0.041862 |  | 0.92 | 1.05 | 0.1303 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | SHAM 4WT | 0.96078 | 0.91892 | -0.041862 |  | 0.92 | 1.05 | 0.18174 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | SHAM 4WT | 0.96078 | 0.91892 | -0.041862 |  | 0.92 | 1.05 | 0.18244 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | SHAM 4WT | 0.96078 | 0.91892 | -0.041862 |  | 0.92 | 1.05 | 0.19275 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | SHAM 4WT | 0.96078 | 0.91892 | -0.041862 |  | 0.92 | 1.05 | 0.19304 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | SHAM 4WT | 0.96078 | 0.91892 | -0.041862 |  | 0.92 | 1.05 | 0.19068 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | SHAM 4WT | 0.96078 | 0.91892 | -0.041862 |  | 0.92 | 1.05 | 0.19114 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | SHAM 4WT | 0.96078 | 0.91892 | -0.041862 |  | 0.92 | 1.05 | 0.19232 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | SHAM 4WT | 0.96078 | 0.91892 | -0.041862 |  | 0.92 | 1.05 | 0.17996 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | SHAM 4WT | 0.96078 | 0.91892 | -0.041862 |  | 0.92 | 1.05 | 0.17996 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | SHAM 4WT | 0.96078 | 0.91892 | -0.041862 |  | 0.92 | 1.05 | 0.18769 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | SHAM 4WT | 0.96078 | 0.91892 | -0.041862 |  | 0.92 | 1.05 | 0.18769 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | SHAM 4WT | 0.96078 | 0.91892 | -0.041862 |  | 0.92 | 1.05 | 0.4918 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | SHAM 4WT | 0.96078 | 0.91892 | -0.041862 |  | 0.92 | 1.05 | 0.1947 | P12:345:SPS:J01:1:TUCOINT_O.K.U___:EHV: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | WELL 4WT | 0.95585 | 0.90958 | -0.046271 |  | 0.92 | 1.05 | 0.081174 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | WELL 4WT | 0.95585 | 0.90958 | -0.046271 |  | 0.92 | 1.05 | 0.19645 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | WELL 4WT | 0.95585 | 0.90958 | -0.046271 |  | 0.92 | 1.05 | 0.23843 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | WELL 4WT | 0.95585 | 0.90958 | -0.046271 |  | 0.92 | 1.05 | 0.23843 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | WELL 4WT | 0.95585 | 0.90958 | -0.046271 |  | 0.92 | 1.05 | 0.17969 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | WELL 4WT | 0.95585 | 0.90958 | -0.046271 |  | 0.92 | 1.05 | 0.17406 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | WELL 4WT | 0.95585 | 0.90958 | -0.046271 |  | 0.92 | 1.05 | 0.17754 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | WELL 4WT | 0.95585 | 0.90958 | -0.046271 |  | 0.92 | 1.05 | 0.1303 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | WELL 4WT | 0.95585 | 0.90958 | -0.046271 |  | 0.92 | 1.05 | 0.1303 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | WELL 4WT | 0.95585 | 0.90958 | -0.046271 |  | 0.92 | 1.05 | 0.18174 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | WELL 4WT | 0.95585 | 0.90958 | -0.046271 |  | 0.92 | 1.05 | 0.18244 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | WELL 4WT | 0.95585 | 0.90958 | -0.046271 |  | 0.92 | 1.05 | 0.19275 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | WELL 4WT | 0.95585 | 0.90958 | -0.046271 |  | 0.92 | 1.05 | 0.19304 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | WELL 4WT | 0.95585 | 0.90958 | -0.046271 |  | 0.92 | 1.05 | 0.19068 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | WELL 4WT | 0.95585 | 0.90958 | -0.046271 |  | 0.92 | 1.05 | 0.19114 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | WELL 4WT | 0.95585 | 0.90958 | -0.046271 |  | 0.92 | 1.05 | 0.19232 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | WELL 4WT | 0.95585 | 0.90958 | -0.046271 |  | 0.92 | 1.05 | 0.17996 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | WELL 4WT | 0.95585 | 0.90958 | -0.046271 |  | 0.92 | 1.05 | 0.17996 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | WELL 4WT | 0.95585 | 0.90958 | -0.046271 |  | 0.92 | 1.05 | 0.18769 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | WELL 4WT | 0.95585 | 0.90958 | -0.046271 |  | 0.92 | 1.05 | 0.18769 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | WELL 4WT | 0.95585 | 0.90958 | -0.046271 |  | 0.92 | 1.05 | 0.4918 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | WELL 4WT | 0.95585 | 0.90958 | -0.046271 |  | 0.92 | 1.05 | 0.1947 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | WELL 4WT | 0.95976 | 0.9191 | -0.040656 |  | 0.92 | 1.05 | 0.081174 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | WELL 4WT | 0.95976 | 0.9191 | -0.040656 |  | 0.92 | 1.05 | 0.19645 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | WELL 4WT | 0.95976 | 0.9191 | -0.040656 |  | 0.92 | 1.05 | 0.23843 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | WELL 4WT | 0.95976 | 0.9191 | -0.040656 |  | 0.92 | 1.05 | 0.23843 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | WELL 4WT | 0.95976 | 0.9191 | -0.040656 |  | 0.92 | 1.05 | 0.17969 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | WELL 4WT | 0.95976 | 0.9191 | -0.040656 |  | 0.92 | 1.05 | 0.17406 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | WELL 4WT | 0.95976 | 0.9191 | -0.040656 |  | 0.92 | 1.05 | 0.17754 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | WELL 4WT | 0.95976 | 0.9191 | -0.040656 |  | 0.92 | 1.05 | 0.1303 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | WELL 4WT | 0.95976 | 0.9191 | -0.040656 |  | 0.92 | 1.05 | 0.1303 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | WELL 4WT | 0.95976 | 0.9191 | -0.040656 |  | 0.92 | 1.05 | 0.18174 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | WELL 4WT | 0.95976 | 0.9191 | -0.040656 |  | 0.92 | 1.05 | 0.18244 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | WELL 4WT | 0.95976 | 0.9191 | -0.040656 |  | 0.92 | 1.05 | 0.19275 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | WELL 4WT | 0.95976 | 0.9191 | -0.040656 |  | 0.92 | 1.05 | 0.19304 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | WELL 4WT | 0.95976 | 0.9191 | -0.040656 |  | 0.92 | 1.05 | 0.19068 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | WELL 4WT | 0.95976 | 0.9191 | -0.040656 |  | 0.92 | 1.05 | 0.19114 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | WELL 4WT | 0.95976 | 0.9191 | -0.040656 |  | 0.92 | 1.05 | 0.19232 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | WELL 4WT | 0.95976 | 0.9191 | -0.040656 |  | 0.92 | 1.05 | 0.17996 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | WELL 4WT | 0.95976 | 0.9191 | -0.040656 |  | 0.92 | 1.05 | 0.17996 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | WELL 4WT | 0.95976 | 0.9191 | -0.040656 |  | 0.92 | 1.05 | 0.18769 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | WELL 4WT | 0.95976 | 0.9191 | -0.040656 |  | 0.92 | 1.05 | 0.18769 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | WELL 4WT | 0.95976 | 0.9191 | -0.040656 |  | 0.92 | 1.05 | 0.4918 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | WELL 4WT | 0.95976 | 0.9191 | -0.040656 |  | 0.92 | 1.05 | 0.1947 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | WELLGS4 | 0.9558 | 0.90938 | -0.046418 |  | 0.92 | 1.05 | 0.081174 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | WELLGS4 | 0.9558 | 0.90938 | -0.046418 |  | 0.92 | 1.05 | 0.19645 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | WELLGS4 | 0.9558 | 0.90938 | -0.046418 |  | 0.92 | 1.05 | 0.23843 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | WELLGS4 | 0.9558 | 0.90938 | -0.046418 |  | 0.92 | 1.05 | 0.23843 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | WELLGS4 | 0.9558 | 0.90938 | -0.046418 |  | 0.92 | 1.05 | 0.17969 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | WELLGS4 | 0.9558 | 0.90938 | -0.046418 |  | 0.92 | 1.05 | 0.17406 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | WELLGS4 | 0.9558 | 0.90938 | -0.046418 |  | 0.92 | 1.05 | 0.17754 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | WELLGS4 | 0.9558 | 0.90938 | -0.046418 |  | 0.92 | 1.05 | 0.1303 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | WELLGS4 | 0.9558 | 0.90938 | -0.046418 |  | 0.92 | 1.05 | 0.1303 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | WELLGS4 | 0.9558 | 0.90938 | -0.046418 |  | 0.92 | 1.05 | 0.18174 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | WELLGS4 | 0.9558 | 0.90938 | -0.046418 |  | 0.92 | 1.05 | 0.18244 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | WELLGS4 | 0.9558 | 0.90938 | -0.046418 |  | 0.92 | 1.05 | 0.19275 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | WELLGS4 | 0.9558 | 0.90938 | -0.046418 |  | 0.92 | 1.05 | 0.19304 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | WELLGS4 | 0.9558 | 0.90938 | -0.046418 |  | 0.92 | 1.05 | 0.19068 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | WELLGS4 | 0.9558 | 0.90938 | -0.046418 |  | 0.92 | 1.05 | 0.19114 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | WELLGS4 | 0.9558 | 0.90938 | -0.046418 |  | 0.92 | 1.05 | 0.19232 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | WELLGS4 | 0.9558 | 0.90938 | -0.046418 |  | 0.92 | 1.05 | 0.17996 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | WELLGS4 | 0.9558 | 0.90938 | -0.046418 |  | 0.92 | 1.05 | 0.17996 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | WELLGS4 | 0.9558 | 0.90938 | -0.046418 |  | 0.92 | 1.05 | 0.18769 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | WELLGS4 | 0.9558 | 0.90938 | -0.046418 |  | 0.92 | 1.05 | 0.18769 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | WELLGS4 | 0.9558 | 0.90938 | -0.046418 |  | 0.92 | 1.05 | 0.4918 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | WELLGS4 | 0.9558 | 0.90938 | -0.046418 |  | 0.92 | 1.05 | 0.1947 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | ASGI-2024-002 | WELLGS4 | 0.95971 | 0.91892 | -0.040792 |  | 0.92 | 1.05 | 0.081174 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-015 | WELLGS4 | 0.95971 | 0.91892 | -0.040792 |  | 0.92 | 1.05 | 0.19645 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-041 | WELLGS4 | 0.95971 | 0.91892 | -0.040792 |  | 0.92 | 1.05 | 0.23843 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-042 | WELLGS4 | 0.95971 | 0.91892 | -0.040792 |  | 0.92 | 1.05 | 0.23843 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-043 | WELLGS4 | 0.95971 | 0.91892 | -0.040792 |  | 0.92 | 1.05 | 0.17969 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-099 | WELLGS4 | 0.95971 | 0.91892 | -0.040792 |  | 0.92 | 1.05 | 0.17406 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-109 | WELLGS4 | 0.95971 | 0.91892 | -0.040792 |  | 0.92 | 1.05 | 0.17754 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-143 | WELLGS4 | 0.95971 | 0.91892 | -0.040792 |  | 0.92 | 1.05 | 0.1303 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-145 | WELLGS4 | 0.95971 | 0.91892 | -0.040792 |  | 0.92 | 1.05 | 0.1303 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-159 | WELLGS4 | 0.95971 | 0.91892 | -0.040792 |  | 0.92 | 1.05 | 0.18174 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-221 | WELLGS4 | 0.95971 | 0.91892 | -0.040792 |  | 0.92 | 1.05 | 0.18244 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-261 | WELLGS4 | 0.95971 | 0.91892 | -0.040792 |  | 0.92 | 1.05 | 0.19275 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-265 | WELLGS4 | 0.95971 | 0.91892 | -0.040792 |  | 0.92 | 1.05 | 0.19304 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-280 | WELLGS4 | 0.95971 | 0.91892 | -0.040792 |  | 0.92 | 1.05 | 0.19068 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-281 | WELLGS4 | 0.95971 | 0.91892 | -0.040792 |  | 0.92 | 1.05 | 0.19114 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-295 | WELLGS4 | 0.95971 | 0.91892 | -0.040792 |  | 0.92 | 1.05 | 0.19232 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-303 | WELLGS4 | 0.95971 | 0.91892 | -0.040792 |  | 0.92 | 1.05 | 0.17996 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-304 | WELLGS4 | 0.95971 | 0.91892 | -0.040792 |  | 0.92 | 1.05 | 0.17996 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-310 | WELLGS4 | 0.95971 | 0.91892 | -0.040792 |  | 0.92 | 1.05 | 0.18769 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-311 | WELLGS4 | 0.95971 | 0.91892 | -0.040792 |  | 0.92 | 1.05 | 0.18769 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-317 | WELLGS4 | 0.95971 | 0.91892 | -0.040792 |  | 0.92 | 1.05 | 0.4918 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | 05ALL | 2 | 26SP | V | GEN-2024-336 | WELLGS4 | 0.95971 | 0.91892 | -0.040792 |  | 0.92 | 1.05 | 0.1947 | P52:345:AEPW:NR5O.K.U.-7:::: | Add 15 MVAR switched shunt at GB-SHAMROCK 69 kV
Voltage | WECC | 2 | 26SP | WECC | N/A | None | [7 empty] | None | None
Voltage | 04ALL | 2 | 29L | V | GEN-2024-235 | RSS T1 4 | 1.0306 | 1.0524 | 0.021819 |  | 0.92 | 1.05 | 0.038066 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Add 13 MVAR switched shunt at RSS T1 4 138 kV; Add 14 MVAR switched shunt at T.P.S.-2 69 kV
Voltage | 04ALL | 2 | 29L | V | GEN-2024-344 | RSS T1 4 | 1.0306 | 1.0524 | 0.021819 |  | 0.92 | 1.05 | 0.10782 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Add 13 MVAR switched shunt at RSS T1 4 138 kV; Add 14 MVAR switched shunt at T.P.S.-2 69 kV
Voltage | 04ALL | 2 | 29L | V | GEN-2024-235 | RSS T2 4 | 1.0304 | 1.0522 | 0.021736 |  | 0.92 | 1.05 | 0.038066 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Add 13 MVAR switched shunt at RSS T1 4 138 kV; Add 14 MVAR switched shunt at T.P.S.-2 69 kV
Voltage | 04ALL | 2 | 29L | V | GEN-2024-344 | RSS T2 4 | 1.0304 | 1.0522 | 0.021736 |  | 0.92 | 1.05 | 0.10782 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Add 13 MVAR switched shunt at RSS T1 4 138 kV; Add 14 MVAR switched shunt at T.P.S.-2 69 kV
Voltage | 04ALL | 2 | 29L | V | GEN-2024-235 | T.P.S.-2 | 1.043 | 1.0647 | 0.021718 |  | 0.92 | 1.05 | 0.038066 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Add 13 MVAR switched shunt at RSS T1 4 138 kV; Add 14 MVAR switched shunt at T.P.S.-2 69 kV
Voltage | 04ALL | 2 | 29L | V | GEN-2024-344 | T.P.S.-2 | 1.043 | 1.0647 | 0.021718 |  | 0.92 | 1.05 | 0.10782 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Add 13 MVAR switched shunt at RSS T1 4 138 kV; Add 14 MVAR switched shunt at T.P.S.-2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-003 | G17-140-BUS | 1.1233 | 1.2099 | 0.086559 |  | 0.92 | 1.05 | 0.15454 | P22:345:EES:MUSKOGE7!:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-013 | G17-140-BUS | 1.1233 | 1.2099 | 0.086559 |  | 0.92 | 1.05 | 0.060254 | P22:345:EES:MUSKOGE7!:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-128 | G17-140-BUS | 1.1233 | 1.2099 | 0.086559 |  | 0.92 | 1.05 | 0.052755 | P22:345:EES:MUSKOGE7!:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-252 | G17-140-BUS | 1.1233 | 1.2099 | 0.086559 |  | 0.92 | 1.05 | 0.042261 | P22:345:EES:MUSKOGE7!:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-254 | G17-140-BUS | 1.1233 | 1.2099 | 0.086559 |  | 0.92 | 1.05 | 0.036734 | P22:345:EES:MUSKOGE7!:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-255 | G17-140-BUS | 1.1233 | 1.2099 | 0.086559 |  | 0.92 | 1.05 | 0.031872 | P22:345:EES:MUSKOGE7!:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-286 | G17-140-BUS | 1.1233 | 1.2099 | 0.086559 |  | 0.92 | 1.05 | 0.16815 | P22:345:EES:MUSKOGE7!:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-293 | G17-140-BUS | 1.1233 | 1.2099 | 0.086559 |  | 0.92 | 1.05 | 1 | P22:345:EES:MUSKOGE7!:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-299 | G17-140-BUS | 1.1233 | 1.2099 | 0.086559 |  | 0.92 | 1.05 | 0.19238 | P22:345:EES:MUSKOGE7!:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-321 | G17-140-BUS | 1.1233 | 1.2099 | 0.086559 |  | 0.92 | 1.05 | 0.093153 | P22:345:EES:MUSKOGE7!:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-323 | G17-140-BUS | 1.1233 | 1.2099 | 0.086559 |  | 0.92 | 1.05 | 0.092305 | P22:345:EES:MUSKOGE7!:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-341 | G17-140-BUS | 1.1233 | 1.2099 | 0.086559 |  | 0.92 | 1.05 | 0.12621 | P22:345:EES:MUSKOGE7!:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-343 | G17-140-BUS | 1.1233 | 1.2099 | 0.086559 |  | 0.92 | 1.05 | 0.086037 | P22:345:EES:MUSKOGE7!:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-377 | G17-140-BUS | 1.1233 | 1.2099 | 0.086559 |  | 0.92 | 1.05 | 0.08614 | P22:345:EES:MUSKOGE7!:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-379 | G17-140-BUS | 1.1233 | 1.2099 | 0.086559 |  | 0.92 | 1.05 | 0.084532 | P22:345:EES:MUSKOGE7!:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-003 | G17-140-BUS | 1.1225 | 1.2086 | 0.086074 |  | 0.92 | 1.05 | 0.12685 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-013 | G17-140-BUS | 1.1225 | 1.2086 | 0.086074 |  | 0.92 | 1.05 | 0.052498 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-128 | G17-140-BUS | 1.1225 | 1.2086 | 0.086074 |  | 0.92 | 1.05 | 0.047367 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-252 | G17-140-BUS | 1.1225 | 1.2086 | 0.086074 |  | 0.92 | 1.05 | 0.036037 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-254 | G17-140-BUS | 1.1225 | 1.2086 | 0.086074 |  | 0.92 | 1.05 | 0.030772 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-286 | G17-140-BUS | 1.1225 | 1.2086 | 0.086074 |  | 0.92 | 1.05 | 0.14152 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-293 | G17-140-BUS | 1.1225 | 1.2086 | 0.086074 |  | 0.92 | 1.05 | 0.27709 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-299 | G17-140-BUS | 1.1225 | 1.2086 | 0.086074 |  | 0.92 | 1.05 | 0.19238 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-321 | G17-140-BUS | 1.1225 | 1.2086 | 0.086074 |  | 0.92 | 1.05 | 0.080581 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-323 | G17-140-BUS | 1.1225 | 1.2086 | 0.086074 |  | 0.92 | 1.05 | 0.092305 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-341 | G17-140-BUS | 1.1225 | 1.2086 | 0.086074 |  | 0.92 | 1.05 | 0.11373 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-343 | G17-140-BUS | 1.1225 | 1.2086 | 0.086074 |  | 0.92 | 1.05 | 0.086037 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-377 | G17-140-BUS | 1.1225 | 1.2086 | 0.086074 |  | 0.92 | 1.05 | 0.08614 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-379 | G17-140-BUS | 1.1225 | 1.2086 | 0.086074 |  | 0.92 | 1.05 | 0.084532 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-001 | G17-140-BUS | 1.1238 | 1.2026 | 0.078803 |  | 0.92 | 1.05 | 0.06791 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-007 | G17-140-BUS | 1.1238 | 1.2026 | 0.078803 |  | 0.92 | 1.05 | 0.051538 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-008 | G17-140-BUS | 1.1238 | 1.2026 | 0.078803 |  | 0.92 | 1.05 | 0.051538 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-017 | G17-140-BUS | 1.1238 | 1.2026 | 0.078803 |  | 0.92 | 1.05 | 0.033764 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-018 | G17-140-BUS | 1.1238 | 1.2026 | 0.078803 |  | 0.92 | 1.05 | 0.031273 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-019 | G17-140-BUS | 1.1238 | 1.2026 | 0.078803 |  | 0.92 | 1.05 | 0.031273 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-020 | G17-140-BUS | 1.1238 | 1.2026 | 0.078803 |  | 0.92 | 1.05 | 0.033764 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-021 | G17-140-BUS | 1.1238 | 1.2026 | 0.078803 |  | 0.92 | 1.05 | 0.033764 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-022 | G17-140-BUS | 1.1238 | 1.2026 | 0.078803 |  | 0.92 | 1.05 | 0.031273 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-023 | G17-140-BUS | 1.1238 | 1.2026 | 0.078803 |  | 0.92 | 1.05 | 0.031273 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-081 | G17-140-BUS | 1.1238 | 1.2026 | 0.078803 |  | 0.92 | 1.05 | 0.061462 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-082 | G17-140-BUS | 1.1238 | 1.2026 | 0.078803 |  | 0.92 | 1.05 | 0.061462 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-211 | G17-140-BUS | 1.1238 | 1.2026 | 0.078803 |  | 0.92 | 1.05 | 0.040559 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-212 | G17-140-BUS | 1.1238 | 1.2026 | 0.078803 |  | 0.92 | 1.05 | 0.040559 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-213 | G17-140-BUS | 1.1238 | 1.2026 | 0.078803 |  | 0.92 | 1.05 | 0.040559 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-343 | G17-140-BUS | 1.1238 | 1.2026 | 0.078803 |  | 0.92 | 1.05 | 0.11433 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-377 | G17-140-BUS | 1.1238 | 1.2026 | 0.078803 |  | 0.92 | 1.05 | 0.11364 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-379 | G17-140-BUS | 1.1238 | 1.2026 | 0.078803 |  | 0.92 | 1.05 | 0.14842 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-001 | G17-140-BUS | 1.1238 | 1.2026 | 0.078788 |  | 0.92 | 1.05 | 0.06791 | P42:500:OKGE:SB_FTTH8585:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-007 | G17-140-BUS | 1.1238 | 1.2026 | 0.078788 |  | 0.92 | 1.05 | 0.051538 | P42:500:OKGE:SB_FTTH8585:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-008 | G17-140-BUS | 1.1238 | 1.2026 | 0.078788 |  | 0.92 | 1.05 | 0.051538 | P42:500:OKGE:SB_FTTH8585:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-003 | G17-140-BUS | 1.1238 | 1.2026 | 0.078788 |  | 0.92 | 1.05 | 0.063216 | P42:500:OKGE:SB_FTTH8585:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-017 | G17-140-BUS | 1.1238 | 1.2026 | 0.078788 |  | 0.92 | 1.05 | 0.033764 | P42:500:OKGE:SB_FTTH8585:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-018 | G17-140-BUS | 1.1238 | 1.2026 | 0.078788 |  | 0.92 | 1.05 | 0.031273 | P42:500:OKGE:SB_FTTH8585:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-019 | G17-140-BUS | 1.1238 | 1.2026 | 0.078788 |  | 0.92 | 1.05 | 0.031273 | P42:500:OKGE:SB_FTTH8585:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-020 | G17-140-BUS | 1.1238 | 1.2026 | 0.078788 |  | 0.92 | 1.05 | 0.033764 | P42:500:OKGE:SB_FTTH8585:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-021 | G17-140-BUS | 1.1238 | 1.2026 | 0.078788 |  | 0.92 | 1.05 | 0.033764 | P42:500:OKGE:SB_FTTH8585:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-022 | G17-140-BUS | 1.1238 | 1.2026 | 0.078788 |  | 0.92 | 1.05 | 0.031273 | P42:500:OKGE:SB_FTTH8585:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-023 | G17-140-BUS | 1.1238 | 1.2026 | 0.078788 |  | 0.92 | 1.05 | 0.031273 | P42:500:OKGE:SB_FTTH8585:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-081 | G17-140-BUS | 1.1238 | 1.2026 | 0.078788 |  | 0.92 | 1.05 | 0.061462 | P42:500:OKGE:SB_FTTH8585:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-082 | G17-140-BUS | 1.1238 | 1.2026 | 0.078788 |  | 0.92 | 1.05 | 0.061462 | P42:500:OKGE:SB_FTTH8585:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-211 | G17-140-BUS | 1.1238 | 1.2026 | 0.078788 |  | 0.92 | 1.05 | 0.040559 | P42:500:OKGE:SB_FTTH8585:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-212 | G17-140-BUS | 1.1238 | 1.2026 | 0.078788 |  | 0.92 | 1.05 | 0.040559 | P42:500:OKGE:SB_FTTH8585:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-213 | G17-140-BUS | 1.1238 | 1.2026 | 0.078788 |  | 0.92 | 1.05 | 0.040559 | P42:500:OKGE:SB_FTTH8585:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-286 | G17-140-BUS | 1.1238 | 1.2026 | 0.078788 |  | 0.92 | 1.05 | 0.062263 | P42:500:OKGE:SB_FTTH8585:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-343 | G17-140-BUS | 1.1238 | 1.2026 | 0.078788 |  | 0.92 | 1.05 | 0.11433 | P42:500:OKGE:SB_FTTH8585:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-377 | G17-140-BUS | 1.1238 | 1.2026 | 0.078788 |  | 0.92 | 1.05 | 0.11364 | P42:500:OKGE:SB_FTTH8585:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-379 | G17-140-BUS | 1.1238 | 1.2026 | 0.078788 |  | 0.92 | 1.05 | 0.14842 | P42:500:OKGE:SB_FTTH8585:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-001 | G17-140-BUS | 1.1238 | 1.2026 | 0.078786 |  | 0.92 | 1.05 | 0.06791 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-007 | G17-140-BUS | 1.1238 | 1.2026 | 0.078786 |  | 0.92 | 1.05 | 0.051538 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-008 | G17-140-BUS | 1.1238 | 1.2026 | 0.078786 |  | 0.92 | 1.05 | 0.051538 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-003 | G17-140-BUS | 1.1238 | 1.2026 | 0.078786 |  | 0.92 | 1.05 | 0.11645 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-017 | G17-140-BUS | 1.1238 | 1.2026 | 0.078786 |  | 0.92 | 1.05 | 0.033764 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-018 | G17-140-BUS | 1.1238 | 1.2026 | 0.078786 |  | 0.92 | 1.05 | 0.031273 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-019 | G17-140-BUS | 1.1238 | 1.2026 | 0.078786 |  | 0.92 | 1.05 | 0.031273 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-020 | G17-140-BUS | 1.1238 | 1.2026 | 0.078786 |  | 0.92 | 1.05 | 0.033764 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-021 | G17-140-BUS | 1.1238 | 1.2026 | 0.078786 |  | 0.92 | 1.05 | 0.033764 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-022 | G17-140-BUS | 1.1238 | 1.2026 | 0.078786 |  | 0.92 | 1.05 | 0.031273 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-023 | G17-140-BUS | 1.1238 | 1.2026 | 0.078786 |  | 0.92 | 1.05 | 0.031273 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-081 | G17-140-BUS | 1.1238 | 1.2026 | 0.078786 |  | 0.92 | 1.05 | 0.061462 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-082 | G17-140-BUS | 1.1238 | 1.2026 | 0.078786 |  | 0.92 | 1.05 | 0.061462 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-211 | G17-140-BUS | 1.1238 | 1.2026 | 0.078786 |  | 0.92 | 1.05 | 0.040559 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-212 | G17-140-BUS | 1.1238 | 1.2026 | 0.078786 |  | 0.92 | 1.05 | 0.040559 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-213 | G17-140-BUS | 1.1238 | 1.2026 | 0.078786 |  | 0.92 | 1.05 | 0.040559 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-286 | G17-140-BUS | 1.1238 | 1.2026 | 0.078786 |  | 0.92 | 1.05 | 0.12668 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-293 | G17-140-BUS | 1.1238 | 1.2026 | 0.078786 |  | 0.92 | 1.05 | 0.063331 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-299 | G17-140-BUS | 1.1238 | 1.2026 | 0.078786 |  | 0.92 | 1.05 | 0.12924 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-340 | G17-140-BUS | 1.1238 | 1.2026 | 0.078786 |  | 0.92 | 1.05 | 0.033772 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-343 | G17-140-BUS | 1.1238 | 1.2026 | 0.078786 |  | 0.92 | 1.05 | 0.11433 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-377 | G17-140-BUS | 1.1238 | 1.2026 | 0.078786 |  | 0.92 | 1.05 | 0.11364 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-379 | G17-140-BUS | 1.1238 | 1.2026 | 0.078786 |  | 0.92 | 1.05 | 0.14842 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-003 | GEN-2017-140 | 1.1234 | 1.2099 | 0.086446 |  | 0.92 | 1.05 | 0.15454 | P22:345:EES:MUSKOGE7!:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-013 | GEN-2017-140 | 1.1234 | 1.2099 | 0.086446 |  | 0.92 | 1.05 | 0.060254 | P22:345:EES:MUSKOGE7!:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-128 | GEN-2017-140 | 1.1234 | 1.2099 | 0.086446 |  | 0.92 | 1.05 | 0.052755 | P22:345:EES:MUSKOGE7!:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2017-140 | 1.1234 | 1.2099 | 0.086446 |  | 0.92 | 1.05 | 0.042261 | P22:345:EES:MUSKOGE7!:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2017-140 | 1.1234 | 1.2099 | 0.086446 |  | 0.92 | 1.05 | 0.036734 | P22:345:EES:MUSKOGE7!:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-255 | GEN-2017-140 | 1.1234 | 1.2099 | 0.086446 |  | 0.92 | 1.05 | 0.031872 | P22:345:EES:MUSKOGE7!:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-286 | GEN-2017-140 | 1.1234 | 1.2099 | 0.086446 |  | 0.92 | 1.05 | 0.16815 | P22:345:EES:MUSKOGE7!:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-293 | GEN-2017-140 | 1.1234 | 1.2099 | 0.086446 |  | 0.92 | 1.05 | 1 | P22:345:EES:MUSKOGE7!:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-299 | GEN-2017-140 | 1.1234 | 1.2099 | 0.086446 |  | 0.92 | 1.05 | 0.19238 | P22:345:EES:MUSKOGE7!:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-321 | GEN-2017-140 | 1.1234 | 1.2099 | 0.086446 |  | 0.92 | 1.05 | 0.093153 | P22:345:EES:MUSKOGE7!:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-323 | GEN-2017-140 | 1.1234 | 1.2099 | 0.086446 |  | 0.92 | 1.05 | 0.092305 | P22:345:EES:MUSKOGE7!:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-341 | GEN-2017-140 | 1.1234 | 1.2099 | 0.086446 |  | 0.92 | 1.05 | 0.12621 | P22:345:EES:MUSKOGE7!:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-343 | GEN-2017-140 | 1.1234 | 1.2099 | 0.086446 |  | 0.92 | 1.05 | 0.086037 | P22:345:EES:MUSKOGE7!:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-377 | GEN-2017-140 | 1.1234 | 1.2099 | 0.086446 |  | 0.92 | 1.05 | 0.08614 | P22:345:EES:MUSKOGE7!:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-379 | GEN-2017-140 | 1.1234 | 1.2099 | 0.086446 |  | 0.92 | 1.05 | 0.084532 | P22:345:EES:MUSKOGE7!:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-003 | GEN-2017-140 | 1.1226 | 1.2086 | 0.085961 |  | 0.92 | 1.05 | 0.12685 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-013 | GEN-2017-140 | 1.1226 | 1.2086 | 0.085961 |  | 0.92 | 1.05 | 0.052498 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-128 | GEN-2017-140 | 1.1226 | 1.2086 | 0.085961 |  | 0.92 | 1.05 | 0.047367 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-252 | GEN-2017-140 | 1.1226 | 1.2086 | 0.085961 |  | 0.92 | 1.05 | 0.036037 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-254 | GEN-2017-140 | 1.1226 | 1.2086 | 0.085961 |  | 0.92 | 1.05 | 0.030772 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-286 | GEN-2017-140 | 1.1226 | 1.2086 | 0.085961 |  | 0.92 | 1.05 | 0.14152 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-293 | GEN-2017-140 | 1.1226 | 1.2086 | 0.085961 |  | 0.92 | 1.05 | 0.27709 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-299 | GEN-2017-140 | 1.1226 | 1.2086 | 0.085961 |  | 0.92 | 1.05 | 0.19238 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-321 | GEN-2017-140 | 1.1226 | 1.2086 | 0.085961 |  | 0.92 | 1.05 | 0.080581 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-323 | GEN-2017-140 | 1.1226 | 1.2086 | 0.085961 |  | 0.92 | 1.05 | 0.092305 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-341 | GEN-2017-140 | 1.1226 | 1.2086 | 0.085961 |  | 0.92 | 1.05 | 0.11373 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-343 | GEN-2017-140 | 1.1226 | 1.2086 | 0.085961 |  | 0.92 | 1.05 | 0.086037 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-377 | GEN-2017-140 | 1.1226 | 1.2086 | 0.085961 |  | 0.92 | 1.05 | 0.08614 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-379 | GEN-2017-140 | 1.1226 | 1.2086 | 0.085961 |  | 0.92 | 1.05 | 0.084532 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-001 | GEN-2017-140 | 1.1239 | 1.2026 | 0.078691 |  | 0.92 | 1.05 | 0.06791 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-007 | GEN-2017-140 | 1.1239 | 1.2026 | 0.078691 |  | 0.92 | 1.05 | 0.051538 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-008 | GEN-2017-140 | 1.1239 | 1.2026 | 0.078691 |  | 0.92 | 1.05 | 0.051538 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-017 | GEN-2017-140 | 1.1239 | 1.2026 | 0.078691 |  | 0.92 | 1.05 | 0.033764 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-018 | GEN-2017-140 | 1.1239 | 1.2026 | 0.078691 |  | 0.92 | 1.05 | 0.031273 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-019 | GEN-2017-140 | 1.1239 | 1.2026 | 0.078691 |  | 0.92 | 1.05 | 0.031273 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-020 | GEN-2017-140 | 1.1239 | 1.2026 | 0.078691 |  | 0.92 | 1.05 | 0.033764 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-021 | GEN-2017-140 | 1.1239 | 1.2026 | 0.078691 |  | 0.92 | 1.05 | 0.033764 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-022 | GEN-2017-140 | 1.1239 | 1.2026 | 0.078691 |  | 0.92 | 1.05 | 0.031273 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-023 | GEN-2017-140 | 1.1239 | 1.2026 | 0.078691 |  | 0.92 | 1.05 | 0.031273 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-081 | GEN-2017-140 | 1.1239 | 1.2026 | 0.078691 |  | 0.92 | 1.05 | 0.061462 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-082 | GEN-2017-140 | 1.1239 | 1.2026 | 0.078691 |  | 0.92 | 1.05 | 0.061462 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-211 | GEN-2017-140 | 1.1239 | 1.2026 | 0.078691 |  | 0.92 | 1.05 | 0.040559 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-212 | GEN-2017-140 | 1.1239 | 1.2026 | 0.078691 |  | 0.92 | 1.05 | 0.040559 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-213 | GEN-2017-140 | 1.1239 | 1.2026 | 0.078691 |  | 0.92 | 1.05 | 0.040559 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-343 | GEN-2017-140 | 1.1239 | 1.2026 | 0.078691 |  | 0.92 | 1.05 | 0.11433 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-377 | GEN-2017-140 | 1.1239 | 1.2026 | 0.078691 |  | 0.92 | 1.05 | 0.11364 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-379 | GEN-2017-140 | 1.1239 | 1.2026 | 0.078691 |  | 0.92 | 1.05 | 0.14842 | P12:500:EES:8ANO%:FTSMITH8:1:EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-001 | GEN-2017-140 | 1.1239 | 1.2026 | 0.078676 |  | 0.92 | 1.05 | 0.06791 | P42:500:OKGE:SB_FTTH8585:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-007 | GEN-2017-140 | 1.1239 | 1.2026 | 0.078676 |  | 0.92 | 1.05 | 0.051538 | P42:500:OKGE:SB_FTTH8585:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-008 | GEN-2017-140 | 1.1239 | 1.2026 | 0.078676 |  | 0.92 | 1.05 | 0.051538 | P42:500:OKGE:SB_FTTH8585:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-003 | GEN-2017-140 | 1.1239 | 1.2026 | 0.078676 |  | 0.92 | 1.05 | 0.063216 | P42:500:OKGE:SB_FTTH8585:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-017 | GEN-2017-140 | 1.1239 | 1.2026 | 0.078676 |  | 0.92 | 1.05 | 0.033764 | P42:500:OKGE:SB_FTTH8585:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-018 | GEN-2017-140 | 1.1239 | 1.2026 | 0.078676 |  | 0.92 | 1.05 | 0.031273 | P42:500:OKGE:SB_FTTH8585:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-019 | GEN-2017-140 | 1.1239 | 1.2026 | 0.078676 |  | 0.92 | 1.05 | 0.031273 | P42:500:OKGE:SB_FTTH8585:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-020 | GEN-2017-140 | 1.1239 | 1.2026 | 0.078676 |  | 0.92 | 1.05 | 0.033764 | P42:500:OKGE:SB_FTTH8585:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-021 | GEN-2017-140 | 1.1239 | 1.2026 | 0.078676 |  | 0.92 | 1.05 | 0.033764 | P42:500:OKGE:SB_FTTH8585:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-022 | GEN-2017-140 | 1.1239 | 1.2026 | 0.078676 |  | 0.92 | 1.05 | 0.031273 | P42:500:OKGE:SB_FTTH8585:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-023 | GEN-2017-140 | 1.1239 | 1.2026 | 0.078676 |  | 0.92 | 1.05 | 0.031273 | P42:500:OKGE:SB_FTTH8585:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-081 | GEN-2017-140 | 1.1239 | 1.2026 | 0.078676 |  | 0.92 | 1.05 | 0.061462 | P42:500:OKGE:SB_FTTH8585:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-082 | GEN-2017-140 | 1.1239 | 1.2026 | 0.078676 |  | 0.92 | 1.05 | 0.061462 | P42:500:OKGE:SB_FTTH8585:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-211 | GEN-2017-140 | 1.1239 | 1.2026 | 0.078676 |  | 0.92 | 1.05 | 0.040559 | P42:500:OKGE:SB_FTTH8585:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-212 | GEN-2017-140 | 1.1239 | 1.2026 | 0.078676 |  | 0.92 | 1.05 | 0.040559 | P42:500:OKGE:SB_FTTH8585:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-213 | GEN-2017-140 | 1.1239 | 1.2026 | 0.078676 |  | 0.92 | 1.05 | 0.040559 | P42:500:OKGE:SB_FTTH8585:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-286 | GEN-2017-140 | 1.1239 | 1.2026 | 0.078676 |  | 0.92 | 1.05 | 0.062263 | P42:500:OKGE:SB_FTTH8585:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-343 | GEN-2017-140 | 1.1239 | 1.2026 | 0.078676 |  | 0.92 | 1.05 | 0.11433 | P42:500:OKGE:SB_FTTH8585:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-377 | GEN-2017-140 | 1.1239 | 1.2026 | 0.078676 |  | 0.92 | 1.05 | 0.11364 | P42:500:OKGE:SB_FTTH8585:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-379 | GEN-2017-140 | 1.1239 | 1.2026 | 0.078676 |  | 0.92 | 1.05 | 0.14842 | P42:500:OKGE:SB_FTTH8585:::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-001 | GEN-2017-140 | 1.1239 | 1.2026 | 0.078673 |  | 0.92 | 1.05 | 0.06791 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-007 | GEN-2017-140 | 1.1239 | 1.2026 | 0.078673 |  | 0.92 | 1.05 | 0.051538 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-008 | GEN-2017-140 | 1.1239 | 1.2026 | 0.078673 |  | 0.92 | 1.05 | 0.051538 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-003 | GEN-2017-140 | 1.1239 | 1.2026 | 0.078673 |  | 0.92 | 1.05 | 0.11645 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-017 | GEN-2017-140 | 1.1239 | 1.2026 | 0.078673 |  | 0.92 | 1.05 | 0.033764 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-018 | GEN-2017-140 | 1.1239 | 1.2026 | 0.078673 |  | 0.92 | 1.05 | 0.031273 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-019 | GEN-2017-140 | 1.1239 | 1.2026 | 0.078673 |  | 0.92 | 1.05 | 0.031273 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-020 | GEN-2017-140 | 1.1239 | 1.2026 | 0.078673 |  | 0.92 | 1.05 | 0.033764 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-021 | GEN-2017-140 | 1.1239 | 1.2026 | 0.078673 |  | 0.92 | 1.05 | 0.033764 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-022 | GEN-2017-140 | 1.1239 | 1.2026 | 0.078673 |  | 0.92 | 1.05 | 0.031273 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-023 | GEN-2017-140 | 1.1239 | 1.2026 | 0.078673 |  | 0.92 | 1.05 | 0.031273 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-081 | GEN-2017-140 | 1.1239 | 1.2026 | 0.078673 |  | 0.92 | 1.05 | 0.061462 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-082 | GEN-2017-140 | 1.1239 | 1.2026 | 0.078673 |  | 0.92 | 1.05 | 0.061462 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-211 | GEN-2017-140 | 1.1239 | 1.2026 | 0.078673 |  | 0.92 | 1.05 | 0.040559 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-212 | GEN-2017-140 | 1.1239 | 1.2026 | 0.078673 |  | 0.92 | 1.05 | 0.040559 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-213 | GEN-2017-140 | 1.1239 | 1.2026 | 0.078673 |  | 0.92 | 1.05 | 0.040559 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-286 | GEN-2017-140 | 1.1239 | 1.2026 | 0.078673 |  | 0.92 | 1.05 | 0.12668 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-293 | GEN-2017-140 | 1.1239 | 1.2026 | 0.078673 |  | 0.92 | 1.05 | 0.063331 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-299 | GEN-2017-140 | 1.1239 | 1.2026 | 0.078673 |  | 0.92 | 1.05 | 0.12924 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-340 | GEN-2017-140 | 1.1239 | 1.2026 | 0.078673 |  | 0.92 | 1.05 | 0.033772 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-343 | GEN-2017-140 | 1.1239 | 1.2026 | 0.078673 |  | 0.92 | 1.05 | 0.11433 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-377 | GEN-2017-140 | 1.1239 | 1.2026 | 0.078673 |  | 0.92 | 1.05 | 0.11364 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-379 | GEN-2017-140 | 1.1239 | 1.2026 | 0.078673 |  | 0.92 | 1.05 | 0.14842 | P23:500:EES-EAI:ARK_NU:B5106::EHV: | Add 2 MVAR switched shunt at GEN-2017-140 345 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-007 | MALTABN5 | 0.9871 | 0.90596 | -0.081139 |  | 0.93 | 1.05 | 0.058785 | Single 543059 MALTABN5 161 543064 NORTON5 161 1 | Add 7 MVAR switched shunt at SWAVRLY5 161 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-008 | MALTABN5 | 0.9871 | 0.90596 | -0.081139 |  | 0.93 | 1.05 | 0.058785 | Single 543059 MALTABN5 161 543064 NORTON5 161 1 | Add 7 MVAR switched shunt at SWAVRLY5 161 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-001 | NP-GLAZIR_G2 | 0.70153 | 0.66129 | -0.040241 |  | 0.9 | 1.05 | 0.036526 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-020 | NP-GLAZIR_G2 | 0.70153 | 0.66129 | -0.040241 |  | 0.9 | 1.05 | 0.044321 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-017 | NP-GLAZIR_G2 | 0.70153 | 0.66129 | -0.040241 |  | 0.9 | 1.05 | 0.049912 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-018 | NP-GLAZIR_G2 | 0.70153 | 0.66129 | -0.040241 |  | 0.9 | 1.05 | 0.050386 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-019 | NP-GLAZIR_G2 | 0.70153 | 0.66129 | -0.040241 |  | 0.9 | 1.05 | 0.050386 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-020 | NP-GLAZIR_G2 | 0.70153 | 0.66129 | -0.040241 |  | 0.9 | 1.05 | 0.049912 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-021 | NP-GLAZIR_G2 | 0.70153 | 0.66129 | -0.040241 |  | 0.9 | 1.05 | 0.049912 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-022 | NP-GLAZIR_G2 | 0.70153 | 0.66129 | -0.040241 |  | 0.9 | 1.05 | 0.050386 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-023 | NP-GLAZIR_G2 | 0.70153 | 0.66129 | -0.040241 |  | 0.9 | 1.05 | 0.050386 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-081 | NP-GLAZIR_G2 | 0.70153 | 0.66129 | -0.040241 |  | 0.9 | 1.05 | 0.045015 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-082 | NP-GLAZIR_G2 | 0.70153 | 0.66129 | -0.040241 |  | 0.9 | 1.05 | 0.045015 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-211 | NP-GLAZIR_G2 | 0.70153 | 0.66129 | -0.040241 |  | 0.9 | 1.05 | 0.04323 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-212 | NP-GLAZIR_G2 | 0.70153 | 0.66129 | -0.040241 |  | 0.9 | 1.05 | 0.04323 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-213 | NP-GLAZIR_G2 | 0.70153 | 0.66129 | -0.040241 |  | 0.9 | 1.05 | 0.04323 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-249 | NP-GLAZIR_G2 | 0.70153 | 0.66129 | -0.040241 |  | 0.9 | 1.05 | 0.030179 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-001 | NP-GLAZIR_G2 | 0.70253 | 0.66209 | -0.040437 |  | 0.9 | 1.05 | 0.036526 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-020 | NP-GLAZIR_G2 | 0.70253 | 0.66209 | -0.040437 |  | 0.9 | 1.05 | 0.044321 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-017 | NP-GLAZIR_G2 | 0.70253 | 0.66209 | -0.040437 |  | 0.9 | 1.05 | 0.049912 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-018 | NP-GLAZIR_G2 | 0.70253 | 0.66209 | -0.040437 |  | 0.9 | 1.05 | 0.050386 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-019 | NP-GLAZIR_G2 | 0.70253 | 0.66209 | -0.040437 |  | 0.9 | 1.05 | 0.050386 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-020 | NP-GLAZIR_G2 | 0.70253 | 0.66209 | -0.040437 |  | 0.9 | 1.05 | 0.049912 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-021 | NP-GLAZIR_G2 | 0.70253 | 0.66209 | -0.040437 |  | 0.9 | 1.05 | 0.049912 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-022 | NP-GLAZIR_G2 | 0.70253 | 0.66209 | -0.040437 |  | 0.9 | 1.05 | 0.050386 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-023 | NP-GLAZIR_G2 | 0.70253 | 0.66209 | -0.040437 |  | 0.9 | 1.05 | 0.050386 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-081 | NP-GLAZIR_G2 | 0.70253 | 0.66209 | -0.040437 |  | 0.9 | 1.05 | 0.045015 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-082 | NP-GLAZIR_G2 | 0.70253 | 0.66209 | -0.040437 |  | 0.9 | 1.05 | 0.045015 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-211 | NP-GLAZIR_G2 | 0.70253 | 0.66209 | -0.040437 |  | 0.9 | 1.05 | 0.04323 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-212 | NP-GLAZIR_G2 | 0.70253 | 0.66209 | -0.040437 |  | 0.9 | 1.05 | 0.04323 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-213 | NP-GLAZIR_G2 | 0.70253 | 0.66209 | -0.040437 |  | 0.9 | 1.05 | 0.04323 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-249 | NP-GLAZIR_G2 | 0.70253 | 0.66209 | -0.040437 |  | 0.9 | 1.05 | 0.030179 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-001 | NP-GLAZIR_G2 | 0.70253 | 0.66209 | -0.040437 |  | 0.9 | 1.05 | 0.036526 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-020 | NP-GLAZIR_G2 | 0.70253 | 0.66209 | -0.040437 |  | 0.9 | 1.05 | 0.044321 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-017 | NP-GLAZIR_G2 | 0.70253 | 0.66209 | -0.040437 |  | 0.9 | 1.05 | 0.049912 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-018 | NP-GLAZIR_G2 | 0.70253 | 0.66209 | -0.040437 |  | 0.9 | 1.05 | 0.050386 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-019 | NP-GLAZIR_G2 | 0.70253 | 0.66209 | -0.040437 |  | 0.9 | 1.05 | 0.050386 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-020 | NP-GLAZIR_G2 | 0.70253 | 0.66209 | -0.040437 |  | 0.9 | 1.05 | 0.049912 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-021 | NP-GLAZIR_G2 | 0.70253 | 0.66209 | -0.040437 |  | 0.9 | 1.05 | 0.049912 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-022 | NP-GLAZIR_G2 | 0.70253 | 0.66209 | -0.040437 |  | 0.9 | 1.05 | 0.050386 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-023 | NP-GLAZIR_G2 | 0.70253 | 0.66209 | -0.040437 |  | 0.9 | 1.05 | 0.050386 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-081 | NP-GLAZIR_G2 | 0.70253 | 0.66209 | -0.040437 |  | 0.9 | 1.05 | 0.045015 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-082 | NP-GLAZIR_G2 | 0.70253 | 0.66209 | -0.040437 |  | 0.9 | 1.05 | 0.045015 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-211 | NP-GLAZIR_G2 | 0.70253 | 0.66209 | -0.040437 |  | 0.9 | 1.05 | 0.04323 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-212 | NP-GLAZIR_G2 | 0.70253 | 0.66209 | -0.040437 |  | 0.9 | 1.05 | 0.04323 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-213 | NP-GLAZIR_G2 | 0.70253 | 0.66209 | -0.040437 |  | 0.9 | 1.05 | 0.04323 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-249 | NP-GLAZIR_G2 | 0.70253 | 0.66209 | -0.040437 |  | 0.9 | 1.05 | 0.030179 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-020 | NP-GLAZIR_G2 | 0.70212 | 0.66596 | -0.036161 |  | 0.9 | 1.05 | 0.050823 | P23:345:SUNC:BU_BRK488:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-249 | NP-GLAZIR_G2 | 0.70212 | 0.66596 | -0.036161 |  | 0.9 | 1.05 | 0.030898 | P23:345:SUNC:BU_BRK488:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-020 | NP-GLAZIR_G2 | 0.70208 | 0.66596 | -0.03612 |  | 0.9 | 1.05 | 0.050823 | Single 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-249 | NP-GLAZIR_G2 | 0.70208 | 0.66596 | -0.03612 |  | 0.9 | 1.05 | 0.030898 | Single 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-001 | NP-LIPSCOMB2 | 0.66172 | 0.61984 | -0.041882 |  | 0.9 | 1.05 | 0.036526 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-020 | NP-LIPSCOMB2 | 0.66172 | 0.61984 | -0.041882 |  | 0.9 | 1.05 | 0.044321 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-017 | NP-LIPSCOMB2 | 0.66172 | 0.61984 | -0.041882 |  | 0.9 | 1.05 | 0.049912 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-018 | NP-LIPSCOMB2 | 0.66172 | 0.61984 | -0.041882 |  | 0.9 | 1.05 | 0.050386 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-019 | NP-LIPSCOMB2 | 0.66172 | 0.61984 | -0.041882 |  | 0.9 | 1.05 | 0.050386 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-020 | NP-LIPSCOMB2 | 0.66172 | 0.61984 | -0.041882 |  | 0.9 | 1.05 | 0.049912 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-021 | NP-LIPSCOMB2 | 0.66172 | 0.61984 | -0.041882 |  | 0.9 | 1.05 | 0.049912 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-022 | NP-LIPSCOMB2 | 0.66172 | 0.61984 | -0.041882 |  | 0.9 | 1.05 | 0.050386 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-023 | NP-LIPSCOMB2 | 0.66172 | 0.61984 | -0.041882 |  | 0.9 | 1.05 | 0.050386 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-081 | NP-LIPSCOMB2 | 0.66172 | 0.61984 | -0.041882 |  | 0.9 | 1.05 | 0.045015 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-082 | NP-LIPSCOMB2 | 0.66172 | 0.61984 | -0.041882 |  | 0.9 | 1.05 | 0.045015 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-211 | NP-LIPSCOMB2 | 0.66172 | 0.61984 | -0.041882 |  | 0.9 | 1.05 | 0.04323 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-212 | NP-LIPSCOMB2 | 0.66172 | 0.61984 | -0.041882 |  | 0.9 | 1.05 | 0.04323 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-213 | NP-LIPSCOMB2 | 0.66172 | 0.61984 | -0.041882 |  | 0.9 | 1.05 | 0.04323 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-249 | NP-LIPSCOMB2 | 0.66172 | 0.61984 | -0.041882 |  | 0.9 | 1.05 | 0.030179 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-001 | NP-LIPSCOMB2 | 0.66276 | 0.62066 | -0.042098 |  | 0.9 | 1.05 | 0.036526 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-020 | NP-LIPSCOMB2 | 0.66276 | 0.62066 | -0.042098 |  | 0.9 | 1.05 | 0.044321 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-017 | NP-LIPSCOMB2 | 0.66276 | 0.62066 | -0.042098 |  | 0.9 | 1.05 | 0.049912 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-018 | NP-LIPSCOMB2 | 0.66276 | 0.62066 | -0.042098 |  | 0.9 | 1.05 | 0.050386 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-019 | NP-LIPSCOMB2 | 0.66276 | 0.62066 | -0.042098 |  | 0.9 | 1.05 | 0.050386 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-020 | NP-LIPSCOMB2 | 0.66276 | 0.62066 | -0.042098 |  | 0.9 | 1.05 | 0.049912 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-021 | NP-LIPSCOMB2 | 0.66276 | 0.62066 | -0.042098 |  | 0.9 | 1.05 | 0.049912 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-022 | NP-LIPSCOMB2 | 0.66276 | 0.62066 | -0.042098 |  | 0.9 | 1.05 | 0.050386 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-023 | NP-LIPSCOMB2 | 0.66276 | 0.62066 | -0.042098 |  | 0.9 | 1.05 | 0.050386 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-081 | NP-LIPSCOMB2 | 0.66276 | 0.62066 | -0.042098 |  | 0.9 | 1.05 | 0.045015 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-082 | NP-LIPSCOMB2 | 0.66276 | 0.62066 | -0.042098 |  | 0.9 | 1.05 | 0.045015 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-211 | NP-LIPSCOMB2 | 0.66276 | 0.62066 | -0.042098 |  | 0.9 | 1.05 | 0.04323 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-212 | NP-LIPSCOMB2 | 0.66276 | 0.62066 | -0.042098 |  | 0.9 | 1.05 | 0.04323 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-213 | NP-LIPSCOMB2 | 0.66276 | 0.62066 | -0.042098 |  | 0.9 | 1.05 | 0.04323 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-249 | NP-LIPSCOMB2 | 0.66276 | 0.62066 | -0.042098 |  | 0.9 | 1.05 | 0.030179 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-001 | NP-LIPSCOMB2 | 0.66276 | 0.62066 | -0.042098 |  | 0.9 | 1.05 | 0.036526 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-020 | NP-LIPSCOMB2 | 0.66276 | 0.62066 | -0.042098 |  | 0.9 | 1.05 | 0.044321 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-017 | NP-LIPSCOMB2 | 0.66276 | 0.62066 | -0.042098 |  | 0.9 | 1.05 | 0.049912 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-018 | NP-LIPSCOMB2 | 0.66276 | 0.62066 | -0.042098 |  | 0.9 | 1.05 | 0.050386 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-019 | NP-LIPSCOMB2 | 0.66276 | 0.62066 | -0.042098 |  | 0.9 | 1.05 | 0.050386 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-020 | NP-LIPSCOMB2 | 0.66276 | 0.62066 | -0.042098 |  | 0.9 | 1.05 | 0.049912 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-021 | NP-LIPSCOMB2 | 0.66276 | 0.62066 | -0.042098 |  | 0.9 | 1.05 | 0.049912 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-022 | NP-LIPSCOMB2 | 0.66276 | 0.62066 | -0.042098 |  | 0.9 | 1.05 | 0.050386 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-023 | NP-LIPSCOMB2 | 0.66276 | 0.62066 | -0.042098 |  | 0.9 | 1.05 | 0.050386 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-081 | NP-LIPSCOMB2 | 0.66276 | 0.62066 | -0.042098 |  | 0.9 | 1.05 | 0.045015 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-082 | NP-LIPSCOMB2 | 0.66276 | 0.62066 | -0.042098 |  | 0.9 | 1.05 | 0.045015 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-211 | NP-LIPSCOMB2 | 0.66276 | 0.62066 | -0.042098 |  | 0.9 | 1.05 | 0.04323 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-212 | NP-LIPSCOMB2 | 0.66276 | 0.62066 | -0.042098 |  | 0.9 | 1.05 | 0.04323 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-213 | NP-LIPSCOMB2 | 0.66276 | 0.62066 | -0.042098 |  | 0.9 | 1.05 | 0.04323 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-249 | NP-LIPSCOMB2 | 0.66276 | 0.62066 | -0.042098 |  | 0.9 | 1.05 | 0.030179 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-020 | NP-LIPSCOMB2 | 0.66233 | 0.62466 | -0.037667 |  | 0.9 | 1.05 | 0.050823 | P23:345:SUNC:BU_BRK488:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-249 | NP-LIPSCOMB2 | 0.66233 | 0.62466 | -0.037667 |  | 0.9 | 1.05 | 0.030898 | P23:345:SUNC:BU_BRK488:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-020 | NP-LIPSCOMB2 | 0.66229 | 0.62466 | -0.037625 |  | 0.9 | 1.05 | 0.050823 | Single 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-249 | NP-LIPSCOMB2 | 0.66229 | 0.62466 | -0.037625 |  | 0.9 | 1.05 | 0.030898 | Single 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-001 | NP-LIPS_SHA2 | 0.66172 | 0.61984 | -0.041882 |  | 0.9 | 1.05 | 0.036526 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-020 | NP-LIPS_SHA2 | 0.66172 | 0.61984 | -0.041882 |  | 0.9 | 1.05 | 0.044321 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-017 | NP-LIPS_SHA2 | 0.66172 | 0.61984 | -0.041882 |  | 0.9 | 1.05 | 0.049912 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-018 | NP-LIPS_SHA2 | 0.66172 | 0.61984 | -0.041882 |  | 0.9 | 1.05 | 0.050386 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-019 | NP-LIPS_SHA2 | 0.66172 | 0.61984 | -0.041882 |  | 0.9 | 1.05 | 0.050386 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-020 | NP-LIPS_SHA2 | 0.66172 | 0.61984 | -0.041882 |  | 0.9 | 1.05 | 0.049912 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-021 | NP-LIPS_SHA2 | 0.66172 | 0.61984 | -0.041882 |  | 0.9 | 1.05 | 0.049912 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-022 | NP-LIPS_SHA2 | 0.66172 | 0.61984 | -0.041882 |  | 0.9 | 1.05 | 0.050386 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-023 | NP-LIPS_SHA2 | 0.66172 | 0.61984 | -0.041882 |  | 0.9 | 1.05 | 0.050386 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-081 | NP-LIPS_SHA2 | 0.66172 | 0.61984 | -0.041882 |  | 0.9 | 1.05 | 0.045015 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-082 | NP-LIPS_SHA2 | 0.66172 | 0.61984 | -0.041882 |  | 0.9 | 1.05 | 0.045015 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-211 | NP-LIPS_SHA2 | 0.66172 | 0.61984 | -0.041882 |  | 0.9 | 1.05 | 0.04323 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-212 | NP-LIPS_SHA2 | 0.66172 | 0.61984 | -0.041882 |  | 0.9 | 1.05 | 0.04323 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-213 | NP-LIPS_SHA2 | 0.66172 | 0.61984 | -0.041882 |  | 0.9 | 1.05 | 0.04323 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-249 | NP-LIPS_SHA2 | 0.66172 | 0.61984 | -0.041882 |  | 0.9 | 1.05 | 0.030179 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-001 | NP-LIPS_SHA2 | 0.66276 | 0.62066 | -0.042098 |  | 0.9 | 1.05 | 0.036526 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-020 | NP-LIPS_SHA2 | 0.66276 | 0.62066 | -0.042098 |  | 0.9 | 1.05 | 0.044321 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-017 | NP-LIPS_SHA2 | 0.66276 | 0.62066 | -0.042098 |  | 0.9 | 1.05 | 0.049912 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-018 | NP-LIPS_SHA2 | 0.66276 | 0.62066 | -0.042098 |  | 0.9 | 1.05 | 0.050386 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-019 | NP-LIPS_SHA2 | 0.66276 | 0.62066 | -0.042098 |  | 0.9 | 1.05 | 0.050386 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-020 | NP-LIPS_SHA2 | 0.66276 | 0.62066 | -0.042098 |  | 0.9 | 1.05 | 0.049912 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-021 | NP-LIPS_SHA2 | 0.66276 | 0.62066 | -0.042098 |  | 0.9 | 1.05 | 0.049912 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-022 | NP-LIPS_SHA2 | 0.66276 | 0.62066 | -0.042098 |  | 0.9 | 1.05 | 0.050386 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-023 | NP-LIPS_SHA2 | 0.66276 | 0.62066 | -0.042098 |  | 0.9 | 1.05 | 0.050386 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-081 | NP-LIPS_SHA2 | 0.66276 | 0.62066 | -0.042098 |  | 0.9 | 1.05 | 0.045015 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-082 | NP-LIPS_SHA2 | 0.66276 | 0.62066 | -0.042098 |  | 0.9 | 1.05 | 0.045015 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-211 | NP-LIPS_SHA2 | 0.66276 | 0.62066 | -0.042098 |  | 0.9 | 1.05 | 0.04323 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-212 | NP-LIPS_SHA2 | 0.66276 | 0.62066 | -0.042098 |  | 0.9 | 1.05 | 0.04323 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-213 | NP-LIPS_SHA2 | 0.66276 | 0.62066 | -0.042098 |  | 0.9 | 1.05 | 0.04323 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-249 | NP-LIPS_SHA2 | 0.66276 | 0.62066 | -0.042098 |  | 0.9 | 1.05 | 0.030179 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-001 | NP-LIPS_SHA2 | 0.66276 | 0.62066 | -0.042098 |  | 0.9 | 1.05 | 0.036526 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-020 | NP-LIPS_SHA2 | 0.66276 | 0.62066 | -0.042098 |  | 0.9 | 1.05 | 0.044321 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-017 | NP-LIPS_SHA2 | 0.66276 | 0.62066 | -0.042098 |  | 0.9 | 1.05 | 0.049912 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-018 | NP-LIPS_SHA2 | 0.66276 | 0.62066 | -0.042098 |  | 0.9 | 1.05 | 0.050386 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-019 | NP-LIPS_SHA2 | 0.66276 | 0.62066 | -0.042098 |  | 0.9 | 1.05 | 0.050386 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-020 | NP-LIPS_SHA2 | 0.66276 | 0.62066 | -0.042098 |  | 0.9 | 1.05 | 0.049912 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-021 | NP-LIPS_SHA2 | 0.66276 | 0.62066 | -0.042098 |  | 0.9 | 1.05 | 0.049912 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-022 | NP-LIPS_SHA2 | 0.66276 | 0.62066 | -0.042098 |  | 0.9 | 1.05 | 0.050386 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-023 | NP-LIPS_SHA2 | 0.66276 | 0.62066 | -0.042098 |  | 0.9 | 1.05 | 0.050386 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-081 | NP-LIPS_SHA2 | 0.66276 | 0.62066 | -0.042098 |  | 0.9 | 1.05 | 0.045015 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-082 | NP-LIPS_SHA2 | 0.66276 | 0.62066 | -0.042098 |  | 0.9 | 1.05 | 0.045015 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-211 | NP-LIPS_SHA2 | 0.66276 | 0.62066 | -0.042098 |  | 0.9 | 1.05 | 0.04323 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-212 | NP-LIPS_SHA2 | 0.66276 | 0.62066 | -0.042098 |  | 0.9 | 1.05 | 0.04323 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-213 | NP-LIPS_SHA2 | 0.66276 | 0.62066 | -0.042098 |  | 0.9 | 1.05 | 0.04323 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-249 | NP-LIPS_SHA2 | 0.66276 | 0.62066 | -0.042098 |  | 0.9 | 1.05 | 0.030179 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-020 | NP-LIPS_SHA2 | 0.66233 | 0.62466 | -0.037667 |  | 0.9 | 1.05 | 0.050823 | P23:345:SUNC:BU_BRK488:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-249 | NP-LIPS_SHA2 | 0.66233 | 0.62466 | -0.037667 |  | 0.9 | 1.05 | 0.030898 | P23:345:SUNC:BU_BRK488:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-020 | NP-LIPS_SHA2 | 0.66229 | 0.62466 | -0.037625 |  | 0.9 | 1.05 | 0.050823 | Single 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-249 | NP-LIPS_SHA2 | 0.66229 | 0.62466 | -0.037625 |  | 0.9 | 1.05 | 0.030898 | Single 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-001 | NP-LUCKY_CR2 | 0.79447 | 0.75863 | -0.035835 |  | 0.9 | 1.05 | 0.036526 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-020 | NP-LUCKY_CR2 | 0.79447 | 0.75863 | -0.035835 |  | 0.9 | 1.05 | 0.044321 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-017 | NP-LUCKY_CR2 | 0.79447 | 0.75863 | -0.035835 |  | 0.9 | 1.05 | 0.049912 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-018 | NP-LUCKY_CR2 | 0.79447 | 0.75863 | -0.035835 |  | 0.9 | 1.05 | 0.050386 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-019 | NP-LUCKY_CR2 | 0.79447 | 0.75863 | -0.035835 |  | 0.9 | 1.05 | 0.050386 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-020 | NP-LUCKY_CR2 | 0.79447 | 0.75863 | -0.035835 |  | 0.9 | 1.05 | 0.049912 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-021 | NP-LUCKY_CR2 | 0.79447 | 0.75863 | -0.035835 |  | 0.9 | 1.05 | 0.049912 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-022 | NP-LUCKY_CR2 | 0.79447 | 0.75863 | -0.035835 |  | 0.9 | 1.05 | 0.050386 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-023 | NP-LUCKY_CR2 | 0.79447 | 0.75863 | -0.035835 |  | 0.9 | 1.05 | 0.050386 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-081 | NP-LUCKY_CR2 | 0.79447 | 0.75863 | -0.035835 |  | 0.9 | 1.05 | 0.045015 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-082 | NP-LUCKY_CR2 | 0.79447 | 0.75863 | -0.035835 |  | 0.9 | 1.05 | 0.045015 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-211 | NP-LUCKY_CR2 | 0.79447 | 0.75863 | -0.035835 |  | 0.9 | 1.05 | 0.04323 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-212 | NP-LUCKY_CR2 | 0.79447 | 0.75863 | -0.035835 |  | 0.9 | 1.05 | 0.04323 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-213 | NP-LUCKY_CR2 | 0.79447 | 0.75863 | -0.035835 |  | 0.9 | 1.05 | 0.04323 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-249 | NP-LUCKY_CR2 | 0.79447 | 0.75863 | -0.035835 |  | 0.9 | 1.05 | 0.030179 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-001 | NP-LUCKY_CR2 | 0.79534 | 0.75936 | -0.035981 |  | 0.9 | 1.05 | 0.036526 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-020 | NP-LUCKY_CR2 | 0.79534 | 0.75936 | -0.035981 |  | 0.9 | 1.05 | 0.044321 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-017 | NP-LUCKY_CR2 | 0.79534 | 0.75936 | -0.035981 |  | 0.9 | 1.05 | 0.049912 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-018 | NP-LUCKY_CR2 | 0.79534 | 0.75936 | -0.035981 |  | 0.9 | 1.05 | 0.050386 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-019 | NP-LUCKY_CR2 | 0.79534 | 0.75936 | -0.035981 |  | 0.9 | 1.05 | 0.050386 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-020 | NP-LUCKY_CR2 | 0.79534 | 0.75936 | -0.035981 |  | 0.9 | 1.05 | 0.049912 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-021 | NP-LUCKY_CR2 | 0.79534 | 0.75936 | -0.035981 |  | 0.9 | 1.05 | 0.049912 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-022 | NP-LUCKY_CR2 | 0.79534 | 0.75936 | -0.035981 |  | 0.9 | 1.05 | 0.050386 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-023 | NP-LUCKY_CR2 | 0.79534 | 0.75936 | -0.035981 |  | 0.9 | 1.05 | 0.050386 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-081 | NP-LUCKY_CR2 | 0.79534 | 0.75936 | -0.035981 |  | 0.9 | 1.05 | 0.045015 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-082 | NP-LUCKY_CR2 | 0.79534 | 0.75936 | -0.035981 |  | 0.9 | 1.05 | 0.045015 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-211 | NP-LUCKY_CR2 | 0.79534 | 0.75936 | -0.035981 |  | 0.9 | 1.05 | 0.04323 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-212 | NP-LUCKY_CR2 | 0.79534 | 0.75936 | -0.035981 |  | 0.9 | 1.05 | 0.04323 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-213 | NP-LUCKY_CR2 | 0.79534 | 0.75936 | -0.035981 |  | 0.9 | 1.05 | 0.04323 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-249 | NP-LUCKY_CR2 | 0.79534 | 0.75936 | -0.035981 |  | 0.9 | 1.05 | 0.030179 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-001 | NP-LUCKY_CR2 | 0.79534 | 0.75936 | -0.035981 |  | 0.9 | 1.05 | 0.036526 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-020 | NP-LUCKY_CR2 | 0.79534 | 0.75936 | -0.035981 |  | 0.9 | 1.05 | 0.044321 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-017 | NP-LUCKY_CR2 | 0.79534 | 0.75936 | -0.035981 |  | 0.9 | 1.05 | 0.049912 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-018 | NP-LUCKY_CR2 | 0.79534 | 0.75936 | -0.035981 |  | 0.9 | 1.05 | 0.050386 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-019 | NP-LUCKY_CR2 | 0.79534 | 0.75936 | -0.035981 |  | 0.9 | 1.05 | 0.050386 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-020 | NP-LUCKY_CR2 | 0.79534 | 0.75936 | -0.035981 |  | 0.9 | 1.05 | 0.049912 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-021 | NP-LUCKY_CR2 | 0.79534 | 0.75936 | -0.035981 |  | 0.9 | 1.05 | 0.049912 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-022 | NP-LUCKY_CR2 | 0.79534 | 0.75936 | -0.035981 |  | 0.9 | 1.05 | 0.050386 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-023 | NP-LUCKY_CR2 | 0.79534 | 0.75936 | -0.035981 |  | 0.9 | 1.05 | 0.050386 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-081 | NP-LUCKY_CR2 | 0.79534 | 0.75936 | -0.035981 |  | 0.9 | 1.05 | 0.045015 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-082 | NP-LUCKY_CR2 | 0.79534 | 0.75936 | -0.035981 |  | 0.9 | 1.05 | 0.045015 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-211 | NP-LUCKY_CR2 | 0.79534 | 0.75936 | -0.035981 |  | 0.9 | 1.05 | 0.04323 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-212 | NP-LUCKY_CR2 | 0.79534 | 0.75936 | -0.035981 |  | 0.9 | 1.05 | 0.04323 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-213 | NP-LUCKY_CR2 | 0.79534 | 0.75936 | -0.035981 |  | 0.9 | 1.05 | 0.04323 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-249 | NP-LUCKY_CR2 | 0.79534 | 0.75936 | -0.035981 |  | 0.9 | 1.05 | 0.030179 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-020 | NP-LUCKY_CR2 | 0.79498 | 0.76285 | -0.032126 |  | 0.9 | 1.05 | 0.050823 | P23:345:SUNC:BU_BRK488:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-249 | NP-LUCKY_CR2 | 0.79498 | 0.76285 | -0.032126 |  | 0.9 | 1.05 | 0.030898 | P23:345:SUNC:BU_BRK488:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-020 | NP-LUCKY_CR2 | 0.79494 | 0.76285 | -0.03209 |  | 0.9 | 1.05 | 0.050823 | Single 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-249 | NP-LUCKY_CR2 | 0.79494 | 0.76285 | -0.03209 |  | 0.9 | 1.05 | 0.030898 | Single 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-001 | NP-LUCKY_G 2 | 0.79462 | 0.75879 | -0.035828 |  | 0.9 | 1.05 | 0.036526 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-020 | NP-LUCKY_G 2 | 0.79462 | 0.75879 | -0.035828 |  | 0.9 | 1.05 | 0.044321 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-017 | NP-LUCKY_G 2 | 0.79462 | 0.75879 | -0.035828 |  | 0.9 | 1.05 | 0.049912 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-018 | NP-LUCKY_G 2 | 0.79462 | 0.75879 | -0.035828 |  | 0.9 | 1.05 | 0.050386 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-019 | NP-LUCKY_G 2 | 0.79462 | 0.75879 | -0.035828 |  | 0.9 | 1.05 | 0.050386 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-020 | NP-LUCKY_G 2 | 0.79462 | 0.75879 | -0.035828 |  | 0.9 | 1.05 | 0.049912 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-021 | NP-LUCKY_G 2 | 0.79462 | 0.75879 | -0.035828 |  | 0.9 | 1.05 | 0.049912 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-022 | NP-LUCKY_G 2 | 0.79462 | 0.75879 | -0.035828 |  | 0.9 | 1.05 | 0.050386 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-023 | NP-LUCKY_G 2 | 0.79462 | 0.75879 | -0.035828 |  | 0.9 | 1.05 | 0.050386 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-081 | NP-LUCKY_G 2 | 0.79462 | 0.75879 | -0.035828 |  | 0.9 | 1.05 | 0.045015 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-082 | NP-LUCKY_G 2 | 0.79462 | 0.75879 | -0.035828 |  | 0.9 | 1.05 | 0.045015 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-211 | NP-LUCKY_G 2 | 0.79462 | 0.75879 | -0.035828 |  | 0.9 | 1.05 | 0.04323 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-212 | NP-LUCKY_G 2 | 0.79462 | 0.75879 | -0.035828 |  | 0.9 | 1.05 | 0.04323 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-213 | NP-LUCKY_G 2 | 0.79462 | 0.75879 | -0.035828 |  | 0.9 | 1.05 | 0.04323 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-249 | NP-LUCKY_G 2 | 0.79462 | 0.75879 | -0.035828 |  | 0.9 | 1.05 | 0.030179 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-001 | NP-LUCKY_G 2 | 0.79549 | 0.75951 | -0.035974 |  | 0.9 | 1.05 | 0.036526 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-020 | NP-LUCKY_G 2 | 0.79549 | 0.75951 | -0.035974 |  | 0.9 | 1.05 | 0.044321 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-017 | NP-LUCKY_G 2 | 0.79549 | 0.75951 | -0.035974 |  | 0.9 | 1.05 | 0.049912 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-018 | NP-LUCKY_G 2 | 0.79549 | 0.75951 | -0.035974 |  | 0.9 | 1.05 | 0.050386 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-019 | NP-LUCKY_G 2 | 0.79549 | 0.75951 | -0.035974 |  | 0.9 | 1.05 | 0.050386 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-020 | NP-LUCKY_G 2 | 0.79549 | 0.75951 | -0.035974 |  | 0.9 | 1.05 | 0.049912 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-021 | NP-LUCKY_G 2 | 0.79549 | 0.75951 | -0.035974 |  | 0.9 | 1.05 | 0.049912 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-022 | NP-LUCKY_G 2 | 0.79549 | 0.75951 | -0.035974 |  | 0.9 | 1.05 | 0.050386 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-023 | NP-LUCKY_G 2 | 0.79549 | 0.75951 | -0.035974 |  | 0.9 | 1.05 | 0.050386 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-081 | NP-LUCKY_G 2 | 0.79549 | 0.75951 | -0.035974 |  | 0.9 | 1.05 | 0.045015 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-082 | NP-LUCKY_G 2 | 0.79549 | 0.75951 | -0.035974 |  | 0.9 | 1.05 | 0.045015 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-211 | NP-LUCKY_G 2 | 0.79549 | 0.75951 | -0.035974 |  | 0.9 | 1.05 | 0.04323 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-212 | NP-LUCKY_G 2 | 0.79549 | 0.75951 | -0.035974 |  | 0.9 | 1.05 | 0.04323 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-213 | NP-LUCKY_G 2 | 0.79549 | 0.75951 | -0.035974 |  | 0.9 | 1.05 | 0.04323 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-249 | NP-LUCKY_G 2 | 0.79549 | 0.75951 | -0.035974 |  | 0.9 | 1.05 | 0.030179 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-001 | NP-LUCKY_G 2 | 0.79549 | 0.75951 | -0.035974 |  | 0.9 | 1.05 | 0.036526 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-020 | NP-LUCKY_G 2 | 0.79549 | 0.75951 | -0.035974 |  | 0.9 | 1.05 | 0.044321 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-017 | NP-LUCKY_G 2 | 0.79549 | 0.75951 | -0.035974 |  | 0.9 | 1.05 | 0.049912 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-018 | NP-LUCKY_G 2 | 0.79549 | 0.75951 | -0.035974 |  | 0.9 | 1.05 | 0.050386 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-019 | NP-LUCKY_G 2 | 0.79549 | 0.75951 | -0.035974 |  | 0.9 | 1.05 | 0.050386 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-020 | NP-LUCKY_G 2 | 0.79549 | 0.75951 | -0.035974 |  | 0.9 | 1.05 | 0.049912 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-021 | NP-LUCKY_G 2 | 0.79549 | 0.75951 | -0.035974 |  | 0.9 | 1.05 | 0.049912 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-022 | NP-LUCKY_G 2 | 0.79549 | 0.75951 | -0.035974 |  | 0.9 | 1.05 | 0.050386 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-023 | NP-LUCKY_G 2 | 0.79549 | 0.75951 | -0.035974 |  | 0.9 | 1.05 | 0.050386 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-081 | NP-LUCKY_G 2 | 0.79549 | 0.75951 | -0.035974 |  | 0.9 | 1.05 | 0.045015 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-082 | NP-LUCKY_G 2 | 0.79549 | 0.75951 | -0.035974 |  | 0.9 | 1.05 | 0.045015 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-211 | NP-LUCKY_G 2 | 0.79549 | 0.75951 | -0.035974 |  | 0.9 | 1.05 | 0.04323 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-212 | NP-LUCKY_G 2 | 0.79549 | 0.75951 | -0.035974 |  | 0.9 | 1.05 | 0.04323 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-213 | NP-LUCKY_G 2 | 0.79549 | 0.75951 | -0.035974 |  | 0.9 | 1.05 | 0.04323 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-249 | NP-LUCKY_G 2 | 0.79549 | 0.75951 | -0.035974 |  | 0.9 | 1.05 | 0.030179 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-020 | NP-LUCKY_G 2 | 0.79513 | 0.76301 | -0.032119 |  | 0.9 | 1.05 | 0.050823 | P23:345:SUNC:BU_BRK488:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-249 | NP-LUCKY_G 2 | 0.79513 | 0.76301 | -0.032119 |  | 0.9 | 1.05 | 0.030898 | P23:345:SUNC:BU_BRK488:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-020 | NP-LUCKY_G 2 | 0.79509 | 0.76301 | -0.032083 |  | 0.9 | 1.05 | 0.050823 | Single 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-249 | NP-LUCKY_G 2 | 0.79509 | 0.76301 | -0.032083 |  | 0.9 | 1.05 | 0.030898 | Single 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-001 | NP-SHATTUCK2 | 0.63951 | 0.59682 | -0.042692 |  | 0.9 | 1.05 | 0.036526 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-020 | NP-SHATTUCK2 | 0.63951 | 0.59682 | -0.042692 |  | 0.9 | 1.05 | 0.044321 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-017 | NP-SHATTUCK2 | 0.63951 | 0.59682 | -0.042692 |  | 0.9 | 1.05 | 0.049912 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-018 | NP-SHATTUCK2 | 0.63951 | 0.59682 | -0.042692 |  | 0.9 | 1.05 | 0.050386 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-019 | NP-SHATTUCK2 | 0.63951 | 0.59682 | -0.042692 |  | 0.9 | 1.05 | 0.050386 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-020 | NP-SHATTUCK2 | 0.63951 | 0.59682 | -0.042692 |  | 0.9 | 1.05 | 0.049912 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-021 | NP-SHATTUCK2 | 0.63951 | 0.59682 | -0.042692 |  | 0.9 | 1.05 | 0.049912 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-022 | NP-SHATTUCK2 | 0.63951 | 0.59682 | -0.042692 |  | 0.9 | 1.05 | 0.050386 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-023 | NP-SHATTUCK2 | 0.63951 | 0.59682 | -0.042692 |  | 0.9 | 1.05 | 0.050386 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-081 | NP-SHATTUCK2 | 0.63951 | 0.59682 | -0.042692 |  | 0.9 | 1.05 | 0.045015 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-082 | NP-SHATTUCK2 | 0.63951 | 0.59682 | -0.042692 |  | 0.9 | 1.05 | 0.045015 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-211 | NP-SHATTUCK2 | 0.63951 | 0.59682 | -0.042692 |  | 0.9 | 1.05 | 0.04323 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-212 | NP-SHATTUCK2 | 0.63951 | 0.59682 | -0.042692 |  | 0.9 | 1.05 | 0.04323 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-213 | NP-SHATTUCK2 | 0.63951 | 0.59682 | -0.042692 |  | 0.9 | 1.05 | 0.04323 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-249 | NP-SHATTUCK2 | 0.63951 | 0.59682 | -0.042692 |  | 0.9 | 1.05 | 0.030179 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-001 | NP-SHATTUCK2 | 0.64058 | 0.59766 | -0.04292 |  | 0.9 | 1.05 | 0.036526 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-020 | NP-SHATTUCK2 | 0.64058 | 0.59766 | -0.04292 |  | 0.9 | 1.05 | 0.044321 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-017 | NP-SHATTUCK2 | 0.64058 | 0.59766 | -0.04292 |  | 0.9 | 1.05 | 0.049912 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-018 | NP-SHATTUCK2 | 0.64058 | 0.59766 | -0.04292 |  | 0.9 | 1.05 | 0.050386 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-019 | NP-SHATTUCK2 | 0.64058 | 0.59766 | -0.04292 |  | 0.9 | 1.05 | 0.050386 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-020 | NP-SHATTUCK2 | 0.64058 | 0.59766 | -0.04292 |  | 0.9 | 1.05 | 0.049912 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-021 | NP-SHATTUCK2 | 0.64058 | 0.59766 | -0.04292 |  | 0.9 | 1.05 | 0.049912 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-022 | NP-SHATTUCK2 | 0.64058 | 0.59766 | -0.04292 |  | 0.9 | 1.05 | 0.050386 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-023 | NP-SHATTUCK2 | 0.64058 | 0.59766 | -0.04292 |  | 0.9 | 1.05 | 0.050386 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-081 | NP-SHATTUCK2 | 0.64058 | 0.59766 | -0.04292 |  | 0.9 | 1.05 | 0.045015 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-082 | NP-SHATTUCK2 | 0.64058 | 0.59766 | -0.04292 |  | 0.9 | 1.05 | 0.045015 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-211 | NP-SHATTUCK2 | 0.64058 | 0.59766 | -0.04292 |  | 0.9 | 1.05 | 0.04323 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-212 | NP-SHATTUCK2 | 0.64058 | 0.59766 | -0.04292 |  | 0.9 | 1.05 | 0.04323 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-213 | NP-SHATTUCK2 | 0.64058 | 0.59766 | -0.04292 |  | 0.9 | 1.05 | 0.04323 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-249 | NP-SHATTUCK2 | 0.64058 | 0.59766 | -0.04292 |  | 0.9 | 1.05 | 0.030179 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-001 | NP-SHATTUCK2 | 0.64058 | 0.59766 | -0.04292 |  | 0.9 | 1.05 | 0.036526 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-020 | NP-SHATTUCK2 | 0.64058 | 0.59766 | -0.04292 |  | 0.9 | 1.05 | 0.044321 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-017 | NP-SHATTUCK2 | 0.64058 | 0.59766 | -0.04292 |  | 0.9 | 1.05 | 0.049912 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-018 | NP-SHATTUCK2 | 0.64058 | 0.59766 | -0.04292 |  | 0.9 | 1.05 | 0.050386 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-019 | NP-SHATTUCK2 | 0.64058 | 0.59766 | -0.04292 |  | 0.9 | 1.05 | 0.050386 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-020 | NP-SHATTUCK2 | 0.64058 | 0.59766 | -0.04292 |  | 0.9 | 1.05 | 0.049912 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-021 | NP-SHATTUCK2 | 0.64058 | 0.59766 | -0.04292 |  | 0.9 | 1.05 | 0.049912 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-022 | NP-SHATTUCK2 | 0.64058 | 0.59766 | -0.04292 |  | 0.9 | 1.05 | 0.050386 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-023 | NP-SHATTUCK2 | 0.64058 | 0.59766 | -0.04292 |  | 0.9 | 1.05 | 0.050386 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-081 | NP-SHATTUCK2 | 0.64058 | 0.59766 | -0.04292 |  | 0.9 | 1.05 | 0.045015 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-082 | NP-SHATTUCK2 | 0.64058 | 0.59766 | -0.04292 |  | 0.9 | 1.05 | 0.045015 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-211 | NP-SHATTUCK2 | 0.64058 | 0.59766 | -0.04292 |  | 0.9 | 1.05 | 0.04323 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-212 | NP-SHATTUCK2 | 0.64058 | 0.59766 | -0.04292 |  | 0.9 | 1.05 | 0.04323 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-213 | NP-SHATTUCK2 | 0.64058 | 0.59766 | -0.04292 |  | 0.9 | 1.05 | 0.04323 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-249 | NP-SHATTUCK2 | 0.64058 | 0.59766 | -0.04292 |  | 0.9 | 1.05 | 0.030179 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-020 | NP-SHATTUCK2 | 0.64014 | 0.60173 | -0.038413 |  | 0.9 | 1.05 | 0.050823 | P23:345:SUNC:BU_BRK488:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-249 | NP-SHATTUCK2 | 0.64014 | 0.60173 | -0.038413 |  | 0.9 | 1.05 | 0.030898 | P23:345:SUNC:BU_BRK488:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-020 | NP-SHATTUCK2 | 0.6401 | 0.60173 | -0.038369 |  | 0.9 | 1.05 | 0.050823 | Single 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-249 | NP-SHATTUCK2 | 0.6401 | 0.60173 | -0.038369 |  | 0.9 | 1.05 | 0.030898 | Single 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-001 | NP-SUB_A 2 | 0.86247 | 0.83009 | -0.032387 |  | 0.9 | 1.05 | 0.036526 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-020 | NP-SUB_A 2 | 0.86247 | 0.83009 | -0.032387 |  | 0.9 | 1.05 | 0.044321 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-017 | NP-SUB_A 2 | 0.86247 | 0.83009 | -0.032387 |  | 0.9 | 1.05 | 0.049912 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-018 | NP-SUB_A 2 | 0.86247 | 0.83009 | -0.032387 |  | 0.9 | 1.05 | 0.050386 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-019 | NP-SUB_A 2 | 0.86247 | 0.83009 | -0.032387 |  | 0.9 | 1.05 | 0.050386 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-020 | NP-SUB_A 2 | 0.86247 | 0.83009 | -0.032387 |  | 0.9 | 1.05 | 0.049912 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-021 | NP-SUB_A 2 | 0.86247 | 0.83009 | -0.032387 |  | 0.9 | 1.05 | 0.049912 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-022 | NP-SUB_A 2 | 0.86247 | 0.83009 | -0.032387 |  | 0.9 | 1.05 | 0.050386 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-023 | NP-SUB_A 2 | 0.86247 | 0.83009 | -0.032387 |  | 0.9 | 1.05 | 0.050386 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-081 | NP-SUB_A 2 | 0.86247 | 0.83009 | -0.032387 |  | 0.9 | 1.05 | 0.045015 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-082 | NP-SUB_A 2 | 0.86247 | 0.83009 | -0.032387 |  | 0.9 | 1.05 | 0.045015 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-211 | NP-SUB_A 2 | 0.86247 | 0.83009 | -0.032387 |  | 0.9 | 1.05 | 0.04323 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-212 | NP-SUB_A 2 | 0.86247 | 0.83009 | -0.032387 |  | 0.9 | 1.05 | 0.04323 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-213 | NP-SUB_A 2 | 0.86247 | 0.83009 | -0.032387 |  | 0.9 | 1.05 | 0.04323 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-249 | NP-SUB_A 2 | 0.86247 | 0.83009 | -0.032387 |  | 0.9 | 1.05 | 0.030179 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-001 | NP-SUB_A 2 | 0.86326 | 0.83075 | -0.032507 |  | 0.9 | 1.05 | 0.036526 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-020 | NP-SUB_A 2 | 0.86326 | 0.83075 | -0.032507 |  | 0.9 | 1.05 | 0.044321 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-017 | NP-SUB_A 2 | 0.86326 | 0.83075 | -0.032507 |  | 0.9 | 1.05 | 0.049912 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-018 | NP-SUB_A 2 | 0.86326 | 0.83075 | -0.032507 |  | 0.9 | 1.05 | 0.050386 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-019 | NP-SUB_A 2 | 0.86326 | 0.83075 | -0.032507 |  | 0.9 | 1.05 | 0.050386 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-020 | NP-SUB_A 2 | 0.86326 | 0.83075 | -0.032507 |  | 0.9 | 1.05 | 0.049912 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-021 | NP-SUB_A 2 | 0.86326 | 0.83075 | -0.032507 |  | 0.9 | 1.05 | 0.049912 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-022 | NP-SUB_A 2 | 0.86326 | 0.83075 | -0.032507 |  | 0.9 | 1.05 | 0.050386 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-023 | NP-SUB_A 2 | 0.86326 | 0.83075 | -0.032507 |  | 0.9 | 1.05 | 0.050386 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-081 | NP-SUB_A 2 | 0.86326 | 0.83075 | -0.032507 |  | 0.9 | 1.05 | 0.045015 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-082 | NP-SUB_A 2 | 0.86326 | 0.83075 | -0.032507 |  | 0.9 | 1.05 | 0.045015 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-211 | NP-SUB_A 2 | 0.86326 | 0.83075 | -0.032507 |  | 0.9 | 1.05 | 0.04323 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-212 | NP-SUB_A 2 | 0.86326 | 0.83075 | -0.032507 |  | 0.9 | 1.05 | 0.04323 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-213 | NP-SUB_A 2 | 0.86326 | 0.83075 | -0.032507 |  | 0.9 | 1.05 | 0.04323 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-249 | NP-SUB_A 2 | 0.86326 | 0.83075 | -0.032507 |  | 0.9 | 1.05 | 0.030179 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-001 | NP-SUB_A 2 | 0.86326 | 0.83075 | -0.032507 |  | 0.9 | 1.05 | 0.036526 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-020 | NP-SUB_A 2 | 0.86326 | 0.83075 | -0.032507 |  | 0.9 | 1.05 | 0.044321 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-017 | NP-SUB_A 2 | 0.86326 | 0.83075 | -0.032507 |  | 0.9 | 1.05 | 0.049912 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-018 | NP-SUB_A 2 | 0.86326 | 0.83075 | -0.032507 |  | 0.9 | 1.05 | 0.050386 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-019 | NP-SUB_A 2 | 0.86326 | 0.83075 | -0.032507 |  | 0.9 | 1.05 | 0.050386 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-020 | NP-SUB_A 2 | 0.86326 | 0.83075 | -0.032507 |  | 0.9 | 1.05 | 0.049912 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-021 | NP-SUB_A 2 | 0.86326 | 0.83075 | -0.032507 |  | 0.9 | 1.05 | 0.049912 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-022 | NP-SUB_A 2 | 0.86326 | 0.83075 | -0.032507 |  | 0.9 | 1.05 | 0.050386 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-023 | NP-SUB_A 2 | 0.86326 | 0.83075 | -0.032507 |  | 0.9 | 1.05 | 0.050386 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-081 | NP-SUB_A 2 | 0.86326 | 0.83075 | -0.032507 |  | 0.9 | 1.05 | 0.045015 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-082 | NP-SUB_A 2 | 0.86326 | 0.83075 | -0.032507 |  | 0.9 | 1.05 | 0.045015 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-211 | NP-SUB_A 2 | 0.86326 | 0.83075 | -0.032507 |  | 0.9 | 1.05 | 0.04323 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-212 | NP-SUB_A 2 | 0.86326 | 0.83075 | -0.032507 |  | 0.9 | 1.05 | 0.04323 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-213 | NP-SUB_A 2 | 0.86326 | 0.83075 | -0.032507 |  | 0.9 | 1.05 | 0.04323 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-249 | NP-SUB_A 2 | 0.86326 | 0.83075 | -0.032507 |  | 0.9 | 1.05 | 0.030179 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-020 | NP-SUB_A 2 | 0.86293 | 0.83393 | -0.029003 |  | 0.9 | 1.05 | 0.050823 | P23:345:SUNC:BU_BRK488:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-249 | NP-SUB_A 2 | 0.86293 | 0.83393 | -0.029003 |  | 0.9 | 1.05 | 0.030898 | P23:345:SUNC:BU_BRK488:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-020 | NP-SUB_A 2 | 0.8629 | 0.83393 | -0.028971 |  | 0.9 | 1.05 | 0.050823 | Single 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-249 | NP-SUB_A 2 | 0.8629 | 0.83393 | -0.028971 |  | 0.9 | 1.05 | 0.030898 | Single 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-001 | NP-VALERO_P2 | 0.67008 | 0.62853 | -0.041555 |  | 0.9 | 1.05 | 0.036526 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-020 | NP-VALERO_P2 | 0.67008 | 0.62853 | -0.041555 |  | 0.9 | 1.05 | 0.044321 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-017 | NP-VALERO_P2 | 0.67008 | 0.62853 | -0.041555 |  | 0.9 | 1.05 | 0.049912 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-018 | NP-VALERO_P2 | 0.67008 | 0.62853 | -0.041555 |  | 0.9 | 1.05 | 0.050386 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-019 | NP-VALERO_P2 | 0.67008 | 0.62853 | -0.041555 |  | 0.9 | 1.05 | 0.050386 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-020 | NP-VALERO_P2 | 0.67008 | 0.62853 | -0.041555 |  | 0.9 | 1.05 | 0.049912 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-021 | NP-VALERO_P2 | 0.67008 | 0.62853 | -0.041555 |  | 0.9 | 1.05 | 0.049912 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-022 | NP-VALERO_P2 | 0.67008 | 0.62853 | -0.041555 |  | 0.9 | 1.05 | 0.050386 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-023 | NP-VALERO_P2 | 0.67008 | 0.62853 | -0.041555 |  | 0.9 | 1.05 | 0.050386 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-081 | NP-VALERO_P2 | 0.67008 | 0.62853 | -0.041555 |  | 0.9 | 1.05 | 0.045015 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-082 | NP-VALERO_P2 | 0.67008 | 0.62853 | -0.041555 |  | 0.9 | 1.05 | 0.045015 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-211 | NP-VALERO_P2 | 0.67008 | 0.62853 | -0.041555 |  | 0.9 | 1.05 | 0.04323 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-212 | NP-VALERO_P2 | 0.67008 | 0.62853 | -0.041555 |  | 0.9 | 1.05 | 0.04323 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-213 | NP-VALERO_P2 | 0.67008 | 0.62853 | -0.041555 |  | 0.9 | 1.05 | 0.04323 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-249 | NP-VALERO_P2 | 0.67008 | 0.62853 | -0.041555 |  | 0.9 | 1.05 | 0.030179 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-001 | NP-VALERO_P2 | 0.67112 | 0.62935 | -0.041767 |  | 0.9 | 1.05 | 0.036526 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-020 | NP-VALERO_P2 | 0.67112 | 0.62935 | -0.041767 |  | 0.9 | 1.05 | 0.044321 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-017 | NP-VALERO_P2 | 0.67112 | 0.62935 | -0.041767 |  | 0.9 | 1.05 | 0.049912 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-018 | NP-VALERO_P2 | 0.67112 | 0.62935 | -0.041767 |  | 0.9 | 1.05 | 0.050386 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-019 | NP-VALERO_P2 | 0.67112 | 0.62935 | -0.041767 |  | 0.9 | 1.05 | 0.050386 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-020 | NP-VALERO_P2 | 0.67112 | 0.62935 | -0.041767 |  | 0.9 | 1.05 | 0.049912 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-021 | NP-VALERO_P2 | 0.67112 | 0.62935 | -0.041767 |  | 0.9 | 1.05 | 0.049912 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-022 | NP-VALERO_P2 | 0.67112 | 0.62935 | -0.041767 |  | 0.9 | 1.05 | 0.050386 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-023 | NP-VALERO_P2 | 0.67112 | 0.62935 | -0.041767 |  | 0.9 | 1.05 | 0.050386 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-081 | NP-VALERO_P2 | 0.67112 | 0.62935 | -0.041767 |  | 0.9 | 1.05 | 0.045015 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-082 | NP-VALERO_P2 | 0.67112 | 0.62935 | -0.041767 |  | 0.9 | 1.05 | 0.045015 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-211 | NP-VALERO_P2 | 0.67112 | 0.62935 | -0.041767 |  | 0.9 | 1.05 | 0.04323 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-212 | NP-VALERO_P2 | 0.67112 | 0.62935 | -0.041767 |  | 0.9 | 1.05 | 0.04323 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-213 | NP-VALERO_P2 | 0.67112 | 0.62935 | -0.041767 |  | 0.9 | 1.05 | 0.04323 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-249 | NP-VALERO_P2 | 0.67112 | 0.62935 | -0.041767 |  | 0.9 | 1.05 | 0.030179 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-001 | NP-VALERO_P2 | 0.67112 | 0.62935 | -0.041767 |  | 0.9 | 1.05 | 0.036526 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-020 | NP-VALERO_P2 | 0.67112 | 0.62935 | -0.041767 |  | 0.9 | 1.05 | 0.044321 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-017 | NP-VALERO_P2 | 0.67112 | 0.62935 | -0.041767 |  | 0.9 | 1.05 | 0.049912 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-018 | NP-VALERO_P2 | 0.67112 | 0.62935 | -0.041767 |  | 0.9 | 1.05 | 0.050386 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-019 | NP-VALERO_P2 | 0.67112 | 0.62935 | -0.041767 |  | 0.9 | 1.05 | 0.050386 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-020 | NP-VALERO_P2 | 0.67112 | 0.62935 | -0.041767 |  | 0.9 | 1.05 | 0.049912 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-021 | NP-VALERO_P2 | 0.67112 | 0.62935 | -0.041767 |  | 0.9 | 1.05 | 0.049912 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-022 | NP-VALERO_P2 | 0.67112 | 0.62935 | -0.041767 |  | 0.9 | 1.05 | 0.050386 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-023 | NP-VALERO_P2 | 0.67112 | 0.62935 | -0.041767 |  | 0.9 | 1.05 | 0.050386 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-081 | NP-VALERO_P2 | 0.67112 | 0.62935 | -0.041767 |  | 0.9 | 1.05 | 0.045015 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-082 | NP-VALERO_P2 | 0.67112 | 0.62935 | -0.041767 |  | 0.9 | 1.05 | 0.045015 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-211 | NP-VALERO_P2 | 0.67112 | 0.62935 | -0.041767 |  | 0.9 | 1.05 | 0.04323 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-212 | NP-VALERO_P2 | 0.67112 | 0.62935 | -0.041767 |  | 0.9 | 1.05 | 0.04323 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-213 | NP-VALERO_P2 | 0.67112 | 0.62935 | -0.041767 |  | 0.9 | 1.05 | 0.04323 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-249 | NP-VALERO_P2 | 0.67112 | 0.62935 | -0.041767 |  | 0.9 | 1.05 | 0.030179 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-020 | NP-VALERO_P2 | 0.67069 | 0.63332 | -0.037367 |  | 0.9 | 1.05 | 0.050823 | P23:345:SUNC:BU_BRK488:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-249 | NP-VALERO_P2 | 0.67069 | 0.63332 | -0.037367 |  | 0.9 | 1.05 | 0.030898 | P23:345:SUNC:BU_BRK488:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-020 | NP-VALERO_P2 | 0.67065 | 0.63332 | -0.037325 |  | 0.9 | 1.05 | 0.050823 | Single 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-249 | NP-VALERO_P2 | 0.67065 | 0.63332 | -0.037325 |  | 0.9 | 1.05 | 0.030898 | Single 531449 HOLCOMB7 345 531501 BUCKNER7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-003 | RB-NMO1_SW 2 | 0.92616 | 0.89929 | -0.026873 |  | 0.9 | 1.05 | 0.034963 | P12:345:OKGE:BKRBKR3360:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-013 | RB-NMO1_SW 2 | 0.92616 | 0.89929 | -0.026873 |  | 0.9 | 1.05 | 0.06687 | P12:345:OKGE:BKRBKR3360:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-128 | RB-NMO1_SW 2 | 0.92616 | 0.89929 | -0.026873 |  | 0.9 | 1.05 | 0.031468 | P12:345:OKGE:BKRBKR3360:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-252 | RB-NMO1_SW 2 | 0.92616 | 0.89929 | -0.026873 |  | 0.9 | 1.05 | 0.082111 | P12:345:OKGE:BKRBKR3360:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-254 | RB-NMO1_SW 2 | 0.92616 | 0.89929 | -0.026873 |  | 0.9 | 1.05 | 0.096271 | P12:345:OKGE:BKRBKR3360:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-255 | RB-NMO1_SW 2 | 0.92616 | 0.89929 | -0.026873 |  | 0.9 | 1.05 | 0.079014 | P12:345:OKGE:BKRBKR3360:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-286 | RB-NMO1_SW 2 | 0.92616 | 0.89929 | -0.026873 |  | 0.9 | 1.05 | 0.036822 | P12:345:OKGE:BKRBKR3360:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-293 | RB-NMO1_SW 2 | 0.92616 | 0.89929 | -0.026873 |  | 0.9 | 1.05 | 0.042755 | P12:345:OKGE:BKRBKR3360:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-299 | RB-NMO1_SW 2 | 0.92616 | 0.89929 | -0.026873 |  | 0.9 | 1.05 | 0.038102 | P12:345:OKGE:BKRBKR3360:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-321 | RB-NMO1_SW 2 | 0.92616 | 0.89929 | -0.026873 |  | 0.9 | 1.05 | 0.060194 | P12:345:OKGE:BKRBKR3360:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-323 | RB-NMO1_SW 2 | 0.92616 | 0.89929 | -0.026873 |  | 0.9 | 1.05 | 0.040838 | P12:345:OKGE:BKRBKR3360:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-334 | RB-NMO1_SW 2 | 0.92616 | 0.89929 | -0.026873 |  | 0.9 | 1.05 | 0.031837 | P12:345:OKGE:BKRBKR3360:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-340 | RB-NMO1_SW 2 | 0.92616 | 0.89929 | -0.026873 |  | 0.9 | 1.05 | 0.062755 | P12:345:OKGE:BKRBKR3360:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-341 | RB-NMO1_SW 2 | 0.92616 | 0.89929 | -0.026873 |  | 0.9 | 1.05 | 0.048238 | P12:345:OKGE:BKRBKR3360:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-343 | RB-NMO1_SW 2 | 0.92616 | 0.89929 | -0.026873 |  | 0.9 | 1.05 | 0.034061 | P12:345:OKGE:BKRBKR3360:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-377 | RB-NMO1_SW 2 | 0.92616 | 0.89929 | -0.026873 |  | 0.9 | 1.05 | 0.034125 | P12:345:OKGE:BKRBKR3360:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-379 | RB-NMO1_SW 2 | 0.92616 | 0.89929 | -0.026873 |  | 0.9 | 1.05 | 0.032061 | P12:345:OKGE:BKRBKR3360:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-003 | RB-NMO1_SW 2 | 0.92616 | 0.89929 | -0.026873 |  | 0.9 | 1.05 | 0.035414 | P12:345:OKGE:BKRBKR3362:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-013 | RB-NMO1_SW 2 | 0.92616 | 0.89929 | -0.026873 |  | 0.9 | 1.05 | 0.067733 | P12:345:OKGE:BKRBKR3362:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-128 | RB-NMO1_SW 2 | 0.92616 | 0.89929 | -0.026873 |  | 0.9 | 1.05 | 0.031874 | P12:345:OKGE:BKRBKR3362:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-252 | RB-NMO1_SW 2 | 0.92616 | 0.89929 | -0.026873 |  | 0.9 | 1.05 | 0.083171 | P12:345:OKGE:BKRBKR3362:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-254 | RB-NMO1_SW 2 | 0.92616 | 0.89929 | -0.026873 |  | 0.9 | 1.05 | 0.097514 | P12:345:OKGE:BKRBKR3362:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-255 | RB-NMO1_SW 2 | 0.92616 | 0.89929 | -0.026873 |  | 0.9 | 1.05 | 0.080034 | P12:345:OKGE:BKRBKR3362:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-286 | RB-NMO1_SW 2 | 0.92616 | 0.89929 | -0.026873 |  | 0.9 | 1.05 | 0.037297 | P12:345:OKGE:BKRBKR3362:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-293 | RB-NMO1_SW 2 | 0.92616 | 0.89929 | -0.026873 |  | 0.9 | 1.05 | 0.043307 | P12:345:OKGE:BKRBKR3362:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-299 | RB-NMO1_SW 2 | 0.92616 | 0.89929 | -0.026873 |  | 0.9 | 1.05 | 0.038594 | P12:345:OKGE:BKRBKR3362:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-321 | RB-NMO1_SW 2 | 0.92616 | 0.89929 | -0.026873 |  | 0.9 | 1.05 | 0.060971 | P12:345:OKGE:BKRBKR3362:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-323 | RB-NMO1_SW 2 | 0.92616 | 0.89929 | -0.026873 |  | 0.9 | 1.05 | 0.041365 | P12:345:OKGE:BKRBKR3362:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-334 | RB-NMO1_SW 2 | 0.92616 | 0.89929 | -0.026873 |  | 0.9 | 1.05 | 0.032247 | P12:345:OKGE:BKRBKR3362:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-340 | RB-NMO1_SW 2 | 0.92616 | 0.89929 | -0.026873 |  | 0.9 | 1.05 | 0.063565 | P12:345:OKGE:BKRBKR3362:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-341 | RB-NMO1_SW 2 | 0.92616 | 0.89929 | -0.026873 |  | 0.9 | 1.05 | 0.048861 | P12:345:OKGE:BKRBKR3362:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-343 | RB-NMO1_SW 2 | 0.92616 | 0.89929 | -0.026873 |  | 0.9 | 1.05 | 0.034501 | P12:345:OKGE:BKRBKR3362:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-377 | RB-NMO1_SW 2 | 0.92616 | 0.89929 | -0.026873 |  | 0.9 | 1.05 | 0.034566 | P12:345:OKGE:BKRBKR3362:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-379 | RB-NMO1_SW 2 | 0.92616 | 0.89929 | -0.026873 |  | 0.9 | 1.05 | 0.032475 | P12:345:OKGE:BKRBKR3362:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-003 | RB-NMO1_SW 2 | 0.92653 | 0.89935 | -0.027181 |  | 0.9 | 1.05 | 0.052763 | P42:345:OKGE:SB_GRIN7312:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-286 | RB-NMO1_SW 2 | 0.92653 | 0.89935 | -0.027181 |  | 0.9 | 1.05 | 0.056996 | P42:345:OKGE:SB_GRIN7312:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-293 | RB-NMO1_SW 2 | 0.92653 | 0.89935 | -0.027181 |  | 0.9 | 1.05 | 0.17539 | P42:345:OKGE:SB_GRIN7312:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-299 | RB-NMO1_SW 2 | 0.92653 | 0.89935 | -0.027181 |  | 0.9 | 1.05 | 0.10985 | P42:345:OKGE:SB_GRIN7312:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-323 | RB-NMO1_SW 2 | 0.92653 | 0.89935 | -0.027181 |  | 0.9 | 1.05 | 0.041529 | P42:345:OKGE:SB_GRIN7312:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-341 | RB-NMO1_SW 2 | 0.92653 | 0.89935 | -0.027181 |  | 0.9 | 1.05 | 0.053987 | P42:345:OKGE:SB_GRIN7312:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-343 | RB-NMO1_SW 2 | 0.92653 | 0.89935 | -0.027181 |  | 0.9 | 1.05 | 0.043045 | P42:345:OKGE:SB_GRIN7312:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-377 | RB-NMO1_SW 2 | 0.92653 | 0.89935 | -0.027181 |  | 0.9 | 1.05 | 0.043062 | P42:345:OKGE:SB_GRIN7312:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-379 | RB-NMO1_SW 2 | 0.92653 | 0.89935 | -0.027181 |  | 0.9 | 1.05 | 0.043596 | P42:345:OKGE:SB_GRIN7312:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-001 | RB-NMO1_SW 2 | 0.92587 | 0.89931 | -0.026565 |  | 0.9 | 1.05 | 0.032839 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-020 | RB-NMO1_SW 2 | 0.92587 | 0.89931 | -0.026565 |  | 0.9 | 1.05 | 0.038314 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-017 | RB-NMO1_SW 2 | 0.92587 | 0.89931 | -0.026565 |  | 0.9 | 1.05 | 0.044423 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-018 | RB-NMO1_SW 2 | 0.92587 | 0.89931 | -0.026565 |  | 0.9 | 1.05 | 0.044795 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-019 | RB-NMO1_SW 2 | 0.92587 | 0.89931 | -0.026565 |  | 0.9 | 1.05 | 0.044795 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-020 | RB-NMO1_SW 2 | 0.92587 | 0.89931 | -0.026565 |  | 0.9 | 1.05 | 0.044423 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-021 | RB-NMO1_SW 2 | 0.92587 | 0.89931 | -0.026565 |  | 0.9 | 1.05 | 0.044423 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-022 | RB-NMO1_SW 2 | 0.92587 | 0.89931 | -0.026565 |  | 0.9 | 1.05 | 0.044795 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-023 | RB-NMO1_SW 2 | 0.92587 | 0.89931 | -0.026565 |  | 0.9 | 1.05 | 0.044795 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-081 | RB-NMO1_SW 2 | 0.92587 | 0.89931 | -0.026565 |  | 0.9 | 1.05 | 0.040334 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-082 | RB-NMO1_SW 2 | 0.92587 | 0.89931 | -0.026565 |  | 0.9 | 1.05 | 0.040334 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-128 | RB-NMO1_SW 2 | 0.92587 | 0.89931 | -0.026565 |  | 0.9 | 1.05 | 0.038612 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-211 | RB-NMO1_SW 2 | 0.92587 | 0.89931 | -0.026565 |  | 0.9 | 1.05 | 0.03861 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-212 | RB-NMO1_SW 2 | 0.92587 | 0.89931 | -0.026565 |  | 0.9 | 1.05 | 0.03861 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-213 | RB-NMO1_SW 2 | 0.92587 | 0.89931 | -0.026565 |  | 0.9 | 1.05 | 0.03861 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-001 | RB-NMO1_SW 2 | 0.92562 | 0.89933 | -0.026287 |  | 0.9 | 1.05 | 0.032839 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-020 | RB-NMO1_SW 2 | 0.92562 | 0.89933 | -0.026287 |  | 0.9 | 1.05 | 0.038314 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-017 | RB-NMO1_SW 2 | 0.92562 | 0.89933 | -0.026287 |  | 0.9 | 1.05 | 0.044423 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-018 | RB-NMO1_SW 2 | 0.92562 | 0.89933 | -0.026287 |  | 0.9 | 1.05 | 0.044795 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-019 | RB-NMO1_SW 2 | 0.92562 | 0.89933 | -0.026287 |  | 0.9 | 1.05 | 0.044795 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-020 | RB-NMO1_SW 2 | 0.92562 | 0.89933 | -0.026287 |  | 0.9 | 1.05 | 0.044423 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-021 | RB-NMO1_SW 2 | 0.92562 | 0.89933 | -0.026287 |  | 0.9 | 1.05 | 0.044423 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-022 | RB-NMO1_SW 2 | 0.92562 | 0.89933 | -0.026287 |  | 0.9 | 1.05 | 0.044795 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-023 | RB-NMO1_SW 2 | 0.92562 | 0.89933 | -0.026287 |  | 0.9 | 1.05 | 0.044795 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-081 | RB-NMO1_SW 2 | 0.92562 | 0.89933 | -0.026287 |  | 0.9 | 1.05 | 0.040334 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-082 | RB-NMO1_SW 2 | 0.92562 | 0.89933 | -0.026287 |  | 0.9 | 1.05 | 0.040334 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-211 | RB-NMO1_SW 2 | 0.92562 | 0.89933 | -0.026287 |  | 0.9 | 1.05 | 0.03861 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-212 | RB-NMO1_SW 2 | 0.92562 | 0.89933 | -0.026287 |  | 0.9 | 1.05 | 0.03861 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-213 | RB-NMO1_SW 2 | 0.92562 | 0.89933 | -0.026287 |  | 0.9 | 1.05 | 0.03861 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-003 | RB-TEXLINE 2 | 0.92616 | 0.89929 | -0.026873 |  | 0.9 | 1.05 | 0.034963 | P12:345:OKGE:BKRBKR3360:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-013 | RB-TEXLINE 2 | 0.92616 | 0.89929 | -0.026873 |  | 0.9 | 1.05 | 0.06687 | P12:345:OKGE:BKRBKR3360:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-128 | RB-TEXLINE 2 | 0.92616 | 0.89929 | -0.026873 |  | 0.9 | 1.05 | 0.031468 | P12:345:OKGE:BKRBKR3360:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-252 | RB-TEXLINE 2 | 0.92616 | 0.89929 | -0.026873 |  | 0.9 | 1.05 | 0.082111 | P12:345:OKGE:BKRBKR3360:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-254 | RB-TEXLINE 2 | 0.92616 | 0.89929 | -0.026873 |  | 0.9 | 1.05 | 0.096271 | P12:345:OKGE:BKRBKR3360:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-255 | RB-TEXLINE 2 | 0.92616 | 0.89929 | -0.026873 |  | 0.9 | 1.05 | 0.079014 | P12:345:OKGE:BKRBKR3360:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-286 | RB-TEXLINE 2 | 0.92616 | 0.89929 | -0.026873 |  | 0.9 | 1.05 | 0.036822 | P12:345:OKGE:BKRBKR3360:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-293 | RB-TEXLINE 2 | 0.92616 | 0.89929 | -0.026873 |  | 0.9 | 1.05 | 0.042755 | P12:345:OKGE:BKRBKR3360:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-299 | RB-TEXLINE 2 | 0.92616 | 0.89929 | -0.026873 |  | 0.9 | 1.05 | 0.038102 | P12:345:OKGE:BKRBKR3360:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-321 | RB-TEXLINE 2 | 0.92616 | 0.89929 | -0.026873 |  | 0.9 | 1.05 | 0.060194 | P12:345:OKGE:BKRBKR3360:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-323 | RB-TEXLINE 2 | 0.92616 | 0.89929 | -0.026873 |  | 0.9 | 1.05 | 0.040838 | P12:345:OKGE:BKRBKR3360:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-334 | RB-TEXLINE 2 | 0.92616 | 0.89929 | -0.026873 |  | 0.9 | 1.05 | 0.031837 | P12:345:OKGE:BKRBKR3360:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-340 | RB-TEXLINE 2 | 0.92616 | 0.89929 | -0.026873 |  | 0.9 | 1.05 | 0.062755 | P12:345:OKGE:BKRBKR3360:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-341 | RB-TEXLINE 2 | 0.92616 | 0.89929 | -0.026873 |  | 0.9 | 1.05 | 0.048238 | P12:345:OKGE:BKRBKR3360:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-343 | RB-TEXLINE 2 | 0.92616 | 0.89929 | -0.026873 |  | 0.9 | 1.05 | 0.034061 | P12:345:OKGE:BKRBKR3360:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-377 | RB-TEXLINE 2 | 0.92616 | 0.89929 | -0.026873 |  | 0.9 | 1.05 | 0.034125 | P12:345:OKGE:BKRBKR3360:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-379 | RB-TEXLINE 2 | 0.92616 | 0.89929 | -0.026873 |  | 0.9 | 1.05 | 0.032061 | P12:345:OKGE:BKRBKR3360:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-003 | RB-TEXLINE 2 | 0.92616 | 0.89929 | -0.026873 |  | 0.9 | 1.05 | 0.035414 | P12:345:OKGE:BKRBKR3362:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-013 | RB-TEXLINE 2 | 0.92616 | 0.89929 | -0.026873 |  | 0.9 | 1.05 | 0.067733 | P12:345:OKGE:BKRBKR3362:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-128 | RB-TEXLINE 2 | 0.92616 | 0.89929 | -0.026873 |  | 0.9 | 1.05 | 0.031874 | P12:345:OKGE:BKRBKR3362:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-252 | RB-TEXLINE 2 | 0.92616 | 0.89929 | -0.026873 |  | 0.9 | 1.05 | 0.083171 | P12:345:OKGE:BKRBKR3362:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-254 | RB-TEXLINE 2 | 0.92616 | 0.89929 | -0.026873 |  | 0.9 | 1.05 | 0.097514 | P12:345:OKGE:BKRBKR3362:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-255 | RB-TEXLINE 2 | 0.92616 | 0.89929 | -0.026873 |  | 0.9 | 1.05 | 0.080034 | P12:345:OKGE:BKRBKR3362:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-286 | RB-TEXLINE 2 | 0.92616 | 0.89929 | -0.026873 |  | 0.9 | 1.05 | 0.037297 | P12:345:OKGE:BKRBKR3362:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-293 | RB-TEXLINE 2 | 0.92616 | 0.89929 | -0.026873 |  | 0.9 | 1.05 | 0.043307 | P12:345:OKGE:BKRBKR3362:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-299 | RB-TEXLINE 2 | 0.92616 | 0.89929 | -0.026873 |  | 0.9 | 1.05 | 0.038594 | P12:345:OKGE:BKRBKR3362:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-321 | RB-TEXLINE 2 | 0.92616 | 0.89929 | -0.026873 |  | 0.9 | 1.05 | 0.060971 | P12:345:OKGE:BKRBKR3362:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-323 | RB-TEXLINE 2 | 0.92616 | 0.89929 | -0.026873 |  | 0.9 | 1.05 | 0.041365 | P12:345:OKGE:BKRBKR3362:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-334 | RB-TEXLINE 2 | 0.92616 | 0.89929 | -0.026873 |  | 0.9 | 1.05 | 0.032247 | P12:345:OKGE:BKRBKR3362:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-340 | RB-TEXLINE 2 | 0.92616 | 0.89929 | -0.026873 |  | 0.9 | 1.05 | 0.063565 | P12:345:OKGE:BKRBKR3362:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-341 | RB-TEXLINE 2 | 0.92616 | 0.89929 | -0.026873 |  | 0.9 | 1.05 | 0.048861 | P12:345:OKGE:BKRBKR3362:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-343 | RB-TEXLINE 2 | 0.92616 | 0.89929 | -0.026873 |  | 0.9 | 1.05 | 0.034501 | P12:345:OKGE:BKRBKR3362:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-377 | RB-TEXLINE 2 | 0.92616 | 0.89929 | -0.026873 |  | 0.9 | 1.05 | 0.034566 | P12:345:OKGE:BKRBKR3362:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-379 | RB-TEXLINE 2 | 0.92616 | 0.89929 | -0.026873 |  | 0.9 | 1.05 | 0.032475 | P12:345:OKGE:BKRBKR3362:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-003 | RB-TEXLINE 2 | 0.92653 | 0.89935 | -0.027181 |  | 0.9 | 1.05 | 0.052763 | P42:345:OKGE:SB_GRIN7312:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-286 | RB-TEXLINE 2 | 0.92653 | 0.89935 | -0.027181 |  | 0.9 | 1.05 | 0.056996 | P42:345:OKGE:SB_GRIN7312:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-293 | RB-TEXLINE 2 | 0.92653 | 0.89935 | -0.027181 |  | 0.9 | 1.05 | 0.17539 | P42:345:OKGE:SB_GRIN7312:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-299 | RB-TEXLINE 2 | 0.92653 | 0.89935 | -0.027181 |  | 0.9 | 1.05 | 0.10985 | P42:345:OKGE:SB_GRIN7312:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-323 | RB-TEXLINE 2 | 0.92653 | 0.89935 | -0.027181 |  | 0.9 | 1.05 | 0.041529 | P42:345:OKGE:SB_GRIN7312:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-341 | RB-TEXLINE 2 | 0.92653 | 0.89935 | -0.027181 |  | 0.9 | 1.05 | 0.053987 | P42:345:OKGE:SB_GRIN7312:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-343 | RB-TEXLINE 2 | 0.92653 | 0.89935 | -0.027181 |  | 0.9 | 1.05 | 0.043045 | P42:345:OKGE:SB_GRIN7312:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-377 | RB-TEXLINE 2 | 0.92653 | 0.89935 | -0.027181 |  | 0.9 | 1.05 | 0.043062 | P42:345:OKGE:SB_GRIN7312:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-379 | RB-TEXLINE 2 | 0.92653 | 0.89935 | -0.027181 |  | 0.9 | 1.05 | 0.043596 | P42:345:OKGE:SB_GRIN7312:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-001 | RB-TEXLINE 2 | 0.92587 | 0.89931 | -0.026565 |  | 0.9 | 1.05 | 0.032839 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-020 | RB-TEXLINE 2 | 0.92587 | 0.89931 | -0.026565 |  | 0.9 | 1.05 | 0.038314 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-017 | RB-TEXLINE 2 | 0.92587 | 0.89931 | -0.026565 |  | 0.9 | 1.05 | 0.044423 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-018 | RB-TEXLINE 2 | 0.92587 | 0.89931 | -0.026565 |  | 0.9 | 1.05 | 0.044795 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-019 | RB-TEXLINE 2 | 0.92587 | 0.89931 | -0.026565 |  | 0.9 | 1.05 | 0.044795 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-020 | RB-TEXLINE 2 | 0.92587 | 0.89931 | -0.026565 |  | 0.9 | 1.05 | 0.044423 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-021 | RB-TEXLINE 2 | 0.92587 | 0.89931 | -0.026565 |  | 0.9 | 1.05 | 0.044423 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-022 | RB-TEXLINE 2 | 0.92587 | 0.89931 | -0.026565 |  | 0.9 | 1.05 | 0.044795 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-023 | RB-TEXLINE 2 | 0.92587 | 0.89931 | -0.026565 |  | 0.9 | 1.05 | 0.044795 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-081 | RB-TEXLINE 2 | 0.92587 | 0.89931 | -0.026565 |  | 0.9 | 1.05 | 0.040334 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-082 | RB-TEXLINE 2 | 0.92587 | 0.89931 | -0.026565 |  | 0.9 | 1.05 | 0.040334 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-128 | RB-TEXLINE 2 | 0.92587 | 0.89931 | -0.026565 |  | 0.9 | 1.05 | 0.038612 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-211 | RB-TEXLINE 2 | 0.92587 | 0.89931 | -0.026565 |  | 0.9 | 1.05 | 0.03861 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-212 | RB-TEXLINE 2 | 0.92587 | 0.89931 | -0.026565 |  | 0.9 | 1.05 | 0.03861 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-213 | RB-TEXLINE 2 | 0.92587 | 0.89931 | -0.026565 |  | 0.9 | 1.05 | 0.03861 | P42:345:SPS:FINNEY_OR70:::EHV: | None
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-001 | RB-TEXLINE 2 | 0.92562 | 0.89933 | -0.026287 |  | 0.9 | 1.05 | 0.032839 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-020 | RB-TEXLINE 2 | 0.92562 | 0.89933 | -0.026287 |  | 0.9 | 1.05 | 0.038314 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-017 | RB-TEXLINE 2 | 0.92562 | 0.89933 | -0.026287 |  | 0.9 | 1.05 | 0.044423 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-018 | RB-TEXLINE 2 | 0.92562 | 0.89933 | -0.026287 |  | 0.9 | 1.05 | 0.044795 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-019 | RB-TEXLINE 2 | 0.92562 | 0.89933 | -0.026287 |  | 0.9 | 1.05 | 0.044795 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-020 | RB-TEXLINE 2 | 0.92562 | 0.89933 | -0.026287 |  | 0.9 | 1.05 | 0.044423 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-021 | RB-TEXLINE 2 | 0.92562 | 0.89933 | -0.026287 |  | 0.9 | 1.05 | 0.044423 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-022 | RB-TEXLINE 2 | 0.92562 | 0.89933 | -0.026287 |  | 0.9 | 1.05 | 0.044795 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-023 | RB-TEXLINE 2 | 0.92562 | 0.89933 | -0.026287 |  | 0.9 | 1.05 | 0.044795 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-081 | RB-TEXLINE 2 | 0.92562 | 0.89933 | -0.026287 |  | 0.9 | 1.05 | 0.040334 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-082 | RB-TEXLINE 2 | 0.92562 | 0.89933 | -0.026287 |  | 0.9 | 1.05 | 0.040334 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-211 | RB-TEXLINE 2 | 0.92562 | 0.89933 | -0.026287 |  | 0.9 | 1.05 | 0.03861 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-212 | RB-TEXLINE 2 | 0.92562 | 0.89933 | -0.026287 |  | 0.9 | 1.05 | 0.03861 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 00ALL | 2 | 29SP | V | GEN-2024-213 | RB-TEXLINE 2 | 0.92562 | 0.89933 | -0.026287 |  | 0.9 | 1.05 | 0.03861 | Single 523853 FINNEY7 345 772280 G23-015-TAP 345 1 | None
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-007 | SWAVCAP5 | 0.98768 | 0.90657 | -0.081106 |  | 0.93 | 1.05 | 0.058785 | Single 543059 MALTABN5 161 543064 NORTON5 161 1 | Add 7 MVAR switched shunt at SWAVRLY5 161 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-008 | SWAVCAP5 | 0.98768 | 0.90657 | -0.081106 |  | 0.93 | 1.05 | 0.058785 | Single 543059 MALTABN5 161 543064 NORTON5 161 1 | Add 7 MVAR switched shunt at SWAVRLY5 161 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-007 | SWAVRLY5 | 0.98746 | 0.90638 | -0.081088 |  | 0.93 | 1.05 | 0.058785 | Single 543059 MALTABN5 161 543064 NORTON5 161 1 | Add 7 MVAR switched shunt at SWAVRLY5 161 kV
Voltage | 00ALL | 2 | 29SP | V | ASGI-2024-008 | SWAVRLY5 | 0.98746 | 0.90638 | -0.081088 |  | 0.93 | 1.05 | 0.058785 | Single 543059 MALTABN5 161 543064 NORTON5 161 1 | Add 7 MVAR switched shunt at SWAVRLY5 161 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-015 | DEAFSMITH 6 | 0.9472 | 0.84862 | -0.098582 |  | 0.9 | 1.05 | 0.036482 | P12:230:SPS:K11_K21::1_BUSHL_DFSMTH_PLANTX:HV: | Add 10 MVAR switched shunt at DEAFSMITH 6 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-099 | DEAFSMITH 6 | 0.9472 | 0.84862 | -0.098582 |  | 0.9 | 1.05 | 0.041788 | P12:230:SPS:K11_K21::1_BUSHL_DFSMTH_PLANTX:HV: | Add 10 MVAR switched shunt at DEAFSMITH 6 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-109 | DEAFSMITH 6 | 0.9472 | 0.84862 | -0.098582 |  | 0.9 | 1.05 | 0.039928 | P12:230:SPS:K11_K21::1_BUSHL_DFSMTH_PLANTX:HV: | Add 10 MVAR switched shunt at DEAFSMITH 6 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-159 | DEAFSMITH 6 | 0.9472 | 0.84862 | -0.098582 |  | 0.9 | 1.05 | 0.077327 | P12:230:SPS:K11_K21::1_BUSHL_DFSMTH_PLANTX:HV: | Add 10 MVAR switched shunt at DEAFSMITH 6 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-311 | DEAFSMITH 6 | 0.9472 | 0.84862 | -0.098582 |  | 0.9 | 1.05 | 0.031776 | P12:230:SPS:K11_K21::1_BUSHL_DFSMTH_PLANTX:HV: | Add 10 MVAR switched shunt at DEAFSMITH 6 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-374 | DH_CS_EA-TS4 | 0.87819 | 0.7872 | -0.09099 |  | 0.9 | 1.05 | 0.16564 | P12:230.0:UMZ:# N-1 #:: LINE STEGALL 4-STEGALL_-MB4-1 :HV: | Add 0.04 MVAR switched shunt at VICTRYH4 230 kV; Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-374 | DH_CS_EA-TS4 | 0.88256 | 0.78817 | -0.094384 |  | 0.9 | 1.05 | 0.16564 | P13:345-230.0:UMZ:# N-1 #:: 3WND STEGALL_-MB3-STEGALL_-MB4-STEGALL_-MB9-1 SGQ KV3A:EHV: | Add 78 MVAR switched shunt at DH_CS_EA-TS4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-374 | DRYCREEK-BE4 | 0.99868 | 0.88709 | -0.11159 |  | 0.9 | 1.05 | 0.067023 | P12:230.0:UMZ:# N-1 #:: LINE NUNDRWD4-PHILIP_T 4-1 :HV: | Add 60 MVAR switched shunt at NUNDRWD-LNX3 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-374 | DRYCREEK-BE4 | 1.0066 | 0.88928 | -0.11731 |  | 0.9 | 1.05 | 0.077573 | P12:230:UMZ:# 20065 #:: PROPER N-1 FOR TAP PHILIP_T-BE4:HV: | Add 60 MVAR switched shunt at NUNDRWD-LNX3 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-374 | DRYCREEK-BE7 | 1.0005 | 0.89092 | -0.10957 |  | 0.9 | 1.05 | 0.067023 | P12:230.0:UMZ:# N-1 #:: LINE NUNDRWD4-PHILIP_T 4-1 :HV: | Add 60 MVAR switched shunt at NUNDRWD-LNX3 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-374 | DRYCREEK-BE7 | 1.0096 | 0.89319 | -0.11646 |  | 0.9 | 1.05 | 0.077573 | P12:230:UMZ:# 20065 #:: PROPER N-1 FOR TAP PHILIP_T-BE4:HV: | Add 60 MVAR switched shunt at NUNDRWD-LNX3 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-374 | ELKCRK 7 | 1.0024 | 0.89793 | -0.10449 |  | 0.9 | 1.05 | 0.067023 | P12:230.0:UMZ:# N-1 #:: LINE NUNDRWD4-PHILIP_T 4-1 :HV: | Add 60 MVAR switched shunt at NUNDRWD-LNX3 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-374 | ELSWRTH7 | 0.99335 | 0.88579 | -0.10756 |  | 0.9 | 1.05 | 0.067023 | P12:230.0:UMZ:# N-1 #:: LINE NUNDRWD4-PHILIP_T 4-1 :HV: | Add 60 MVAR switched shunt at NUNDRWD-LNX3 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-374 | ELSWRTH7 | 1.0036 | 0.88812 | -0.1155 |  | 0.9 | 1.05 | 0.077573 | P12:230:UMZ:# 20065 #:: PROPER N-1 FOR TAP PHILIP_T-BE4:HV: | Add 60 MVAR switched shunt at NUNDRWD-LNX3 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-374 | FAITH 7 | 1.0204 | 1.0511 | 0.030617 |  | 0.9 | 1.05 | 0.15187 | P12:230.0:UMZ:# N-1 #:: LINE WAYSIDE 4-NUNDRWD4-1 :HV: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-374 | FREEDOM7 | 0.99309 | 0.88597 | -0.10712 |  | 0.9 | 1.05 | 0.067023 | P12:230.0:UMZ:# N-1 #:: LINE NUNDRWD4-PHILIP_T 4-1 :HV: | Add 60 MVAR switched shunt at NUNDRWD-LNX3 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-374 | FREEDOM7 | 1.0035 | 0.8883 | -0.11516 |  | 0.9 | 1.05 | 0.077573 | P12:230:UMZ:# 20065 #:: PROPER N-1 FOR TAP PHILIP_T-BE4:HV: | Add 60 MVAR switched shunt at NUNDRWD-LNX3 230 kV
Voltage | 00NR | 2 | 29SP | V | ASGI-2024-006 | G17-140-BUS | 1.1225 | 1.1815 | 0.059004 |  | 0.92 | 1.05 | 0.034129 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 29SP | V | ASGI-2024-023 | G17-140-BUS | 1.1225 | 1.1815 | 0.059004 |  | 0.92 | 1.05 | 0.084968 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-013 | G17-140-BUS | 1.1225 | 1.1815 | 0.059004 |  | 0.92 | 1.05 | 0.048198 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-025 | G17-140-BUS | 1.1225 | 1.1815 | 0.059004 |  | 0.92 | 1.05 | 0.086306 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-068 | G17-140-BUS | 1.1225 | 1.1815 | 0.059004 |  | 0.92 | 1.05 | 0.085665 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-071 | G17-140-BUS | 1.1225 | 1.1815 | 0.059004 |  | 0.92 | 1.05 | 0.083764 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-113 | G17-140-BUS | 1.1225 | 1.1815 | 0.059004 |  | 0.92 | 1.05 | 0.21329 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-120 | G17-140-BUS | 1.1225 | 1.1815 | 0.059004 |  | 0.92 | 1.05 | 0.030112 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-122 | G17-140-BUS | 1.1225 | 1.1815 | 0.059004 |  | 0.92 | 1.05 | 0.081073 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-128 | G17-140-BUS | 1.1225 | 1.1815 | 0.059004 |  | 0.92 | 1.05 | 0.042038 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-177 | G17-140-BUS | 1.1225 | 1.1815 | 0.059004 |  | 0.92 | 1.05 | 0.080413 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-178 | G17-140-BUS | 1.1225 | 1.1815 | 0.059004 |  | 0.92 | 1.05 | 0.081628 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-204 | G17-140-BUS | 1.1225 | 1.1815 | 0.059004 |  | 0.92 | 1.05 | 0.077302 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-219 | G17-140-BUS | 1.1225 | 1.1815 | 0.059004 |  | 0.92 | 1.05 | 0.071545 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-220 | G17-140-BUS | 1.1225 | 1.1815 | 0.059004 |  | 0.92 | 1.05 | 0.083591 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-232 | G17-140-BUS | 1.1225 | 1.1815 | 0.059004 |  | 0.92 | 1.05 | 0.078881 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-236 | G17-140-BUS | 1.1225 | 1.1815 | 0.059004 |  | 0.92 | 1.05 | 0.13445 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-239 | G17-140-BUS | 1.1225 | 1.1815 | 0.059004 |  | 0.92 | 1.05 | 0.031542 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-241 | G17-140-BUS | 1.1225 | 1.1815 | 0.059004 |  | 0.92 | 1.05 | 0.086306 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-252 | G17-140-BUS | 1.1225 | 1.1815 | 0.059004 |  | 0.92 | 1.05 | 0.031542 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-268 | G17-140-BUS | 1.1225 | 1.1815 | 0.059004 |  | 0.92 | 1.05 | 0.25303 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-296 | G17-140-BUS | 1.1225 | 1.1815 | 0.059004 |  | 0.92 | 1.05 | 0.17362 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-297 | G17-140-BUS | 1.1225 | 1.1815 | 0.059004 |  | 0.92 | 1.05 | 0.17362 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-317 | G17-140-BUS | 1.1225 | 1.1815 | 0.059004 |  | 0.92 | 1.05 | 0.036051 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-321 | G17-140-BUS | 1.1225 | 1.1815 | 0.059004 |  | 0.92 | 1.05 | 0.076847 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-333 | G17-140-BUS | 1.1225 | 1.1815 | 0.059004 |  | 0.92 | 1.05 | 0.033221 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-338 | G17-140-BUS | 1.1225 | 1.1815 | 0.059004 |  | 0.92 | 1.05 | 0.089442 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-341 | G17-140-BUS | 1.1225 | 1.1815 | 0.059004 |  | 0.92 | 1.05 | 0.10952 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-343 | G17-140-BUS | 1.1225 | 1.1815 | 0.059004 |  | 0.92 | 1.05 | 0.081607 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-360 | G17-140-BUS | 1.1225 | 1.1815 | 0.059004 |  | 0.92 | 1.05 | 0.065842 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-362 | G17-140-BUS | 1.1225 | 1.1815 | 0.059004 |  | 0.92 | 1.05 | 0.039382 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-373 | G17-140-BUS | 1.1225 | 1.1815 | 0.059004 |  | 0.92 | 1.05 | 0.083562 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-376 | G17-140-BUS | 1.1225 | 1.1815 | 0.059004 |  | 0.92 | 1.05 | 0.077231 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-377 | G17-140-BUS | 1.1225 | 1.1815 | 0.059004 |  | 0.92 | 1.05 | 0.081694 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-379 | G17-140-BUS | 1.1225 | 1.1815 | 0.059004 |  | 0.92 | 1.05 | 0.080423 | P12:345:AEPW-OKGE:CLARKSV7:MUSKOGE7::: | None
Voltage | 00NR | 2 | 29SP | V | ASGI-2024-006 | G17-140-BUS | 1.1235 | 1.1829 | 0.059421 |  | 0.92 | 1.05 | 0.034129 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 29SP | V | ASGI-2024-023 | G17-140-BUS | 1.1235 | 1.1829 | 0.059421 |  | 0.92 | 1.05 | 0.084968 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-013 | G17-140-BUS | 1.1235 | 1.1829 | 0.059421 |  | 0.92 | 1.05 | 0.048198 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-025 | G17-140-BUS | 1.1235 | 1.1829 | 0.059421 |  | 0.92 | 1.05 | 0.086306 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-068 | G17-140-BUS | 1.1235 | 1.1829 | 0.059421 |  | 0.92 | 1.05 | 0.085665 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-071 | G17-140-BUS | 1.1235 | 1.1829 | 0.059421 |  | 0.92 | 1.05 | 0.083764 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-113 | G17-140-BUS | 1.1235 | 1.1829 | 0.059421 |  | 0.92 | 1.05 | 0.21329 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-120 | G17-140-BUS | 1.1235 | 1.1829 | 0.059421 |  | 0.92 | 1.05 | 0.030112 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-122 | G17-140-BUS | 1.1235 | 1.1829 | 0.059421 |  | 0.92 | 1.05 | 0.081073 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-128 | G17-140-BUS | 1.1235 | 1.1829 | 0.059421 |  | 0.92 | 1.05 | 0.042038 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-177 | G17-140-BUS | 1.1235 | 1.1829 | 0.059421 |  | 0.92 | 1.05 | 0.080413 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-178 | G17-140-BUS | 1.1235 | 1.1829 | 0.059421 |  | 0.92 | 1.05 | 0.081628 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-204 | G17-140-BUS | 1.1235 | 1.1829 | 0.059421 |  | 0.92 | 1.05 | 0.077302 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-219 | G17-140-BUS | 1.1235 | 1.1829 | 0.059421 |  | 0.92 | 1.05 | 0.071545 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-220 | G17-140-BUS | 1.1235 | 1.1829 | 0.059421 |  | 0.92 | 1.05 | 0.083591 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-232 | G17-140-BUS | 1.1235 | 1.1829 | 0.059421 |  | 0.92 | 1.05 | 0.078881 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-236 | G17-140-BUS | 1.1235 | 1.1829 | 0.059421 |  | 0.92 | 1.05 | 0.15521 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-239 | G17-140-BUS | 1.1235 | 1.1829 | 0.059421 |  | 0.92 | 1.05 | 0.031542 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-241 | G17-140-BUS | 1.1235 | 1.1829 | 0.059421 |  | 0.92 | 1.05 | 0.086306 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-252 | G17-140-BUS | 1.1235 | 1.1829 | 0.059421 |  | 0.92 | 1.05 | 0.031542 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-268 | G17-140-BUS | 1.1235 | 1.1829 | 0.059421 |  | 0.92 | 1.05 | 0.33466 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-296 | G17-140-BUS | 1.1235 | 1.1829 | 0.059421 |  | 0.92 | 1.05 | 0.20639 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-297 | G17-140-BUS | 1.1235 | 1.1829 | 0.059421 |  | 0.92 | 1.05 | 0.20639 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-317 | G17-140-BUS | 1.1235 | 1.1829 | 0.059421 |  | 0.92 | 1.05 | 0.036051 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-321 | G17-140-BUS | 1.1235 | 1.1829 | 0.059421 |  | 0.92 | 1.05 | 0.076847 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-333 | G17-140-BUS | 1.1235 | 1.1829 | 0.059421 |  | 0.92 | 1.05 | 0.033221 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-338 | G17-140-BUS | 1.1235 | 1.1829 | 0.059421 |  | 0.92 | 1.05 | 0.089723 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-341 | G17-140-BUS | 1.1235 | 1.1829 | 0.059421 |  | 0.92 | 1.05 | 0.11549 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-343 | G17-140-BUS | 1.1235 | 1.1829 | 0.059421 |  | 0.92 | 1.05 | 0.081607 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-360 | G17-140-BUS | 1.1235 | 1.1829 | 0.059421 |  | 0.92 | 1.05 | 0.065842 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-362 | G17-140-BUS | 1.1235 | 1.1829 | 0.059421 |  | 0.92 | 1.05 | 0.039382 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-373 | G17-140-BUS | 1.1235 | 1.1829 | 0.059421 |  | 0.92 | 1.05 | 0.083562 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-376 | G17-140-BUS | 1.1235 | 1.1829 | 0.059421 |  | 0.92 | 1.05 | 0.077231 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-377 | G17-140-BUS | 1.1235 | 1.1829 | 0.059421 |  | 0.92 | 1.05 | 0.081694 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-379 | G17-140-BUS | 1.1235 | 1.1829 | 0.059421 |  | 0.92 | 1.05 | 0.080423 | P22:345:EES:MUSKOGE7!:::EHV: | None
Voltage | 00NR | 2 | 29SP | V | ASGI-2024-006 | G17-140-BUS | 1.1257 | 1.1791 | 0.053417 |  | 0.92 | 1.05 | 0.036483 | P52:345:AEPW:NR4PITTSB-7:::: | None
Voltage | 00NR | 2 | 29SP | V | ASGI-2024-023 | G17-140-BUS | 1.1257 | 1.1791 | 0.053417 |  | 0.92 | 1.05 | 0.1803 | P52:345:AEPW:NR4PITTSB-7:::: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-013 | G17-140-BUS | 1.1257 | 1.1791 | 0.053417 |  | 0.92 | 1.05 | 0.031611 | P52:345:AEPW:NR4PITTSB-7:::: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-025 | G17-140-BUS | 1.1257 | 1.1791 | 0.053417 |  | 0.92 | 1.05 | 0.23042 | P52:345:AEPW:NR4PITTSB-7:::: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-041 | G17-140-BUS | 1.1257 | 1.1791 | 0.053417 |  | 0.92 | 1.05 | 0.032541 | P52:345:AEPW:NR4PITTSB-7:::: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-042 | G17-140-BUS | 1.1257 | 1.1791 | 0.053417 |  | 0.92 | 1.05 | 0.032541 | P52:345:AEPW:NR4PITTSB-7:::: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-068 | G17-140-BUS | 1.1257 | 1.1791 | 0.053417 |  | 0.92 | 1.05 | 0.21513 | P52:345:AEPW:NR4PITTSB-7:::: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-071 | G17-140-BUS | 1.1257 | 1.1791 | 0.053417 |  | 0.92 | 1.05 | 0.16499 | P52:345:AEPW:NR4PITTSB-7:::: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-113 | G17-140-BUS | 1.1257 | 1.1791 | 0.053417 |  | 0.92 | 1.05 | 0.031555 | P52:345:AEPW:NR4PITTSB-7:::: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-122 | G17-140-BUS | 1.1257 | 1.1791 | 0.053417 |  | 0.92 | 1.05 | 0.10329 | P52:345:AEPW:NR4PITTSB-7:::: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-128 | G17-140-BUS | 1.1257 | 1.1791 | 0.053417 |  | 0.92 | 1.05 | 0.053079 | P52:345:AEPW:NR4PITTSB-7:::: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-177 | G17-140-BUS | 1.1257 | 1.1791 | 0.053417 |  | 0.92 | 1.05 | 0.087979 | P52:345:AEPW:NR4PITTSB-7:::: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-178 | G17-140-BUS | 1.1257 | 1.1791 | 0.053417 |  | 0.92 | 1.05 | 0.12647 | P52:345:AEPW:NR4PITTSB-7:::: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-204 | G17-140-BUS | 1.1257 | 1.1791 | 0.053417 |  | 0.92 | 1.05 | 0.17833 | P52:345:AEPW:NR4PITTSB-7:::: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-219 | G17-140-BUS | 1.1257 | 1.1791 | 0.053417 |  | 0.92 | 1.05 | 0.12821 | P52:345:AEPW:NR4PITTSB-7:::: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-220 | G17-140-BUS | 1.1257 | 1.1791 | 0.053417 |  | 0.92 | 1.05 | 0.15993 | P52:345:AEPW:NR4PITTSB-7:::: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-232 | G17-140-BUS | 1.1257 | 1.1791 | 0.053417 |  | 0.92 | 1.05 | 0.10158 | P52:345:AEPW:NR4PITTSB-7:::: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-241 | G17-140-BUS | 1.1257 | 1.1791 | 0.053417 |  | 0.92 | 1.05 | 0.23042 | P52:345:AEPW:NR4PITTSB-7:::: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-268 | G17-140-BUS | 1.1257 | 1.1791 | 0.053417 |  | 0.92 | 1.05 | 0.036805 | P52:345:AEPW:NR4PITTSB-7:::: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-296 | G17-140-BUS | 1.1257 | 1.1791 | 0.053417 |  | 0.92 | 1.05 | 0.16178 | P52:345:AEPW:NR4PITTSB-7:::: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-297 | G17-140-BUS | 1.1257 | 1.1791 | 0.053417 |  | 0.92 | 1.05 | 0.16178 | P52:345:AEPW:NR4PITTSB-7:::: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-317 | G17-140-BUS | 1.1257 | 1.1791 | 0.053417 |  | 0.92 | 1.05 | 0.061981 | P52:345:AEPW:NR4PITTSB-7:::: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-321 | G17-140-BUS | 1.1257 | 1.1791 | 0.053417 |  | 0.92 | 1.05 | 0.052181 | P52:345:AEPW:NR4PITTSB-7:::: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-338 | G17-140-BUS | 1.1257 | 1.1791 | 0.053417 |  | 0.92 | 1.05 | 0.47467 | P52:345:AEPW:NR4PITTSB-7:::: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-341 | G17-140-BUS | 1.1257 | 1.1791 | 0.053417 |  | 0.92 | 1.05 | 1 | P52:345:AEPW:NR4PITTSB-7:::: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-343 | G17-140-BUS | 1.1257 | 1.1791 | 0.053417 |  | 0.92 | 1.05 | 0.12833 | P52:345:AEPW:NR4PITTSB-7:::: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-360 | G17-140-BUS | 1.1257 | 1.1791 | 0.053417 |  | 0.92 | 1.05 | 0.039741 | P52:345:AEPW:NR4PITTSB-7:::: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-373 | G17-140-BUS | 1.1257 | 1.1791 | 0.053417 |  | 0.92 | 1.05 | 0.16886 | P52:345:AEPW:NR4PITTSB-7:::: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-376 | G17-140-BUS | 1.1257 | 1.1791 | 0.053417 |  | 0.92 | 1.05 | 0.072844 | P52:345:AEPW:NR4PITTSB-7:::: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-377 | G17-140-BUS | 1.1257 | 1.1791 | 0.053417 |  | 0.92 | 1.05 | 0.12918 | P52:345:AEPW:NR4PITTSB-7:::: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-379 | G17-140-BUS | 1.1257 | 1.1791 | 0.053417 |  | 0.92 | 1.05 | 0.079482 | P52:345:AEPW:NR4PITTSB-7:::: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-341 | G17-140-BUS | 1.1243 | 1.1777 | 0.053398 |  | 0.92 | 1.05 | 1 | Single 510907 PITTSB-7 345 787200 GEN-2024-341 345 1 | None
Voltage | 00NR | 2 | 29SP | V | ASGI-2024-006 | G17-140-BUS | 1.1248 | 1.1783 | 0.053514 |  | 0.92 | 1.05 | 0.036367 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | None
Voltage | 00NR | 2 | 29SP | V | ASGI-2024-023 | G17-140-BUS | 1.1248 | 1.1783 | 0.053514 |  | 0.92 | 1.05 | 0.076584 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-025 | G17-140-BUS | 1.1248 | 1.1783 | 0.053514 |  | 0.92 | 1.05 | 0.10091 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-068 | G17-140-BUS | 1.1248 | 1.1783 | 0.053514 |  | 0.92 | 1.05 | 0.095201 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-071 | G17-140-BUS | 1.1248 | 1.1783 | 0.053514 |  | 0.92 | 1.05 | 0.076932 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-122 | G17-140-BUS | 1.1248 | 1.1783 | 0.053514 |  | 0.92 | 1.05 | 0.053642 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-128 | G17-140-BUS | 1.1248 | 1.1783 | 0.053514 |  | 0.92 | 1.05 | 0.038996 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-177 | G17-140-BUS | 1.1248 | 1.1783 | 0.053514 |  | 0.92 | 1.05 | 0.048593 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-178 | G17-140-BUS | 1.1248 | 1.1783 | 0.053514 |  | 0.92 | 1.05 | 0.06074 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-204 | G17-140-BUS | 1.1248 | 1.1783 | 0.053514 |  | 0.92 | 1.05 | 0.1148 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-219 | G17-140-BUS | 1.1248 | 1.1783 | 0.053514 |  | 0.92 | 1.05 | 0.083538 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-220 | G17-140-BUS | 1.1248 | 1.1783 | 0.053514 |  | 0.92 | 1.05 | 0.075209 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-232 | G17-140-BUS | 1.1248 | 1.1783 | 0.053514 |  | 0.92 | 1.05 | 0.042482 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-241 | G17-140-BUS | 1.1248 | 1.1783 | 0.053514 |  | 0.92 | 1.05 | 0.10091 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-296 | G17-140-BUS | 1.1248 | 1.1783 | 0.053514 |  | 0.92 | 1.05 | 0.55781 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-297 | G17-140-BUS | 1.1248 | 1.1783 | 0.053514 |  | 0.92 | 1.05 | 0.55781 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-317 | G17-140-BUS | 1.1248 | 1.1783 | 0.053514 |  | 0.92 | 1.05 | 0.036575 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-321 | G17-140-BUS | 1.1248 | 1.1783 | 0.053514 |  | 0.92 | 1.05 | 0.04438 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-338 | G17-140-BUS | 1.1248 | 1.1783 | 0.053514 |  | 0.92 | 1.05 | 0.16575 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-341 | G17-140-BUS | 1.1248 | 1.1783 | 0.053514 |  | 0.92 | 1.05 | 0.23745 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-343 | G17-140-BUS | 1.1248 | 1.1783 | 0.053514 |  | 0.92 | 1.05 | 0.060955 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-360 | G17-140-BUS | 1.1248 | 1.1783 | 0.053514 |  | 0.92 | 1.05 | 0.045531 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-373 | G17-140-BUS | 1.1248 | 1.1783 | 0.053514 |  | 0.92 | 1.05 | 0.12409 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-377 | G17-140-BUS | 1.1248 | 1.1783 | 0.053514 |  | 0.92 | 1.05 | 0.061543 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-379 | G17-140-BUS | 1.1248 | 1.1783 | 0.053514 |  | 0.92 | 1.05 | 0.037171 | Single 516210 RAVEN7 345 785850 G24-296-TAP 345 1 | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-374 | GEN-2017-097 | 0.99439 | 0.88964 | -0.10476 |  | 0.9 | 1.05 | 0.067023 | P12:230.0:UMZ:# N-1 #:: LINE NUNDRWD4-PHILIP_T 4-1 :HV: | Add 60 MVAR switched shunt at NUNDRWD-LNX3 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-374 | GEN-2017-097 | 0.99439 | 0.88964 | -0.10476 |  | 0.9 | 1.05 | 0.067023 | P12:230.0:UMZ:# N-1 #:: LINE NUNDRWD4-PHILIP_T 4-1 :HV: | Add 60 MVAR switched shunt at NUNDRWD-LNX3 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-374 | GEN-2017-097 | 1.0052 | 0.89197 | -0.11319 |  | 0.9 | 1.05 | 0.077573 | P12:230:UMZ:# 20065 #:: PROPER N-1 FOR TAP PHILIP_T-BE4:HV: | Add 60 MVAR switched shunt at NUNDRWD-LNX3 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-374 | GEN-2017-097 | 1.0052 | 0.89197 | -0.11319 |  | 0.9 | 1.05 | 0.077573 | P12:230:UMZ:# 20065 #:: PROPER N-1 FOR TAP PHILIP_T-BE4:HV: | Add 60 MVAR switched shunt at NUNDRWD-LNX3 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-168 | HASTING4 | 0.97278 | 0.94645 | -0.026331 |  | 0.95 | 1.05 | 0.050075 | System Intact | Add 14 MVAR switched shunt at HASTING4 230 kV
Voltage | 00NR | 2 | 29SP | V | ASGI-2024-003 | JHNCRSOL | 1.0004 | 1.0662 | 0.0658 |  | 0.9 | 1.05 | 0.049766 | P12:115:SUNC:JOHNSONCORNER-ULYSSESPLANT:::HV: | Add 8 MVAR switched shunt at JHNCRSOL 115 kV
Voltage | 00NR | 2 | 29SP | V | ASGI-2024-003 | JHNCRSOL | 0.99985 | 1.0658 | 0.065985 |  | 0.9 | 1.05 | 0.049766 | MULTIGEN531381 | Add 8 MVAR switched shunt at JHNCRSOL 115 kV
Voltage | 00NR | 2 | 29SP | V | ASGI-2024-003 | JHNCRSOL | 0.99834 | 1.0647 | 0.066408 |  | 0.9 | 1.05 | 0.049708 | Single 531381 JOHNCTY3 115 531424 JOHNCR3 115 1 | Add 8 MVAR switched shunt at JHNCRSOL 115 kV
Voltage | 00NR | 2 | 29SP | V | ASGI-2024-003 | MANTER 3 | 0.99961 | 1.0655 | 0.065896 |  | 0.9 | 1.05 | 0.049766 | P12:115:SUNC:JOHNSONCORNER-ULYSSESPLANT:::HV: | Add 8 MVAR switched shunt at JHNCRSOL 115 kV
Voltage | 00NR | 2 | 29SP | V | ASGI-2024-003 | MANTER 3 | 0.99905 | 1.0651 | 0.066081 |  | 0.9 | 1.05 | 0.049766 | MULTIGEN531381 | Add 8 MVAR switched shunt at JHNCRSOL 115 kV
Voltage | 00NR | 2 | 29SP | V | ASGI-2024-003 | MANTER 3 | 0.99753 | 1.064 | 0.066505 |  | 0.9 | 1.05 | 0.049708 | Single 531381 JOHNCTY3 115 531424 JOHNCR3 115 1 | Add 8 MVAR switched shunt at JHNCRSOL 115 kV
Voltage | 00NR | 2 | 29SP | V | ASGI-2024-003 | MANTERT3 | 0.99985 | 1.0657 | 0.065874 |  | 0.9 | 1.05 | 0.049766 | P12:115:SUNC:JOHNSONCORNER-ULYSSESPLANT:::HV: | Add 8 MVAR switched shunt at JHNCRSOL 115 kV
Voltage | 00NR | 2 | 29SP | V | ASGI-2024-003 | MANTERT3 | 0.99929 | 1.0653 | 0.06606 |  | 0.9 | 1.05 | 0.049766 | MULTIGEN531381 | Add 8 MVAR switched shunt at JHNCRSOL 115 kV
Voltage | 00NR | 2 | 29SP | V | ASGI-2024-003 | MANTERT3 | 0.99777 | 1.0643 | 0.066483 |  | 0.9 | 1.05 | 0.049708 | Single 531381 JOHNCTY3 115 531424 JOHNCR3 115 1 | Add 8 MVAR switched shunt at JHNCRSOL 115 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-374 | MAURINE8 | 1.017 | 1.0564 | 0.039344 |  | 0.9 | 1.05 | 0.15187 | P12:230.0:UMZ:# N-1 #:: LINE WAYSIDE 4-NUNDRWD4-1 :HV: | None
Voltage | 00NR | 2 | 29SP | V | ASGI-2024-006 | NP-GLAZIR_G2 | 0.64681 | 0.62694 | -0.019871 |  | 0.9 | 1.05 | 0.076762 | Single 523186 SPEARMAN3 115 523195 HANSFORD3 115 1 | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 29SP | V | ASGI-2024-006 | NP-GLAZIR_G2 | 0.64681 | 0.62694 | -0.019871 |  | 0.9 | 1.05 | 0.076762 | P12:115:SPS:T87.1.SPRMN.HANSFRD:::HV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 29SP | V | ASGI-2024-006 | NP-GLAZIR_G2 | 0.66911 | 0.64846 | -0.020652 |  | 0.9 | 1.05 | 0.076762 | Single 523093 HITCHLAND3 115 523195 HANSFORD3 115 1 | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 29SP | V | ASGI-2024-006 | NP-GLAZIR_G2 | 0.66911 | 0.64846 | -0.020652 |  | 0.9 | 1.05 | 0.076762 | P12:115:SPS:W10.1.HITCH.HANSFRD:::HV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 29SP | V | ASGI-2024-006 | NP-LIPSCOMB2 | 0.60504 | 0.58465 | -0.020388 |  | 0.9 | 1.05 | 0.076762 | Single 523186 SPEARMAN3 115 523195 HANSFORD3 115 1 | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 29SP | V | ASGI-2024-006 | NP-LIPSCOMB2 | 0.60504 | 0.58465 | -0.020388 |  | 0.9 | 1.05 | 0.076762 | P12:115:SPS:T87.1.SPRMN.HANSFRD:::HV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 29SP | V | ASGI-2024-006 | NP-LIPSCOMB2 | 0.62797 | 0.60673 | -0.021244 |  | 0.9 | 1.05 | 0.076762 | Single 523093 HITCHLAND3 115 523195 HANSFORD3 115 1 | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 29SP | V | ASGI-2024-006 | NP-LIPSCOMB2 | 0.62797 | 0.60673 | -0.021244 |  | 0.9 | 1.05 | 0.076762 | P12:115:SPS:W10.1.HITCH.HANSFRD:::HV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-295 | NP-LIPSCOMB2 | 0.64161 | 0.62794 | -0.013671 |  | 0.9 | 1.05 | 0.12959 | P12:115:SPS:W72B.1.NOR.CHIN:::HV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 29SP | V | ASGI-2024-006 | NP-LIPS_SHA2 | 0.60504 | 0.58465 | -0.020388 |  | 0.9 | 1.05 | 0.076762 | Single 523186 SPEARMAN3 115 523195 HANSFORD3 115 1 | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 29SP | V | ASGI-2024-006 | NP-LIPS_SHA2 | 0.60504 | 0.58465 | -0.020388 |  | 0.9 | 1.05 | 0.076762 | P12:115:SPS:T87.1.SPRMN.HANSFRD:::HV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 29SP | V | ASGI-2024-006 | NP-LIPS_SHA2 | 0.62797 | 0.60673 | -0.021244 |  | 0.9 | 1.05 | 0.076762 | Single 523093 HITCHLAND3 115 523195 HANSFORD3 115 1 | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 29SP | V | ASGI-2024-006 | NP-LIPS_SHA2 | 0.62797 | 0.60673 | -0.021244 |  | 0.9 | 1.05 | 0.076762 | P12:115:SPS:W10.1.HITCH.HANSFRD:::HV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-295 | NP-LIPS_SHA2 | 0.64161 | 0.62794 | -0.013671 |  | 0.9 | 1.05 | 0.12959 | P12:115:SPS:W72B.1.NOR.CHIN:::HV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 29SP | V | ASGI-2024-006 | NP-LUCKY_CR2 | 0.74514 | 0.72674 | -0.018406 |  | 0.9 | 1.05 | 0.076762 | Single 523186 SPEARMAN3 115 523195 HANSFORD3 115 1 | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 29SP | V | ASGI-2024-006 | NP-LUCKY_CR2 | 0.74514 | 0.72674 | -0.018406 |  | 0.9 | 1.05 | 0.076762 | P12:115:SPS:T87.1.SPRMN.HANSFRD:::HV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 29SP | V | ASGI-2024-006 | NP-LUCKY_CR2 | 0.76561 | 0.74665 | -0.01896 |  | 0.9 | 1.05 | 0.076762 | Single 523093 HITCHLAND3 115 523195 HANSFORD3 115 1 | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 29SP | V | ASGI-2024-006 | NP-LUCKY_CR2 | 0.76561 | 0.74665 | -0.01896 |  | 0.9 | 1.05 | 0.076762 | P12:115:SPS:W10.1.HITCH.HANSFRD:::HV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 29SP | V | ASGI-2024-006 | NP-VALERO_P2 | 0.61379 | 0.5935 | -0.020288 |  | 0.9 | 1.05 | 0.076762 | Single 523186 SPEARMAN3 115 523195 HANSFORD3 115 1 | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 29SP | V | ASGI-2024-006 | NP-VALERO_P2 | 0.61379 | 0.5935 | -0.020288 |  | 0.9 | 1.05 | 0.076762 | P12:115:SPS:T87.1.SPRMN.HANSFRD:::HV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 29SP | V | ASGI-2024-006 | NP-VALERO_P2 | 0.6366 | 0.61547 | -0.021129 |  | 0.9 | 1.05 | 0.076762 | Single 523093 HITCHLAND3 115 523195 HANSFORD3 115 1 | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 29SP | V | ASGI-2024-006 | NP-VALERO_P2 | 0.6366 | 0.61547 | -0.021129 |  | 0.9 | 1.05 | 0.076762 | P12:115:SPS:W10.1.HITCH.HANSFRD:::HV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-295 | NP-VALERO_P2 | 0.65014 | 0.63657 | -0.013576 |  | 0.9 | 1.05 | 0.12959 | P12:115:SPS:W72B.1.NOR.CHIN:::HV: | Add 3.36 MVAR SVC at NP-LIPS_SHA2 69 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-374 | NUNDRWD-LNX3 | 0.9928 | 0.88176 | -0.11104 |  | 0.9 | 1.05 | 0.067023 | P12:230.0:UMZ:# N-1 #:: LINE NUNDRWD4-PHILIP_T 4-1 :HV: | Add 60 MVAR switched shunt at NUNDRWD-LNX3 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-374 | NUNDRWD-LNX3 | 1.0013 | 0.88391 | -0.1174 |  | 0.9 | 1.05 | 0.077573 | P12:230:UMZ:# 20065 #:: PROPER N-1 FOR TAP PHILIP_T-BE4:HV: | Add 60 MVAR switched shunt at NUNDRWD-LNX3 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-374 | NUNDRWD4 | 0.99288 | 0.88189 | -0.11099 |  | 0.9 | 1.05 | 0.067023 | P12:230.0:UMZ:# N-1 #:: LINE NUNDRWD4-PHILIP_T 4-1 :HV: | Add 60 MVAR switched shunt at NUNDRWD-LNX3 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-374 | NUNDRWD4 | 1.0014 | 0.88404 | -0.11734 |  | 0.9 | 1.05 | 0.077573 | P12:230:UMZ:# 20065 #:: PROPER N-1 FOR TAP PHILIP_T-BE4:HV: | Add 60 MVAR switched shunt at NUNDRWD-LNX3 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-017 | PR BRZ 4 | 1.033 | 1.059 | 0.02608 |  | 0.95 | 1.05 | 0.070452 | Single 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-018 | PR BRZ 4 | 1.033 | 1.059 | 0.02608 |  | 0.95 | 1.05 | 0.065591 | Single 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-019 | PR BRZ 4 | 1.033 | 1.059 | 0.02608 |  | 0.95 | 1.05 | 0.065591 | Single 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-020 | PR BRZ 4 | 1.033 | 1.059 | 0.02608 |  | 0.95 | 1.05 | 0.070452 | Single 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-021 | PR BRZ 4 | 1.033 | 1.059 | 0.02608 |  | 0.95 | 1.05 | 0.070452 | Single 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-022 | PR BRZ 4 | 1.033 | 1.059 | 0.02608 |  | 0.95 | 1.05 | 0.065591 | Single 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-023 | PR BRZ 4 | 1.033 | 1.059 | 0.02608 |  | 0.95 | 1.05 | 0.065591 | Single 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-051 | PR BRZ 4 | 1.033 | 1.059 | 0.02608 |  | 0.95 | 1.05 | 0.078187 | Single 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-168 | PR BRZ 4 | 1.033 | 1.059 | 0.02608 |  | 0.95 | 1.05 | 0.055544 | Single 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-173 | PR BRZ 4 | 1.033 | 1.059 | 0.02608 |  | 0.95 | 1.05 | 0.097366 | Single 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-017 | PR BRZ 4 | 1.0305 | 1.0578 | 0.027317 |  | 0.95 | 1.05 | 0.042185 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOM2-LNX3-GRPRAR2-LNX3-1 :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-018 | PR BRZ 4 | 1.0305 | 1.0578 | 0.027317 |  | 0.95 | 1.05 | 0.042328 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOM2-LNX3-GRPRAR2-LNX3-1 :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-019 | PR BRZ 4 | 1.0305 | 1.0578 | 0.027317 |  | 0.95 | 1.05 | 0.042328 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOM2-LNX3-GRPRAR2-LNX3-1 :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-020 | PR BRZ 4 | 1.0305 | 1.0578 | 0.027317 |  | 0.95 | 1.05 | 0.042185 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOM2-LNX3-GRPRAR2-LNX3-1 :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-021 | PR BRZ 4 | 1.0305 | 1.0578 | 0.027317 |  | 0.95 | 1.05 | 0.042185 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOM2-LNX3-GRPRAR2-LNX3-1 :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-022 | PR BRZ 4 | 1.0305 | 1.0578 | 0.027317 |  | 0.95 | 1.05 | 0.042328 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOM2-LNX3-GRPRAR2-LNX3-1 :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-023 | PR BRZ 4 | 1.0305 | 1.0578 | 0.027317 |  | 0.95 | 1.05 | 0.042328 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOM2-LNX3-GRPRAR2-LNX3-1 :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-051 | PR BRZ 4 | 1.0305 | 1.0578 | 0.027317 |  | 0.95 | 1.05 | 0.038948 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOM2-LNX3-GRPRAR2-LNX3-1 :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-065 | PR BRZ 4 | 1.0305 | 1.0578 | 0.027317 |  | 0.95 | 1.05 | 0.033503 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOM2-LNX3-GRPRAR2-LNX3-1 :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-140 | PR BRZ 4 | 1.0305 | 1.0578 | 0.027317 |  | 0.95 | 1.05 | 0.092488 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOM2-LNX3-GRPRAR2-LNX3-1 :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-168 | PR BRZ 4 | 1.0305 | 1.0578 | 0.027317 |  | 0.95 | 1.05 | 0.056656 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOM2-LNX3-GRPRAR2-LNX3-1 :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-173 | PR BRZ 4 | 1.0305 | 1.0578 | 0.027317 |  | 0.95 | 1.05 | 0.043846 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOM2-LNX3-GRPRAR2-LNX3-1 :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-017 | PR BRZ 4 | 1.0305 | 1.0577 | 0.027235 |  | 0.95 | 1.05 | 0.042185 | P12:345.0:UMZ:# N-1 #:: LINE GR PRAIRIE 3-GRPRAR2-LNX3-Z :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-018 | PR BRZ 4 | 1.0305 | 1.0577 | 0.027235 |  | 0.95 | 1.05 | 0.042328 | P12:345.0:UMZ:# N-1 #:: LINE GR PRAIRIE 3-GRPRAR2-LNX3-Z :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-019 | PR BRZ 4 | 1.0305 | 1.0577 | 0.027235 |  | 0.95 | 1.05 | 0.042328 | P12:345.0:UMZ:# N-1 #:: LINE GR PRAIRIE 3-GRPRAR2-LNX3-Z :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-020 | PR BRZ 4 | 1.0305 | 1.0577 | 0.027235 |  | 0.95 | 1.05 | 0.042185 | P12:345.0:UMZ:# N-1 #:: LINE GR PRAIRIE 3-GRPRAR2-LNX3-Z :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-021 | PR BRZ 4 | 1.0305 | 1.0577 | 0.027235 |  | 0.95 | 1.05 | 0.042185 | P12:345.0:UMZ:# N-1 #:: LINE GR PRAIRIE 3-GRPRAR2-LNX3-Z :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-022 | PR BRZ 4 | 1.0305 | 1.0577 | 0.027235 |  | 0.95 | 1.05 | 0.042328 | P12:345.0:UMZ:# N-1 #:: LINE GR PRAIRIE 3-GRPRAR2-LNX3-Z :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-023 | PR BRZ 4 | 1.0305 | 1.0577 | 0.027235 |  | 0.95 | 1.05 | 0.042328 | P12:345.0:UMZ:# N-1 #:: LINE GR PRAIRIE 3-GRPRAR2-LNX3-Z :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-051 | PR BRZ 4 | 1.0305 | 1.0577 | 0.027235 |  | 0.95 | 1.05 | 0.038948 | P12:345.0:UMZ:# N-1 #:: LINE GR PRAIRIE 3-GRPRAR2-LNX3-Z :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-065 | PR BRZ 4 | 1.0305 | 1.0577 | 0.027235 |  | 0.95 | 1.05 | 0.033503 | P12:345.0:UMZ:# N-1 #:: LINE GR PRAIRIE 3-GRPRAR2-LNX3-Z :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-140 | PR BRZ 4 | 1.0305 | 1.0577 | 0.027235 |  | 0.95 | 1.05 | 0.092488 | P12:345.0:UMZ:# N-1 #:: LINE GR PRAIRIE 3-GRPRAR2-LNX3-Z :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-168 | PR BRZ 4 | 1.0305 | 1.0577 | 0.027235 |  | 0.95 | 1.05 | 0.056656 | P12:345.0:UMZ:# N-1 #:: LINE GR PRAIRIE 3-GRPRAR2-LNX3-Z :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-173 | PR BRZ 4 | 1.0305 | 1.0577 | 0.027235 |  | 0.95 | 1.05 | 0.043846 | P12:345.0:UMZ:# N-1 #:: LINE GR PRAIRIE 3-GRPRAR2-LNX3-Z :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-017 | PR BRZ 4 | 1.0305 | 1.0577 | 0.027229 |  | 0.95 | 1.05 | 0.042185 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOMP3-FTTHOM2-LNX3-Z :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-018 | PR BRZ 4 | 1.0305 | 1.0577 | 0.027229 |  | 0.95 | 1.05 | 0.042328 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOMP3-FTTHOM2-LNX3-Z :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-019 | PR BRZ 4 | 1.0305 | 1.0577 | 0.027229 |  | 0.95 | 1.05 | 0.042328 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOMP3-FTTHOM2-LNX3-Z :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-020 | PR BRZ 4 | 1.0305 | 1.0577 | 0.027229 |  | 0.95 | 1.05 | 0.042185 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOMP3-FTTHOM2-LNX3-Z :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-021 | PR BRZ 4 | 1.0305 | 1.0577 | 0.027229 |  | 0.95 | 1.05 | 0.042185 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOMP3-FTTHOM2-LNX3-Z :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-022 | PR BRZ 4 | 1.0305 | 1.0577 | 0.027229 |  | 0.95 | 1.05 | 0.042328 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOMP3-FTTHOM2-LNX3-Z :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-023 | PR BRZ 4 | 1.0305 | 1.0577 | 0.027229 |  | 0.95 | 1.05 | 0.042328 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOMP3-FTTHOM2-LNX3-Z :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-051 | PR BRZ 4 | 1.0305 | 1.0577 | 0.027229 |  | 0.95 | 1.05 | 0.038948 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOMP3-FTTHOM2-LNX3-Z :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-065 | PR BRZ 4 | 1.0305 | 1.0577 | 0.027229 |  | 0.95 | 1.05 | 0.033503 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOMP3-FTTHOM2-LNX3-Z :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-140 | PR BRZ 4 | 1.0305 | 1.0577 | 0.027229 |  | 0.95 | 1.05 | 0.092488 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOMP3-FTTHOM2-LNX3-Z :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-168 | PR BRZ 4 | 1.0305 | 1.0577 | 0.027229 |  | 0.95 | 1.05 | 0.056656 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOMP3-FTTHOM2-LNX3-Z :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-173 | PR BRZ 4 | 1.0305 | 1.0577 | 0.027229 |  | 0.95 | 1.05 | 0.043846 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOMP3-FTTHOM2-LNX3-Z :EHV: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29SP | V | ASGI-2024-003 | PR BRZ 4 | 1.032 | 1.0576 | 0.025574 |  | 0.95 | 1.05 | 0.034985 | P42:345:NPPD:BKR-HOS-3308:::: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-017 | PR BRZ 4 | 1.032 | 1.0576 | 0.025574 |  | 0.95 | 1.05 | 0.070452 | P42:345:NPPD:BKR-HOS-3308:::: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-018 | PR BRZ 4 | 1.032 | 1.0576 | 0.025574 |  | 0.95 | 1.05 | 0.065591 | P42:345:NPPD:BKR-HOS-3308:::: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-019 | PR BRZ 4 | 1.032 | 1.0576 | 0.025574 |  | 0.95 | 1.05 | 0.065591 | P42:345:NPPD:BKR-HOS-3308:::: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-020 | PR BRZ 4 | 1.032 | 1.0576 | 0.025574 |  | 0.95 | 1.05 | 0.070452 | P42:345:NPPD:BKR-HOS-3308:::: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-021 | PR BRZ 4 | 1.032 | 1.0576 | 0.025574 |  | 0.95 | 1.05 | 0.070452 | P42:345:NPPD:BKR-HOS-3308:::: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-022 | PR BRZ 4 | 1.032 | 1.0576 | 0.025574 |  | 0.95 | 1.05 | 0.065591 | P42:345:NPPD:BKR-HOS-3308:::: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-023 | PR BRZ 4 | 1.032 | 1.0576 | 0.025574 |  | 0.95 | 1.05 | 0.065591 | P42:345:NPPD:BKR-HOS-3308:::: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-051 | PR BRZ 4 | 1.032 | 1.0576 | 0.025574 |  | 0.95 | 1.05 | 0.078187 | P42:345:NPPD:BKR-HOS-3308:::: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-140 | PR BRZ 4 | 1.032 | 1.0576 | 0.025574 |  | 0.95 | 1.05 | 0.57869 | P42:345:NPPD:BKR-HOS-3308:::: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-168 | PR BRZ 4 | 1.032 | 1.0576 | 0.025574 |  | 0.95 | 1.05 | 0.055544 | P42:345:NPPD:BKR-HOS-3308:::: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-173 | PR BRZ 4 | 1.032 | 1.0576 | 0.025574 |  | 0.95 | 1.05 | 0.097366 | P42:345:NPPD:BKR-HOS-3308:::: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-374 | PR BRZ 4 | 1.032 | 1.0576 | 0.025574 |  | 0.95 | 1.05 | 0.063842 | P42:345:NPPD:BKR-HOS-3308:::: | Add 45 MVAR switched shunt at PR BRZ 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-374 | RAPIDCTY-RM8 | 0.99904 | 0.89008 | -0.10896 |  | 0.9 | 1.05 | 0.067023 | P12:230.0:UMZ:# N-1 #:: LINE NUNDRWD4-PHILIP_T 4-1 :HV: | Add 60 MVAR switched shunt at NUNDRWD-LNX3 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-374 | RAPIDCTY-RM8 | 1.0088 | 0.89238 | -0.1164 |  | 0.9 | 1.05 | 0.077573 | P12:230:UMZ:# 20065 #:: PROPER N-1 FOR TAP PHILIP_T-BE4:HV: | Add 60 MVAR switched shunt at NUNDRWD-LNX3 230 kV
Voltage | 00NR | 2 | 29SP | V | ASGI-2024-003 | RICHFLD3 | 0.99762 | 1.0637 | 0.066065 |  | 0.9 | 1.05 | 0.049766 | P12:115:SUNC:JOHNSONCORNER-ULYSSESPLANT:::HV: | Add 8 MVAR switched shunt at JHNCRSOL 115 kV
Voltage | 00NR | 2 | 29SP | V | ASGI-2024-003 | RICHFLD3 | 0.99705 | 1.0633 | 0.066251 |  | 0.9 | 1.05 | 0.049766 | MULTIGEN531381 | Add 8 MVAR switched shunt at JHNCRSOL 115 kV
Voltage | 00NR | 2 | 29SP | V | ASGI-2024-003 | RICHFLD3 | 0.99553 | 1.0622 | 0.066677 |  | 0.9 | 1.05 | 0.049708 | Single 531381 JOHNCTY3 115 531424 JOHNCR3 115 1 | Add 8 MVAR switched shunt at JHNCRSOL 115 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-374 | RUSHMORE-RM7 | 1.0004 | 0.8922 | -0.10819 |  | 0.9 | 1.05 | 0.067023 | P12:230.0:UMZ:# N-1 #:: LINE NUNDRWD4-PHILIP_T 4-1 :HV: | Add 60 MVAR switched shunt at NUNDRWD-LNX3 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-374 | RUSHMORE-RM7 | 1.0104 | 0.89451 | -0.11592 |  | 0.9 | 1.05 | 0.077573 | P12:230:UMZ:# 20065 #:: PROPER N-1 FOR TAP PHILIP_T-BE4:HV: | Add 60 MVAR switched shunt at NUNDRWD-LNX3 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-374 | STEGALL 4 | 0.87819 | 0.7872 | -0.09099 |  | 0.9 | 1.05 | 0.16564 | P12:230.0:UMZ:# N-1 #:: LINE STEGALL 4-STEGALL_-MB4-1 :HV: | Add 0.04 MVAR switched shunt at VICTRYH4 230 kV; Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-374 | STEGALL 4 | 0.88256 | 0.78817 | -0.094384 |  | 0.9 | 1.05 | 0.16564 | P13:345-230.0:UMZ:# N-1 #:: 3WND STEGALL_-MB3-STEGALL_-MB4-STEGALL_-MB9-1 SGQ KV3A:EHV: | Add 78 MVAR switched shunt at DH_CS_EA-TS4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-374 | STEGALL-LNX3 | 0.87819 | 0.7872 | -0.09099 |  | 0.9 | 1.05 | 0.16564 | P12:230.0:UMZ:# N-1 #:: LINE STEGALL 4-STEGALL_-MB4-1 :HV: | Add 0.04 MVAR switched shunt at VICTRYH4 230 kV; Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-374 | STEGALL-LNX3 | 0.97165 | 0.8873 | -0.084349 |  | 0.9 | 1.05 | 0.13666 | P12:230.0:UMZ:# N-1 #:: LINE STEGALL 4-STEGALL-LNX3-Z :HV: | Add 23 MVAR switched shunt at STEGALL-LNX3 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-374 | STEGALL-LNX3 | 0.88256 | 0.78817 | -0.094384 |  | 0.9 | 1.05 | 0.16564 | P13:345-230.0:UMZ:# N-1 #:: 3WND STEGALL_-MB3-STEGALL_-MB4-STEGALL_-MB9-1 SGQ KV3A:EHV: | Add 78 MVAR switched shunt at DH_CS_EA-TS4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-374 | STEGALL_-MB4 | 0.88257 | 0.78819 | -0.094385 |  | 0.9 | 1.05 | 0.16564 | P13:345-230.0:UMZ:# N-1 #:: 3WND STEGALL_-MB3-STEGALL_-MB4-STEGALL_-MB9-1 SGQ KV3A:EHV: | Add 78 MVAR switched shunt at DH_CS_EA-TS4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-374 | SULPHUR | 1.0237 | 1.0576 | 0.033912 |  | 0.9 | 1.05 | 0.15187 | P12:230.0:UMZ:# N-1 #:: LINE WAYSIDE 4-NUNDRWD4-1 :HV: | None
Voltage | 00NR | 2 | 29SP | V | GEN-2024-374 | VICTRYH4 | 0.88917 | 0.80685 | -0.08232 |  | 0.9 | 1.05 | 0.16564 | P12:230.0:UMZ:# N-1 #:: LINE STEGALL 4-STEGALL_-MB4-1 :HV: | Add 0.04 MVAR switched shunt at VICTRYH4 230 kV; Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-374 | VICTRYH4 | 0.89339 | 0.80771 | -0.085686 |  | 0.9 | 1.05 | 0.16564 | P13:345-230.0:UMZ:# N-1 #:: 3WND STEGALL_-MB3-STEGALL_-MB4-STEGALL_-MB9-1 SGQ KV3A:EHV: | Add 78 MVAR switched shunt at DH_CS_EA-TS4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-374 | WAYSIDE 4 | 0.93784 | 0.83916 | -0.098679 |  | 0.9 | 1.05 | 0.16564 | P12:230.0:UMZ:# N-1 #:: LINE STEGALL 4-STEGALL_-MB4-1 :HV: | Add 0.04 MVAR switched shunt at VICTRYH4 230 kV; Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-017 | WAYSIDE 4 | 0.99659 | 0.85919 | -0.13739 |  | 0.9 | 1.05 | 0.042185 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOM2-LNX3-GRPRAR2-LNX3-1 :EHV: | Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-018 | WAYSIDE 4 | 0.99659 | 0.85919 | -0.13739 |  | 0.9 | 1.05 | 0.042328 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOM2-LNX3-GRPRAR2-LNX3-1 :EHV: | Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-019 | WAYSIDE 4 | 0.99659 | 0.85919 | -0.13739 |  | 0.9 | 1.05 | 0.042328 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOM2-LNX3-GRPRAR2-LNX3-1 :EHV: | Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-020 | WAYSIDE 4 | 0.99659 | 0.85919 | -0.13739 |  | 0.9 | 1.05 | 0.042185 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOM2-LNX3-GRPRAR2-LNX3-1 :EHV: | Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-021 | WAYSIDE 4 | 0.99659 | 0.85919 | -0.13739 |  | 0.9 | 1.05 | 0.042185 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOM2-LNX3-GRPRAR2-LNX3-1 :EHV: | Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-022 | WAYSIDE 4 | 0.99659 | 0.85919 | -0.13739 |  | 0.9 | 1.05 | 0.042328 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOM2-LNX3-GRPRAR2-LNX3-1 :EHV: | Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-023 | WAYSIDE 4 | 0.99659 | 0.85919 | -0.13739 |  | 0.9 | 1.05 | 0.042328 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOM2-LNX3-GRPRAR2-LNX3-1 :EHV: | Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-051 | WAYSIDE 4 | 0.99659 | 0.85919 | -0.13739 |  | 0.9 | 1.05 | 0.038948 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOM2-LNX3-GRPRAR2-LNX3-1 :EHV: | Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-065 | WAYSIDE 4 | 0.99659 | 0.85919 | -0.13739 |  | 0.9 | 1.05 | 0.033503 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOM2-LNX3-GRPRAR2-LNX3-1 :EHV: | Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-140 | WAYSIDE 4 | 0.99659 | 0.85919 | -0.13739 |  | 0.9 | 1.05 | 0.092488 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOM2-LNX3-GRPRAR2-LNX3-1 :EHV: | Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-168 | WAYSIDE 4 | 0.99659 | 0.85919 | -0.13739 |  | 0.9 | 1.05 | 0.056656 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOM2-LNX3-GRPRAR2-LNX3-1 :EHV: | Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-173 | WAYSIDE 4 | 0.99659 | 0.85919 | -0.13739 |  | 0.9 | 1.05 | 0.043846 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOM2-LNX3-GRPRAR2-LNX3-1 :EHV: | Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-017 | WAYSIDE 4 | 0.99659 | 0.85929 | -0.1373 |  | 0.9 | 1.05 | 0.042185 | P12:345.0:UMZ:# N-1 #:: LINE GR PRAIRIE 3-GRPRAR2-LNX3-Z :EHV: | Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-018 | WAYSIDE 4 | 0.99659 | 0.85929 | -0.1373 |  | 0.9 | 1.05 | 0.042328 | P12:345.0:UMZ:# N-1 #:: LINE GR PRAIRIE 3-GRPRAR2-LNX3-Z :EHV: | Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-019 | WAYSIDE 4 | 0.99659 | 0.85929 | -0.1373 |  | 0.9 | 1.05 | 0.042328 | P12:345.0:UMZ:# N-1 #:: LINE GR PRAIRIE 3-GRPRAR2-LNX3-Z :EHV: | Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-020 | WAYSIDE 4 | 0.99659 | 0.85929 | -0.1373 |  | 0.9 | 1.05 | 0.042185 | P12:345.0:UMZ:# N-1 #:: LINE GR PRAIRIE 3-GRPRAR2-LNX3-Z :EHV: | Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-021 | WAYSIDE 4 | 0.99659 | 0.85929 | -0.1373 |  | 0.9 | 1.05 | 0.042185 | P12:345.0:UMZ:# N-1 #:: LINE GR PRAIRIE 3-GRPRAR2-LNX3-Z :EHV: | Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-022 | WAYSIDE 4 | 0.99659 | 0.85929 | -0.1373 |  | 0.9 | 1.05 | 0.042328 | P12:345.0:UMZ:# N-1 #:: LINE GR PRAIRIE 3-GRPRAR2-LNX3-Z :EHV: | Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-023 | WAYSIDE 4 | 0.99659 | 0.85929 | -0.1373 |  | 0.9 | 1.05 | 0.042328 | P12:345.0:UMZ:# N-1 #:: LINE GR PRAIRIE 3-GRPRAR2-LNX3-Z :EHV: | Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-051 | WAYSIDE 4 | 0.99659 | 0.85929 | -0.1373 |  | 0.9 | 1.05 | 0.038948 | P12:345.0:UMZ:# N-1 #:: LINE GR PRAIRIE 3-GRPRAR2-LNX3-Z :EHV: | Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-065 | WAYSIDE 4 | 0.99659 | 0.85929 | -0.1373 |  | 0.9 | 1.05 | 0.033503 | P12:345.0:UMZ:# N-1 #:: LINE GR PRAIRIE 3-GRPRAR2-LNX3-Z :EHV: | Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-140 | WAYSIDE 4 | 0.99659 | 0.85929 | -0.1373 |  | 0.9 | 1.05 | 0.092488 | P12:345.0:UMZ:# N-1 #:: LINE GR PRAIRIE 3-GRPRAR2-LNX3-Z :EHV: | Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-168 | WAYSIDE 4 | 0.99659 | 0.85929 | -0.1373 |  | 0.9 | 1.05 | 0.056656 | P12:345.0:UMZ:# N-1 #:: LINE GR PRAIRIE 3-GRPRAR2-LNX3-Z :EHV: | Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-173 | WAYSIDE 4 | 0.99659 | 0.85929 | -0.1373 |  | 0.9 | 1.05 | 0.043846 | P12:345.0:UMZ:# N-1 #:: LINE GR PRAIRIE 3-GRPRAR2-LNX3-Z :EHV: | Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-017 | WAYSIDE 4 | 0.99659 | 0.85932 | -0.13727 |  | 0.9 | 1.05 | 0.042185 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOMP3-FTTHOM2-LNX3-Z :EHV: | Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-018 | WAYSIDE 4 | 0.99659 | 0.85932 | -0.13727 |  | 0.9 | 1.05 | 0.042328 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOMP3-FTTHOM2-LNX3-Z :EHV: | Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-019 | WAYSIDE 4 | 0.99659 | 0.85932 | -0.13727 |  | 0.9 | 1.05 | 0.042328 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOMP3-FTTHOM2-LNX3-Z :EHV: | Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-020 | WAYSIDE 4 | 0.99659 | 0.85932 | -0.13727 |  | 0.9 | 1.05 | 0.042185 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOMP3-FTTHOM2-LNX3-Z :EHV: | Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-021 | WAYSIDE 4 | 0.99659 | 0.85932 | -0.13727 |  | 0.9 | 1.05 | 0.042185 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOMP3-FTTHOM2-LNX3-Z :EHV: | Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-022 | WAYSIDE 4 | 0.99659 | 0.85932 | -0.13727 |  | 0.9 | 1.05 | 0.042328 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOMP3-FTTHOM2-LNX3-Z :EHV: | Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-023 | WAYSIDE 4 | 0.99659 | 0.85932 | -0.13727 |  | 0.9 | 1.05 | 0.042328 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOMP3-FTTHOM2-LNX3-Z :EHV: | Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-051 | WAYSIDE 4 | 0.99659 | 0.85932 | -0.13727 |  | 0.9 | 1.05 | 0.038948 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOMP3-FTTHOM2-LNX3-Z :EHV: | Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-065 | WAYSIDE 4 | 0.99659 | 0.85932 | -0.13727 |  | 0.9 | 1.05 | 0.033503 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOMP3-FTTHOM2-LNX3-Z :EHV: | Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-140 | WAYSIDE 4 | 0.99659 | 0.85932 | -0.13727 |  | 0.9 | 1.05 | 0.092488 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOMP3-FTTHOM2-LNX3-Z :EHV: | Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-168 | WAYSIDE 4 | 0.99659 | 0.85932 | -0.13727 |  | 0.9 | 1.05 | 0.056656 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOMP3-FTTHOM2-LNX3-Z :EHV: | Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-173 | WAYSIDE 4 | 0.99659 | 0.85932 | -0.13727 |  | 0.9 | 1.05 | 0.043846 | P12:345.0:UMZ:# N-1 #:: LINE FTTHOMP3-FTTHOM2-LNX3-Z :EHV: | Add 154 MVAR SVC at WAYSIDE 4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-374 | WAYSIDE 4 | 0.94166 | 0.83974 | -0.10192 |  | 0.9 | 1.05 | 0.16564 | P13:345-230.0:UMZ:# N-1 #:: 3WND STEGALL_-MB3-STEGALL_-MB4-STEGALL_-MB9-1 SGQ KV3A:EHV: | Add 78 MVAR switched shunt at DH_CS_EA-TS4 230 kV
Voltage | 00NR | 2 | 29SP | V | GEN-2024-374 | WILCRKXFRP 3 | 1.0237 | 1.0576 | 0.033912 |  | 0.9 | 1.05 | 0.15187 | P12:230.0:UMZ:# N-1 #:: LINE WAYSIDE 4-NUNDRWD4-1 :HV: | None
Voltage | 03ALL | 2 | 29SP | V | ASGI-2024-024 | BURLNGTNJCT2 | 0.94597 | 0.91126 | -0.034712 |  | 0.93 | 1.05 | 0.13302 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-054 | BURLNGTNJCT2 | 0.94597 | 0.91126 | -0.034712 |  | 0.93 | 1.05 | 0.040787 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-055 | BURLNGTNJCT2 | 0.94597 | 0.91126 | -0.034712 |  | 0.93 | 1.05 | 0.046288 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-074 | BURLNGTNJCT2 | 0.94597 | 0.91126 | -0.034712 |  | 0.93 | 1.05 | 0.067254 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-076 | BURLNGTNJCT2 | 0.94597 | 0.91126 | -0.034712 |  | 0.93 | 1.05 | 0.035421 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-090 | BURLNGTNJCT2 | 0.94597 | 0.91126 | -0.034712 |  | 0.93 | 1.05 | 0.073349 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-139 | BURLNGTNJCT2 | 0.94597 | 0.91126 | -0.034712 |  | 0.93 | 1.05 | 0.034571 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-170 | BURLNGTNJCT2 | 0.94597 | 0.91126 | -0.034712 |  | 0.93 | 1.05 | 0.073415 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-253 | BURLNGTNJCT2 | 0.94597 | 0.91126 | -0.034712 |  | 0.93 | 1.05 | 0.070344 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-258 | BURLNGTNJCT2 | 0.94597 | 0.91126 | -0.034712 |  | 0.93 | 1.05 | 0.032402 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-260 | BURLNGTNJCT2 | 0.94597 | 0.91126 | -0.034712 |  | 0.93 | 1.05 | 0.13211 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-276 | BURLNGTNJCT2 | 0.94597 | 0.91126 | -0.034712 |  | 0.93 | 1.05 | 0.050915 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-277 | BURLNGTNJCT2 | 0.94597 | 0.91126 | -0.034712 |  | 0.93 | 1.05 | 0.050915 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-287 | BURLNGTNJCT2 | 0.94597 | 0.91126 | -0.034712 |  | 0.93 | 1.05 | 0.030578 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-319 | BURLNGTNJCT2 | 0.94597 | 0.91126 | -0.034712 |  | 0.93 | 1.05 | 0.059767 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-320 | BURLNGTNJCT2 | 0.94597 | 0.91126 | -0.034712 |  | 0.93 | 1.05 | 0.06434 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-339 | BURLNGTNJCT2 | 0.94597 | 0.91126 | -0.034712 |  | 0.93 | 1.05 | 0.074026 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-352 | BURLNGTNJCT2 | 0.94597 | 0.91126 | -0.034712 |  | 0.93 | 1.05 | 0.10772 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-370 | BURLNGTNJCT2 | 0.94597 | 0.91126 | -0.034712 |  | 0.93 | 1.05 | 0.073349 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | ASGI-2024-024 | BURLNGTNJCT2 | 0.94968 | 0.92809 | -0.021596 |  | 0.93 | 1.05 | 0.1874 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-054 | BURLNGTNJCT2 | 0.94968 | 0.92809 | -0.021596 |  | 0.93 | 1.05 | 0.032663 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-055 | BURLNGTNJCT2 | 0.94968 | 0.92809 | -0.021596 |  | 0.93 | 1.05 | 0.052451 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-074 | BURLNGTNJCT2 | 0.94968 | 0.92809 | -0.021596 |  | 0.93 | 1.05 | 0.072212 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-076 | BURLNGTNJCT2 | 0.94968 | 0.92809 | -0.021596 |  | 0.93 | 1.05 | 0.042339 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-090 | BURLNGTNJCT2 | 0.94968 | 0.92809 | -0.021596 |  | 0.93 | 1.05 | 0.10618 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-139 | BURLNGTNJCT2 | 0.94968 | 0.92809 | -0.021596 |  | 0.93 | 1.05 | 0.038127 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-170 | BURLNGTNJCT2 | 0.94968 | 0.92809 | -0.021596 |  | 0.93 | 1.05 | 0.065102 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-253 | BURLNGTNJCT2 | 0.94968 | 0.92809 | -0.021596 |  | 0.93 | 1.05 | 0.095208 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-258 | BURLNGTNJCT2 | 0.94968 | 0.92809 | -0.021596 |  | 0.93 | 1.05 | 0.035057 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-260 | BURLNGTNJCT2 | 0.94968 | 0.92809 | -0.021596 |  | 0.93 | 1.05 | 0.18643 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-276 | BURLNGTNJCT2 | 0.94968 | 0.92809 | -0.021596 |  | 0.93 | 1.05 | 0.053424 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-277 | BURLNGTNJCT2 | 0.94968 | 0.92809 | -0.021596 |  | 0.93 | 1.05 | 0.053424 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-287 | BURLNGTNJCT2 | 0.94968 | 0.92809 | -0.021596 |  | 0.93 | 1.05 | 0.032476 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-319 | BURLNGTNJCT2 | 0.94968 | 0.92809 | -0.021596 |  | 0.93 | 1.05 | 0.084299 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-320 | BURLNGTNJCT2 | 0.94968 | 0.92809 | -0.021596 |  | 0.93 | 1.05 | 0.084751 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-339 | BURLNGTNJCT2 | 0.94968 | 0.92809 | -0.021596 |  | 0.93 | 1.05 | 0.096534 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-352 | BURLNGTNJCT2 | 0.94968 | 0.92809 | -0.021596 |  | 0.93 | 1.05 | 0.064307 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-370 | BURLNGTNJCT2 | 0.94968 | 0.92809 | -0.021596 |  | 0.93 | 1.05 | 0.10618 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | ASGI-2024-003 | DVRSION-WIND | 1.0349 | 1.0705 | 0.035561 |  | 0.92 | 1.05 | 0.033223 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | None
Voltage | 03ALL | 2 | 29SP | V | ASGI-2024-006 | DVRSION-WIND | 1.0349 | 1.0705 | 0.035561 |  | 0.92 | 1.05 | 0.069949 | Single 511456 O.K.U.-7 345 511607 O.K.U.3-7 345 Z1 | None
Voltage | 03ALL | 2 | 29SP | V | ASGI-2024-024 | FAIRFAX2 | 0.93559 | 0.90024 | -0.035345 |  | 0.93 | 1.05 | 0.13302 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-054 | FAIRFAX2 | 0.93559 | 0.90024 | -0.035345 |  | 0.93 | 1.05 | 0.040787 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-055 | FAIRFAX2 | 0.93559 | 0.90024 | -0.035345 |  | 0.93 | 1.05 | 0.046288 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-074 | FAIRFAX2 | 0.93559 | 0.90024 | -0.035345 |  | 0.93 | 1.05 | 0.067254 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-076 | FAIRFAX2 | 0.93559 | 0.90024 | -0.035345 |  | 0.93 | 1.05 | 0.035421 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-090 | FAIRFAX2 | 0.93559 | 0.90024 | -0.035345 |  | 0.93 | 1.05 | 0.073349 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-139 | FAIRFAX2 | 0.93559 | 0.90024 | -0.035345 |  | 0.93 | 1.05 | 0.034571 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-170 | FAIRFAX2 | 0.93559 | 0.90024 | -0.035345 |  | 0.93 | 1.05 | 0.073415 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-253 | FAIRFAX2 | 0.93559 | 0.90024 | -0.035345 |  | 0.93 | 1.05 | 0.070344 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-258 | FAIRFAX2 | 0.93559 | 0.90024 | -0.035345 |  | 0.93 | 1.05 | 0.032402 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-260 | FAIRFAX2 | 0.93559 | 0.90024 | -0.035345 |  | 0.93 | 1.05 | 0.13211 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-276 | FAIRFAX2 | 0.93559 | 0.90024 | -0.035345 |  | 0.93 | 1.05 | 0.050915 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-277 | FAIRFAX2 | 0.93559 | 0.90024 | -0.035345 |  | 0.93 | 1.05 | 0.050915 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-287 | FAIRFAX2 | 0.93559 | 0.90024 | -0.035345 |  | 0.93 | 1.05 | 0.030578 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-319 | FAIRFAX2 | 0.93559 | 0.90024 | -0.035345 |  | 0.93 | 1.05 | 0.059767 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-320 | FAIRFAX2 | 0.93559 | 0.90024 | -0.035345 |  | 0.93 | 1.05 | 0.06434 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-339 | FAIRFAX2 | 0.93559 | 0.90024 | -0.035345 |  | 0.93 | 1.05 | 0.074026 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-352 | FAIRFAX2 | 0.93559 | 0.90024 | -0.035345 |  | 0.93 | 1.05 | 0.10772 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-370 | FAIRFAX2 | 0.93559 | 0.90024 | -0.035345 |  | 0.93 | 1.05 | 0.073349 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | ASGI-2024-024 | FAIRFAX2 | 0.93937 | 0.91738 | -0.021982 |  | 0.93 | 1.05 | 0.1874 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-054 | FAIRFAX2 | 0.93937 | 0.91738 | -0.021982 |  | 0.93 | 1.05 | 0.032663 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-055 | FAIRFAX2 | 0.93937 | 0.91738 | -0.021982 |  | 0.93 | 1.05 | 0.052451 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-074 | FAIRFAX2 | 0.93937 | 0.91738 | -0.021982 |  | 0.93 | 1.05 | 0.072212 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-076 | FAIRFAX2 | 0.93937 | 0.91738 | -0.021982 |  | 0.93 | 1.05 | 0.042339 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-090 | FAIRFAX2 | 0.93937 | 0.91738 | -0.021982 |  | 0.93 | 1.05 | 0.10618 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-139 | FAIRFAX2 | 0.93937 | 0.91738 | -0.021982 |  | 0.93 | 1.05 | 0.038127 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-170 | FAIRFAX2 | 0.93937 | 0.91738 | -0.021982 |  | 0.93 | 1.05 | 0.065102 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-253 | FAIRFAX2 | 0.93937 | 0.91738 | -0.021982 |  | 0.93 | 1.05 | 0.095208 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-258 | FAIRFAX2 | 0.93937 | 0.91738 | -0.021982 |  | 0.93 | 1.05 | 0.035057 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-260 | FAIRFAX2 | 0.93937 | 0.91738 | -0.021982 |  | 0.93 | 1.05 | 0.18643 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-276 | FAIRFAX2 | 0.93937 | 0.91738 | -0.021982 |  | 0.93 | 1.05 | 0.053424 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-277 | FAIRFAX2 | 0.93937 | 0.91738 | -0.021982 |  | 0.93 | 1.05 | 0.053424 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-287 | FAIRFAX2 | 0.93937 | 0.91738 | -0.021982 |  | 0.93 | 1.05 | 0.032476 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-319 | FAIRFAX2 | 0.93937 | 0.91738 | -0.021982 |  | 0.93 | 1.05 | 0.084299 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-320 | FAIRFAX2 | 0.93937 | 0.91738 | -0.021982 |  | 0.93 | 1.05 | 0.084751 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-339 | FAIRFAX2 | 0.93937 | 0.91738 | -0.021982 |  | 0.93 | 1.05 | 0.096534 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-352 | FAIRFAX2 | 0.93937 | 0.91738 | -0.021982 |  | 0.93 | 1.05 | 0.064307 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-370 | FAIRFAX2 | 0.93937 | 0.91738 | -0.021982 |  | 0.93 | 1.05 | 0.10618 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | ASGI-2024-024 | FILLMORE_TP2 | 0.95521 | 0.92111 | -0.034108 |  | 0.93 | 1.05 | 0.13302 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-054 | FILLMORE_TP2 | 0.95521 | 0.92111 | -0.034108 |  | 0.93 | 1.05 | 0.040787 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-055 | FILLMORE_TP2 | 0.95521 | 0.92111 | -0.034108 |  | 0.93 | 1.05 | 0.046288 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-074 | FILLMORE_TP2 | 0.95521 | 0.92111 | -0.034108 |  | 0.93 | 1.05 | 0.067254 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-076 | FILLMORE_TP2 | 0.95521 | 0.92111 | -0.034108 |  | 0.93 | 1.05 | 0.035421 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-090 | FILLMORE_TP2 | 0.95521 | 0.92111 | -0.034108 |  | 0.93 | 1.05 | 0.073349 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-139 | FILLMORE_TP2 | 0.95521 | 0.92111 | -0.034108 |  | 0.93 | 1.05 | 0.034571 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-170 | FILLMORE_TP2 | 0.95521 | 0.92111 | -0.034108 |  | 0.93 | 1.05 | 0.073415 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-253 | FILLMORE_TP2 | 0.95521 | 0.92111 | -0.034108 |  | 0.93 | 1.05 | 0.070344 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-258 | FILLMORE_TP2 | 0.95521 | 0.92111 | -0.034108 |  | 0.93 | 1.05 | 0.032402 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-260 | FILLMORE_TP2 | 0.95521 | 0.92111 | -0.034108 |  | 0.93 | 1.05 | 0.13211 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-276 | FILLMORE_TP2 | 0.95521 | 0.92111 | -0.034108 |  | 0.93 | 1.05 | 0.050915 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-277 | FILLMORE_TP2 | 0.95521 | 0.92111 | -0.034108 |  | 0.93 | 1.05 | 0.050915 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-287 | FILLMORE_TP2 | 0.95521 | 0.92111 | -0.034108 |  | 0.93 | 1.05 | 0.030578 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-319 | FILLMORE_TP2 | 0.95521 | 0.92111 | -0.034108 |  | 0.93 | 1.05 | 0.059767 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-320 | FILLMORE_TP2 | 0.95521 | 0.92111 | -0.034108 |  | 0.93 | 1.05 | 0.06434 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-339 | FILLMORE_TP2 | 0.95521 | 0.92111 | -0.034108 |  | 0.93 | 1.05 | 0.074026 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-352 | FILLMORE_TP2 | 0.95521 | 0.92111 | -0.034108 |  | 0.93 | 1.05 | 0.10772 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-370 | FILLMORE_TP2 | 0.95521 | 0.92111 | -0.034108 |  | 0.93 | 1.05 | 0.073349 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | ASGI-2024-024 | FILMORE2 | 0.95403 | 0.91988 | -0.034152 |  | 0.93 | 1.05 | 0.13302 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-054 | FILMORE2 | 0.95403 | 0.91988 | -0.034152 |  | 0.93 | 1.05 | 0.040787 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-055 | FILMORE2 | 0.95403 | 0.91988 | -0.034152 |  | 0.93 | 1.05 | 0.046288 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-074 | FILMORE2 | 0.95403 | 0.91988 | -0.034152 |  | 0.93 | 1.05 | 0.067254 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-076 | FILMORE2 | 0.95403 | 0.91988 | -0.034152 |  | 0.93 | 1.05 | 0.035421 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-090 | FILMORE2 | 0.95403 | 0.91988 | -0.034152 |  | 0.93 | 1.05 | 0.073349 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-139 | FILMORE2 | 0.95403 | 0.91988 | -0.034152 |  | 0.93 | 1.05 | 0.034571 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-170 | FILMORE2 | 0.95403 | 0.91988 | -0.034152 |  | 0.93 | 1.05 | 0.073415 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-253 | FILMORE2 | 0.95403 | 0.91988 | -0.034152 |  | 0.93 | 1.05 | 0.070344 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-258 | FILMORE2 | 0.95403 | 0.91988 | -0.034152 |  | 0.93 | 1.05 | 0.032402 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-260 | FILMORE2 | 0.95403 | 0.91988 | -0.034152 |  | 0.93 | 1.05 | 0.13211 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-276 | FILMORE2 | 0.95403 | 0.91988 | -0.034152 |  | 0.93 | 1.05 | 0.050915 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-277 | FILMORE2 | 0.95403 | 0.91988 | -0.034152 |  | 0.93 | 1.05 | 0.050915 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-287 | FILMORE2 | 0.95403 | 0.91988 | -0.034152 |  | 0.93 | 1.05 | 0.030578 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-319 | FILMORE2 | 0.95403 | 0.91988 | -0.034152 |  | 0.93 | 1.05 | 0.059767 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-320 | FILMORE2 | 0.95403 | 0.91988 | -0.034152 |  | 0.93 | 1.05 | 0.06434 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-339 | FILMORE2 | 0.95403 | 0.91988 | -0.034152 |  | 0.93 | 1.05 | 0.074026 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-352 | FILMORE2 | 0.95403 | 0.91988 | -0.034152 |  | 0.93 | 1.05 | 0.10772 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-370 | FILMORE2 | 0.95403 | 0.91988 | -0.034152 |  | 0.93 | 1.05 | 0.073349 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | ASGI-2024-024 | G20-094-TAP | 0.99103 | 0.94764 | -0.043386 |  | 0.95 | 1.05 | 0.13302 | P55:345:OPPD:S3458 3::FN13:EHV: | None
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-054 | G20-094-TAP | 0.99103 | 0.94764 | -0.043386 |  | 0.95 | 1.05 | 0.040787 | P55:345:OPPD:S3458 3::FN13:EHV: | None
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-055 | G20-094-TAP | 0.99103 | 0.94764 | -0.043386 |  | 0.95 | 1.05 | 0.046288 | P55:345:OPPD:S3458 3::FN13:EHV: | None
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-074 | G20-094-TAP | 0.99103 | 0.94764 | -0.043386 |  | 0.95 | 1.05 | 0.067254 | P55:345:OPPD:S3458 3::FN13:EHV: | None
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-076 | G20-094-TAP | 0.99103 | 0.94764 | -0.043386 |  | 0.95 | 1.05 | 0.035421 | P55:345:OPPD:S3458 3::FN13:EHV: | None
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-090 | G20-094-TAP | 0.99103 | 0.94764 | -0.043386 |  | 0.95 | 1.05 | 0.073349 | P55:345:OPPD:S3458 3::FN13:EHV: | None
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-139 | G20-094-TAP | 0.99103 | 0.94764 | -0.043386 |  | 0.95 | 1.05 | 0.034571 | P55:345:OPPD:S3458 3::FN13:EHV: | None
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-170 | G20-094-TAP | 0.99103 | 0.94764 | -0.043386 |  | 0.95 | 1.05 | 0.073415 | P55:345:OPPD:S3458 3::FN13:EHV: | None
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-253 | G20-094-TAP | 0.99103 | 0.94764 | -0.043386 |  | 0.95 | 1.05 | 0.070344 | P55:345:OPPD:S3458 3::FN13:EHV: | None
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-258 | G20-094-TAP | 0.99103 | 0.94764 | -0.043386 |  | 0.95 | 1.05 | 0.032402 | P55:345:OPPD:S3458 3::FN13:EHV: | None
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-260 | G20-094-TAP | 0.99103 | 0.94764 | -0.043386 |  | 0.95 | 1.05 | 0.13211 | P55:345:OPPD:S3458 3::FN13:EHV: | None
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-276 | G20-094-TAP | 0.99103 | 0.94764 | -0.043386 |  | 0.95 | 1.05 | 0.050915 | P55:345:OPPD:S3458 3::FN13:EHV: | None
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-277 | G20-094-TAP | 0.99103 | 0.94764 | -0.043386 |  | 0.95 | 1.05 | 0.050915 | P55:345:OPPD:S3458 3::FN13:EHV: | None
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-287 | G20-094-TAP | 0.99103 | 0.94764 | -0.043386 |  | 0.95 | 1.05 | 0.030578 | P55:345:OPPD:S3458 3::FN13:EHV: | None
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-319 | G20-094-TAP | 0.99103 | 0.94764 | -0.043386 |  | 0.95 | 1.05 | 0.059767 | P55:345:OPPD:S3458 3::FN13:EHV: | None
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-320 | G20-094-TAP | 0.99103 | 0.94764 | -0.043386 |  | 0.95 | 1.05 | 0.06434 | P55:345:OPPD:S3458 3::FN13:EHV: | None
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-339 | G20-094-TAP | 0.99103 | 0.94764 | -0.043386 |  | 0.95 | 1.05 | 0.074026 | P55:345:OPPD:S3458 3::FN13:EHV: | None
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-352 | G20-094-TAP | 0.99103 | 0.94764 | -0.043386 |  | 0.95 | 1.05 | 0.10772 | P55:345:OPPD:S3458 3::FN13:EHV: | None
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-370 | G20-094-TAP | 0.99103 | 0.94764 | -0.043386 |  | 0.95 | 1.05 | 0.073349 | P55:345:OPPD:S3458 3::FN13:EHV: | None
Voltage | 03ALL | 2 | 29SP | V | ASGI-2024-024 | GEN-2020-094 | 0.99103 | 0.94764 | -0.043386 |  | 0.95 | 1.05 | 0.13302 | P55:345:OPPD:S3458 3::FN13:EHV: | None
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-054 | GEN-2020-094 | 0.99103 | 0.94764 | -0.043386 |  | 0.95 | 1.05 | 0.040787 | P55:345:OPPD:S3458 3::FN13:EHV: | None
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-055 | GEN-2020-094 | 0.99103 | 0.94764 | -0.043386 |  | 0.95 | 1.05 | 0.046288 | P55:345:OPPD:S3458 3::FN13:EHV: | None
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-074 | GEN-2020-094 | 0.99103 | 0.94764 | -0.043386 |  | 0.95 | 1.05 | 0.067254 | P55:345:OPPD:S3458 3::FN13:EHV: | None
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-076 | GEN-2020-094 | 0.99103 | 0.94764 | -0.043386 |  | 0.95 | 1.05 | 0.035421 | P55:345:OPPD:S3458 3::FN13:EHV: | None
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-090 | GEN-2020-094 | 0.99103 | 0.94764 | -0.043386 |  | 0.95 | 1.05 | 0.073349 | P55:345:OPPD:S3458 3::FN13:EHV: | None
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-139 | GEN-2020-094 | 0.99103 | 0.94764 | -0.043386 |  | 0.95 | 1.05 | 0.034571 | P55:345:OPPD:S3458 3::FN13:EHV: | None
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-170 | GEN-2020-094 | 0.99103 | 0.94764 | -0.043386 |  | 0.95 | 1.05 | 0.073415 | P55:345:OPPD:S3458 3::FN13:EHV: | None
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-253 | GEN-2020-094 | 0.99103 | 0.94764 | -0.043386 |  | 0.95 | 1.05 | 0.070344 | P55:345:OPPD:S3458 3::FN13:EHV: | None
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-258 | GEN-2020-094 | 0.99103 | 0.94764 | -0.043386 |  | 0.95 | 1.05 | 0.032402 | P55:345:OPPD:S3458 3::FN13:EHV: | None
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-260 | GEN-2020-094 | 0.99103 | 0.94764 | -0.043386 |  | 0.95 | 1.05 | 0.13211 | P55:345:OPPD:S3458 3::FN13:EHV: | None
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-276 | GEN-2020-094 | 0.99103 | 0.94764 | -0.043386 |  | 0.95 | 1.05 | 0.050915 | P55:345:OPPD:S3458 3::FN13:EHV: | None
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-277 | GEN-2020-094 | 0.99103 | 0.94764 | -0.043386 |  | 0.95 | 1.05 | 0.050915 | P55:345:OPPD:S3458 3::FN13:EHV: | None
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-287 | GEN-2020-094 | 0.99103 | 0.94764 | -0.043386 |  | 0.95 | 1.05 | 0.030578 | P55:345:OPPD:S3458 3::FN13:EHV: | None
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-319 | GEN-2020-094 | 0.99103 | 0.94764 | -0.043386 |  | 0.95 | 1.05 | 0.059767 | P55:345:OPPD:S3458 3::FN13:EHV: | None
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-320 | GEN-2020-094 | 0.99103 | 0.94764 | -0.043386 |  | 0.95 | 1.05 | 0.06434 | P55:345:OPPD:S3458 3::FN13:EHV: | None
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-339 | GEN-2020-094 | 0.99103 | 0.94764 | -0.043386 |  | 0.95 | 1.05 | 0.074026 | P55:345:OPPD:S3458 3::FN13:EHV: | None
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-352 | GEN-2020-094 | 0.99103 | 0.94764 | -0.043386 |  | 0.95 | 1.05 | 0.10772 | P55:345:OPPD:S3458 3::FN13:EHV: | None
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-370 | GEN-2020-094 | 0.99103 | 0.94764 | -0.043386 |  | 0.95 | 1.05 | 0.073349 | P55:345:OPPD:S3458 3::FN13:EHV: | None
Voltage | 03ALL | 2 | 29SP | V | ASGI-2024-024 | HUMBOLT5 | 0.989 | 0.93682 | -0.052189 |  | 0.95 | 1.05 | 0.13302 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-054 | HUMBOLT5 | 0.989 | 0.93682 | -0.052189 |  | 0.95 | 1.05 | 0.040787 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-055 | HUMBOLT5 | 0.989 | 0.93682 | -0.052189 |  | 0.95 | 1.05 | 0.046288 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-074 | HUMBOLT5 | 0.989 | 0.93682 | -0.052189 |  | 0.95 | 1.05 | 0.067254 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-076 | HUMBOLT5 | 0.989 | 0.93682 | -0.052189 |  | 0.95 | 1.05 | 0.035421 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-090 | HUMBOLT5 | 0.989 | 0.93682 | -0.052189 |  | 0.95 | 1.05 | 0.073349 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-139 | HUMBOLT5 | 0.989 | 0.93682 | -0.052189 |  | 0.95 | 1.05 | 0.034571 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-170 | HUMBOLT5 | 0.989 | 0.93682 | -0.052189 |  | 0.95 | 1.05 | 0.073415 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-253 | HUMBOLT5 | 0.989 | 0.93682 | -0.052189 |  | 0.95 | 1.05 | 0.070344 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-258 | HUMBOLT5 | 0.989 | 0.93682 | -0.052189 |  | 0.95 | 1.05 | 0.032402 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-260 | HUMBOLT5 | 0.989 | 0.93682 | -0.052189 |  | 0.95 | 1.05 | 0.13211 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-276 | HUMBOLT5 | 0.989 | 0.93682 | -0.052189 |  | 0.95 | 1.05 | 0.050915 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-277 | HUMBOLT5 | 0.989 | 0.93682 | -0.052189 |  | 0.95 | 1.05 | 0.050915 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-287 | HUMBOLT5 | 0.989 | 0.93682 | -0.052189 |  | 0.95 | 1.05 | 0.030578 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-319 | HUMBOLT5 | 0.989 | 0.93682 | -0.052189 |  | 0.95 | 1.05 | 0.059767 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-320 | HUMBOLT5 | 0.989 | 0.93682 | -0.052189 |  | 0.95 | 1.05 | 0.06434 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-339 | HUMBOLT5 | 0.989 | 0.93682 | -0.052189 |  | 0.95 | 1.05 | 0.074026 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-352 | HUMBOLT5 | 0.989 | 0.93682 | -0.052189 |  | 0.95 | 1.05 | 0.10772 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-370 | HUMBOLT5 | 0.989 | 0.93682 | -0.052189 |  | 0.95 | 1.05 | 0.073349 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | ASGI-2024-024 | MRVL#2 | 0.95582 | 0.92174 | -0.034085 |  | 0.93 | 1.05 | 0.13302 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-054 | MRVL#2 | 0.95582 | 0.92174 | -0.034085 |  | 0.93 | 1.05 | 0.040787 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-055 | MRVL#2 | 0.95582 | 0.92174 | -0.034085 |  | 0.93 | 1.05 | 0.046288 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-074 | MRVL#2 | 0.95582 | 0.92174 | -0.034085 |  | 0.93 | 1.05 | 0.067254 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-076 | MRVL#2 | 0.95582 | 0.92174 | -0.034085 |  | 0.93 | 1.05 | 0.035421 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-090 | MRVL#2 | 0.95582 | 0.92174 | -0.034085 |  | 0.93 | 1.05 | 0.073349 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-139 | MRVL#2 | 0.95582 | 0.92174 | -0.034085 |  | 0.93 | 1.05 | 0.034571 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-170 | MRVL#2 | 0.95582 | 0.92174 | -0.034085 |  | 0.93 | 1.05 | 0.073415 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-253 | MRVL#2 | 0.95582 | 0.92174 | -0.034085 |  | 0.93 | 1.05 | 0.070344 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-258 | MRVL#2 | 0.95582 | 0.92174 | -0.034085 |  | 0.93 | 1.05 | 0.032402 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-260 | MRVL#2 | 0.95582 | 0.92174 | -0.034085 |  | 0.93 | 1.05 | 0.13211 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-276 | MRVL#2 | 0.95582 | 0.92174 | -0.034085 |  | 0.93 | 1.05 | 0.050915 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-277 | MRVL#2 | 0.95582 | 0.92174 | -0.034085 |  | 0.93 | 1.05 | 0.050915 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-287 | MRVL#2 | 0.95582 | 0.92174 | -0.034085 |  | 0.93 | 1.05 | 0.030578 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-319 | MRVL#2 | 0.95582 | 0.92174 | -0.034085 |  | 0.93 | 1.05 | 0.059767 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-320 | MRVL#2 | 0.95582 | 0.92174 | -0.034085 |  | 0.93 | 1.05 | 0.06434 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-339 | MRVL#2 | 0.95582 | 0.92174 | -0.034085 |  | 0.93 | 1.05 | 0.074026 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-352 | MRVL#2 | 0.95582 | 0.92174 | -0.034085 |  | 0.93 | 1.05 | 0.10772 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-370 | MRVL#2 | 0.95582 | 0.92174 | -0.034085 |  | 0.93 | 1.05 | 0.073349 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | ASGI-2024-024 | NC1HS 5 | 0.98719 | 0.94039 | -0.046804 |  | 0.95 | 1.05 | 0.13302 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-054 | NC1HS 5 | 0.98719 | 0.94039 | -0.046804 |  | 0.95 | 1.05 | 0.040787 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-055 | NC1HS 5 | 0.98719 | 0.94039 | -0.046804 |  | 0.95 | 1.05 | 0.046288 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-074 | NC1HS 5 | 0.98719 | 0.94039 | -0.046804 |  | 0.95 | 1.05 | 0.067254 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-076 | NC1HS 5 | 0.98719 | 0.94039 | -0.046804 |  | 0.95 | 1.05 | 0.035421 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-090 | NC1HS 5 | 0.98719 | 0.94039 | -0.046804 |  | 0.95 | 1.05 | 0.073349 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-139 | NC1HS 5 | 0.98719 | 0.94039 | -0.046804 |  | 0.95 | 1.05 | 0.034571 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-170 | NC1HS 5 | 0.98719 | 0.94039 | -0.046804 |  | 0.95 | 1.05 | 0.073415 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-253 | NC1HS 5 | 0.98719 | 0.94039 | -0.046804 |  | 0.95 | 1.05 | 0.070344 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-258 | NC1HS 5 | 0.98719 | 0.94039 | -0.046804 |  | 0.95 | 1.05 | 0.032402 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-260 | NC1HS 5 | 0.98719 | 0.94039 | -0.046804 |  | 0.95 | 1.05 | 0.13211 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-276 | NC1HS 5 | 0.98719 | 0.94039 | -0.046804 |  | 0.95 | 1.05 | 0.050915 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-277 | NC1HS 5 | 0.98719 | 0.94039 | -0.046804 |  | 0.95 | 1.05 | 0.050915 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-287 | NC1HS 5 | 0.98719 | 0.94039 | -0.046804 |  | 0.95 | 1.05 | 0.030578 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-319 | NC1HS 5 | 0.98719 | 0.94039 | -0.046804 |  | 0.95 | 1.05 | 0.059767 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-320 | NC1HS 5 | 0.98719 | 0.94039 | -0.046804 |  | 0.95 | 1.05 | 0.06434 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-339 | NC1HS 5 | 0.98719 | 0.94039 | -0.046804 |  | 0.95 | 1.05 | 0.074026 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-352 | NC1HS 5 | 0.98719 | 0.94039 | -0.046804 |  | 0.95 | 1.05 | 0.10772 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-370 | NC1HS 5 | 0.98719 | 0.94039 | -0.046804 |  | 0.95 | 1.05 | 0.073349 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | ASGI-2024-024 | NC2HS 5 | 0.98719 | 0.94039 | -0.046804 |  | 0.95 | 1.05 | 0.13302 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-054 | NC2HS 5 | 0.98719 | 0.94039 | -0.046804 |  | 0.95 | 1.05 | 0.040787 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-055 | NC2HS 5 | 0.98719 | 0.94039 | -0.046804 |  | 0.95 | 1.05 | 0.046288 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-074 | NC2HS 5 | 0.98719 | 0.94039 | -0.046804 |  | 0.95 | 1.05 | 0.067254 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-076 | NC2HS 5 | 0.98719 | 0.94039 | -0.046804 |  | 0.95 | 1.05 | 0.035421 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-090 | NC2HS 5 | 0.98719 | 0.94039 | -0.046804 |  | 0.95 | 1.05 | 0.073349 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-139 | NC2HS 5 | 0.98719 | 0.94039 | -0.046804 |  | 0.95 | 1.05 | 0.034571 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-170 | NC2HS 5 | 0.98719 | 0.94039 | -0.046804 |  | 0.95 | 1.05 | 0.073415 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-253 | NC2HS 5 | 0.98719 | 0.94039 | -0.046804 |  | 0.95 | 1.05 | 0.070344 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-258 | NC2HS 5 | 0.98719 | 0.94039 | -0.046804 |  | 0.95 | 1.05 | 0.032402 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-260 | NC2HS 5 | 0.98719 | 0.94039 | -0.046804 |  | 0.95 | 1.05 | 0.13211 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-276 | NC2HS 5 | 0.98719 | 0.94039 | -0.046804 |  | 0.95 | 1.05 | 0.050915 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-277 | NC2HS 5 | 0.98719 | 0.94039 | -0.046804 |  | 0.95 | 1.05 | 0.050915 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-287 | NC2HS 5 | 0.98719 | 0.94039 | -0.046804 |  | 0.95 | 1.05 | 0.030578 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-319 | NC2HS 5 | 0.98719 | 0.94039 | -0.046804 |  | 0.95 | 1.05 | 0.059767 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-320 | NC2HS 5 | 0.98719 | 0.94039 | -0.046804 |  | 0.95 | 1.05 | 0.06434 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-339 | NC2HS 5 | 0.98719 | 0.94039 | -0.046804 |  | 0.95 | 1.05 | 0.074026 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-352 | NC2HS 5 | 0.98719 | 0.94039 | -0.046804 |  | 0.95 | 1.05 | 0.10772 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-370 | NC2HS 5 | 0.98719 | 0.94039 | -0.046804 |  | 0.95 | 1.05 | 0.073349 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | ASGI-2024-003 | NP-GLAZIR_G2 | 0.71549 | 0.67076 | -0.044733 |  | 0.9 | 1.05 | 0.10368 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | ASGI-2024-006 | NP-GLAZIR_G2 | 0.71549 | 0.67076 | -0.044733 |  | 0.9 | 1.05 | 0.077176 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-067 | NP-GLAZIR_G2 | 0.71549 | 0.67076 | -0.044733 |  | 0.9 | 1.05 | 0.03818 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-205 | NP-GLAZIR_G2 | 0.71549 | 0.67076 | -0.044733 |  | 0.9 | 1.05 | 0.053685 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-215 | NP-GLAZIR_G2 | 0.71549 | 0.67076 | -0.044733 |  | 0.9 | 1.05 | 0.038922 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-067 | NP-GLAZIR_G2 | 0.71588 | 0.67115 | -0.044735 |  | 0.9 | 1.05 | 0.03818 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-205 | NP-GLAZIR_G2 | 0.71588 | 0.67115 | -0.044735 |  | 0.9 | 1.05 | 0.053685 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-215 | NP-GLAZIR_G2 | 0.71588 | 0.67115 | -0.044735 |  | 0.9 | 1.05 | 0.038922 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-067 | NP-GLAZIR_G2 | 0.71588 | 0.67115 | -0.044735 |  | 0.9 | 1.05 | 0.03818 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-205 | NP-GLAZIR_G2 | 0.71588 | 0.67115 | -0.044735 |  | 0.9 | 1.05 | 0.053685 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-215 | NP-GLAZIR_G2 | 0.71588 | 0.67115 | -0.044735 |  | 0.9 | 1.05 | 0.038922 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-067 | NP-GLAZIR_G2 | 0.71588 | 0.67115 | -0.044735 |  | 0.9 | 1.05 | 0.03818 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-205 | NP-GLAZIR_G2 | 0.71588 | 0.67115 | -0.044735 |  | 0.9 | 1.05 | 0.053685 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-215 | NP-GLAZIR_G2 | 0.71588 | 0.67115 | -0.044735 |  | 0.9 | 1.05 | 0.038922 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-067 | NP-GLAZIR_G2 | 0.71655 | 0.67239 | -0.044159 |  | 0.9 | 1.05 | 0.03818 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-166 | NP-GLAZIR_G2 | 0.71655 | 0.67239 | -0.044159 |  | 0.9 | 1.05 | 0.041651 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-205 | NP-GLAZIR_G2 | 0.71655 | 0.67239 | -0.044159 |  | 0.9 | 1.05 | 0.065404 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-215 | NP-GLAZIR_G2 | 0.71655 | 0.67239 | -0.044159 |  | 0.9 | 1.05 | 0.038922 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-330 | NP-GLAZIR_G2 | 0.71655 | 0.67239 | -0.044159 |  | 0.9 | 1.05 | 0.037455 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | ASGI-2024-003 | NP-LIPSCOMB2 | 0.67637 | 0.62964 | -0.04673 |  | 0.9 | 1.05 | 0.10368 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | ASGI-2024-006 | NP-LIPSCOMB2 | 0.67637 | 0.62964 | -0.04673 |  | 0.9 | 1.05 | 0.077176 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-067 | NP-LIPSCOMB2 | 0.67637 | 0.62964 | -0.04673 |  | 0.9 | 1.05 | 0.03818 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-205 | NP-LIPSCOMB2 | 0.67637 | 0.62964 | -0.04673 |  | 0.9 | 1.05 | 0.053685 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-215 | NP-LIPSCOMB2 | 0.67637 | 0.62964 | -0.04673 |  | 0.9 | 1.05 | 0.038922 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-067 | NP-LIPSCOMB2 | 0.67678 | 0.63004 | -0.046738 |  | 0.9 | 1.05 | 0.03818 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-205 | NP-LIPSCOMB2 | 0.67678 | 0.63004 | -0.046738 |  | 0.9 | 1.05 | 0.053685 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-215 | NP-LIPSCOMB2 | 0.67678 | 0.63004 | -0.046738 |  | 0.9 | 1.05 | 0.038922 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-067 | NP-LIPSCOMB2 | 0.67678 | 0.63004 | -0.046738 |  | 0.9 | 1.05 | 0.03818 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-205 | NP-LIPSCOMB2 | 0.67678 | 0.63004 | -0.046738 |  | 0.9 | 1.05 | 0.053685 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-215 | NP-LIPSCOMB2 | 0.67678 | 0.63004 | -0.046738 |  | 0.9 | 1.05 | 0.038922 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-067 | NP-LIPSCOMB2 | 0.67678 | 0.63004 | -0.046738 |  | 0.9 | 1.05 | 0.03818 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-205 | NP-LIPSCOMB2 | 0.67678 | 0.63004 | -0.046738 |  | 0.9 | 1.05 | 0.053685 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-215 | NP-LIPSCOMB2 | 0.67678 | 0.63004 | -0.046738 |  | 0.9 | 1.05 | 0.038922 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-067 | NP-LIPSCOMB2 | 0.67748 | 0.63133 | -0.04615 |  | 0.9 | 1.05 | 0.03818 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-166 | NP-LIPSCOMB2 | 0.67748 | 0.63133 | -0.04615 |  | 0.9 | 1.05 | 0.041651 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-205 | NP-LIPSCOMB2 | 0.67748 | 0.63133 | -0.04615 |  | 0.9 | 1.05 | 0.065404 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-215 | NP-LIPSCOMB2 | 0.67748 | 0.63133 | -0.04615 |  | 0.9 | 1.05 | 0.038922 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-330 | NP-LIPSCOMB2 | 0.67748 | 0.63133 | -0.04615 |  | 0.9 | 1.05 | 0.037455 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | ASGI-2024-003 | NP-LIPS_SHA2 | 0.67637 | 0.62964 | -0.04673 |  | 0.9 | 1.05 | 0.10368 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | ASGI-2024-006 | NP-LIPS_SHA2 | 0.67637 | 0.62964 | -0.04673 |  | 0.9 | 1.05 | 0.077176 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-067 | NP-LIPS_SHA2 | 0.67637 | 0.62964 | -0.04673 |  | 0.9 | 1.05 | 0.03818 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-205 | NP-LIPS_SHA2 | 0.67637 | 0.62964 | -0.04673 |  | 0.9 | 1.05 | 0.053685 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-215 | NP-LIPS_SHA2 | 0.67637 | 0.62964 | -0.04673 |  | 0.9 | 1.05 | 0.038922 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-067 | NP-LIPS_SHA2 | 0.67678 | 0.63004 | -0.046738 |  | 0.9 | 1.05 | 0.03818 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-205 | NP-LIPS_SHA2 | 0.67678 | 0.63004 | -0.046738 |  | 0.9 | 1.05 | 0.053685 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-215 | NP-LIPS_SHA2 | 0.67678 | 0.63004 | -0.046738 |  | 0.9 | 1.05 | 0.038922 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-067 | NP-LIPS_SHA2 | 0.67678 | 0.63004 | -0.046738 |  | 0.9 | 1.05 | 0.03818 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-205 | NP-LIPS_SHA2 | 0.67678 | 0.63004 | -0.046738 |  | 0.9 | 1.05 | 0.053685 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-215 | NP-LIPS_SHA2 | 0.67678 | 0.63004 | -0.046738 |  | 0.9 | 1.05 | 0.038922 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-067 | NP-LIPS_SHA2 | 0.67678 | 0.63004 | -0.046738 |  | 0.9 | 1.05 | 0.03818 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-205 | NP-LIPS_SHA2 | 0.67678 | 0.63004 | -0.046738 |  | 0.9 | 1.05 | 0.053685 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-215 | NP-LIPS_SHA2 | 0.67678 | 0.63004 | -0.046738 |  | 0.9 | 1.05 | 0.038922 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-067 | NP-LIPS_SHA2 | 0.67748 | 0.63133 | -0.04615 |  | 0.9 | 1.05 | 0.03818 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-166 | NP-LIPS_SHA2 | 0.67748 | 0.63133 | -0.04615 |  | 0.9 | 1.05 | 0.041651 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-205 | NP-LIPS_SHA2 | 0.67748 | 0.63133 | -0.04615 |  | 0.9 | 1.05 | 0.065404 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-215 | NP-LIPS_SHA2 | 0.67748 | 0.63133 | -0.04615 |  | 0.9 | 1.05 | 0.038922 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-330 | NP-LIPS_SHA2 | 0.67748 | 0.63133 | -0.04615 |  | 0.9 | 1.05 | 0.037455 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | ASGI-2024-003 | NP-LUCKY_CR2 | 0.8066 | 0.76718 | -0.03942 |  | 0.9 | 1.05 | 0.10368 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | ASGI-2024-006 | NP-LUCKY_CR2 | 0.8066 | 0.76718 | -0.03942 |  | 0.9 | 1.05 | 0.077176 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-067 | NP-LUCKY_CR2 | 0.8066 | 0.76718 | -0.03942 |  | 0.9 | 1.05 | 0.03818 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-205 | NP-LUCKY_CR2 | 0.8066 | 0.76718 | -0.03942 |  | 0.9 | 1.05 | 0.053685 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-215 | NP-LUCKY_CR2 | 0.8066 | 0.76718 | -0.03942 |  | 0.9 | 1.05 | 0.038922 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-067 | NP-LUCKY_CR2 | 0.80694 | 0.76753 | -0.039408 |  | 0.9 | 1.05 | 0.03818 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-205 | NP-LUCKY_CR2 | 0.80694 | 0.76753 | -0.039408 |  | 0.9 | 1.05 | 0.053685 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-215 | NP-LUCKY_CR2 | 0.80694 | 0.76753 | -0.039408 |  | 0.9 | 1.05 | 0.038922 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-067 | NP-LUCKY_CR2 | 0.80694 | 0.76753 | -0.039408 |  | 0.9 | 1.05 | 0.03818 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-205 | NP-LUCKY_CR2 | 0.80694 | 0.76753 | -0.039408 |  | 0.9 | 1.05 | 0.053685 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-215 | NP-LUCKY_CR2 | 0.80694 | 0.76753 | -0.039408 |  | 0.9 | 1.05 | 0.038922 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-067 | NP-LUCKY_CR2 | 0.80694 | 0.76753 | -0.039408 |  | 0.9 | 1.05 | 0.03818 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-205 | NP-LUCKY_CR2 | 0.80694 | 0.76753 | -0.039408 |  | 0.9 | 1.05 | 0.053685 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-215 | NP-LUCKY_CR2 | 0.80694 | 0.76753 | -0.039408 |  | 0.9 | 1.05 | 0.038922 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-067 | NP-LUCKY_CR2 | 0.80751 | 0.76865 | -0.038867 |  | 0.9 | 1.05 | 0.03818 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-166 | NP-LUCKY_CR2 | 0.80751 | 0.76865 | -0.038867 |  | 0.9 | 1.05 | 0.041651 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-205 | NP-LUCKY_CR2 | 0.80751 | 0.76865 | -0.038867 |  | 0.9 | 1.05 | 0.065404 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-215 | NP-LUCKY_CR2 | 0.80751 | 0.76865 | -0.038867 |  | 0.9 | 1.05 | 0.038922 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-330 | NP-LUCKY_CR2 | 0.80751 | 0.76865 | -0.038867 |  | 0.9 | 1.05 | 0.037455 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | ASGI-2024-003 | NP-LUCKY_G 2 | 0.80675 | 0.76734 | -0.039412 |  | 0.9 | 1.05 | 0.10368 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | ASGI-2024-006 | NP-LUCKY_G 2 | 0.80675 | 0.76734 | -0.039412 |  | 0.9 | 1.05 | 0.077176 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-067 | NP-LUCKY_G 2 | 0.80675 | 0.76734 | -0.039412 |  | 0.9 | 1.05 | 0.03818 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-205 | NP-LUCKY_G 2 | 0.80675 | 0.76734 | -0.039412 |  | 0.9 | 1.05 | 0.053685 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-215 | NP-LUCKY_G 2 | 0.80675 | 0.76734 | -0.039412 |  | 0.9 | 1.05 | 0.038922 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-067 | NP-LUCKY_G 2 | 0.80708 | 0.76768 | -0.0394 |  | 0.9 | 1.05 | 0.03818 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-205 | NP-LUCKY_G 2 | 0.80708 | 0.76768 | -0.0394 |  | 0.9 | 1.05 | 0.053685 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-215 | NP-LUCKY_G 2 | 0.80708 | 0.76768 | -0.0394 |  | 0.9 | 1.05 | 0.038922 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-067 | NP-LUCKY_G 2 | 0.80708 | 0.76768 | -0.0394 |  | 0.9 | 1.05 | 0.03818 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-205 | NP-LUCKY_G 2 | 0.80708 | 0.76768 | -0.0394 |  | 0.9 | 1.05 | 0.053685 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-215 | NP-LUCKY_G 2 | 0.80708 | 0.76768 | -0.0394 |  | 0.9 | 1.05 | 0.038922 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-067 | NP-LUCKY_G 2 | 0.80708 | 0.76768 | -0.0394 |  | 0.9 | 1.05 | 0.03818 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-205 | NP-LUCKY_G 2 | 0.80708 | 0.76768 | -0.0394 |  | 0.9 | 1.05 | 0.053685 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-215 | NP-LUCKY_G 2 | 0.80708 | 0.76768 | -0.0394 |  | 0.9 | 1.05 | 0.038922 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-067 | NP-LUCKY_G 2 | 0.80766 | 0.7688 | -0.038859 |  | 0.9 | 1.05 | 0.03818 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-166 | NP-LUCKY_G 2 | 0.80766 | 0.7688 | -0.038859 |  | 0.9 | 1.05 | 0.041651 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-205 | NP-LUCKY_G 2 | 0.80766 | 0.7688 | -0.038859 |  | 0.9 | 1.05 | 0.065404 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-215 | NP-LUCKY_G 2 | 0.80766 | 0.7688 | -0.038859 |  | 0.9 | 1.05 | 0.038922 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-330 | NP-LUCKY_G 2 | 0.80766 | 0.7688 | -0.038859 |  | 0.9 | 1.05 | 0.037455 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | ASGI-2024-003 | NP-SHATTUCK2 | 0.65452 | 0.60679 | -0.047727 |  | 0.9 | 1.05 | 0.10368 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | ASGI-2024-006 | NP-SHATTUCK2 | 0.65452 | 0.60679 | -0.047727 |  | 0.9 | 1.05 | 0.077176 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-067 | NP-SHATTUCK2 | 0.65452 | 0.60679 | -0.047727 |  | 0.9 | 1.05 | 0.03818 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-205 | NP-SHATTUCK2 | 0.65452 | 0.60679 | -0.047727 |  | 0.9 | 1.05 | 0.053685 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-215 | NP-SHATTUCK2 | 0.65452 | 0.60679 | -0.047727 |  | 0.9 | 1.05 | 0.038922 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-067 | NP-SHATTUCK2 | 0.65493 | 0.6072 | -0.047738 |  | 0.9 | 1.05 | 0.03818 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-205 | NP-SHATTUCK2 | 0.65493 | 0.6072 | -0.047738 |  | 0.9 | 1.05 | 0.053685 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-215 | NP-SHATTUCK2 | 0.65493 | 0.6072 | -0.047738 |  | 0.9 | 1.05 | 0.038922 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-067 | NP-SHATTUCK2 | 0.65493 | 0.6072 | -0.047738 |  | 0.9 | 1.05 | 0.03818 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-205 | NP-SHATTUCK2 | 0.65493 | 0.6072 | -0.047738 |  | 0.9 | 1.05 | 0.053685 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-215 | NP-SHATTUCK2 | 0.65493 | 0.6072 | -0.047738 |  | 0.9 | 1.05 | 0.038922 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-067 | NP-SHATTUCK2 | 0.65493 | 0.6072 | -0.047738 |  | 0.9 | 1.05 | 0.03818 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-205 | NP-SHATTUCK2 | 0.65493 | 0.6072 | -0.047738 |  | 0.9 | 1.05 | 0.053685 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-215 | NP-SHATTUCK2 | 0.65493 | 0.6072 | -0.047738 |  | 0.9 | 1.05 | 0.038922 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-067 | NP-SHATTUCK2 | 0.65566 | 0.60851 | -0.047145 |  | 0.9 | 1.05 | 0.03818 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-166 | NP-SHATTUCK2 | 0.65566 | 0.60851 | -0.047145 |  | 0.9 | 1.05 | 0.041651 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-205 | NP-SHATTUCK2 | 0.65566 | 0.60851 | -0.047145 |  | 0.9 | 1.05 | 0.065404 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-215 | NP-SHATTUCK2 | 0.65566 | 0.60851 | -0.047145 |  | 0.9 | 1.05 | 0.038922 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-330 | NP-SHATTUCK2 | 0.65566 | 0.60851 | -0.047145 |  | 0.9 | 1.05 | 0.037455 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | ASGI-2024-003 | NP-SUB_A 2 | 0.87331 | 0.83786 | -0.035452 |  | 0.9 | 1.05 | 0.10368 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | ASGI-2024-006 | NP-SUB_A 2 | 0.87331 | 0.83786 | -0.035452 |  | 0.9 | 1.05 | 0.077176 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-067 | NP-SUB_A 2 | 0.87331 | 0.83786 | -0.035452 |  | 0.9 | 1.05 | 0.03818 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-205 | NP-SUB_A 2 | 0.87331 | 0.83786 | -0.035452 |  | 0.9 | 1.05 | 0.053685 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-215 | NP-SUB_A 2 | 0.87331 | 0.83786 | -0.035452 |  | 0.9 | 1.05 | 0.038922 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-067 | NP-SUB_A 2 | 0.87361 | 0.83818 | -0.035436 |  | 0.9 | 1.05 | 0.03818 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-205 | NP-SUB_A 2 | 0.87361 | 0.83818 | -0.035436 |  | 0.9 | 1.05 | 0.053685 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-215 | NP-SUB_A 2 | 0.87361 | 0.83818 | -0.035436 |  | 0.9 | 1.05 | 0.038922 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-067 | NP-SUB_A 2 | 0.87361 | 0.83818 | -0.035436 |  | 0.9 | 1.05 | 0.03818 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-205 | NP-SUB_A 2 | 0.87361 | 0.83818 | -0.035436 |  | 0.9 | 1.05 | 0.053685 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-215 | NP-SUB_A 2 | 0.87361 | 0.83818 | -0.035436 |  | 0.9 | 1.05 | 0.038922 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-067 | NP-SUB_A 2 | 0.87361 | 0.83818 | -0.035436 |  | 0.9 | 1.05 | 0.03818 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-205 | NP-SUB_A 2 | 0.87361 | 0.83818 | -0.035436 |  | 0.9 | 1.05 | 0.053685 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-215 | NP-SUB_A 2 | 0.87361 | 0.83818 | -0.035436 |  | 0.9 | 1.05 | 0.038922 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-067 | NP-SUB_A 2 | 0.87413 | 0.83919 | -0.034935 |  | 0.9 | 1.05 | 0.03818 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-166 | NP-SUB_A 2 | 0.87413 | 0.83919 | -0.034935 |  | 0.9 | 1.05 | 0.041651 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-205 | NP-SUB_A 2 | 0.87413 | 0.83919 | -0.034935 |  | 0.9 | 1.05 | 0.065404 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-215 | NP-SUB_A 2 | 0.87413 | 0.83919 | -0.034935 |  | 0.9 | 1.05 | 0.038922 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-330 | NP-SUB_A 2 | 0.87413 | 0.83919 | -0.034935 |  | 0.9 | 1.05 | 0.037455 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | ASGI-2024-003 | NP-VALERO_P2 | 0.68459 | 0.63826 | -0.04633 |  | 0.9 | 1.05 | 0.10368 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | ASGI-2024-006 | NP-VALERO_P2 | 0.68459 | 0.63826 | -0.04633 |  | 0.9 | 1.05 | 0.077176 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-067 | NP-VALERO_P2 | 0.68459 | 0.63826 | -0.04633 |  | 0.9 | 1.05 | 0.03818 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-205 | NP-VALERO_P2 | 0.68459 | 0.63826 | -0.04633 |  | 0.9 | 1.05 | 0.053685 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-215 | NP-VALERO_P2 | 0.68459 | 0.63826 | -0.04633 |  | 0.9 | 1.05 | 0.038922 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-067 | NP-VALERO_P2 | 0.685 | 0.63866 | -0.046337 |  | 0.9 | 1.05 | 0.03818 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-205 | NP-VALERO_P2 | 0.685 | 0.63866 | -0.046337 |  | 0.9 | 1.05 | 0.053685 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-215 | NP-VALERO_P2 | 0.685 | 0.63866 | -0.046337 |  | 0.9 | 1.05 | 0.038922 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-067 | NP-VALERO_P2 | 0.685 | 0.63866 | -0.046337 |  | 0.9 | 1.05 | 0.03818 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-205 | NP-VALERO_P2 | 0.685 | 0.63866 | -0.046337 |  | 0.9 | 1.05 | 0.053685 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-215 | NP-VALERO_P2 | 0.685 | 0.63866 | -0.046337 |  | 0.9 | 1.05 | 0.038922 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-067 | NP-VALERO_P2 | 0.685 | 0.63866 | -0.046337 |  | 0.9 | 1.05 | 0.03818 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-205 | NP-VALERO_P2 | 0.685 | 0.63866 | -0.046337 |  | 0.9 | 1.05 | 0.053685 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-215 | NP-VALERO_P2 | 0.685 | 0.63866 | -0.046337 |  | 0.9 | 1.05 | 0.038922 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-067 | NP-VALERO_P2 | 0.68569 | 0.63994 | -0.045751 |  | 0.9 | 1.05 | 0.03818 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-166 | NP-VALERO_P2 | 0.68569 | 0.63994 | -0.045751 |  | 0.9 | 1.05 | 0.041651 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-205 | NP-VALERO_P2 | 0.68569 | 0.63994 | -0.045751 |  | 0.9 | 1.05 | 0.065404 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-215 | NP-VALERO_P2 | 0.68569 | 0.63994 | -0.045751 |  | 0.9 | 1.05 | 0.038922 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-330 | NP-VALERO_P2 | 0.68569 | 0.63994 | -0.045751 |  | 0.9 | 1.05 | 0.037455 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 0.16 MVAR switched shunt at NP-LUCKY_G 2 69 kV
Voltage | 03ALL | 2 | 29SP | V | ASGI-2024-024 | NTHWARD2 | 0.93542 | 0.90006 | -0.035366 |  | 0.93 | 1.05 | 0.13302 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-054 | NTHWARD2 | 0.93542 | 0.90006 | -0.035366 |  | 0.93 | 1.05 | 0.040787 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-055 | NTHWARD2 | 0.93542 | 0.90006 | -0.035366 |  | 0.93 | 1.05 | 0.046288 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-074 | NTHWARD2 | 0.93542 | 0.90006 | -0.035366 |  | 0.93 | 1.05 | 0.067254 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-076 | NTHWARD2 | 0.93542 | 0.90006 | -0.035366 |  | 0.93 | 1.05 | 0.035421 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-090 | NTHWARD2 | 0.93542 | 0.90006 | -0.035366 |  | 0.93 | 1.05 | 0.073349 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-139 | NTHWARD2 | 0.93542 | 0.90006 | -0.035366 |  | 0.93 | 1.05 | 0.034571 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-170 | NTHWARD2 | 0.93542 | 0.90006 | -0.035366 |  | 0.93 | 1.05 | 0.073415 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-253 | NTHWARD2 | 0.93542 | 0.90006 | -0.035366 |  | 0.93 | 1.05 | 0.070344 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-258 | NTHWARD2 | 0.93542 | 0.90006 | -0.035366 |  | 0.93 | 1.05 | 0.032402 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-260 | NTHWARD2 | 0.93542 | 0.90006 | -0.035366 |  | 0.93 | 1.05 | 0.13211 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-276 | NTHWARD2 | 0.93542 | 0.90006 | -0.035366 |  | 0.93 | 1.05 | 0.050915 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-277 | NTHWARD2 | 0.93542 | 0.90006 | -0.035366 |  | 0.93 | 1.05 | 0.050915 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-287 | NTHWARD2 | 0.93542 | 0.90006 | -0.035366 |  | 0.93 | 1.05 | 0.030578 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-319 | NTHWARD2 | 0.93542 | 0.90006 | -0.035366 |  | 0.93 | 1.05 | 0.059767 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-320 | NTHWARD2 | 0.93542 | 0.90006 | -0.035366 |  | 0.93 | 1.05 | 0.06434 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-339 | NTHWARD2 | 0.93542 | 0.90006 | -0.035366 |  | 0.93 | 1.05 | 0.074026 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-352 | NTHWARD2 | 0.93542 | 0.90006 | -0.035366 |  | 0.93 | 1.05 | 0.10772 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-370 | NTHWARD2 | 0.93542 | 0.90006 | -0.035366 |  | 0.93 | 1.05 | 0.073349 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | ASGI-2024-024 | NTHWARD2 | 0.9392 | 0.9172 | -0.021995 |  | 0.93 | 1.05 | 0.1874 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-054 | NTHWARD2 | 0.9392 | 0.9172 | -0.021995 |  | 0.93 | 1.05 | 0.032663 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-055 | NTHWARD2 | 0.9392 | 0.9172 | -0.021995 |  | 0.93 | 1.05 | 0.052451 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-074 | NTHWARD2 | 0.9392 | 0.9172 | -0.021995 |  | 0.93 | 1.05 | 0.072212 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-076 | NTHWARD2 | 0.9392 | 0.9172 | -0.021995 |  | 0.93 | 1.05 | 0.042339 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-090 | NTHWARD2 | 0.9392 | 0.9172 | -0.021995 |  | 0.93 | 1.05 | 0.10618 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-139 | NTHWARD2 | 0.9392 | 0.9172 | -0.021995 |  | 0.93 | 1.05 | 0.038127 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-170 | NTHWARD2 | 0.9392 | 0.9172 | -0.021995 |  | 0.93 | 1.05 | 0.065102 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-253 | NTHWARD2 | 0.9392 | 0.9172 | -0.021995 |  | 0.93 | 1.05 | 0.095208 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-258 | NTHWARD2 | 0.9392 | 0.9172 | -0.021995 |  | 0.93 | 1.05 | 0.035057 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-260 | NTHWARD2 | 0.9392 | 0.9172 | -0.021995 |  | 0.93 | 1.05 | 0.18643 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-276 | NTHWARD2 | 0.9392 | 0.9172 | -0.021995 |  | 0.93 | 1.05 | 0.053424 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-277 | NTHWARD2 | 0.9392 | 0.9172 | -0.021995 |  | 0.93 | 1.05 | 0.053424 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-287 | NTHWARD2 | 0.9392 | 0.9172 | -0.021995 |  | 0.93 | 1.05 | 0.032476 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-319 | NTHWARD2 | 0.9392 | 0.9172 | -0.021995 |  | 0.93 | 1.05 | 0.084299 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-320 | NTHWARD2 | 0.9392 | 0.9172 | -0.021995 |  | 0.93 | 1.05 | 0.084751 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-339 | NTHWARD2 | 0.9392 | 0.9172 | -0.021995 |  | 0.93 | 1.05 | 0.096534 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-352 | NTHWARD2 | 0.9392 | 0.9172 | -0.021995 |  | 0.93 | 1.05 | 0.064307 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-370 | NTHWARD2 | 0.9392 | 0.9172 | -0.021995 |  | 0.93 | 1.05 | 0.10618 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | ASGI-2024-024 | PICKRG_2 | 0.95165 | 0.9173 | -0.034351 |  | 0.93 | 1.05 | 0.13302 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-054 | PICKRG_2 | 0.95165 | 0.9173 | -0.034351 |  | 0.93 | 1.05 | 0.040787 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-055 | PICKRG_2 | 0.95165 | 0.9173 | -0.034351 |  | 0.93 | 1.05 | 0.046288 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-074 | PICKRG_2 | 0.95165 | 0.9173 | -0.034351 |  | 0.93 | 1.05 | 0.067254 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-076 | PICKRG_2 | 0.95165 | 0.9173 | -0.034351 |  | 0.93 | 1.05 | 0.035421 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-090 | PICKRG_2 | 0.95165 | 0.9173 | -0.034351 |  | 0.93 | 1.05 | 0.073349 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-139 | PICKRG_2 | 0.95165 | 0.9173 | -0.034351 |  | 0.93 | 1.05 | 0.034571 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-170 | PICKRG_2 | 0.95165 | 0.9173 | -0.034351 |  | 0.93 | 1.05 | 0.073415 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-253 | PICKRG_2 | 0.95165 | 0.9173 | -0.034351 |  | 0.93 | 1.05 | 0.070344 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-258 | PICKRG_2 | 0.95165 | 0.9173 | -0.034351 |  | 0.93 | 1.05 | 0.032402 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-260 | PICKRG_2 | 0.95165 | 0.9173 | -0.034351 |  | 0.93 | 1.05 | 0.13211 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-276 | PICKRG_2 | 0.95165 | 0.9173 | -0.034351 |  | 0.93 | 1.05 | 0.050915 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-277 | PICKRG_2 | 0.95165 | 0.9173 | -0.034351 |  | 0.93 | 1.05 | 0.050915 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-287 | PICKRG_2 | 0.95165 | 0.9173 | -0.034351 |  | 0.93 | 1.05 | 0.030578 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-319 | PICKRG_2 | 0.95165 | 0.9173 | -0.034351 |  | 0.93 | 1.05 | 0.059767 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-320 | PICKRG_2 | 0.95165 | 0.9173 | -0.034351 |  | 0.93 | 1.05 | 0.06434 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-339 | PICKRG_2 | 0.95165 | 0.9173 | -0.034351 |  | 0.93 | 1.05 | 0.074026 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-352 | PICKRG_2 | 0.95165 | 0.9173 | -0.034351 |  | 0.93 | 1.05 | 0.10772 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-370 | PICKRG_2 | 0.95165 | 0.9173 | -0.034351 |  | 0.93 | 1.05 | 0.073349 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | ASGI-2024-024 | PICKRG_TP_2 | 0.95535 | 0.92124 | -0.034116 |  | 0.93 | 1.05 | 0.13302 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-054 | PICKRG_TP_2 | 0.95535 | 0.92124 | -0.034116 |  | 0.93 | 1.05 | 0.040787 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-055 | PICKRG_TP_2 | 0.95535 | 0.92124 | -0.034116 |  | 0.93 | 1.05 | 0.046288 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-074 | PICKRG_TP_2 | 0.95535 | 0.92124 | -0.034116 |  | 0.93 | 1.05 | 0.067254 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-076 | PICKRG_TP_2 | 0.95535 | 0.92124 | -0.034116 |  | 0.93 | 1.05 | 0.035421 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-090 | PICKRG_TP_2 | 0.95535 | 0.92124 | -0.034116 |  | 0.93 | 1.05 | 0.073349 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-139 | PICKRG_TP_2 | 0.95535 | 0.92124 | -0.034116 |  | 0.93 | 1.05 | 0.034571 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-170 | PICKRG_TP_2 | 0.95535 | 0.92124 | -0.034116 |  | 0.93 | 1.05 | 0.073415 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-253 | PICKRG_TP_2 | 0.95535 | 0.92124 | -0.034116 |  | 0.93 | 1.05 | 0.070344 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-258 | PICKRG_TP_2 | 0.95535 | 0.92124 | -0.034116 |  | 0.93 | 1.05 | 0.032402 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-260 | PICKRG_TP_2 | 0.95535 | 0.92124 | -0.034116 |  | 0.93 | 1.05 | 0.13211 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-276 | PICKRG_TP_2 | 0.95535 | 0.92124 | -0.034116 |  | 0.93 | 1.05 | 0.050915 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-277 | PICKRG_TP_2 | 0.95535 | 0.92124 | -0.034116 |  | 0.93 | 1.05 | 0.050915 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-287 | PICKRG_TP_2 | 0.95535 | 0.92124 | -0.034116 |  | 0.93 | 1.05 | 0.030578 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-319 | PICKRG_TP_2 | 0.95535 | 0.92124 | -0.034116 |  | 0.93 | 1.05 | 0.059767 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-320 | PICKRG_TP_2 | 0.95535 | 0.92124 | -0.034116 |  | 0.93 | 1.05 | 0.06434 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-339 | PICKRG_TP_2 | 0.95535 | 0.92124 | -0.034116 |  | 0.93 | 1.05 | 0.074026 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-352 | PICKRG_TP_2 | 0.95535 | 0.92124 | -0.034116 |  | 0.93 | 1.05 | 0.10772 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-370 | PICKRG_TP_2 | 0.95535 | 0.92124 | -0.034116 |  | 0.93 | 1.05 | 0.073349 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | ASGI-2024-024 | S1258 5 | 0.9872 | 0.94039 | -0.046805 |  | 0.95 | 1.05 | 0.13302 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-054 | S1258 5 | 0.9872 | 0.94039 | -0.046805 |  | 0.95 | 1.05 | 0.040787 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-055 | S1258 5 | 0.9872 | 0.94039 | -0.046805 |  | 0.95 | 1.05 | 0.046288 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-074 | S1258 5 | 0.9872 | 0.94039 | -0.046805 |  | 0.95 | 1.05 | 0.067254 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-076 | S1258 5 | 0.9872 | 0.94039 | -0.046805 |  | 0.95 | 1.05 | 0.035421 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-090 | S1258 5 | 0.9872 | 0.94039 | -0.046805 |  | 0.95 | 1.05 | 0.073349 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-139 | S1258 5 | 0.9872 | 0.94039 | -0.046805 |  | 0.95 | 1.05 | 0.034571 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-170 | S1258 5 | 0.9872 | 0.94039 | -0.046805 |  | 0.95 | 1.05 | 0.073415 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-253 | S1258 5 | 0.9872 | 0.94039 | -0.046805 |  | 0.95 | 1.05 | 0.070344 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-258 | S1258 5 | 0.9872 | 0.94039 | -0.046805 |  | 0.95 | 1.05 | 0.032402 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-260 | S1258 5 | 0.9872 | 0.94039 | -0.046805 |  | 0.95 | 1.05 | 0.13211 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-276 | S1258 5 | 0.9872 | 0.94039 | -0.046805 |  | 0.95 | 1.05 | 0.050915 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-277 | S1258 5 | 0.9872 | 0.94039 | -0.046805 |  | 0.95 | 1.05 | 0.050915 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-287 | S1258 5 | 0.9872 | 0.94039 | -0.046805 |  | 0.95 | 1.05 | 0.030578 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-319 | S1258 5 | 0.9872 | 0.94039 | -0.046805 |  | 0.95 | 1.05 | 0.059767 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-320 | S1258 5 | 0.9872 | 0.94039 | -0.046805 |  | 0.95 | 1.05 | 0.06434 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-339 | S1258 5 | 0.9872 | 0.94039 | -0.046805 |  | 0.95 | 1.05 | 0.074026 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-352 | S1258 5 | 0.9872 | 0.94039 | -0.046805 |  | 0.95 | 1.05 | 0.10772 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-370 | S1258 5 | 0.9872 | 0.94039 | -0.046805 |  | 0.95 | 1.05 | 0.073349 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | ASGI-2024-024 | S1263 5 | 0.98811 | 0.93681 | -0.0513 |  | 0.95 | 1.05 | 0.13302 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-054 | S1263 5 | 0.98811 | 0.93681 | -0.0513 |  | 0.95 | 1.05 | 0.040787 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-055 | S1263 5 | 0.98811 | 0.93681 | -0.0513 |  | 0.95 | 1.05 | 0.046288 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-074 | S1263 5 | 0.98811 | 0.93681 | -0.0513 |  | 0.95 | 1.05 | 0.067254 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-076 | S1263 5 | 0.98811 | 0.93681 | -0.0513 |  | 0.95 | 1.05 | 0.035421 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-090 | S1263 5 | 0.98811 | 0.93681 | -0.0513 |  | 0.95 | 1.05 | 0.073349 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-139 | S1263 5 | 0.98811 | 0.93681 | -0.0513 |  | 0.95 | 1.05 | 0.034571 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-170 | S1263 5 | 0.98811 | 0.93681 | -0.0513 |  | 0.95 | 1.05 | 0.073415 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-253 | S1263 5 | 0.98811 | 0.93681 | -0.0513 |  | 0.95 | 1.05 | 0.070344 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-258 | S1263 5 | 0.98811 | 0.93681 | -0.0513 |  | 0.95 | 1.05 | 0.032402 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-260 | S1263 5 | 0.98811 | 0.93681 | -0.0513 |  | 0.95 | 1.05 | 0.13211 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-276 | S1263 5 | 0.98811 | 0.93681 | -0.0513 |  | 0.95 | 1.05 | 0.050915 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-277 | S1263 5 | 0.98811 | 0.93681 | -0.0513 |  | 0.95 | 1.05 | 0.050915 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-287 | S1263 5 | 0.98811 | 0.93681 | -0.0513 |  | 0.95 | 1.05 | 0.030578 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-319 | S1263 5 | 0.98811 | 0.93681 | -0.0513 |  | 0.95 | 1.05 | 0.059767 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-320 | S1263 5 | 0.98811 | 0.93681 | -0.0513 |  | 0.95 | 1.05 | 0.06434 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-339 | S1263 5 | 0.98811 | 0.93681 | -0.0513 |  | 0.95 | 1.05 | 0.074026 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-352 | S1263 5 | 0.98811 | 0.93681 | -0.0513 |  | 0.95 | 1.05 | 0.10772 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-370 | S1263 5 | 0.98811 | 0.93681 | -0.0513 |  | 0.95 | 1.05 | 0.073349 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | ASGI-2024-024 | S1280 5 | 0.99418 | 0.94289 | -0.051289 |  | 0.95 | 1.05 | 0.13302 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-054 | S1280 5 | 0.99418 | 0.94289 | -0.051289 |  | 0.95 | 1.05 | 0.040787 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-055 | S1280 5 | 0.99418 | 0.94289 | -0.051289 |  | 0.95 | 1.05 | 0.046288 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-074 | S1280 5 | 0.99418 | 0.94289 | -0.051289 |  | 0.95 | 1.05 | 0.067254 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-076 | S1280 5 | 0.99418 | 0.94289 | -0.051289 |  | 0.95 | 1.05 | 0.035421 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-090 | S1280 5 | 0.99418 | 0.94289 | -0.051289 |  | 0.95 | 1.05 | 0.073349 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-139 | S1280 5 | 0.99418 | 0.94289 | -0.051289 |  | 0.95 | 1.05 | 0.034571 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-170 | S1280 5 | 0.99418 | 0.94289 | -0.051289 |  | 0.95 | 1.05 | 0.073415 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-253 | S1280 5 | 0.99418 | 0.94289 | -0.051289 |  | 0.95 | 1.05 | 0.070344 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-258 | S1280 5 | 0.99418 | 0.94289 | -0.051289 |  | 0.95 | 1.05 | 0.032402 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-260 | S1280 5 | 0.99418 | 0.94289 | -0.051289 |  | 0.95 | 1.05 | 0.13211 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-276 | S1280 5 | 0.99418 | 0.94289 | -0.051289 |  | 0.95 | 1.05 | 0.050915 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-277 | S1280 5 | 0.99418 | 0.94289 | -0.051289 |  | 0.95 | 1.05 | 0.050915 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-287 | S1280 5 | 0.99418 | 0.94289 | -0.051289 |  | 0.95 | 1.05 | 0.030578 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-319 | S1280 5 | 0.99418 | 0.94289 | -0.051289 |  | 0.95 | 1.05 | 0.059767 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-320 | S1280 5 | 0.99418 | 0.94289 | -0.051289 |  | 0.95 | 1.05 | 0.06434 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-339 | S1280 5 | 0.99418 | 0.94289 | -0.051289 |  | 0.95 | 1.05 | 0.074026 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-352 | S1280 5 | 0.99418 | 0.94289 | -0.051289 |  | 0.95 | 1.05 | 0.10772 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-370 | S1280 5 | 0.99418 | 0.94289 | -0.051289 |  | 0.95 | 1.05 | 0.073349 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | ASGI-2024-024 | S1398 5 | 0.98858 | 0.9402 | -0.04838 |  | 0.95 | 1.05 | 0.13302 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-054 | S1398 5 | 0.98858 | 0.9402 | -0.04838 |  | 0.95 | 1.05 | 0.040787 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-055 | S1398 5 | 0.98858 | 0.9402 | -0.04838 |  | 0.95 | 1.05 | 0.046288 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-074 | S1398 5 | 0.98858 | 0.9402 | -0.04838 |  | 0.95 | 1.05 | 0.067254 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-076 | S1398 5 | 0.98858 | 0.9402 | -0.04838 |  | 0.95 | 1.05 | 0.035421 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-090 | S1398 5 | 0.98858 | 0.9402 | -0.04838 |  | 0.95 | 1.05 | 0.073349 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-139 | S1398 5 | 0.98858 | 0.9402 | -0.04838 |  | 0.95 | 1.05 | 0.034571 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-170 | S1398 5 | 0.98858 | 0.9402 | -0.04838 |  | 0.95 | 1.05 | 0.073415 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-253 | S1398 5 | 0.98858 | 0.9402 | -0.04838 |  | 0.95 | 1.05 | 0.070344 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-258 | S1398 5 | 0.98858 | 0.9402 | -0.04838 |  | 0.95 | 1.05 | 0.032402 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-260 | S1398 5 | 0.98858 | 0.9402 | -0.04838 |  | 0.95 | 1.05 | 0.13211 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-276 | S1398 5 | 0.98858 | 0.9402 | -0.04838 |  | 0.95 | 1.05 | 0.050915 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-277 | S1398 5 | 0.98858 | 0.9402 | -0.04838 |  | 0.95 | 1.05 | 0.050915 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-287 | S1398 5 | 0.98858 | 0.9402 | -0.04838 |  | 0.95 | 1.05 | 0.030578 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-319 | S1398 5 | 0.98858 | 0.9402 | -0.04838 |  | 0.95 | 1.05 | 0.059767 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-320 | S1398 5 | 0.98858 | 0.9402 | -0.04838 |  | 0.95 | 1.05 | 0.06434 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-339 | S1398 5 | 0.98858 | 0.9402 | -0.04838 |  | 0.95 | 1.05 | 0.074026 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-352 | S1398 5 | 0.98858 | 0.9402 | -0.04838 |  | 0.95 | 1.05 | 0.10772 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-370 | S1398 5 | 0.98858 | 0.9402 | -0.04838 |  | 0.95 | 1.05 | 0.073349 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 16 MVAR switched shunt at HUMBOLT5 161 kV; Add 21 MVAR switched shunt at S1263 5 161 kV
Voltage | 03ALL | 2 | 29SP | V | ASGI-2024-024 | TARKIO_2 | 0.93633 | 0.90105 | -0.035282 |  | 0.93 | 1.05 | 0.13302 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-054 | TARKIO_2 | 0.93633 | 0.90105 | -0.035282 |  | 0.93 | 1.05 | 0.040787 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-055 | TARKIO_2 | 0.93633 | 0.90105 | -0.035282 |  | 0.93 | 1.05 | 0.046288 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-074 | TARKIO_2 | 0.93633 | 0.90105 | -0.035282 |  | 0.93 | 1.05 | 0.067254 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-076 | TARKIO_2 | 0.93633 | 0.90105 | -0.035282 |  | 0.93 | 1.05 | 0.035421 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-090 | TARKIO_2 | 0.93633 | 0.90105 | -0.035282 |  | 0.93 | 1.05 | 0.073349 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-139 | TARKIO_2 | 0.93633 | 0.90105 | -0.035282 |  | 0.93 | 1.05 | 0.034571 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-170 | TARKIO_2 | 0.93633 | 0.90105 | -0.035282 |  | 0.93 | 1.05 | 0.073415 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-253 | TARKIO_2 | 0.93633 | 0.90105 | -0.035282 |  | 0.93 | 1.05 | 0.070344 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-258 | TARKIO_2 | 0.93633 | 0.90105 | -0.035282 |  | 0.93 | 1.05 | 0.032402 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-260 | TARKIO_2 | 0.93633 | 0.90105 | -0.035282 |  | 0.93 | 1.05 | 0.13211 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-276 | TARKIO_2 | 0.93633 | 0.90105 | -0.035282 |  | 0.93 | 1.05 | 0.050915 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-277 | TARKIO_2 | 0.93633 | 0.90105 | -0.035282 |  | 0.93 | 1.05 | 0.050915 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-287 | TARKIO_2 | 0.93633 | 0.90105 | -0.035282 |  | 0.93 | 1.05 | 0.030578 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-319 | TARKIO_2 | 0.93633 | 0.90105 | -0.035282 |  | 0.93 | 1.05 | 0.059767 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-320 | TARKIO_2 | 0.93633 | 0.90105 | -0.035282 |  | 0.93 | 1.05 | 0.06434 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-339 | TARKIO_2 | 0.93633 | 0.90105 | -0.035282 |  | 0.93 | 1.05 | 0.074026 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-352 | TARKIO_2 | 0.93633 | 0.90105 | -0.035282 |  | 0.93 | 1.05 | 0.10772 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-370 | TARKIO_2 | 0.93633 | 0.90105 | -0.035282 |  | 0.93 | 1.05 | 0.073349 | P55:345:OPPD:S3458 3::FN13:EHV: | Add 8 MVAR switched shunt at BURLNGTNJCT2 69 kV
Voltage | 03ALL | 2 | 29SP | V | ASGI-2024-024 | TARKIO_2 | 0.9401 | 0.91816 | -0.021944 |  | 0.93 | 1.05 | 0.1874 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-054 | TARKIO_2 | 0.9401 | 0.91816 | -0.021944 |  | 0.93 | 1.05 | 0.032663 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-055 | TARKIO_2 | 0.9401 | 0.91816 | -0.021944 |  | 0.93 | 1.05 | 0.052451 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-074 | TARKIO_2 | 0.9401 | 0.91816 | -0.021944 |  | 0.93 | 1.05 | 0.072212 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-076 | TARKIO_2 | 0.9401 | 0.91816 | -0.021944 |  | 0.93 | 1.05 | 0.042339 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-090 | TARKIO_2 | 0.9401 | 0.91816 | -0.021944 |  | 0.93 | 1.05 | 0.10618 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-139 | TARKIO_2 | 0.9401 | 0.91816 | -0.021944 |  | 0.93 | 1.05 | 0.038127 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-170 | TARKIO_2 | 0.9401 | 0.91816 | -0.021944 |  | 0.93 | 1.05 | 0.065102 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-253 | TARKIO_2 | 0.9401 | 0.91816 | -0.021944 |  | 0.93 | 1.05 | 0.095208 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-258 | TARKIO_2 | 0.9401 | 0.91816 | -0.021944 |  | 0.93 | 1.05 | 0.035057 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-260 | TARKIO_2 | 0.9401 | 0.91816 | -0.021944 |  | 0.93 | 1.05 | 0.18643 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-276 | TARKIO_2 | 0.9401 | 0.91816 | -0.021944 |  | 0.93 | 1.05 | 0.053424 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-277 | TARKIO_2 | 0.9401 | 0.91816 | -0.021944 |  | 0.93 | 1.05 | 0.053424 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-287 | TARKIO_2 | 0.9401 | 0.91816 | -0.021944 |  | 0.93 | 1.05 | 0.032476 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-319 | TARKIO_2 | 0.9401 | 0.91816 | -0.021944 |  | 0.93 | 1.05 | 0.084299 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-320 | TARKIO_2 | 0.9401 | 0.91816 | -0.021944 |  | 0.93 | 1.05 | 0.084751 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-339 | TARKIO_2 | 0.9401 | 0.91816 | -0.021944 |  | 0.93 | 1.05 | 0.096534 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-352 | TARKIO_2 | 0.9401 | 0.91816 | -0.021944 |  | 0.93 | 1.05 | 0.064307 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 03ALL | 2 | 29SP | V | GEN-2024-370 | TARKIO_2 | 0.9401 | 0.91816 | -0.021944 |  | 0.93 | 1.05 | 0.10618 | P42:345:NPPD:BKR-CPR-3304:::: | Add 0.11 MVAR switched shunt at NTHWARD2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | 15THSTRT | 0.98692 | 0.91275 | -0.074174 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | 15THSTRT | 0.98692 | 0.91275 | -0.074174 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | 15THSTRT | 0.98692 | 0.91275 | -0.074174 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | 15THSTRT | 0.98692 | 0.91275 | -0.074174 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | 15THSTRT | 0.98692 | 0.91275 | -0.074174 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | 15THSTRT | 0.98692 | 0.91275 | -0.074174 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | 15THSTRT | 0.98692 | 0.91275 | -0.074174 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | 15THSTRT | 0.98692 | 0.91275 | -0.074174 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | 15THSTRT | 0.98692 | 0.91275 | -0.074174 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | 15THSTRT | 0.98692 | 0.91275 | -0.074174 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | 15THSTRT | 0.98692 | 0.91275 | -0.074174 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | 15THSTRT | 0.98692 | 0.91275 | -0.074174 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | 15THSTRT | 0.98692 | 0.91275 | -0.074174 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | 15THSTRT | 0.98692 | 0.91275 | -0.074174 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | 15THSTRT | 0.98692 | 0.91275 | -0.074174 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | 15THSTRT | 0.98692 | 0.91275 | -0.074174 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | 15THSTRT | 0.98692 | 0.91275 | -0.074174 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | 15THSTRT | 0.98692 | 0.91275 | -0.074174 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | 15THSTRT | 0.98692 | 0.91275 | -0.074174 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | 15THSTRT | 0.98692 | 0.91275 | -0.074174 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | 15THSTRT | 0.98692 | 0.91275 | -0.074174 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | 15THSTRT | 0.98692 | 0.91275 | -0.074174 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | 15THSTRT | 0.98692 | 0.91275 | -0.074174 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | 15THSTRT | 0.98692 | 0.91275 | -0.074174 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | 15THSTRT | 0.98692 | 0.91275 | -0.074174 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | 15THSTRT | 0.98692 | 0.91275 | -0.074174 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | 15THSTRT | 0.98692 | 0.91275 | -0.074174 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | 15THSTRT | 0.98692 | 0.91275 | -0.074174 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | 19THST 3 | 0.96507 | 0.92433 | -0.040741 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | 19THST 3 | 0.96507 | 0.92433 | -0.040741 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | 19THST 3 | 0.96507 | 0.92433 | -0.040741 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | 19THST 3 | 0.96507 | 0.92433 | -0.040741 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | 19THST 3 | 0.96507 | 0.92433 | -0.040741 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | 19THST 3 | 0.96507 | 0.92433 | -0.040741 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | 19THST 3 | 0.96507 | 0.92433 | -0.040741 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | 19THST 3 | 0.96507 | 0.92433 | -0.040741 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | 19THST 3 | 0.96507 | 0.92433 | -0.040741 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | 19THST 3 | 0.96507 | 0.92433 | -0.040741 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | 19THST 3 | 0.96507 | 0.92433 | -0.040741 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | 19THST 3 | 0.96507 | 0.92433 | -0.040741 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | 19THST 3 | 0.96507 | 0.92433 | -0.040741 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | 19THST 3 | 0.96507 | 0.92433 | -0.040741 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | 19THST 3 | 0.96507 | 0.92433 | -0.040741 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | 19THST 3 | 0.96507 | 0.92433 | -0.040741 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | 19THST 3 | 0.96507 | 0.92433 | -0.040741 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | 19THST 3 | 0.96507 | 0.92433 | -0.040741 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | 19THST 3 | 0.96507 | 0.92433 | -0.040741 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | 19THST 3 | 0.96507 | 0.92433 | -0.040741 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | 19THST 3 | 0.97104 | 0.92738 | -0.043668 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | 19THST 3 | 0.97104 | 0.92738 | -0.043668 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | 19THST 3 | 0.97104 | 0.92738 | -0.043668 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | 19THST 3 | 0.97104 | 0.92738 | -0.043668 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | 19THST 3 | 0.97104 | 0.92738 | -0.043668 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | 19THST 3 | 0.97104 | 0.92738 | -0.043668 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | 19THST 3 | 0.97104 | 0.92738 | -0.043668 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | 19THST 3 | 0.97104 | 0.92738 | -0.043668 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | 19THST 3 | 0.97104 | 0.92738 | -0.043668 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | 19THST 3 | 0.97104 | 0.92738 | -0.043668 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | 19THST 3 | 0.97104 | 0.92738 | -0.043668 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | 19THST 3 | 0.97104 | 0.92738 | -0.043668 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | 19THST 3 | 0.97104 | 0.92738 | -0.043668 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | 19THST 3 | 0.97104 | 0.92738 | -0.043668 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | 19THST 3 | 0.97104 | 0.92738 | -0.043668 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | 19THST 3 | 0.97104 | 0.92738 | -0.043668 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | 19THST 3 | 0.97104 | 0.92738 | -0.043668 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | 19THST 3 | 0.97104 | 0.92738 | -0.043668 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | 19THST 3 | 0.97104 | 0.92738 | -0.043668 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | 19THST 3 | 0.97104 | 0.92738 | -0.043668 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | 19THST 3 | 0.97699 | 0.9252 | -0.051789 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | 19THST 3 | 0.97699 | 0.9252 | -0.051789 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | 19THST 3 | 0.97699 | 0.9252 | -0.051789 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | 19THST 3 | 0.97699 | 0.9252 | -0.051789 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | 19THST 3 | 0.97699 | 0.9252 | -0.051789 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | 19THST 3 | 0.97699 | 0.9252 | -0.051789 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | 19THST 3 | 0.97699 | 0.9252 | -0.051789 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | 19THST 3 | 0.97699 | 0.9252 | -0.051789 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | 19THST 3 | 0.97699 | 0.9252 | -0.051789 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | 19THST 3 | 0.97699 | 0.9252 | -0.051789 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | 19THST 3 | 0.97699 | 0.9252 | -0.051789 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | 19THST 3 | 0.97699 | 0.9252 | -0.051789 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | 19THST 3 | 0.97699 | 0.9252 | -0.051789 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | 19THST 3 | 0.97699 | 0.9252 | -0.051789 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | 19THST 3 | 0.97699 | 0.9252 | -0.051789 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | 19THST 3 | 0.97699 | 0.9252 | -0.051789 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | 19THST 3 | 0.97699 | 0.9252 | -0.051789 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | 19THST 3 | 0.97699 | 0.9252 | -0.051789 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | 19THST 3 | 0.97699 | 0.9252 | -0.051789 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | 19THST 3 | 0.97699 | 0.9252 | -0.051789 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | 19THST 3 | 0.97699 | 0.9252 | -0.051789 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | 19THST 3 | 0.97699 | 0.9252 | -0.051789 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | 19THST 3 | 0.97699 | 0.9252 | -0.051789 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | 19THST 3 | 0.97699 | 0.9252 | -0.051789 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | 19THST 3 | 0.97699 | 0.9252 | -0.051789 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | 19THST 3 | 0.97699 | 0.9252 | -0.051789 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | 19THST 3 | 0.97699 | 0.9252 | -0.051789 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | 19THST 3 | 0.97699 | 0.9252 | -0.051789 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | ASGI-2024-023 | 2WEIRGAT | 0.93925 | 0.90335 | -0.035897 |  | 0.92 | 1.05 | 0.036967 | P23:345:EES::7ROCKYCRK%:1:EHV: | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-025 | 2WEIRGAT | 0.93925 | 0.90335 | -0.035897 |  | 0.92 | 1.05 | 0.054441 | P23:345:EES::7ROCKYCRK%:1:EHV: | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-068 | 2WEIRGAT | 0.93925 | 0.90335 | -0.035897 |  | 0.92 | 1.05 | 0.058243 | P23:345:EES::7ROCKYCRK%:1:EHV: | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-071 | 2WEIRGAT | 0.93925 | 0.90335 | -0.035897 |  | 0.92 | 1.05 | 0.061467 | P23:345:EES::7ROCKYCRK%:1:EHV: | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-122 | 2WEIRGAT | 0.93925 | 0.90335 | -0.035897 |  | 0.92 | 1.05 | 0.060212 | P23:345:EES::7ROCKYCRK%:1:EHV: | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-177 | 2WEIRGAT | 0.93925 | 0.90335 | -0.035897 |  | 0.92 | 1.05 | 0.047926 | P23:345:EES::7ROCKYCRK%:1:EHV: | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-178 | 2WEIRGAT | 0.93925 | 0.90335 | -0.035897 |  | 0.92 | 1.05 | 0.11352 | P23:345:EES::7ROCKYCRK%:1:EHV: | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-220 | 2WEIRGAT | 0.93925 | 0.90335 | -0.035897 |  | 0.92 | 1.05 | 0.057503 | P23:345:EES::7ROCKYCRK%:1:EHV: | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-232 | 2WEIRGAT | 0.93925 | 0.90335 | -0.035897 |  | 0.92 | 1.05 | 0.39492 | P23:345:EES::7ROCKYCRK%:1:EHV: | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-241 | 2WEIRGAT | 0.93925 | 0.90335 | -0.035897 |  | 0.92 | 1.05 | 0.054441 | P23:345:EES::7ROCKYCRK%:1:EHV: | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV
Voltage | 04ALL | 2 | 29SP | V | ASGI-2024-023 | 2WEIRGAT | 0.94212 | 0.90641 | -0.035706 |  | 0.92 | 1.05 | 0.036967 | Single 334197 7ROCKYCRK% 345 783930 G24-232-TAP 345 1 | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-025 | 2WEIRGAT | 0.94212 | 0.90641 | -0.035706 |  | 0.92 | 1.05 | 0.054441 | Single 334197 7ROCKYCRK% 345 783930 G24-232-TAP 345 1 | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-068 | 2WEIRGAT | 0.94212 | 0.90641 | -0.035706 |  | 0.92 | 1.05 | 0.058243 | Single 334197 7ROCKYCRK% 345 783930 G24-232-TAP 345 1 | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-071 | 2WEIRGAT | 0.94212 | 0.90641 | -0.035706 |  | 0.92 | 1.05 | 0.061467 | Single 334197 7ROCKYCRK% 345 783930 G24-232-TAP 345 1 | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-122 | 2WEIRGAT | 0.94212 | 0.90641 | -0.035706 |  | 0.92 | 1.05 | 0.060212 | Single 334197 7ROCKYCRK% 345 783930 G24-232-TAP 345 1 | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-177 | 2WEIRGAT | 0.94212 | 0.90641 | -0.035706 |  | 0.92 | 1.05 | 0.047926 | Single 334197 7ROCKYCRK% 345 783930 G24-232-TAP 345 1 | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-178 | 2WEIRGAT | 0.94212 | 0.90641 | -0.035706 |  | 0.92 | 1.05 | 0.11352 | Single 334197 7ROCKYCRK% 345 783930 G24-232-TAP 345 1 | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-220 | 2WEIRGAT | 0.94212 | 0.90641 | -0.035706 |  | 0.92 | 1.05 | 0.057503 | Single 334197 7ROCKYCRK% 345 783930 G24-232-TAP 345 1 | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-232 | 2WEIRGAT | 0.94212 | 0.90641 | -0.035706 |  | 0.92 | 1.05 | 0.39492 | Single 334197 7ROCKYCRK% 345 783930 G24-232-TAP 345 1 | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-241 | 2WEIRGAT | 0.94212 | 0.90641 | -0.035706 |  | 0.92 | 1.05 | 0.054441 | Single 334197 7ROCKYCRK% 345 783930 G24-232-TAP 345 1 | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-025 | 2WEIRGAT | 0.94103 | 0.91955 | -0.021478 |  | 0.92 | 1.05 | 0.031126 | P12:345:EES:7GRIMES%:7ROCKYCRK%:1:EHV: | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-068 | 2WEIRGAT | 0.94103 | 0.91955 | -0.021478 |  | 0.92 | 1.05 | 0.033301 | P12:345:EES:7GRIMES%:7ROCKYCRK%:1:EHV: | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-071 | 2WEIRGAT | 0.94103 | 0.91955 | -0.021478 |  | 0.92 | 1.05 | 0.035114 | P12:345:EES:7GRIMES%:7ROCKYCRK%:1:EHV: | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-122 | 2WEIRGAT | 0.94103 | 0.91955 | -0.021478 |  | 0.92 | 1.05 | 0.034301 | P12:345:EES:7GRIMES%:7ROCKYCRK%:1:EHV: | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-178 | 2WEIRGAT | 0.94103 | 0.91955 | -0.021478 |  | 0.92 | 1.05 | 0.065006 | P12:345:EES:7GRIMES%:7ROCKYCRK%:1:EHV: | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-220 | 2WEIRGAT | 0.94103 | 0.91955 | -0.021478 |  | 0.92 | 1.05 | 0.032822 | P12:345:EES:7GRIMES%:7ROCKYCRK%:1:EHV: | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-232 | 2WEIRGAT | 0.94103 | 0.91955 | -0.021478 |  | 0.92 | 1.05 | 0.2274 | P12:345:EES:7GRIMES%:7ROCKYCRK%:1:EHV: | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-241 | 2WEIRGAT | 0.94103 | 0.91955 | -0.021478 |  | 0.92 | 1.05 | 0.031126 | P12:345:EES:7GRIMES%:7ROCKYCRK%:1:EHV: | Add 3.6 MVAR switched shunt at 2WEIRGAT 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | 4CORNER3 | 0.96741 | 0.90384 | -0.063565 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | 4CORNER3 | 0.96741 | 0.90384 | -0.063565 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | 4CORNER3 | 0.96741 | 0.90384 | -0.063565 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | 4CORNER3 | 0.96741 | 0.90384 | -0.063565 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | 4CORNER3 | 0.96741 | 0.90384 | -0.063565 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | 4CORNER3 | 0.96741 | 0.90384 | -0.063565 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | 4CORNER3 | 0.96741 | 0.90384 | -0.063565 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | 4CORNER3 | 0.96741 | 0.90384 | -0.063565 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | 4CORNER3 | 0.96741 | 0.90384 | -0.063565 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | 4CORNER3 | 0.96741 | 0.90384 | -0.063565 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | 4CORNER3 | 0.96741 | 0.90384 | -0.063565 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | 4CORNER3 | 0.96741 | 0.90384 | -0.063565 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | 4CORNER3 | 0.96741 | 0.90384 | -0.063565 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | 4CORNER3 | 0.96741 | 0.90384 | -0.063565 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | 4CORNER3 | 0.96741 | 0.90384 | -0.063565 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | 4CORNER3 | 0.96741 | 0.90384 | -0.063565 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | 4CORNER3 | 0.96741 | 0.90384 | -0.063565 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | 4CORNER3 | 0.96741 | 0.90384 | -0.063565 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | 4CORNER3 | 0.96741 | 0.90384 | -0.063565 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | 4CORNER3 | 0.96741 | 0.90384 | -0.063565 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | 4CORNER3 | 0.96741 | 0.90384 | -0.063565 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | 4CORNER3 | 0.96741 | 0.90384 | -0.063565 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | 4CORNER3 | 0.96741 | 0.90384 | -0.063565 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | 4CORNER3 | 0.96741 | 0.90384 | -0.063565 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | 4CORNER3 | 0.96741 | 0.90384 | -0.063565 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | 4CORNER3 | 0.96741 | 0.90384 | -0.063565 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | 4CORNER3 | 0.96741 | 0.90384 | -0.063565 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | 4CORNER3 | 0.96741 | 0.90384 | -0.063565 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | 6TH ST 3 | 0.96875 | 0.92843 | -0.04032 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | 6TH ST 3 | 0.96875 | 0.92843 | -0.04032 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | 6TH ST 3 | 0.96875 | 0.92843 | -0.04032 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | 6TH ST 3 | 0.96875 | 0.92843 | -0.04032 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | 6TH ST 3 | 0.96875 | 0.92843 | -0.04032 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | 6TH ST 3 | 0.96875 | 0.92843 | -0.04032 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | 6TH ST 3 | 0.96875 | 0.92843 | -0.04032 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | 6TH ST 3 | 0.96875 | 0.92843 | -0.04032 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | 6TH ST 3 | 0.96875 | 0.92843 | -0.04032 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | 6TH ST 3 | 0.96875 | 0.92843 | -0.04032 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | 6TH ST 3 | 0.96875 | 0.92843 | -0.04032 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | 6TH ST 3 | 0.96875 | 0.92843 | -0.04032 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | 6TH ST 3 | 0.96875 | 0.92843 | -0.04032 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | 6TH ST 3 | 0.96875 | 0.92843 | -0.04032 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | 6TH ST 3 | 0.96875 | 0.92843 | -0.04032 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | 6TH ST 3 | 0.96875 | 0.92843 | -0.04032 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | 6TH ST 3 | 0.96875 | 0.92843 | -0.04032 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | 6TH ST 3 | 0.96875 | 0.92843 | -0.04032 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | 6TH ST 3 | 0.96875 | 0.92843 | -0.04032 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | 6TH ST 3 | 0.96875 | 0.92843 | -0.04032 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | 87TH 3 | 0.96737 | 0.92678 | -0.040589 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | 87TH 3 | 0.96737 | 0.92678 | -0.040589 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | 87TH 3 | 0.96737 | 0.92678 | -0.040589 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | 87TH 3 | 0.96737 | 0.92678 | -0.040589 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | 87TH 3 | 0.96737 | 0.92678 | -0.040589 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | 87TH 3 | 0.96737 | 0.92678 | -0.040589 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | 87TH 3 | 0.96737 | 0.92678 | -0.040589 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | 87TH 3 | 0.96737 | 0.92678 | -0.040589 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | 87TH 3 | 0.96737 | 0.92678 | -0.040589 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | 87TH 3 | 0.96737 | 0.92678 | -0.040589 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | 87TH 3 | 0.96737 | 0.92678 | -0.040589 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | 87TH 3 | 0.96737 | 0.92678 | -0.040589 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | 87TH 3 | 0.96737 | 0.92678 | -0.040589 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | 87TH 3 | 0.96737 | 0.92678 | -0.040589 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | 87TH 3 | 0.96737 | 0.92678 | -0.040589 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | 87TH 3 | 0.96737 | 0.92678 | -0.040589 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | 87TH 3 | 0.96737 | 0.92678 | -0.040589 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | 87TH 3 | 0.96737 | 0.92678 | -0.040589 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | 87TH 3 | 0.96737 | 0.92678 | -0.040589 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | 87TH 3 | 0.96737 | 0.92678 | -0.040589 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | 87TH 3 | 0.98226 | 0.9195 | -0.062766 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | 87TH 3 | 0.98226 | 0.9195 | -0.062766 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | 87TH 3 | 0.98226 | 0.9195 | -0.062766 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | 87TH 3 | 0.98226 | 0.9195 | -0.062766 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | 87TH 3 | 0.98226 | 0.9195 | -0.062766 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | 87TH 3 | 0.98226 | 0.9195 | -0.062766 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | 87TH 3 | 0.98226 | 0.9195 | -0.062766 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | 87TH 3 | 0.98226 | 0.9195 | -0.062766 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | 87TH 3 | 0.98226 | 0.9195 | -0.062766 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | 87TH 3 | 0.98226 | 0.9195 | -0.062766 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | 87TH 3 | 0.98226 | 0.9195 | -0.062766 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | 87TH 3 | 0.98226 | 0.9195 | -0.062766 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | 87TH 3 | 0.98226 | 0.9195 | -0.062766 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | 87TH 3 | 0.98226 | 0.9195 | -0.062766 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | 87TH 3 | 0.98226 | 0.9195 | -0.062766 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | 87TH 3 | 0.98226 | 0.9195 | -0.062766 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | 87TH 3 | 0.98226 | 0.9195 | -0.062766 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | 87TH 3 | 0.98226 | 0.9195 | -0.062766 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | 87TH 3 | 0.98226 | 0.9195 | -0.062766 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | 87TH 3 | 0.98226 | 0.9195 | -0.062766 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | 87TH 3 | 0.98226 | 0.9195 | -0.062766 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | 87TH 3 | 0.98226 | 0.9195 | -0.062766 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | 87TH 3 | 0.98226 | 0.9195 | -0.062766 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | 87TH 3 | 0.98226 | 0.9195 | -0.062766 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | 87TH 3 | 0.98226 | 0.9195 | -0.062766 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | 87TH 3 | 0.98226 | 0.9195 | -0.062766 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | 87TH 3 | 0.98226 | 0.9195 | -0.062766 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | 87TH 3 | 0.98226 | 0.9195 | -0.062766 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | 87TH 7 | 0.97317 | 0.93977 | -0.033408 |  | 0.95 | 1.05 | 0.03768 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | 87TH 7 | 0.97317 | 0.93977 | -0.033408 |  | 0.95 | 1.05 | 0.054649 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | 87TH 7 | 0.97317 | 0.93977 | -0.033408 |  | 0.95 | 1.05 | 0.041275 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | 87TH 7 | 0.97317 | 0.93977 | -0.033408 |  | 0.95 | 1.05 | 0.032793 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | 87TH 7 | 0.97317 | 0.93977 | -0.033408 |  | 0.95 | 1.05 | 0.043592 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | 87TH 7 | 0.97317 | 0.93977 | -0.033408 |  | 0.95 | 1.05 | 0.040246 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | 87TH 7 | 0.97317 | 0.93977 | -0.033408 |  | 0.95 | 1.05 | 0.030207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | 87TH 7 | 0.97317 | 0.93977 | -0.033408 |  | 0.95 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | 87TH 7 | 0.97317 | 0.93977 | -0.033408 |  | 0.95 | 1.05 | 0.069525 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | 87TH 7 | 0.97317 | 0.93977 | -0.033408 |  | 0.95 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | 87TH 7 | 0.97317 | 0.93977 | -0.033408 |  | 0.95 | 1.05 | 0.032357 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | 87TH 7 | 0.97317 | 0.93977 | -0.033408 |  | 0.95 | 1.05 | 0.033611 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | 87TH 7 | 0.97317 | 0.93977 | -0.033408 |  | 0.95 | 1.05 | 0.030163 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | 87TH 7 | 0.97317 | 0.93977 | -0.033408 |  | 0.95 | 1.05 | 0.042714 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | 87TH 7 | 0.97317 | 0.93977 | -0.033408 |  | 0.95 | 1.05 | 0.042627 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | 87TH 7 | 0.97317 | 0.93977 | -0.033408 |  | 0.95 | 1.05 | 0.032319 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | 87TH 7 | 0.97317 | 0.93977 | -0.033408 |  | 0.95 | 1.05 | 0.034532 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | 87TH 7 | 0.97317 | 0.93977 | -0.033408 |  | 0.95 | 1.05 | 0.030438 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | 87TH 7 | 0.97317 | 0.93977 | -0.033408 |  | 0.95 | 1.05 | 0.035207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | 87TH 7 | 0.97317 | 0.93977 | -0.033408 |  | 0.95 | 1.05 | 0.030949 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | 87TH 7 | 0.96789 | 0.92979 | -0.038098 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | 87TH 7 | 0.96789 | 0.92979 | -0.038098 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | 87TH 7 | 0.96789 | 0.92979 | -0.038098 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | 87TH 7 | 0.96789 | 0.92979 | -0.038098 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | 87TH 7 | 0.96789 | 0.92979 | -0.038098 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | 87TH 7 | 0.96789 | 0.92979 | -0.038098 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | 87TH 7 | 0.96789 | 0.92979 | -0.038098 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | 87TH 7 | 0.96789 | 0.92979 | -0.038098 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | 87TH 7 | 0.96789 | 0.92979 | -0.038098 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | 87TH 7 | 0.96789 | 0.92979 | -0.038098 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | 87TH 7 | 0.96789 | 0.92979 | -0.038098 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | 87TH 7 | 0.96789 | 0.92979 | -0.038098 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | 87TH 7 | 0.96789 | 0.92979 | -0.038098 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | 87TH 7 | 0.96789 | 0.92979 | -0.038098 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | 87TH 7 | 0.96789 | 0.92979 | -0.038098 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | 87TH 7 | 0.96789 | 0.92979 | -0.038098 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | 87TH 7 | 0.96789 | 0.92979 | -0.038098 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | 87TH 7 | 0.96789 | 0.92979 | -0.038098 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | 87TH 7 | 0.96789 | 0.92979 | -0.038098 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | 87TH 7 | 0.96789 | 0.92979 | -0.038098 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | 87TH 7 | 0.97646 | 0.93491 | -0.041552 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | 87TH 7 | 0.97646 | 0.93491 | -0.041552 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | 87TH 7 | 0.97646 | 0.93491 | -0.041552 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | 87TH 7 | 0.97646 | 0.93491 | -0.041552 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | 87TH 7 | 0.97646 | 0.93491 | -0.041552 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | 87TH 7 | 0.97646 | 0.93491 | -0.041552 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | 87TH 7 | 0.97646 | 0.93491 | -0.041552 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | 87TH 7 | 0.97646 | 0.93491 | -0.041552 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | 87TH 7 | 0.97646 | 0.93491 | -0.041552 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | 87TH 7 | 0.97646 | 0.93491 | -0.041552 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | 87TH 7 | 0.97646 | 0.93491 | -0.041552 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | 87TH 7 | 0.97646 | 0.93491 | -0.041552 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | 87TH 7 | 0.97646 | 0.93491 | -0.041552 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | 87TH 7 | 0.97646 | 0.93491 | -0.041552 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | 87TH 7 | 0.97646 | 0.93491 | -0.041552 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | 87TH 7 | 0.97646 | 0.93491 | -0.041552 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | 87TH 7 | 0.97646 | 0.93491 | -0.041552 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | 87TH 7 | 0.97646 | 0.93491 | -0.041552 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | 87TH 7 | 0.97646 | 0.93491 | -0.041552 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | 87TH 7 | 0.97646 | 0.93491 | -0.041552 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | 87TH 7 | 0.98165 | 0.92264 | -0.05901 |  | 0.95 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | 87TH 7 | 0.98165 | 0.92264 | -0.05901 |  | 0.95 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | 87TH 7 | 0.98165 | 0.92264 | -0.05901 |  | 0.95 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | 87TH 7 | 0.98165 | 0.92264 | -0.05901 |  | 0.95 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | 87TH 7 | 0.98165 | 0.92264 | -0.05901 |  | 0.95 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | 87TH 7 | 0.98165 | 0.92264 | -0.05901 |  | 0.95 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | 87TH 7 | 0.98165 | 0.92264 | -0.05901 |  | 0.95 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | 87TH 7 | 0.98165 | 0.92264 | -0.05901 |  | 0.95 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | 87TH 7 | 0.98165 | 0.92264 | -0.05901 |  | 0.95 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | 87TH 7 | 0.98165 | 0.92264 | -0.05901 |  | 0.95 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | 87TH 7 | 0.98165 | 0.92264 | -0.05901 |  | 0.95 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | 87TH 7 | 0.98165 | 0.92264 | -0.05901 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | 87TH 7 | 0.98165 | 0.92264 | -0.05901 |  | 0.95 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | 87TH 7 | 0.98165 | 0.92264 | -0.05901 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | 87TH 7 | 0.98165 | 0.92264 | -0.05901 |  | 0.95 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | 87TH 7 | 0.98165 | 0.92264 | -0.05901 |  | 0.95 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | 87TH 7 | 0.98165 | 0.92264 | -0.05901 |  | 0.95 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | 87TH 7 | 0.98165 | 0.92264 | -0.05901 |  | 0.95 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | 87TH 7 | 0.98165 | 0.92264 | -0.05901 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | 87TH 7 | 0.98165 | 0.92264 | -0.05901 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | 87TH 7 | 0.98165 | 0.92264 | -0.05901 |  | 0.95 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | 87TH 7 | 0.98165 | 0.92264 | -0.05901 |  | 0.95 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | 87TH 7 | 0.98165 | 0.92264 | -0.05901 |  | 0.95 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | 87TH 7 | 0.98165 | 0.92264 | -0.05901 |  | 0.95 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | 87TH 7 | 0.98165 | 0.92264 | -0.05901 |  | 0.95 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | 87TH 7 | 0.98165 | 0.92264 | -0.05901 |  | 0.95 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | 87TH 7 | 0.98165 | 0.92264 | -0.05901 |  | 0.95 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | 87TH 7 | 0.98165 | 0.92264 | -0.05901 |  | 0.95 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | 87TH 7 | 0.97261 | 0.93822 | -0.034391 |  | 0.95 | 1.05 | 0.03768 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | 87TH 7 | 0.97261 | 0.93822 | -0.034391 |  | 0.95 | 1.05 | 0.054649 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | 87TH 7 | 0.97261 | 0.93822 | -0.034391 |  | 0.95 | 1.05 | 0.041275 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | 87TH 7 | 0.97261 | 0.93822 | -0.034391 |  | 0.95 | 1.05 | 0.032793 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | 87TH 7 | 0.97261 | 0.93822 | -0.034391 |  | 0.95 | 1.05 | 0.043592 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | 87TH 7 | 0.97261 | 0.93822 | -0.034391 |  | 0.95 | 1.05 | 0.040246 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | 87TH 7 | 0.97261 | 0.93822 | -0.034391 |  | 0.95 | 1.05 | 0.030207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | 87TH 7 | 0.97261 | 0.93822 | -0.034391 |  | 0.95 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | 87TH 7 | 0.97261 | 0.93822 | -0.034391 |  | 0.95 | 1.05 | 0.069525 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | 87TH 7 | 0.97261 | 0.93822 | -0.034391 |  | 0.95 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | 87TH 7 | 0.97261 | 0.93822 | -0.034391 |  | 0.95 | 1.05 | 0.032357 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | 87TH 7 | 0.97261 | 0.93822 | -0.034391 |  | 0.95 | 1.05 | 0.033611 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | 87TH 7 | 0.97261 | 0.93822 | -0.034391 |  | 0.95 | 1.05 | 0.030163 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | 87TH 7 | 0.97261 | 0.93822 | -0.034391 |  | 0.95 | 1.05 | 0.042714 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | 87TH 7 | 0.97261 | 0.93822 | -0.034391 |  | 0.95 | 1.05 | 0.042627 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | 87TH 7 | 0.97261 | 0.93822 | -0.034391 |  | 0.95 | 1.05 | 0.032319 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | 87TH 7 | 0.97261 | 0.93822 | -0.034391 |  | 0.95 | 1.05 | 0.034532 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | 87TH 7 | 0.97261 | 0.93822 | -0.034391 |  | 0.95 | 1.05 | 0.030438 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | 87TH 7 | 0.97261 | 0.93822 | -0.034391 |  | 0.95 | 1.05 | 0.035207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | 87TH 7 | 0.97261 | 0.93822 | -0.034391 |  | 0.95 | 1.05 | 0.030949 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | ADRIAN 5 | 0.97625 | 0.92134 | -0.05491 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | ADRIAN 5 | 0.97625 | 0.92134 | -0.05491 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | ADRIAN 5 | 0.97625 | 0.92134 | -0.05491 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | ADRIAN 5 | 0.97625 | 0.92134 | -0.05491 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | ADRIAN 5 | 0.97625 | 0.92134 | -0.05491 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | ADRIAN 5 | 0.97625 | 0.92134 | -0.05491 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | ADRIAN 5 | 0.97625 | 0.92134 | -0.05491 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | ADRIAN 5 | 0.97625 | 0.92134 | -0.05491 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | ADRIAN 5 | 0.97625 | 0.92134 | -0.05491 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | ADRIAN 5 | 0.97625 | 0.92134 | -0.05491 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | ADRIAN 5 | 0.97625 | 0.92134 | -0.05491 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | ADRIAN 5 | 0.97625 | 0.92134 | -0.05491 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | ADRIAN 5 | 0.97625 | 0.92134 | -0.05491 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | ADRIAN 5 | 0.97625 | 0.92134 | -0.05491 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | ADRIAN 5 | 0.97625 | 0.92134 | -0.05491 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | ADRIAN 5 | 0.97625 | 0.92134 | -0.05491 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | ADRIAN 5 | 0.97625 | 0.92134 | -0.05491 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | ADRIAN 5 | 0.97625 | 0.92134 | -0.05491 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | ADRIAN 5 | 0.97625 | 0.92134 | -0.05491 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | ADRIAN 5 | 0.97625 | 0.92134 | -0.05491 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | ADRIAN 5 | 0.97625 | 0.92134 | -0.05491 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | ADRIAN 5 | 0.97625 | 0.92134 | -0.05491 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | ADRIAN 5 | 0.97625 | 0.92134 | -0.05491 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | ADRIAN 5 | 0.97625 | 0.92134 | -0.05491 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | ADRIAN 5 | 0.97625 | 0.92134 | -0.05491 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | ADRIAN 5 | 0.97625 | 0.92134 | -0.05491 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | ADRIAN 5 | 0.97625 | 0.92134 | -0.05491 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | ADRIAN 5 | 0.97625 | 0.92134 | -0.05491 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | ASGI-2024-023 | ALTAMNS2 | 0.94311 | 0.8995 | -0.043609 |  | 0.93 | 1.05 | 0.077629 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-025 | ALTAMNS2 | 0.94311 | 0.8995 | -0.043609 |  | 0.93 | 1.05 | 0.06446 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-068 | ALTAMNS2 | 0.94311 | 0.8995 | -0.043609 |  | 0.93 | 1.05 | 0.066434 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-071 | ALTAMNS2 | 0.94311 | 0.8995 | -0.043609 |  | 0.93 | 1.05 | 0.073293 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | ALTAMNS2 | 0.94311 | 0.8995 | -0.043609 |  | 0.93 | 1.05 | 0.053415 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-122 | ALTAMNS2 | 0.94311 | 0.8995 | -0.043609 |  | 0.93 | 1.05 | 0.08103 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-177 | ALTAMNS2 | 0.94311 | 0.8995 | -0.043609 |  | 0.93 | 1.05 | 0.08268 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-178 | ALTAMNS2 | 0.94311 | 0.8995 | -0.043609 |  | 0.93 | 1.05 | 0.077122 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | ALTAMNS2 | 0.94311 | 0.8995 | -0.043609 |  | 0.93 | 1.05 | 0.032185 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-220 | ALTAMNS2 | 0.94311 | 0.8995 | -0.043609 |  | 0.93 | 1.05 | 0.073922 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-232 | ALTAMNS2 | 0.94311 | 0.8995 | -0.043609 |  | 0.93 | 1.05 | 0.076776 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-241 | ALTAMNS2 | 0.94311 | 0.8995 | -0.043609 |  | 0.93 | 1.05 | 0.06446 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | ALTAMNS2 | 0.94311 | 0.8995 | -0.043609 |  | 0.93 | 1.05 | 0.038841 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | ALTAMNS2 | 0.94311 | 0.8995 | -0.043609 |  | 0.93 | 1.05 | 0.034687 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | ALTAMNS2 | 0.94311 | 0.8995 | -0.043609 |  | 0.93 | 1.05 | 0.034687 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | ALTAMNS2 | 0.94311 | 0.8995 | -0.043609 |  | 0.93 | 1.05 | 0.031574 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | ALTAMNS2 | 0.94311 | 0.8995 | -0.043609 |  | 0.93 | 1.05 | 0.042889 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-376 | ALTAMNS2 | 0.94311 | 0.8995 | -0.043609 |  | 0.93 | 1.05 | 0.079908 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | ALTAMNS2 | 0.94009 | 0.90052 | -0.039576 |  | 0.93 | 1.05 | 0.040299 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | ALTAMNS2 | 0.94009 | 0.90052 | -0.039576 |  | 0.93 | 1.05 | 0.048812 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | ALTAMNS2 | 0.94009 | 0.90052 | -0.039576 |  | 0.93 | 1.05 | 0.076211 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | ALTAMNS2 | 0.94009 | 0.90052 | -0.039576 |  | 0.93 | 1.05 | 0.069331 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | ALTAMNS2 | 0.94009 | 0.90052 | -0.039576 |  | 0.93 | 1.05 | 0.035943 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | ALTAMNS2 | 0.94009 | 0.90052 | -0.039576 |  | 0.93 | 1.05 | 0.034061 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | ALTAMNS2 | 0.94009 | 0.90052 | -0.039576 |  | 0.93 | 1.05 | 0.064216 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | ALTAMNS2 | 0.94009 | 0.90052 | -0.039576 |  | 0.93 | 1.05 | 0.045005 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | ALTAMNS2 | 0.94009 | 0.90052 | -0.039576 |  | 0.93 | 1.05 | 0.13572 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | ALTAMNS2 | 0.94009 | 0.90052 | -0.039576 |  | 0.93 | 1.05 | 0.037472 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | ALTAMNS2 | 0.94009 | 0.90052 | -0.039576 |  | 0.93 | 1.05 | 0.037472 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | ALTAMNS2 | 0.94009 | 0.90052 | -0.039576 |  | 0.93 | 1.05 | 0.06894 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | ALTAMNS2 | 0.94009 | 0.90052 | -0.039576 |  | 0.93 | 1.05 | 0.034713 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | ALTAMNS2 | 0.94009 | 0.90052 | -0.039576 |  | 0.93 | 1.05 | 0.035229 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | ALTAMNS2 | 0.9401 | 0.90074 | -0.03936 |  | 0.93 | 1.05 | 0.094783 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | ALTAMNS2 | 0.9401 | 0.90074 | -0.03936 |  | 0.93 | 1.05 | 0.03645 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | ALTAMNS2 | 0.9401 | 0.90074 | -0.03936 |  | 0.93 | 1.05 | 0.04755 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | ALTAMNS2 | 0.9401 | 0.90074 | -0.03936 |  | 0.93 | 1.05 | 0.06097 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | ALTAMNS2 | 0.9401 | 0.90074 | -0.03936 |  | 0.93 | 1.05 | 0.061051 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | ALTAMNS2 | 0.9401 | 0.90074 | -0.03936 |  | 0.93 | 1.05 | 0.04456 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | ALTAMNS2 | 0.9401 | 0.90074 | -0.03936 |  | 0.93 | 1.05 | 0.048811 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | ALTAMNS2 | 0.9401 | 0.90074 | -0.03936 |  | 0.93 | 1.05 | 0.13004 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | ALTAMNS2 | 0.9401 | 0.90074 | -0.03936 |  | 0.93 | 1.05 | 0.049018 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | ALTAMNS2 | 0.9401 | 0.90074 | -0.03936 |  | 0.93 | 1.05 | 0.059524 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | ALTAMNS2 | 0.9401 | 0.90074 | -0.03936 |  | 0.93 | 1.05 | 0.059524 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | ALTAMNS2 | 0.9401 | 0.90074 | -0.03936 |  | 0.93 | 1.05 | 0.05974 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | ALTAMNS2 | 0.9401 | 0.90074 | -0.03936 |  | 0.93 | 1.05 | 0.076949 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | ALTAMNS2 | 0.9401 | 0.90074 | -0.03936 |  | 0.93 | 1.05 | 0.042157 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | ALTAMNS2 | 0.9401 | 0.90074 | -0.03936 |  | 0.93 | 1.05 | 0.040957 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | ALTAMNS2 | 0.9401 | 0.90074 | -0.03936 |  | 0.93 | 1.05 | 0.044127 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | ALTAMNS2 | 0.9401 | 0.90074 | -0.03936 |  | 0.93 | 1.05 | 0.044127 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | ALTAMNS2 | 0.9401 | 0.90074 | -0.03936 |  | 0.93 | 1.05 | 0.054637 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | ALTAMNS2 | 0.9401 | 0.90074 | -0.03936 |  | 0.93 | 1.05 | 0.060597 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | ALTAMNS2 | 0.9401 | 0.90074 | -0.03936 |  | 0.93 | 1.05 | 0.044286 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | ALTAMNS2 | 0.9401 | 0.90074 | -0.03936 |  | 0.93 | 1.05 | 0.059107 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | ALTAMNS2 | 0.9401 | 0.90074 | -0.03936 |  | 0.93 | 1.05 | 0.052698 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | ALTAMNS2 | 0.9401 | 0.90074 | -0.03936 |  | 0.93 | 1.05 | 0.067422 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | ALTAMNS2 | 0.9401 | 0.90074 | -0.03936 |  | 0.93 | 1.05 | 0.053768 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | ALTAMNS2 | 0.9401 | 0.90074 | -0.03936 |  | 0.93 | 1.05 | 0.03909 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | ALTAMNS2 | 0.93896 | 0.89661 | -0.042349 |  | 0.93 | 1.05 | 0.040163 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | ALTAMNS2 | 0.93896 | 0.89661 | -0.042349 |  | 0.93 | 1.05 | 0.035544 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | ALTAMNS2 | 0.93896 | 0.89661 | -0.042349 |  | 0.93 | 1.05 | 0.048812 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | ALTAMNS2 | 0.93896 | 0.89661 | -0.042349 |  | 0.93 | 1.05 | 0.049073 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | ALTAMNS2 | 0.93896 | 0.89661 | -0.042349 |  | 0.93 | 1.05 | 0.035142 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | ALTAMNS2 | 0.93896 | 0.89661 | -0.042349 |  | 0.93 | 1.05 | 0.037502 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | ALTAMNS2 | 0.93896 | 0.89661 | -0.042349 |  | 0.93 | 1.05 | 0.04571 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | ALTAMNS2 | 0.93896 | 0.89661 | -0.042349 |  | 0.93 | 1.05 | 0.03081 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | ALTAMNS2 | 0.93896 | 0.89661 | -0.042349 |  | 0.93 | 1.05 | 0.03835 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | ALTAMNS2 | 0.93896 | 0.89661 | -0.042349 |  | 0.93 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | ALTAMNS2 | 0.93896 | 0.89661 | -0.042349 |  | 0.93 | 1.05 | 0.064216 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | ALTAMNS2 | 0.93896 | 0.89661 | -0.042349 |  | 0.93 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | ALTAMNS2 | 0.93896 | 0.89661 | -0.042349 |  | 0.93 | 1.05 | 0.037545 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | ALTAMNS2 | 0.93896 | 0.89661 | -0.042349 |  | 0.93 | 1.05 | 0.037793 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | ALTAMNS2 | 0.93896 | 0.89661 | -0.042349 |  | 0.93 | 1.05 | 0.035866 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | ALTAMNS2 | 0.93896 | 0.89661 | -0.042349 |  | 0.93 | 1.05 | 0.064223 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | ALTAMNS2 | 0.93896 | 0.89661 | -0.042349 |  | 0.93 | 1.05 | 0.046439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | ALTAMNS2 | 0.93896 | 0.89661 | -0.042349 |  | 0.93 | 1.05 | 0.03576 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | ALTAMNS2 | 0.93896 | 0.89661 | -0.042349 |  | 0.93 | 1.05 | 0.032864 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | ALTAMNS2 | 0.93896 | 0.89661 | -0.042349 |  | 0.93 | 1.05 | 0.032012 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | ALTAMNS2 | 0.93896 | 0.89661 | -0.042349 |  | 0.93 | 1.05 | 0.033901 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | ALTAMNS2 | 0.93896 | 0.89661 | -0.042349 |  | 0.93 | 1.05 | 0.035381 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | ALTAMNS2 | 0.9393 | 0.88165 | -0.057649 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | ALTAMNS2 | 0.9393 | 0.88165 | -0.057649 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | ALTAMNS2 | 0.9393 | 0.88165 | -0.057649 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | ALTAMNS2 | 0.9393 | 0.88165 | -0.057649 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | ALTAMNS2 | 0.9393 | 0.88165 | -0.057649 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | ALTAMNS2 | 0.9393 | 0.88165 | -0.057649 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | ALTAMNS2 | 0.9393 | 0.88165 | -0.057649 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | ALTAMNS2 | 0.9393 | 0.88165 | -0.057649 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | ALTAMNS2 | 0.9393 | 0.88165 | -0.057649 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | ALTAMNS2 | 0.9393 | 0.88165 | -0.057649 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | ALTAMNS2 | 0.9393 | 0.88165 | -0.057649 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | ALTAMNS2 | 0.9393 | 0.88165 | -0.057649 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | ALTAMNS2 | 0.9393 | 0.88165 | -0.057649 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | ALTAMNS2 | 0.9393 | 0.88165 | -0.057649 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | ALTAMNS2 | 0.9393 | 0.88165 | -0.057649 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | ALTAMNS2 | 0.9393 | 0.88165 | -0.057649 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | ALTAMNS2 | 0.9393 | 0.88165 | -0.057649 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | ALTAMNS2 | 0.9393 | 0.88165 | -0.057649 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | ALTAMNS2 | 0.9393 | 0.88165 | -0.057649 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | ALTAMNS2 | 0.9393 | 0.88165 | -0.057649 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | ALTAMNS2 | 0.9393 | 0.88165 | -0.057649 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | ALTAMNS2 | 0.9393 | 0.88165 | -0.057649 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | ALTAMNS2 | 0.9393 | 0.88165 | -0.057649 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | ALTAMNS2 | 0.9393 | 0.88165 | -0.057649 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | ALTAMNS2 | 0.9393 | 0.88165 | -0.057649 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | ALTAMNS2 | 0.9393 | 0.88165 | -0.057649 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | ALTAMNS2 | 0.9393 | 0.88165 | -0.057649 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | ALTAMNS2 | 0.9393 | 0.88165 | -0.057649 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | ASGI-2024-023 | ALTAMNT2 | 0.93644 | 0.89249 | -0.043946 |  | 0.93 | 1.05 | 0.077629 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-025 | ALTAMNT2 | 0.93644 | 0.89249 | -0.043946 |  | 0.93 | 1.05 | 0.06446 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-068 | ALTAMNT2 | 0.93644 | 0.89249 | -0.043946 |  | 0.93 | 1.05 | 0.066434 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-071 | ALTAMNT2 | 0.93644 | 0.89249 | -0.043946 |  | 0.93 | 1.05 | 0.073293 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | ALTAMNT2 | 0.93644 | 0.89249 | -0.043946 |  | 0.93 | 1.05 | 0.053415 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-122 | ALTAMNT2 | 0.93644 | 0.89249 | -0.043946 |  | 0.93 | 1.05 | 0.08103 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-177 | ALTAMNT2 | 0.93644 | 0.89249 | -0.043946 |  | 0.93 | 1.05 | 0.08268 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-178 | ALTAMNT2 | 0.93644 | 0.89249 | -0.043946 |  | 0.93 | 1.05 | 0.077122 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | ALTAMNT2 | 0.93644 | 0.89249 | -0.043946 |  | 0.93 | 1.05 | 0.032185 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-220 | ALTAMNT2 | 0.93644 | 0.89249 | -0.043946 |  | 0.93 | 1.05 | 0.073922 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-232 | ALTAMNT2 | 0.93644 | 0.89249 | -0.043946 |  | 0.93 | 1.05 | 0.076776 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-241 | ALTAMNT2 | 0.93644 | 0.89249 | -0.043946 |  | 0.93 | 1.05 | 0.06446 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | ALTAMNT2 | 0.93644 | 0.89249 | -0.043946 |  | 0.93 | 1.05 | 0.038841 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | ALTAMNT2 | 0.93644 | 0.89249 | -0.043946 |  | 0.93 | 1.05 | 0.034687 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | ALTAMNT2 | 0.93644 | 0.89249 | -0.043946 |  | 0.93 | 1.05 | 0.034687 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | ALTAMNT2 | 0.93644 | 0.89249 | -0.043946 |  | 0.93 | 1.05 | 0.031574 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | ALTAMNT2 | 0.93644 | 0.89249 | -0.043946 |  | 0.93 | 1.05 | 0.042889 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-376 | ALTAMNT2 | 0.93644 | 0.89249 | -0.043946 |  | 0.93 | 1.05 | 0.079908 | P23:500:EES-EAI:KEO:B4941::EHV: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | ALTAMNT2 | 0.93341 | 0.89352 | -0.039883 |  | 0.93 | 1.05 | 0.040299 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | ALTAMNT2 | 0.93341 | 0.89352 | -0.039883 |  | 0.93 | 1.05 | 0.048812 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | ALTAMNT2 | 0.93341 | 0.89352 | -0.039883 |  | 0.93 | 1.05 | 0.076211 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | ALTAMNT2 | 0.93341 | 0.89352 | -0.039883 |  | 0.93 | 1.05 | 0.069331 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | ALTAMNT2 | 0.93341 | 0.89352 | -0.039883 |  | 0.93 | 1.05 | 0.035943 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | ALTAMNT2 | 0.93341 | 0.89352 | -0.039883 |  | 0.93 | 1.05 | 0.034061 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | ALTAMNT2 | 0.93341 | 0.89352 | -0.039883 |  | 0.93 | 1.05 | 0.064216 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | ALTAMNT2 | 0.93341 | 0.89352 | -0.039883 |  | 0.93 | 1.05 | 0.045005 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | ALTAMNT2 | 0.93341 | 0.89352 | -0.039883 |  | 0.93 | 1.05 | 0.13572 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | ALTAMNT2 | 0.93341 | 0.89352 | -0.039883 |  | 0.93 | 1.05 | 0.037472 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | ALTAMNT2 | 0.93341 | 0.89352 | -0.039883 |  | 0.93 | 1.05 | 0.037472 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | ALTAMNT2 | 0.93341 | 0.89352 | -0.039883 |  | 0.93 | 1.05 | 0.06894 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | ALTAMNT2 | 0.93341 | 0.89352 | -0.039883 |  | 0.93 | 1.05 | 0.034713 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | ALTAMNT2 | 0.93341 | 0.89352 | -0.039883 |  | 0.93 | 1.05 | 0.035229 | P12:345:AECI:BLCKBRRY:SPRTSMN3_2::: | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 0.25 MVAR switched shunt at LABETTS2 69 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | ALTAMNT2 | 0.93341 | 0.89374 | -0.039665 |  | 0.93 | 1.05 | 0.094783 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | ALTAMNT2 | 0.93341 | 0.89374 | -0.039665 |  | 0.93 | 1.05 | 0.03645 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | ALTAMNT2 | 0.93341 | 0.89374 | -0.039665 |  | 0.93 | 1.05 | 0.04755 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | ALTAMNT2 | 0.93341 | 0.89374 | -0.039665 |  | 0.93 | 1.05 | 0.06097 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | ALTAMNT2 | 0.93341 | 0.89374 | -0.039665 |  | 0.93 | 1.05 | 0.061051 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | ALTAMNT2 | 0.93341 | 0.89374 | -0.039665 |  | 0.93 | 1.05 | 0.04456 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | ALTAMNT2 | 0.93341 | 0.89374 | -0.039665 |  | 0.93 | 1.05 | 0.048811 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | ALTAMNT2 | 0.93341 | 0.89374 | -0.039665 |  | 0.93 | 1.05 | 0.13004 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | ALTAMNT2 | 0.93341 | 0.89374 | -0.039665 |  | 0.93 | 1.05 | 0.049018 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | ALTAMNT2 | 0.93341 | 0.89374 | -0.039665 |  | 0.93 | 1.05 | 0.059524 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | ALTAMNT2 | 0.93341 | 0.89374 | -0.039665 |  | 0.93 | 1.05 | 0.059524 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | ALTAMNT2 | 0.93341 | 0.89374 | -0.039665 |  | 0.93 | 1.05 | 0.05974 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | ALTAMNT2 | 0.93341 | 0.89374 | -0.039665 |  | 0.93 | 1.05 | 0.076949 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | ALTAMNT2 | 0.93341 | 0.89374 | -0.039665 |  | 0.93 | 1.05 | 0.042157 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | ALTAMNT2 | 0.93341 | 0.89374 | -0.039665 |  | 0.93 | 1.05 | 0.040957 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | ALTAMNT2 | 0.93341 | 0.89374 | -0.039665 |  | 0.93 | 1.05 | 0.044127 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | ALTAMNT2 | 0.93341 | 0.89374 | -0.039665 |  | 0.93 | 1.05 | 0.044127 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | ALTAMNT2 | 0.93341 | 0.89374 | -0.039665 |  | 0.93 | 1.05 | 0.054637 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | ALTAMNT2 | 0.93341 | 0.89374 | -0.039665 |  | 0.93 | 1.05 | 0.060597 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | ALTAMNT2 | 0.93341 | 0.89374 | -0.039665 |  | 0.93 | 1.05 | 0.044286 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | ALTAMNT2 | 0.93341 | 0.89374 | -0.039665 |  | 0.93 | 1.05 | 0.059107 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | ALTAMNT2 | 0.93341 | 0.89374 | -0.039665 |  | 0.93 | 1.05 | 0.052698 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | ALTAMNT2 | 0.93341 | 0.89374 | -0.039665 |  | 0.93 | 1.05 | 0.067422 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | ALTAMNT2 | 0.93341 | 0.89374 | -0.039665 |  | 0.93 | 1.05 | 0.053768 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | ALTAMNT2 | 0.93341 | 0.89374 | -0.039665 |  | 0.93 | 1.05 | 0.03909 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | ALTAMNT2 | 0.93226 | 0.88958 | -0.042679 |  | 0.93 | 1.05 | 0.040163 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | ALTAMNT2 | 0.93226 | 0.88958 | -0.042679 |  | 0.93 | 1.05 | 0.035544 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | ALTAMNT2 | 0.93226 | 0.88958 | -0.042679 |  | 0.93 | 1.05 | 0.048812 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | ALTAMNT2 | 0.93226 | 0.88958 | -0.042679 |  | 0.93 | 1.05 | 0.049073 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | ALTAMNT2 | 0.93226 | 0.88958 | -0.042679 |  | 0.93 | 1.05 | 0.035142 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | ALTAMNT2 | 0.93226 | 0.88958 | -0.042679 |  | 0.93 | 1.05 | 0.037502 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | ALTAMNT2 | 0.93226 | 0.88958 | -0.042679 |  | 0.93 | 1.05 | 0.04571 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | ALTAMNT2 | 0.93226 | 0.88958 | -0.042679 |  | 0.93 | 1.05 | 0.03081 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | ALTAMNT2 | 0.93226 | 0.88958 | -0.042679 |  | 0.93 | 1.05 | 0.03835 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | ALTAMNT2 | 0.93226 | 0.88958 | -0.042679 |  | 0.93 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | ALTAMNT2 | 0.93226 | 0.88958 | -0.042679 |  | 0.93 | 1.05 | 0.064216 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | ALTAMNT2 | 0.93226 | 0.88958 | -0.042679 |  | 0.93 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | ALTAMNT2 | 0.93226 | 0.88958 | -0.042679 |  | 0.93 | 1.05 | 0.037545 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | ALTAMNT2 | 0.93226 | 0.88958 | -0.042679 |  | 0.93 | 1.05 | 0.037793 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | ALTAMNT2 | 0.93226 | 0.88958 | -0.042679 |  | 0.93 | 1.05 | 0.035866 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | ALTAMNT2 | 0.93226 | 0.88958 | -0.042679 |  | 0.93 | 1.05 | 0.064223 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | ALTAMNT2 | 0.93226 | 0.88958 | -0.042679 |  | 0.93 | 1.05 | 0.046439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | ALTAMNT2 | 0.93226 | 0.88958 | -0.042679 |  | 0.93 | 1.05 | 0.03576 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | ALTAMNT2 | 0.93226 | 0.88958 | -0.042679 |  | 0.93 | 1.05 | 0.032864 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | ALTAMNT2 | 0.93226 | 0.88958 | -0.042679 |  | 0.93 | 1.05 | 0.032012 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | ALTAMNT2 | 0.93226 | 0.88958 | -0.042679 |  | 0.93 | 1.05 | 0.033901 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | ALTAMNT2 | 0.93226 | 0.88958 | -0.042679 |  | 0.93 | 1.05 | 0.035381 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | ALTAMNT2 | 0.9326 | 0.8745 | -0.058106 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | ALTAMNT2 | 0.9326 | 0.8745 | -0.058106 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | ALTAMNT2 | 0.9326 | 0.8745 | -0.058106 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | ALTAMNT2 | 0.9326 | 0.8745 | -0.058106 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | ALTAMNT2 | 0.9326 | 0.8745 | -0.058106 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | ALTAMNT2 | 0.9326 | 0.8745 | -0.058106 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | ALTAMNT2 | 0.9326 | 0.8745 | -0.058106 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | ALTAMNT2 | 0.9326 | 0.8745 | -0.058106 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | ALTAMNT2 | 0.9326 | 0.8745 | -0.058106 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | ALTAMNT2 | 0.9326 | 0.8745 | -0.058106 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | ALTAMNT2 | 0.9326 | 0.8745 | -0.058106 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | ALTAMNT2 | 0.9326 | 0.8745 | -0.058106 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | ALTAMNT2 | 0.9326 | 0.8745 | -0.058106 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | ALTAMNT2 | 0.9326 | 0.8745 | -0.058106 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | ALTAMNT2 | 0.9326 | 0.8745 | -0.058106 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | ALTAMNT2 | 0.9326 | 0.8745 | -0.058106 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | ALTAMNT2 | 0.9326 | 0.8745 | -0.058106 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | ALTAMNT2 | 0.9326 | 0.8745 | -0.058106 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | ALTAMNT2 | 0.9326 | 0.8745 | -0.058106 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | ALTAMNT2 | 0.9326 | 0.8745 | -0.058106 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | ALTAMNT2 | 0.9326 | 0.8745 | -0.058106 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | ALTAMNT2 | 0.9326 | 0.8745 | -0.058106 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | ALTAMNT2 | 0.9326 | 0.8745 | -0.058106 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | ALTAMNT2 | 0.9326 | 0.8745 | -0.058106 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | ALTAMNT2 | 0.9326 | 0.8745 | -0.058106 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | ALTAMNT2 | 0.9326 | 0.8745 | -0.058106 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | ALTAMNT2 | 0.9326 | 0.8745 | -0.058106 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | ALTAMNT2 | 0.9326 | 0.8745 | -0.058106 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | ALTOONA4 | 0.96224 | 0.92871 | -0.033529 |  | 0.93 | 1.05 | 0.094783 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | ALTOONA4 | 0.96224 | 0.92871 | -0.033529 |  | 0.93 | 1.05 | 0.03645 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | ALTOONA4 | 0.96224 | 0.92871 | -0.033529 |  | 0.93 | 1.05 | 0.04755 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | ALTOONA4 | 0.96224 | 0.92871 | -0.033529 |  | 0.93 | 1.05 | 0.06097 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | ALTOONA4 | 0.96224 | 0.92871 | -0.033529 |  | 0.93 | 1.05 | 0.061051 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | ALTOONA4 | 0.96224 | 0.92871 | -0.033529 |  | 0.93 | 1.05 | 0.04456 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | ALTOONA4 | 0.96224 | 0.92871 | -0.033529 |  | 0.93 | 1.05 | 0.048811 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | ALTOONA4 | 0.96224 | 0.92871 | -0.033529 |  | 0.93 | 1.05 | 0.13004 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | ALTOONA4 | 0.96224 | 0.92871 | -0.033529 |  | 0.93 | 1.05 | 0.049018 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | ALTOONA4 | 0.96224 | 0.92871 | -0.033529 |  | 0.93 | 1.05 | 0.059524 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | ALTOONA4 | 0.96224 | 0.92871 | -0.033529 |  | 0.93 | 1.05 | 0.059524 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | ALTOONA4 | 0.96224 | 0.92871 | -0.033529 |  | 0.93 | 1.05 | 0.05974 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | ALTOONA4 | 0.96224 | 0.92871 | -0.033529 |  | 0.93 | 1.05 | 0.076949 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | ALTOONA4 | 0.96224 | 0.92871 | -0.033529 |  | 0.93 | 1.05 | 0.042157 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | ALTOONA4 | 0.96224 | 0.92871 | -0.033529 |  | 0.93 | 1.05 | 0.040957 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | ALTOONA4 | 0.96224 | 0.92871 | -0.033529 |  | 0.93 | 1.05 | 0.044127 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | ALTOONA4 | 0.96224 | 0.92871 | -0.033529 |  | 0.93 | 1.05 | 0.044127 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | ALTOONA4 | 0.96224 | 0.92871 | -0.033529 |  | 0.93 | 1.05 | 0.054637 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | ALTOONA4 | 0.96224 | 0.92871 | -0.033529 |  | 0.93 | 1.05 | 0.060597 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | ALTOONA4 | 0.96224 | 0.92871 | -0.033529 |  | 0.93 | 1.05 | 0.044286 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | ALTOONA4 | 0.96224 | 0.92871 | -0.033529 |  | 0.93 | 1.05 | 0.059107 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | ALTOONA4 | 0.96224 | 0.92871 | -0.033529 |  | 0.93 | 1.05 | 0.052698 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | ALTOONA4 | 0.96224 | 0.92871 | -0.033529 |  | 0.93 | 1.05 | 0.067422 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | ALTOONA4 | 0.96224 | 0.92871 | -0.033529 |  | 0.93 | 1.05 | 0.053768 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | ALTOONA4 | 0.96224 | 0.92871 | -0.033529 |  | 0.93 | 1.05 | 0.03909 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | ALTOONA4 | 0.95698 | 0.92257 | -0.034415 |  | 0.93 | 1.05 | 0.040163 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | ALTOONA4 | 0.95698 | 0.92257 | -0.034415 |  | 0.93 | 1.05 | 0.035544 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | ALTOONA4 | 0.95698 | 0.92257 | -0.034415 |  | 0.93 | 1.05 | 0.048812 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | ALTOONA4 | 0.95698 | 0.92257 | -0.034415 |  | 0.93 | 1.05 | 0.049073 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | ALTOONA4 | 0.95698 | 0.92257 | -0.034415 |  | 0.93 | 1.05 | 0.035142 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | ALTOONA4 | 0.95698 | 0.92257 | -0.034415 |  | 0.93 | 1.05 | 0.037502 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | ALTOONA4 | 0.95698 | 0.92257 | -0.034415 |  | 0.93 | 1.05 | 0.04571 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | ALTOONA4 | 0.95698 | 0.92257 | -0.034415 |  | 0.93 | 1.05 | 0.03081 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | ALTOONA4 | 0.95698 | 0.92257 | -0.034415 |  | 0.93 | 1.05 | 0.03835 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | ALTOONA4 | 0.95698 | 0.92257 | -0.034415 |  | 0.93 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | ALTOONA4 | 0.95698 | 0.92257 | -0.034415 |  | 0.93 | 1.05 | 0.064216 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | ALTOONA4 | 0.95698 | 0.92257 | -0.034415 |  | 0.93 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | ALTOONA4 | 0.95698 | 0.92257 | -0.034415 |  | 0.93 | 1.05 | 0.037545 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | ALTOONA4 | 0.95698 | 0.92257 | -0.034415 |  | 0.93 | 1.05 | 0.037793 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | ALTOONA4 | 0.95698 | 0.92257 | -0.034415 |  | 0.93 | 1.05 | 0.035866 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | ALTOONA4 | 0.95698 | 0.92257 | -0.034415 |  | 0.93 | 1.05 | 0.064223 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | ALTOONA4 | 0.95698 | 0.92257 | -0.034415 |  | 0.93 | 1.05 | 0.046439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | ALTOONA4 | 0.95698 | 0.92257 | -0.034415 |  | 0.93 | 1.05 | 0.03576 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | ALTOONA4 | 0.95698 | 0.92257 | -0.034415 |  | 0.93 | 1.05 | 0.032864 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | ALTOONA4 | 0.95698 | 0.92257 | -0.034415 |  | 0.93 | 1.05 | 0.032012 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | ALTOONA4 | 0.95698 | 0.92257 | -0.034415 |  | 0.93 | 1.05 | 0.033901 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | ALTOONA4 | 0.95698 | 0.92257 | -0.034415 |  | 0.93 | 1.05 | 0.035381 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | ALTOONA4 | 0.95959 | 0.90502 | -0.054567 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | ALTOONA4 | 0.95959 | 0.90502 | -0.054567 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | ALTOONA4 | 0.95959 | 0.90502 | -0.054567 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | ALTOONA4 | 0.95959 | 0.90502 | -0.054567 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | ALTOONA4 | 0.95959 | 0.90502 | -0.054567 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | ALTOONA4 | 0.95959 | 0.90502 | -0.054567 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | ALTOONA4 | 0.95959 | 0.90502 | -0.054567 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | ALTOONA4 | 0.95959 | 0.90502 | -0.054567 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | ALTOONA4 | 0.95959 | 0.90502 | -0.054567 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | ALTOONA4 | 0.95959 | 0.90502 | -0.054567 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | ALTOONA4 | 0.95959 | 0.90502 | -0.054567 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | ALTOONA4 | 0.95959 | 0.90502 | -0.054567 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | ALTOONA4 | 0.95959 | 0.90502 | -0.054567 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | ALTOONA4 | 0.95959 | 0.90502 | -0.054567 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | ALTOONA4 | 0.95959 | 0.90502 | -0.054567 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | ALTOONA4 | 0.95959 | 0.90502 | -0.054567 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | ALTOONA4 | 0.95959 | 0.90502 | -0.054567 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | ALTOONA4 | 0.95959 | 0.90502 | -0.054567 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | ALTOONA4 | 0.95959 | 0.90502 | -0.054567 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | ALTOONA4 | 0.95959 | 0.90502 | -0.054567 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | ALTOONA4 | 0.95959 | 0.90502 | -0.054567 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | ALTOONA4 | 0.95959 | 0.90502 | -0.054567 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | ALTOONA4 | 0.95959 | 0.90502 | -0.054567 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | ALTOONA4 | 0.95959 | 0.90502 | -0.054567 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | ALTOONA4 | 0.95959 | 0.90502 | -0.054567 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | ALTOONA4 | 0.95959 | 0.90502 | -0.054567 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | ALTOONA4 | 0.95959 | 0.90502 | -0.054567 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | ALTOONA4 | 0.95959 | 0.90502 | -0.054567 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | ANGELUS | 0.96541 | 0.89863 | -0.066777 |  | 0.9 | 1.05 | 0.041569 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | ANGELUS | 0.96541 | 0.89863 | -0.066777 |  | 0.9 | 1.05 | 0.031515 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | ANGELUS | 0.96541 | 0.89863 | -0.066777 |  | 0.9 | 1.05 | 0.031515 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | ANGELUS | 0.96541 | 0.89863 | -0.066777 |  | 0.9 | 1.05 | 0.03222 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | ANGELUS | 0.96541 | 0.89863 | -0.066777 |  | 0.9 | 1.05 | 0.030633 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | ANGELUS | 0.96541 | 0.89863 | -0.066777 |  | 0.9 | 1.05 | 0.030061 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | ANGELUS | 0.96541 | 0.89863 | -0.066777 |  | 0.9 | 1.05 | 0.031207 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | ANTIOCH5 | 0.96669 | 0.92217 | -0.044512 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | ANTIOCH5 | 0.96669 | 0.92217 | -0.044512 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | ANTIOCH5 | 0.96669 | 0.92217 | -0.044512 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | ANTIOCH5 | 0.96669 | 0.92217 | -0.044512 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | ANTIOCH5 | 0.96669 | 0.92217 | -0.044512 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | ANTIOCH5 | 0.96669 | 0.92217 | -0.044512 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | ANTIOCH5 | 0.96669 | 0.92217 | -0.044512 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | ANTIOCH5 | 0.96669 | 0.92217 | -0.044512 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | ANTIOCH5 | 0.96669 | 0.92217 | -0.044512 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | ANTIOCH5 | 0.96669 | 0.92217 | -0.044512 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | ANTIOCH5 | 0.96669 | 0.92217 | -0.044512 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | ANTIOCH5 | 0.96669 | 0.92217 | -0.044512 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | ANTIOCH5 | 0.96669 | 0.92217 | -0.044512 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | ANTIOCH5 | 0.96669 | 0.92217 | -0.044512 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | ANTIOCH5 | 0.96669 | 0.92217 | -0.044512 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | ANTIOCH5 | 0.96669 | 0.92217 | -0.044512 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | ANTIOCH5 | 0.96669 | 0.92217 | -0.044512 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | ANTIOCH5 | 0.96669 | 0.92217 | -0.044512 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | ANTIOCH5 | 0.96669 | 0.92217 | -0.044512 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | ANTIOCH5 | 0.96669 | 0.92217 | -0.044512 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | ANTIOCH5 | 0.97865 | 0.92958 | -0.049065 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | ANTIOCH5 | 0.97865 | 0.92958 | -0.049065 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | ANTIOCH5 | 0.97865 | 0.92958 | -0.049065 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | ANTIOCH5 | 0.97865 | 0.92958 | -0.049065 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | ANTIOCH5 | 0.97865 | 0.92958 | -0.049065 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | ANTIOCH5 | 0.97865 | 0.92958 | -0.049065 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | ANTIOCH5 | 0.97865 | 0.92958 | -0.049065 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | ANTIOCH5 | 0.97865 | 0.92958 | -0.049065 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | ANTIOCH5 | 0.97865 | 0.92958 | -0.049065 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | ANTIOCH5 | 0.97865 | 0.92958 | -0.049065 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | ANTIOCH5 | 0.97865 | 0.92958 | -0.049065 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | ANTIOCH5 | 0.97865 | 0.92958 | -0.049065 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | ANTIOCH5 | 0.97865 | 0.92958 | -0.049065 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | ANTIOCH5 | 0.97865 | 0.92958 | -0.049065 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | ANTIOCH5 | 0.97865 | 0.92958 | -0.049065 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | ANTIOCH5 | 0.97865 | 0.92958 | -0.049065 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | ANTIOCH5 | 0.97865 | 0.92958 | -0.049065 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | ANTIOCH5 | 0.97865 | 0.92958 | -0.049065 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | ANTIOCH5 | 0.97865 | 0.92958 | -0.049065 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | ANTIOCH5 | 0.97865 | 0.92958 | -0.049065 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | ANTIOCH5 | 0.97927 | 0.89852 | -0.080746 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | ANTIOCH5 | 0.97927 | 0.89852 | -0.080746 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | ANTIOCH5 | 0.97927 | 0.89852 | -0.080746 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | ANTIOCH5 | 0.97927 | 0.89852 | -0.080746 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | ANTIOCH5 | 0.97927 | 0.89852 | -0.080746 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | ANTIOCH5 | 0.97927 | 0.89852 | -0.080746 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | ANTIOCH5 | 0.97927 | 0.89852 | -0.080746 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | ANTIOCH5 | 0.97927 | 0.89852 | -0.080746 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | ANTIOCH5 | 0.97927 | 0.89852 | -0.080746 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | ANTIOCH5 | 0.97927 | 0.89852 | -0.080746 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | ANTIOCH5 | 0.97927 | 0.89852 | -0.080746 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | ANTIOCH5 | 0.97927 | 0.89852 | -0.080746 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | ANTIOCH5 | 0.97927 | 0.89852 | -0.080746 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | ANTIOCH5 | 0.97927 | 0.89852 | -0.080746 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | ANTIOCH5 | 0.97927 | 0.89852 | -0.080746 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | ANTIOCH5 | 0.97927 | 0.89852 | -0.080746 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | ANTIOCH5 | 0.97927 | 0.89852 | -0.080746 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | ANTIOCH5 | 0.97927 | 0.89852 | -0.080746 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | ANTIOCH5 | 0.97927 | 0.89852 | -0.080746 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | ANTIOCH5 | 0.97927 | 0.89852 | -0.080746 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | ANTIOCH5 | 0.97927 | 0.89852 | -0.080746 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | ANTIOCH5 | 0.97927 | 0.89852 | -0.080746 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | ANTIOCH5 | 0.97927 | 0.89852 | -0.080746 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | ANTIOCH5 | 0.97927 | 0.89852 | -0.080746 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | ANTIOCH5 | 0.97927 | 0.89852 | -0.080746 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | ANTIOCH5 | 0.97927 | 0.89852 | -0.080746 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | ANTIOCH5 | 0.97927 | 0.89852 | -0.080746 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | ANTIOCH5 | 0.97927 | 0.89852 | -0.080746 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | ARC250 2 | 0.97643 | 0.92339 | -0.05304 |  | 0.925 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | ARC250 2 | 0.97643 | 0.92339 | -0.05304 |  | 0.925 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | ARC250 2 | 0.97643 | 0.92339 | -0.05304 |  | 0.925 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | ARC250 2 | 0.97643 | 0.92339 | -0.05304 |  | 0.925 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | ARC250 2 | 0.97643 | 0.92339 | -0.05304 |  | 0.925 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | ARC250 2 | 0.97643 | 0.92339 | -0.05304 |  | 0.925 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | ARC250 2 | 0.97643 | 0.92339 | -0.05304 |  | 0.925 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | ARC250 2 | 0.97643 | 0.92339 | -0.05304 |  | 0.925 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | ARC250 2 | 0.97643 | 0.92339 | -0.05304 |  | 0.925 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | ARC250 2 | 0.97643 | 0.92339 | -0.05304 |  | 0.925 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | ARC250 2 | 0.97643 | 0.92339 | -0.05304 |  | 0.925 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | ARC250 2 | 0.97643 | 0.92339 | -0.05304 |  | 0.925 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | ARC250 2 | 0.97643 | 0.92339 | -0.05304 |  | 0.925 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | ARC250 2 | 0.97643 | 0.92339 | -0.05304 |  | 0.925 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | ARC250 2 | 0.97643 | 0.92339 | -0.05304 |  | 0.925 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | ARC250 2 | 0.97643 | 0.92339 | -0.05304 |  | 0.925 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | ARC250 2 | 0.97643 | 0.92339 | -0.05304 |  | 0.925 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | ARC250 2 | 0.97643 | 0.92339 | -0.05304 |  | 0.925 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | ARC250 2 | 0.97643 | 0.92339 | -0.05304 |  | 0.925 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | ARC250 2 | 0.97643 | 0.92339 | -0.05304 |  | 0.925 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | ARC250 2 | 0.97643 | 0.92339 | -0.05304 |  | 0.925 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | ARC250 2 | 0.97643 | 0.92339 | -0.05304 |  | 0.925 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | ARC250 2 | 0.97643 | 0.92339 | -0.05304 |  | 0.925 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | ARC250 2 | 0.97643 | 0.92339 | -0.05304 |  | 0.925 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | ARC250 2 | 0.97643 | 0.92339 | -0.05304 |  | 0.925 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | ARC250 2 | 0.97643 | 0.92339 | -0.05304 |  | 0.925 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | ARC250 2 | 0.97643 | 0.92339 | -0.05304 |  | 0.925 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | ARC250 2 | 0.97643 | 0.92339 | -0.05304 |  | 0.925 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | ARCHIE 5 | 0.99168 | 0.92366 | -0.068021 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | ARCHIE 5 | 0.99168 | 0.92366 | -0.068021 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | ARCHIE 5 | 0.99168 | 0.92366 | -0.068021 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | ARCHIE 5 | 0.99168 | 0.92366 | -0.068021 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | ARCHIE 5 | 0.99168 | 0.92366 | -0.068021 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | ARCHIE 5 | 0.99168 | 0.92366 | -0.068021 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | ARCHIE 5 | 0.99168 | 0.92366 | -0.068021 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | ARCHIE 5 | 0.99168 | 0.92366 | -0.068021 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | ARCHIE 5 | 0.99168 | 0.92366 | -0.068021 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | ARCHIE 5 | 0.99168 | 0.92366 | -0.068021 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | ARCHIE 5 | 0.99168 | 0.92366 | -0.068021 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | ARCHIE 5 | 0.99168 | 0.92366 | -0.068021 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | ARCHIE 5 | 0.99168 | 0.92366 | -0.068021 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | ARCHIE 5 | 0.99168 | 0.92366 | -0.068021 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | ARCHIE 5 | 0.99168 | 0.92366 | -0.068021 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | ARCHIE 5 | 0.99168 | 0.92366 | -0.068021 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | ARCHIE 5 | 0.99168 | 0.92366 | -0.068021 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | ARCHIE 5 | 0.99168 | 0.92366 | -0.068021 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | ARCHIE 5 | 0.99168 | 0.92366 | -0.068021 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | ARCHIE 5 | 0.99168 | 0.92366 | -0.068021 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | ARCHIE 5 | 0.99168 | 0.92366 | -0.068021 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | ARCHIE 5 | 0.99168 | 0.92366 | -0.068021 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | ARCHIE 5 | 0.99168 | 0.92366 | -0.068021 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | ARCHIE 5 | 0.99168 | 0.92366 | -0.068021 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | ARCHIE 5 | 0.99168 | 0.92366 | -0.068021 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | ARCHIE 5 | 0.99168 | 0.92366 | -0.068021 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | ARCHIE 5 | 0.99168 | 0.92366 | -0.068021 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | ARCHIE 5 | 0.99168 | 0.92366 | -0.068021 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | ARNOLD3 | 0.94057 | 0.87467 | -0.065903 |  | 0.9 | 1.05 | 0.046736 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | ARNOLD3 | 0.94057 | 0.87467 | -0.065903 |  | 0.9 | 1.05 | 0.030145 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | ARNOLD3 | 0.94515 | 0.87437 | -0.070784 |  | 0.9 | 1.05 | 0.046736 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | ARNOLD3 | 0.94515 | 0.87437 | -0.070784 |  | 0.9 | 1.05 | 0.030145 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | ARNOLD3 | 0.94515 | 0.87437 | -0.070784 |  | 0.9 | 1.05 | 0.046736 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | ARNOLD3 | 0.94515 | 0.87437 | -0.070784 |  | 0.9 | 1.05 | 0.030145 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | ARNOLD3 | 0.94515 | 0.87437 | -0.070785 |  | 0.9 | 1.05 | 0.046736 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | ARNOLD3 | 0.94515 | 0.87437 | -0.070785 |  | 0.9 | 1.05 | 0.030145 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | ASG-2018-010 | 1.0148 | 0.92915 | -0.085606 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | ASG-2018-010 | 1.0148 | 0.92915 | -0.085606 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | ASG-2018-010 | 1.0148 | 0.92915 | -0.085606 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | ASG-2018-010 | 1.0148 | 0.92915 | -0.085606 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | ASG-2018-010 | 1.0148 | 0.92915 | -0.085606 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | ASG-2018-010 | 1.0148 | 0.92915 | -0.085606 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | ASG-2018-010 | 1.0148 | 0.92915 | -0.085606 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | ASG-2018-010 | 1.0148 | 0.92915 | -0.085606 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | ASG-2018-010 | 1.0148 | 0.92915 | -0.085606 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | ASG-2018-010 | 1.0148 | 0.92915 | -0.085606 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | ASG-2018-010 | 1.0148 | 0.92915 | -0.085606 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | ASG-2018-010 | 1.0148 | 0.92915 | -0.085606 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | ASG-2018-010 | 1.0148 | 0.92915 | -0.085606 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | ASG-2018-010 | 1.0148 | 0.92915 | -0.085606 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | ASG-2018-010 | 1.0148 | 0.92915 | -0.085606 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | ASG-2018-010 | 1.0148 | 0.92915 | -0.085606 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | ASG-2018-010 | 1.0148 | 0.92915 | -0.085606 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | ASG-2018-010 | 1.0148 | 0.92915 | -0.085606 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | ASG-2018-010 | 1.0148 | 0.92915 | -0.085606 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | ASG-2018-010 | 1.0148 | 0.92915 | -0.085606 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | ASG-2018-010 | 1.0148 | 0.92915 | -0.085606 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | ASG-2018-010 | 1.0148 | 0.92915 | -0.085606 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | ASG-2018-010 | 1.0148 | 0.92915 | -0.085606 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | ASG-2018-010 | 1.0148 | 0.92915 | -0.085606 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | ASG-2018-010 | 1.0148 | 0.92915 | -0.085606 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | ASG-2018-010 | 1.0148 | 0.92915 | -0.085606 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | ASG-2018-010 | 1.0148 | 0.92915 | -0.085606 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | ASG-2018-010 | 1.0148 | 0.92915 | -0.085606 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | ASG-2018-011 | 1.0149 | 0.92439 | -0.090536 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | ASG-2018-011 | 1.0149 | 0.92439 | -0.090536 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | ASG-2018-011 | 1.0149 | 0.92439 | -0.090536 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | ASG-2018-011 | 1.0149 | 0.92439 | -0.090536 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | ASG-2018-011 | 1.0149 | 0.92439 | -0.090536 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | ASG-2018-011 | 1.0149 | 0.92439 | -0.090536 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | ASG-2018-011 | 1.0149 | 0.92439 | -0.090536 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | ASG-2018-011 | 1.0149 | 0.92439 | -0.090536 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | ASG-2018-011 | 1.0149 | 0.92439 | -0.090536 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | ASG-2018-011 | 1.0149 | 0.92439 | -0.090536 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | ASG-2018-011 | 1.0149 | 0.92439 | -0.090536 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | ASG-2018-011 | 1.0149 | 0.92439 | -0.090536 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | ASG-2018-011 | 1.0149 | 0.92439 | -0.090536 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | ASG-2018-011 | 1.0149 | 0.92439 | -0.090536 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | ASG-2018-011 | 1.0149 | 0.92439 | -0.090536 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | ASG-2018-011 | 1.0149 | 0.92439 | -0.090536 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | ASG-2018-011 | 1.0149 | 0.92439 | -0.090536 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | ASG-2018-011 | 1.0149 | 0.92439 | -0.090536 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | ASG-2018-011 | 1.0149 | 0.92439 | -0.090536 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | ASG-2018-011 | 1.0149 | 0.92439 | -0.090536 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | ASG-2018-011 | 1.0149 | 0.92439 | -0.090536 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | ASG-2018-011 | 1.0149 | 0.92439 | -0.090536 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | ASG-2018-011 | 1.0149 | 0.92439 | -0.090536 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | ASG-2018-011 | 1.0149 | 0.92439 | -0.090536 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | ASG-2018-011 | 1.0149 | 0.92439 | -0.090536 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | ASG-2018-011 | 1.0149 | 0.92439 | -0.090536 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | ASG-2018-011 | 1.0149 | 0.92439 | -0.090536 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | ASG-2018-011 | 1.0149 | 0.92439 | -0.090536 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | ATLNTIC3 | 0.96606 | 0.92529 | -0.040769 |  | 0.93 | 1.05 | 0.03768 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | ATLNTIC3 | 0.96606 | 0.92529 | -0.040769 |  | 0.93 | 1.05 | 0.054649 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | ATLNTIC3 | 0.96606 | 0.92529 | -0.040769 |  | 0.93 | 1.05 | 0.041275 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | ATLNTIC3 | 0.96606 | 0.92529 | -0.040769 |  | 0.93 | 1.05 | 0.032793 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | ATLNTIC3 | 0.96606 | 0.92529 | -0.040769 |  | 0.93 | 1.05 | 0.043592 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | ATLNTIC3 | 0.96606 | 0.92529 | -0.040769 |  | 0.93 | 1.05 | 0.040246 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | ATLNTIC3 | 0.96606 | 0.92529 | -0.040769 |  | 0.93 | 1.05 | 0.030207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | ATLNTIC3 | 0.96606 | 0.92529 | -0.040769 |  | 0.93 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | ATLNTIC3 | 0.96606 | 0.92529 | -0.040769 |  | 0.93 | 1.05 | 0.069525 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | ATLNTIC3 | 0.96606 | 0.92529 | -0.040769 |  | 0.93 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | ATLNTIC3 | 0.96606 | 0.92529 | -0.040769 |  | 0.93 | 1.05 | 0.032357 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | ATLNTIC3 | 0.96606 | 0.92529 | -0.040769 |  | 0.93 | 1.05 | 0.033611 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | ATLNTIC3 | 0.96606 | 0.92529 | -0.040769 |  | 0.93 | 1.05 | 0.030163 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | ATLNTIC3 | 0.96606 | 0.92529 | -0.040769 |  | 0.93 | 1.05 | 0.042714 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | ATLNTIC3 | 0.96606 | 0.92529 | -0.040769 |  | 0.93 | 1.05 | 0.042627 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | ATLNTIC3 | 0.96606 | 0.92529 | -0.040769 |  | 0.93 | 1.05 | 0.032319 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | ATLNTIC3 | 0.96606 | 0.92529 | -0.040769 |  | 0.93 | 1.05 | 0.034532 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | ATLNTIC3 | 0.96606 | 0.92529 | -0.040769 |  | 0.93 | 1.05 | 0.030438 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | ATLNTIC3 | 0.96606 | 0.92529 | -0.040769 |  | 0.93 | 1.05 | 0.035207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | ATLNTIC3 | 0.96606 | 0.92529 | -0.040769 |  | 0.93 | 1.05 | 0.030949 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | ATLNTIC3 | 0.95919 | 0.91277 | -0.046416 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | ATLNTIC3 | 0.95919 | 0.91277 | -0.046416 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | ATLNTIC3 | 0.95919 | 0.91277 | -0.046416 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | ATLNTIC3 | 0.95919 | 0.91277 | -0.046416 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | ATLNTIC3 | 0.95919 | 0.91277 | -0.046416 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | ATLNTIC3 | 0.95919 | 0.91277 | -0.046416 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | ATLNTIC3 | 0.95919 | 0.91277 | -0.046416 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | ATLNTIC3 | 0.95919 | 0.91277 | -0.046416 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | ATLNTIC3 | 0.95919 | 0.91277 | -0.046416 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | ATLNTIC3 | 0.95919 | 0.91277 | -0.046416 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | ATLNTIC3 | 0.95919 | 0.91277 | -0.046416 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | ATLNTIC3 | 0.95919 | 0.91277 | -0.046416 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | ATLNTIC3 | 0.95919 | 0.91277 | -0.046416 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | ATLNTIC3 | 0.95919 | 0.91277 | -0.046416 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | ATLNTIC3 | 0.95919 | 0.91277 | -0.046416 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | ATLNTIC3 | 0.95919 | 0.91277 | -0.046416 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | ATLNTIC3 | 0.95919 | 0.91277 | -0.046416 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | ATLNTIC3 | 0.95919 | 0.91277 | -0.046416 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | ATLNTIC3 | 0.95919 | 0.91277 | -0.046416 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | ATLNTIC3 | 0.95919 | 0.91277 | -0.046416 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | ATLNTIC3 | 0.97045 | 0.91898 | -0.051471 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | ATLNTIC3 | 0.97045 | 0.91898 | -0.051471 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | ATLNTIC3 | 0.97045 | 0.91898 | -0.051471 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | ATLNTIC3 | 0.97045 | 0.91898 | -0.051471 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | ATLNTIC3 | 0.97045 | 0.91898 | -0.051471 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | ATLNTIC3 | 0.97045 | 0.91898 | -0.051471 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | ATLNTIC3 | 0.97045 | 0.91898 | -0.051471 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | ATLNTIC3 | 0.97045 | 0.91898 | -0.051471 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | ATLNTIC3 | 0.97045 | 0.91898 | -0.051471 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | ATLNTIC3 | 0.97045 | 0.91898 | -0.051471 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | ATLNTIC3 | 0.97045 | 0.91898 | -0.051471 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | ATLNTIC3 | 0.97045 | 0.91898 | -0.051471 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | ATLNTIC3 | 0.97045 | 0.91898 | -0.051471 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | ATLNTIC3 | 0.97045 | 0.91898 | -0.051471 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | ATLNTIC3 | 0.97045 | 0.91898 | -0.051471 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | ATLNTIC3 | 0.97045 | 0.91898 | -0.051471 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | ATLNTIC3 | 0.97045 | 0.91898 | -0.051471 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | ATLNTIC3 | 0.97045 | 0.91898 | -0.051471 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | ATLNTIC3 | 0.97045 | 0.91898 | -0.051471 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | ATLNTIC3 | 0.97045 | 0.91898 | -0.051471 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | ATLNTIC3 | 0.97665 | 0.90459 | -0.072053 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | ATLNTIC3 | 0.97665 | 0.90459 | -0.072053 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | ATLNTIC3 | 0.97665 | 0.90459 | -0.072053 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | ATLNTIC3 | 0.97665 | 0.90459 | -0.072053 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | ATLNTIC3 | 0.97665 | 0.90459 | -0.072053 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | ATLNTIC3 | 0.97665 | 0.90459 | -0.072053 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | ATLNTIC3 | 0.97665 | 0.90459 | -0.072053 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | ATLNTIC3 | 0.97665 | 0.90459 | -0.072053 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | ATLNTIC3 | 0.97665 | 0.90459 | -0.072053 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | ATLNTIC3 | 0.97665 | 0.90459 | -0.072053 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | ATLNTIC3 | 0.97665 | 0.90459 | -0.072053 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | ATLNTIC3 | 0.97665 | 0.90459 | -0.072053 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | ATLNTIC3 | 0.97665 | 0.90459 | -0.072053 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | ATLNTIC3 | 0.97665 | 0.90459 | -0.072053 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | ATLNTIC3 | 0.97665 | 0.90459 | -0.072053 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | ATLNTIC3 | 0.97665 | 0.90459 | -0.072053 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | ATLNTIC3 | 0.97665 | 0.90459 | -0.072053 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | ATLNTIC3 | 0.97665 | 0.90459 | -0.072053 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | ATLNTIC3 | 0.97665 | 0.90459 | -0.072053 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | ATLNTIC3 | 0.97665 | 0.90459 | -0.072053 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | ATLNTIC3 | 0.97665 | 0.90459 | -0.072053 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | ATLNTIC3 | 0.97665 | 0.90459 | -0.072053 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | ATLNTIC3 | 0.97665 | 0.90459 | -0.072053 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | ATLNTIC3 | 0.97665 | 0.90459 | -0.072053 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | ATLNTIC3 | 0.97665 | 0.90459 | -0.072053 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | ATLNTIC3 | 0.97665 | 0.90459 | -0.072053 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | ATLNTIC3 | 0.97665 | 0.90459 | -0.072053 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | ATLNTIC3 | 0.97665 | 0.90459 | -0.072053 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | ATLNTIC3 | 0.96532 | 0.92357 | -0.041753 |  | 0.93 | 1.05 | 0.03768 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | ATLNTIC3 | 0.96532 | 0.92357 | -0.041753 |  | 0.93 | 1.05 | 0.054649 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | ATLNTIC3 | 0.96532 | 0.92357 | -0.041753 |  | 0.93 | 1.05 | 0.041275 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | ATLNTIC3 | 0.96532 | 0.92357 | -0.041753 |  | 0.93 | 1.05 | 0.032793 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | ATLNTIC3 | 0.96532 | 0.92357 | -0.041753 |  | 0.93 | 1.05 | 0.043592 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | ATLNTIC3 | 0.96532 | 0.92357 | -0.041753 |  | 0.93 | 1.05 | 0.040246 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | ATLNTIC3 | 0.96532 | 0.92357 | -0.041753 |  | 0.93 | 1.05 | 0.030207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | ATLNTIC3 | 0.96532 | 0.92357 | -0.041753 |  | 0.93 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | ATLNTIC3 | 0.96532 | 0.92357 | -0.041753 |  | 0.93 | 1.05 | 0.069525 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | ATLNTIC3 | 0.96532 | 0.92357 | -0.041753 |  | 0.93 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | ATLNTIC3 | 0.96532 | 0.92357 | -0.041753 |  | 0.93 | 1.05 | 0.032357 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | ATLNTIC3 | 0.96532 | 0.92357 | -0.041753 |  | 0.93 | 1.05 | 0.033611 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | ATLNTIC3 | 0.96532 | 0.92357 | -0.041753 |  | 0.93 | 1.05 | 0.030163 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | ATLNTIC3 | 0.96532 | 0.92357 | -0.041753 |  | 0.93 | 1.05 | 0.042714 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | ATLNTIC3 | 0.96532 | 0.92357 | -0.041753 |  | 0.93 | 1.05 | 0.042627 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | ATLNTIC3 | 0.96532 | 0.92357 | -0.041753 |  | 0.93 | 1.05 | 0.032319 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | ATLNTIC3 | 0.96532 | 0.92357 | -0.041753 |  | 0.93 | 1.05 | 0.034532 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | ATLNTIC3 | 0.96532 | 0.92357 | -0.041753 |  | 0.93 | 1.05 | 0.030438 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | ATLNTIC3 | 0.96532 | 0.92357 | -0.041753 |  | 0.93 | 1.05 | 0.035207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | ATLNTIC3 | 0.96532 | 0.92357 | -0.041753 |  | 0.93 | 1.05 | 0.030949 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | ATLNTIC7 | 0.96098 | 0.91793 | -0.043045 |  | 0.95 | 1.05 | 0.03768 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | ATLNTIC7 | 0.96098 | 0.91793 | -0.043045 |  | 0.95 | 1.05 | 0.054649 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | ATLNTIC7 | 0.96098 | 0.91793 | -0.043045 |  | 0.95 | 1.05 | 0.041275 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | ATLNTIC7 | 0.96098 | 0.91793 | -0.043045 |  | 0.95 | 1.05 | 0.032793 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | ATLNTIC7 | 0.96098 | 0.91793 | -0.043045 |  | 0.95 | 1.05 | 0.043592 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | ATLNTIC7 | 0.96098 | 0.91793 | -0.043045 |  | 0.95 | 1.05 | 0.040246 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | ATLNTIC7 | 0.96098 | 0.91793 | -0.043045 |  | 0.95 | 1.05 | 0.030207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | ATLNTIC7 | 0.96098 | 0.91793 | -0.043045 |  | 0.95 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | ATLNTIC7 | 0.96098 | 0.91793 | -0.043045 |  | 0.95 | 1.05 | 0.069525 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | ATLNTIC7 | 0.96098 | 0.91793 | -0.043045 |  | 0.95 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | ATLNTIC7 | 0.96098 | 0.91793 | -0.043045 |  | 0.95 | 1.05 | 0.032357 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | ATLNTIC7 | 0.96098 | 0.91793 | -0.043045 |  | 0.95 | 1.05 | 0.033611 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | ATLNTIC7 | 0.96098 | 0.91793 | -0.043045 |  | 0.95 | 1.05 | 0.030163 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | ATLNTIC7 | 0.96098 | 0.91793 | -0.043045 |  | 0.95 | 1.05 | 0.042714 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | ATLNTIC7 | 0.96098 | 0.91793 | -0.043045 |  | 0.95 | 1.05 | 0.042627 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | ATLNTIC7 | 0.96098 | 0.91793 | -0.043045 |  | 0.95 | 1.05 | 0.032319 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | ATLNTIC7 | 0.96098 | 0.91793 | -0.043045 |  | 0.95 | 1.05 | 0.034532 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | ATLNTIC7 | 0.96098 | 0.91793 | -0.043045 |  | 0.95 | 1.05 | 0.030438 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | ATLNTIC7 | 0.96098 | 0.91793 | -0.043045 |  | 0.95 | 1.05 | 0.035207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | ATLNTIC7 | 0.96098 | 0.91793 | -0.043045 |  | 0.95 | 1.05 | 0.030949 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | ATLNTIC7 | 0.95327 | 0.90445 | -0.048825 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | ATLNTIC7 | 0.95327 | 0.90445 | -0.048825 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | ATLNTIC7 | 0.95327 | 0.90445 | -0.048825 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | ATLNTIC7 | 0.95327 | 0.90445 | -0.048825 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | ATLNTIC7 | 0.95327 | 0.90445 | -0.048825 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | ATLNTIC7 | 0.95327 | 0.90445 | -0.048825 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | ATLNTIC7 | 0.95327 | 0.90445 | -0.048825 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | ATLNTIC7 | 0.95327 | 0.90445 | -0.048825 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | ATLNTIC7 | 0.95327 | 0.90445 | -0.048825 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | ATLNTIC7 | 0.95327 | 0.90445 | -0.048825 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | ATLNTIC7 | 0.95327 | 0.90445 | -0.048825 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | ATLNTIC7 | 0.95327 | 0.90445 | -0.048825 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | ATLNTIC7 | 0.95327 | 0.90445 | -0.048825 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | ATLNTIC7 | 0.95327 | 0.90445 | -0.048825 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | ATLNTIC7 | 0.95327 | 0.90445 | -0.048825 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | ATLNTIC7 | 0.95327 | 0.90445 | -0.048825 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | ATLNTIC7 | 0.95327 | 0.90445 | -0.048825 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | ATLNTIC7 | 0.95327 | 0.90445 | -0.048825 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | ATLNTIC7 | 0.95327 | 0.90445 | -0.048825 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | ATLNTIC7 | 0.95327 | 0.90445 | -0.048825 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | ATLNTIC7 | 0.96599 | 0.91118 | -0.054807 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | ATLNTIC7 | 0.96599 | 0.91118 | -0.054807 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | ATLNTIC7 | 0.96599 | 0.91118 | -0.054807 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | ATLNTIC7 | 0.96599 | 0.91118 | -0.054807 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | ATLNTIC7 | 0.96599 | 0.91118 | -0.054807 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | ATLNTIC7 | 0.96599 | 0.91118 | -0.054807 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | ATLNTIC7 | 0.96599 | 0.91118 | -0.054807 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | ATLNTIC7 | 0.96599 | 0.91118 | -0.054807 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | ATLNTIC7 | 0.96599 | 0.91118 | -0.054807 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | ATLNTIC7 | 0.96599 | 0.91118 | -0.054807 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | ATLNTIC7 | 0.96599 | 0.91118 | -0.054807 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | ATLNTIC7 | 0.96599 | 0.91118 | -0.054807 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | ATLNTIC7 | 0.96599 | 0.91118 | -0.054807 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | ATLNTIC7 | 0.96599 | 0.91118 | -0.054807 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | ATLNTIC7 | 0.96599 | 0.91118 | -0.054807 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | ATLNTIC7 | 0.96599 | 0.91118 | -0.054807 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | ATLNTIC7 | 0.96599 | 0.91118 | -0.054807 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | ATLNTIC7 | 0.96599 | 0.91118 | -0.054807 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | ATLNTIC7 | 0.96599 | 0.91118 | -0.054807 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | ATLNTIC7 | 0.96599 | 0.91118 | -0.054807 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | ATLNTIC7 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | ATLNTIC7 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | ATLNTIC7 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | ATLNTIC7 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | ATLNTIC7 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | ATLNTIC7 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | ATLNTIC7 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | ATLNTIC7 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | ATLNTIC7 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | ATLNTIC7 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | ATLNTIC7 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | ATLNTIC7 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | ATLNTIC7 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | ATLNTIC7 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | ATLNTIC7 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | ATLNTIC7 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | ATLNTIC7 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | ATLNTIC7 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | ATLNTIC7 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | ATLNTIC7 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | ATLNTIC7 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | ATLNTIC7 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | ATLNTIC7 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | ATLNTIC7 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | ATLNTIC7 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | ATLNTIC7 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | ATLNTIC7 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | ATLNTIC7 | 0.97205 | 0.89447 | -0.077575 |  | 0.95 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | ATLNTIC7 | 0.96016 | 0.91617 | -0.043992 |  | 0.95 | 1.05 | 0.03768 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | ATLNTIC7 | 0.96016 | 0.91617 | -0.043992 |  | 0.95 | 1.05 | 0.054649 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | ATLNTIC7 | 0.96016 | 0.91617 | -0.043992 |  | 0.95 | 1.05 | 0.041275 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | ATLNTIC7 | 0.96016 | 0.91617 | -0.043992 |  | 0.95 | 1.05 | 0.032793 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | ATLNTIC7 | 0.96016 | 0.91617 | -0.043992 |  | 0.95 | 1.05 | 0.043592 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | ATLNTIC7 | 0.96016 | 0.91617 | -0.043992 |  | 0.95 | 1.05 | 0.040246 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | ATLNTIC7 | 0.96016 | 0.91617 | -0.043992 |  | 0.95 | 1.05 | 0.030207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | ATLNTIC7 | 0.96016 | 0.91617 | -0.043992 |  | 0.95 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | ATLNTIC7 | 0.96016 | 0.91617 | -0.043992 |  | 0.95 | 1.05 | 0.069525 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | ATLNTIC7 | 0.96016 | 0.91617 | -0.043992 |  | 0.95 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | ATLNTIC7 | 0.96016 | 0.91617 | -0.043992 |  | 0.95 | 1.05 | 0.032357 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | ATLNTIC7 | 0.96016 | 0.91617 | -0.043992 |  | 0.95 | 1.05 | 0.033611 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | ATLNTIC7 | 0.96016 | 0.91617 | -0.043992 |  | 0.95 | 1.05 | 0.030163 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | ATLNTIC7 | 0.96016 | 0.91617 | -0.043992 |  | 0.95 | 1.05 | 0.042714 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | ATLNTIC7 | 0.96016 | 0.91617 | -0.043992 |  | 0.95 | 1.05 | 0.042627 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | ATLNTIC7 | 0.96016 | 0.91617 | -0.043992 |  | 0.95 | 1.05 | 0.032319 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | ATLNTIC7 | 0.96016 | 0.91617 | -0.043992 |  | 0.95 | 1.05 | 0.034532 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | ATLNTIC7 | 0.96016 | 0.91617 | -0.043992 |  | 0.95 | 1.05 | 0.030438 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | ATLNTIC7 | 0.96016 | 0.91617 | -0.043992 |  | 0.95 | 1.05 | 0.035207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | ATLNTIC7 | 0.96016 | 0.91617 | -0.043992 |  | 0.95 | 1.05 | 0.030949 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | ATWODSW3 | 0.95717 | 0.89279 | -0.064377 |  | 0.9 | 1.05 | 0.041569 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | ATWODSW3 | 0.95717 | 0.89279 | -0.064377 |  | 0.9 | 1.05 | 0.031515 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | ATWODSW3 | 0.95717 | 0.89279 | -0.064377 |  | 0.9 | 1.05 | 0.031515 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | ATWODSW3 | 0.95717 | 0.89279 | -0.064377 |  | 0.9 | 1.05 | 0.03222 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | ATWODSW3 | 0.95717 | 0.89279 | -0.064377 |  | 0.9 | 1.05 | 0.030633 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | ATWODSW3 | 0.95717 | 0.89279 | -0.064377 |  | 0.9 | 1.05 | 0.030061 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | ATWODSW3 | 0.95717 | 0.89279 | -0.064377 |  | 0.9 | 1.05 | 0.031207 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | ATWODSW3 | 0.95976 | 0.89448 | -0.065274 |  | 0.9 | 1.05 | 0.046736 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | ATWODSW3 | 0.95976 | 0.89448 | -0.065274 |  | 0.9 | 1.05 | 0.030145 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | ATWODSW3 | 0.96028 | 0.89042 | -0.069859 |  | 0.9 | 1.05 | 0.046736 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | ATWODSW3 | 0.96028 | 0.89042 | -0.069859 |  | 0.9 | 1.05 | 0.030145 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | ATWODSW3 | 0.96028 | 0.89042 | -0.069859 |  | 0.9 | 1.05 | 0.046736 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | ATWODSW3 | 0.96028 | 0.89042 | -0.069859 |  | 0.9 | 1.05 | 0.030145 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | ATWODSW3 | 0.96028 | 0.89042 | -0.06986 |  | 0.9 | 1.05 | 0.046736 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | ATWODSW3 | 0.96028 | 0.89042 | -0.06986 |  | 0.9 | 1.05 | 0.030145 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | ATWOOD 3 | 0.95707 | 0.89071 | -0.066358 |  | 0.9 | 1.05 | 0.041569 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | ATWOOD 3 | 0.95707 | 0.89071 | -0.066358 |  | 0.9 | 1.05 | 0.031515 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | ATWOOD 3 | 0.95707 | 0.89071 | -0.066358 |  | 0.9 | 1.05 | 0.031515 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | ATWOOD 3 | 0.95707 | 0.89071 | -0.066358 |  | 0.9 | 1.05 | 0.03222 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | ATWOOD 3 | 0.95707 | 0.89071 | -0.066358 |  | 0.9 | 1.05 | 0.030633 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | ATWOOD 3 | 0.95707 | 0.89071 | -0.066358 |  | 0.9 | 1.05 | 0.030061 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | ATWOOD 3 | 0.95707 | 0.89071 | -0.066358 |  | 0.9 | 1.05 | 0.031207 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | ATWOOD 3 | 0.95723 | 0.89385 | -0.06338 |  | 0.9 | 1.05 | 0.041569 | P42:345:NPPD:BKR-MAC-3304:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | ATWOOD 3 | 0.95723 | 0.89385 | -0.06338 |  | 0.9 | 1.05 | 0.031515 | P42:345:NPPD:BKR-MAC-3304:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | ATWOOD 3 | 0.95723 | 0.89385 | -0.06338 |  | 0.9 | 1.05 | 0.031515 | P42:345:NPPD:BKR-MAC-3304:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | ATWOOD 3 | 0.95723 | 0.89385 | -0.06338 |  | 0.9 | 1.05 | 0.03222 | P42:345:NPPD:BKR-MAC-3304:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | ATWOOD 3 | 0.95723 | 0.89385 | -0.06338 |  | 0.9 | 1.05 | 0.030633 | P42:345:NPPD:BKR-MAC-3304:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | ATWOOD 3 | 0.95723 | 0.89385 | -0.06338 |  | 0.9 | 1.05 | 0.030061 | P42:345:NPPD:BKR-MAC-3304:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | ATWOOD 3 | 0.95723 | 0.89385 | -0.06338 |  | 0.9 | 1.05 | 0.031207 | P42:345:NPPD:BKR-MAC-3304:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | ATWOOD 3 | 0.96085 | 0.89047 | -0.070375 |  | 0.9 | 1.05 | 0.046736 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | ATWOOD 3 | 0.96085 | 0.89047 | -0.070375 |  | 0.9 | 1.05 | 0.030145 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | ATWOOD 3 | 0.96085 | 0.89047 | -0.070375 |  | 0.9 | 1.05 | 0.046736 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | ATWOOD 3 | 0.96085 | 0.89047 | -0.070375 |  | 0.9 | 1.05 | 0.030145 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | ATWOOD 3 | 0.96085 | 0.89047 | -0.070376 |  | 0.9 | 1.05 | 0.046736 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | ATWOOD 3 | 0.96085 | 0.89047 | -0.070376 |  | 0.9 | 1.05 | 0.030145 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | AUBURN 6 | 0.95952 | 0.9253 | -0.034219 |  | 0.95 | 1.05 | 0.03768 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | AUBURN 6 | 0.95952 | 0.9253 | -0.034219 |  | 0.95 | 1.05 | 0.054649 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | AUBURN 6 | 0.95952 | 0.9253 | -0.034219 |  | 0.95 | 1.05 | 0.041275 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | AUBURN 6 | 0.95952 | 0.9253 | -0.034219 |  | 0.95 | 1.05 | 0.032793 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | AUBURN 6 | 0.95952 | 0.9253 | -0.034219 |  | 0.95 | 1.05 | 0.043592 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | AUBURN 6 | 0.95952 | 0.9253 | -0.034219 |  | 0.95 | 1.05 | 0.040246 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | AUBURN 6 | 0.95952 | 0.9253 | -0.034219 |  | 0.95 | 1.05 | 0.030207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | AUBURN 6 | 0.95952 | 0.9253 | -0.034219 |  | 0.95 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | AUBURN 6 | 0.95952 | 0.9253 | -0.034219 |  | 0.95 | 1.05 | 0.069525 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | AUBURN 6 | 0.95952 | 0.9253 | -0.034219 |  | 0.95 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | AUBURN 6 | 0.95952 | 0.9253 | -0.034219 |  | 0.95 | 1.05 | 0.032357 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | AUBURN 6 | 0.95952 | 0.9253 | -0.034219 |  | 0.95 | 1.05 | 0.033611 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | AUBURN 6 | 0.95952 | 0.9253 | -0.034219 |  | 0.95 | 1.05 | 0.030163 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | AUBURN 6 | 0.95952 | 0.9253 | -0.034219 |  | 0.95 | 1.05 | 0.042714 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | AUBURN 6 | 0.95952 | 0.9253 | -0.034219 |  | 0.95 | 1.05 | 0.042627 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | AUBURN 6 | 0.95952 | 0.9253 | -0.034219 |  | 0.95 | 1.05 | 0.032319 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | AUBURN 6 | 0.95952 | 0.9253 | -0.034219 |  | 0.95 | 1.05 | 0.034532 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | AUBURN 6 | 0.95952 | 0.9253 | -0.034219 |  | 0.95 | 1.05 | 0.030438 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | AUBURN 6 | 0.95952 | 0.9253 | -0.034219 |  | 0.95 | 1.05 | 0.035207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | AUBURN 6 | 0.95952 | 0.9253 | -0.034219 |  | 0.95 | 1.05 | 0.030949 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | AUBURN 6 | 0.95645 | 0.91816 | -0.038288 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | AUBURN 6 | 0.95645 | 0.91816 | -0.038288 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | AUBURN 6 | 0.95645 | 0.91816 | -0.038288 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | AUBURN 6 | 0.95645 | 0.91816 | -0.038288 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | AUBURN 6 | 0.95645 | 0.91816 | -0.038288 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | AUBURN 6 | 0.95645 | 0.91816 | -0.038288 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | AUBURN 6 | 0.95645 | 0.91816 | -0.038288 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | AUBURN 6 | 0.95645 | 0.91816 | -0.038288 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | AUBURN 6 | 0.95645 | 0.91816 | -0.038288 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | AUBURN 6 | 0.95645 | 0.91816 | -0.038288 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | AUBURN 6 | 0.95645 | 0.91816 | -0.038288 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | AUBURN 6 | 0.95645 | 0.91816 | -0.038288 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | AUBURN 6 | 0.95645 | 0.91816 | -0.038288 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | AUBURN 6 | 0.95645 | 0.91816 | -0.038288 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | AUBURN 6 | 0.95645 | 0.91816 | -0.038288 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | AUBURN 6 | 0.95645 | 0.91816 | -0.038288 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | AUBURN 6 | 0.95645 | 0.91816 | -0.038288 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | AUBURN 6 | 0.95645 | 0.91816 | -0.038288 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | AUBURN 6 | 0.95645 | 0.91816 | -0.038288 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | AUBURN 6 | 0.95645 | 0.91816 | -0.038288 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | AUBURN 6 | 0.96203 | 0.91881 | -0.043213 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | AUBURN 6 | 0.96203 | 0.91881 | -0.043213 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | AUBURN 6 | 0.96203 | 0.91881 | -0.043213 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | AUBURN 6 | 0.96203 | 0.91881 | -0.043213 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | AUBURN 6 | 0.96203 | 0.91881 | -0.043213 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | AUBURN 6 | 0.96203 | 0.91881 | -0.043213 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | AUBURN 6 | 0.96203 | 0.91881 | -0.043213 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | AUBURN 6 | 0.96203 | 0.91881 | -0.043213 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | AUBURN 6 | 0.96203 | 0.91881 | -0.043213 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | AUBURN 6 | 0.96203 | 0.91881 | -0.043213 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | AUBURN 6 | 0.96203 | 0.91881 | -0.043213 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | AUBURN 6 | 0.96203 | 0.91881 | -0.043213 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | AUBURN 6 | 0.96203 | 0.91881 | -0.043213 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | AUBURN 6 | 0.96203 | 0.91881 | -0.043213 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | AUBURN 6 | 0.96203 | 0.91881 | -0.043213 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | AUBURN 6 | 0.96203 | 0.91881 | -0.043213 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | AUBURN 6 | 0.96203 | 0.91881 | -0.043213 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | AUBURN 6 | 0.96203 | 0.91881 | -0.043213 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | AUBURN 6 | 0.96203 | 0.91881 | -0.043213 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | AUBURN 6 | 0.96203 | 0.91881 | -0.043213 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | AUBURN 6 | 0.96487 | 0.916 | -0.048871 |  | 0.95 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | AUBURN 6 | 0.96487 | 0.916 | -0.048871 |  | 0.95 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | AUBURN 6 | 0.96487 | 0.916 | -0.048871 |  | 0.95 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | AUBURN 6 | 0.96487 | 0.916 | -0.048871 |  | 0.95 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | AUBURN 6 | 0.96487 | 0.916 | -0.048871 |  | 0.95 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | AUBURN 6 | 0.96487 | 0.916 | -0.048871 |  | 0.95 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | AUBURN 6 | 0.96487 | 0.916 | -0.048871 |  | 0.95 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | AUBURN 6 | 0.96487 | 0.916 | -0.048871 |  | 0.95 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | AUBURN 6 | 0.96487 | 0.916 | -0.048871 |  | 0.95 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | AUBURN 6 | 0.96487 | 0.916 | -0.048871 |  | 0.95 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | AUBURN 6 | 0.96487 | 0.916 | -0.048871 |  | 0.95 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | AUBURN 6 | 0.96487 | 0.916 | -0.048871 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | AUBURN 6 | 0.96487 | 0.916 | -0.048871 |  | 0.95 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | AUBURN 6 | 0.96487 | 0.916 | -0.048871 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | AUBURN 6 | 0.96487 | 0.916 | -0.048871 |  | 0.95 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | AUBURN 6 | 0.96487 | 0.916 | -0.048871 |  | 0.95 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | AUBURN 6 | 0.96487 | 0.916 | -0.048871 |  | 0.95 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | AUBURN 6 | 0.96487 | 0.916 | -0.048871 |  | 0.95 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | AUBURN 6 | 0.96487 | 0.916 | -0.048871 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | AUBURN 6 | 0.96487 | 0.916 | -0.048871 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | AUBURN 6 | 0.96487 | 0.916 | -0.048871 |  | 0.95 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | AUBURN 6 | 0.96487 | 0.916 | -0.048871 |  | 0.95 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | AUBURN 6 | 0.96487 | 0.916 | -0.048871 |  | 0.95 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | AUBURN 6 | 0.96487 | 0.916 | -0.048871 |  | 0.95 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | AUBURN 6 | 0.96487 | 0.916 | -0.048871 |  | 0.95 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | AUBURN 6 | 0.96487 | 0.916 | -0.048871 |  | 0.95 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | AUBURN 6 | 0.96487 | 0.916 | -0.048871 |  | 0.95 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | AUBURN 6 | 0.96487 | 0.916 | -0.048871 |  | 0.95 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | AUBURN 6 | 0.95915 | 0.92407 | -0.035073 |  | 0.95 | 1.05 | 0.03768 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | AUBURN 6 | 0.95915 | 0.92407 | -0.035073 |  | 0.95 | 1.05 | 0.054649 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | AUBURN 6 | 0.95915 | 0.92407 | -0.035073 |  | 0.95 | 1.05 | 0.041275 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | AUBURN 6 | 0.95915 | 0.92407 | -0.035073 |  | 0.95 | 1.05 | 0.032793 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | AUBURN 6 | 0.95915 | 0.92407 | -0.035073 |  | 0.95 | 1.05 | 0.043592 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | AUBURN 6 | 0.95915 | 0.92407 | -0.035073 |  | 0.95 | 1.05 | 0.040246 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | AUBURN 6 | 0.95915 | 0.92407 | -0.035073 |  | 0.95 | 1.05 | 0.030207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | AUBURN 6 | 0.95915 | 0.92407 | -0.035073 |  | 0.95 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | AUBURN 6 | 0.95915 | 0.92407 | -0.035073 |  | 0.95 | 1.05 | 0.069525 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | AUBURN 6 | 0.95915 | 0.92407 | -0.035073 |  | 0.95 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | AUBURN 6 | 0.95915 | 0.92407 | -0.035073 |  | 0.95 | 1.05 | 0.032357 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | AUBURN 6 | 0.95915 | 0.92407 | -0.035073 |  | 0.95 | 1.05 | 0.033611 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | AUBURN 6 | 0.95915 | 0.92407 | -0.035073 |  | 0.95 | 1.05 | 0.030163 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | AUBURN 6 | 0.95915 | 0.92407 | -0.035073 |  | 0.95 | 1.05 | 0.042714 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | AUBURN 6 | 0.95915 | 0.92407 | -0.035073 |  | 0.95 | 1.05 | 0.042627 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | AUBURN 6 | 0.95915 | 0.92407 | -0.035073 |  | 0.95 | 1.05 | 0.032319 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | AUBURN 6 | 0.95915 | 0.92407 | -0.035073 |  | 0.95 | 1.05 | 0.034532 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | AUBURN 6 | 0.95915 | 0.92407 | -0.035073 |  | 0.95 | 1.05 | 0.030438 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | AUBURN 6 | 0.95915 | 0.92407 | -0.035073 |  | 0.95 | 1.05 | 0.035207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | AUBURN 6 | 0.95915 | 0.92407 | -0.035073 |  | 0.95 | 1.05 | 0.030949 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | AUR124 5 | 0.96877 | 0.916 | -0.052776 |  | 0.925 | 1.05 | 0.032166 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | AUR124 5 | 0.96877 | 0.916 | -0.052776 |  | 0.925 | 1.05 | 0.040299 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | AUR124 5 | 0.96877 | 0.916 | -0.052776 |  | 0.925 | 1.05 | 0.087845 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | AUR124 5 | 0.96877 | 0.916 | -0.052776 |  | 0.925 | 1.05 | 0.076211 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | AUR124 5 | 0.96877 | 0.916 | -0.052776 |  | 0.925 | 1.05 | 0.069331 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | AUR124 5 | 0.96877 | 0.916 | -0.052776 |  | 0.925 | 1.05 | 0.035943 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | AUR124 5 | 0.96877 | 0.916 | -0.052776 |  | 0.925 | 1.05 | 0.034061 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | AUR124 5 | 0.96877 | 0.916 | -0.052776 |  | 0.925 | 1.05 | 0.16354 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | AUR124 5 | 0.96877 | 0.916 | -0.052776 |  | 0.925 | 1.05 | 0.045005 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | AUR124 5 | 0.96877 | 0.916 | -0.052776 |  | 0.925 | 1.05 | 0.13572 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | AUR124 5 | 0.96877 | 0.916 | -0.052776 |  | 0.925 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | AUR124 5 | 0.96877 | 0.916 | -0.052776 |  | 0.925 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | AUR124 5 | 0.96877 | 0.916 | -0.052776 |  | 0.925 | 1.05 | 0.06894 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | AUR124 5 | 0.96877 | 0.916 | -0.052776 |  | 0.925 | 1.05 | 0.034713 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | AUR124 5 | 0.96877 | 0.916 | -0.052776 |  | 0.925 | 1.05 | 0.035229 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | AUR124 5 | 0.97015 | 0.91793 | -0.052223 |  | 0.925 | 1.05 | 0.040299 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | AUR124 5 | 0.97015 | 0.91793 | -0.052223 |  | 0.925 | 1.05 | 0.087845 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | AUR124 5 | 0.97015 | 0.91793 | -0.052223 |  | 0.925 | 1.05 | 0.076211 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | AUR124 5 | 0.97015 | 0.91793 | -0.052223 |  | 0.925 | 1.05 | 0.069331 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | AUR124 5 | 0.97015 | 0.91793 | -0.052223 |  | 0.925 | 1.05 | 0.035943 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | AUR124 5 | 0.97015 | 0.91793 | -0.052223 |  | 0.925 | 1.05 | 0.034061 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | AUR124 5 | 0.97015 | 0.91793 | -0.052223 |  | 0.925 | 1.05 | 0.16354 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | AUR124 5 | 0.97015 | 0.91793 | -0.052223 |  | 0.925 | 1.05 | 0.045005 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | AUR124 5 | 0.97015 | 0.91793 | -0.052223 |  | 0.925 | 1.05 | 0.13572 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | AUR124 5 | 0.97015 | 0.91793 | -0.052223 |  | 0.925 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | AUR124 5 | 0.97015 | 0.91793 | -0.052223 |  | 0.925 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | AUR124 5 | 0.97015 | 0.91793 | -0.052223 |  | 0.925 | 1.05 | 0.06894 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | AUR124 5 | 0.97015 | 0.91793 | -0.052223 |  | 0.925 | 1.05 | 0.034713 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | AUR124 5 | 0.97015 | 0.91793 | -0.052223 |  | 0.925 | 1.05 | 0.035229 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | AUR124 5 | 0.96958 | 0.92158 | -0.047995 |  | 0.925 | 1.05 | 0.032166 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | AUR124 5 | 0.96958 | 0.92158 | -0.047995 |  | 0.925 | 1.05 | 0.040299 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | AUR124 5 | 0.96958 | 0.92158 | -0.047995 |  | 0.925 | 1.05 | 0.055405 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | AUR124 5 | 0.96958 | 0.92158 | -0.047995 |  | 0.925 | 1.05 | 0.076211 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | AUR124 5 | 0.96958 | 0.92158 | -0.047995 |  | 0.925 | 1.05 | 0.069331 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | AUR124 5 | 0.96958 | 0.92158 | -0.047995 |  | 0.925 | 1.05 | 0.035943 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | AUR124 5 | 0.96958 | 0.92158 | -0.047995 |  | 0.925 | 1.05 | 0.034061 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | AUR124 5 | 0.96958 | 0.92158 | -0.047995 |  | 0.925 | 1.05 | 0.082012 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | AUR124 5 | 0.96958 | 0.92158 | -0.047995 |  | 0.925 | 1.05 | 0.045005 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | AUR124 5 | 0.96958 | 0.92158 | -0.047995 |  | 0.925 | 1.05 | 0.13572 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | AUR124 5 | 0.96958 | 0.92158 | -0.047995 |  | 0.925 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | AUR124 5 | 0.96958 | 0.92158 | -0.047995 |  | 0.925 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | AUR124 5 | 0.96958 | 0.92158 | -0.047995 |  | 0.925 | 1.05 | 0.06894 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | AUR124 5 | 0.96958 | 0.92158 | -0.047995 |  | 0.925 | 1.05 | 0.034713 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | AUR124 5 | 0.96958 | 0.92158 | -0.047995 |  | 0.925 | 1.05 | 0.035229 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | AVOCA 5 | 0.98984 | 0.91749 | -0.07235 |  | 0.92 | 1.05 | 0.032166 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | AVOCA 5 | 0.98984 | 0.91749 | -0.07235 |  | 0.92 | 1.05 | 0.040299 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | AVOCA 5 | 0.98984 | 0.91749 | -0.07235 |  | 0.92 | 1.05 | 0.087845 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | AVOCA 5 | 0.98984 | 0.91749 | -0.07235 |  | 0.92 | 1.05 | 0.076211 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | AVOCA 5 | 0.98984 | 0.91749 | -0.07235 |  | 0.92 | 1.05 | 0.069331 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | AVOCA 5 | 0.98984 | 0.91749 | -0.07235 |  | 0.92 | 1.05 | 0.035943 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | AVOCA 5 | 0.98984 | 0.91749 | -0.07235 |  | 0.92 | 1.05 | 0.034061 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | AVOCA 5 | 0.98984 | 0.91749 | -0.07235 |  | 0.92 | 1.05 | 0.16354 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | AVOCA 5 | 0.98984 | 0.91749 | -0.07235 |  | 0.92 | 1.05 | 0.045005 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | AVOCA 5 | 0.98984 | 0.91749 | -0.07235 |  | 0.92 | 1.05 | 0.13572 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | AVOCA 5 | 0.98984 | 0.91749 | -0.07235 |  | 0.92 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | AVOCA 5 | 0.98984 | 0.91749 | -0.07235 |  | 0.92 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | AVOCA 5 | 0.98984 | 0.91749 | -0.07235 |  | 0.92 | 1.05 | 0.06894 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | AVOCA 5 | 0.98984 | 0.91749 | -0.07235 |  | 0.92 | 1.05 | 0.034713 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | AVOCA 5 | 0.98984 | 0.91749 | -0.07235 |  | 0.92 | 1.05 | 0.035229 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | AVOCA 5 | 0.99063 | 0.91877 | -0.071855 |  | 0.92 | 1.05 | 0.040299 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | AVOCA 5 | 0.99063 | 0.91877 | -0.071855 |  | 0.92 | 1.05 | 0.087845 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | AVOCA 5 | 0.99063 | 0.91877 | -0.071855 |  | 0.92 | 1.05 | 0.076211 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | AVOCA 5 | 0.99063 | 0.91877 | -0.071855 |  | 0.92 | 1.05 | 0.069331 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | AVOCA 5 | 0.99063 | 0.91877 | -0.071855 |  | 0.92 | 1.05 | 0.035943 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | AVOCA 5 | 0.99063 | 0.91877 | -0.071855 |  | 0.92 | 1.05 | 0.034061 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | AVOCA 5 | 0.99063 | 0.91877 | -0.071855 |  | 0.92 | 1.05 | 0.16354 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | AVOCA 5 | 0.99063 | 0.91877 | -0.071855 |  | 0.92 | 1.05 | 0.045005 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | AVOCA 5 | 0.99063 | 0.91877 | -0.071855 |  | 0.92 | 1.05 | 0.13572 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | AVOCA 5 | 0.99063 | 0.91877 | -0.071855 |  | 0.92 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | AVOCA 5 | 0.99063 | 0.91877 | -0.071855 |  | 0.92 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | AVOCA 5 | 0.99063 | 0.91877 | -0.071855 |  | 0.92 | 1.05 | 0.06894 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | AVOCA 5 | 0.99063 | 0.91877 | -0.071855 |  | 0.92 | 1.05 | 0.034713 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | AVOCA 5 | 0.99063 | 0.91877 | -0.071855 |  | 0.92 | 1.05 | 0.035229 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | AXTELL 3 | 0.98873 | 0.94674 | -0.041986 |  | 0.95 | 1.05 | 0.041569 | System Intact | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 48 MVAR switched shunt at MACON 3 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | AXTELL 3 | 0.98873 | 0.94674 | -0.041986 |  | 0.95 | 1.05 | 0.031515 | System Intact | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 48 MVAR switched shunt at MACON 3 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | AXTELL 3 | 0.98873 | 0.94674 | -0.041986 |  | 0.95 | 1.05 | 0.031515 | System Intact | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 48 MVAR switched shunt at MACON 3 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | AXTELL 3 | 0.98873 | 0.94674 | -0.041986 |  | 0.95 | 1.05 | 0.03222 | System Intact | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 48 MVAR switched shunt at MACON 3 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | AXTELL 3 | 0.98873 | 0.94674 | -0.041986 |  | 0.95 | 1.05 | 0.030633 | System Intact | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 48 MVAR switched shunt at MACON 3 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | AXTELL 3 | 0.98873 | 0.94674 | -0.041986 |  | 0.95 | 1.05 | 0.030061 | System Intact | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 48 MVAR switched shunt at MACON 3 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | AXTELL 3 | 0.98873 | 0.94674 | -0.041986 |  | 0.95 | 1.05 | 0.031207 | System Intact | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 48 MVAR switched shunt at MACON 3 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | BALDCRK3 | 0.96823 | 0.92783 | -0.040403 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | BALDCRK3 | 0.96823 | 0.92783 | -0.040403 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | BALDCRK3 | 0.96823 | 0.92783 | -0.040403 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | BALDCRK3 | 0.96823 | 0.92783 | -0.040403 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | BALDCRK3 | 0.96823 | 0.92783 | -0.040403 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | BALDCRK3 | 0.96823 | 0.92783 | -0.040403 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | BALDCRK3 | 0.96823 | 0.92783 | -0.040403 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | BALDCRK3 | 0.96823 | 0.92783 | -0.040403 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | BALDCRK3 | 0.96823 | 0.92783 | -0.040403 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | BALDCRK3 | 0.96823 | 0.92783 | -0.040403 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | BALDCRK3 | 0.96823 | 0.92783 | -0.040403 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | BALDCRK3 | 0.96823 | 0.92783 | -0.040403 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | BALDCRK3 | 0.96823 | 0.92783 | -0.040403 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | BALDCRK3 | 0.96823 | 0.92783 | -0.040403 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | BALDCRK3 | 0.96823 | 0.92783 | -0.040403 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | BALDCRK3 | 0.96823 | 0.92783 | -0.040403 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | BALDCRK3 | 0.96823 | 0.92783 | -0.040403 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | BALDCRK3 | 0.96823 | 0.92783 | -0.040403 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | BALDCRK3 | 0.96823 | 0.92783 | -0.040403 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | BALDCRK3 | 0.96823 | 0.92783 | -0.040403 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | BALDCRK3 | 0.97953 | 0.92924 | -0.050288 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | BALDCRK3 | 0.97953 | 0.92924 | -0.050288 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | BALDCRK3 | 0.97953 | 0.92924 | -0.050288 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | BALDCRK3 | 0.97953 | 0.92924 | -0.050288 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | BALDCRK3 | 0.97953 | 0.92924 | -0.050288 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | BALDCRK3 | 0.97953 | 0.92924 | -0.050288 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | BALDCRK3 | 0.97953 | 0.92924 | -0.050288 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | BALDCRK3 | 0.97953 | 0.92924 | -0.050288 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | BALDCRK3 | 0.97953 | 0.92924 | -0.050288 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | BALDCRK3 | 0.97953 | 0.92924 | -0.050288 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | BALDCRK3 | 0.97953 | 0.92924 | -0.050288 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | BALDCRK3 | 0.97953 | 0.92924 | -0.050288 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | BALDCRK3 | 0.97953 | 0.92924 | -0.050288 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | BALDCRK3 | 0.97953 | 0.92924 | -0.050288 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | BALDCRK3 | 0.97953 | 0.92924 | -0.050288 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | BALDCRK3 | 0.97953 | 0.92924 | -0.050288 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | BALDCRK3 | 0.97953 | 0.92924 | -0.050288 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | BALDCRK3 | 0.97953 | 0.92924 | -0.050288 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | BALDCRK3 | 0.97953 | 0.92924 | -0.050288 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | BALDCRK3 | 0.97953 | 0.92924 | -0.050288 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | BALDCRK3 | 0.97953 | 0.92924 | -0.050288 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | BALDCRK3 | 0.97953 | 0.92924 | -0.050288 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | BALDCRK3 | 0.97953 | 0.92924 | -0.050288 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | BALDCRK3 | 0.97953 | 0.92924 | -0.050288 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | BALDCRK3 | 0.97953 | 0.92924 | -0.050288 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | BALDCRK3 | 0.97953 | 0.92924 | -0.050288 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | BALDCRK3 | 0.97953 | 0.92924 | -0.050288 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | BALDCRK3 | 0.97953 | 0.92924 | -0.050288 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | BEECRK4 | 0.96304 | 0.92516 | -0.03788 |  | 0.93 | 1.05 | 0.094783 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | BEECRK4 | 0.96304 | 0.92516 | -0.03788 |  | 0.93 | 1.05 | 0.03645 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | BEECRK4 | 0.96304 | 0.92516 | -0.03788 |  | 0.93 | 1.05 | 0.04755 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | BEECRK4 | 0.96304 | 0.92516 | -0.03788 |  | 0.93 | 1.05 | 0.06097 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | BEECRK4 | 0.96304 | 0.92516 | -0.03788 |  | 0.93 | 1.05 | 0.061051 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | BEECRK4 | 0.96304 | 0.92516 | -0.03788 |  | 0.93 | 1.05 | 0.04456 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | BEECRK4 | 0.96304 | 0.92516 | -0.03788 |  | 0.93 | 1.05 | 0.048811 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | BEECRK4 | 0.96304 | 0.92516 | -0.03788 |  | 0.93 | 1.05 | 0.13004 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | BEECRK4 | 0.96304 | 0.92516 | -0.03788 |  | 0.93 | 1.05 | 0.049018 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | BEECRK4 | 0.96304 | 0.92516 | -0.03788 |  | 0.93 | 1.05 | 0.059524 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | BEECRK4 | 0.96304 | 0.92516 | -0.03788 |  | 0.93 | 1.05 | 0.059524 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | BEECRK4 | 0.96304 | 0.92516 | -0.03788 |  | 0.93 | 1.05 | 0.05974 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | BEECRK4 | 0.96304 | 0.92516 | -0.03788 |  | 0.93 | 1.05 | 0.076949 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | BEECRK4 | 0.96304 | 0.92516 | -0.03788 |  | 0.93 | 1.05 | 0.042157 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | BEECRK4 | 0.96304 | 0.92516 | -0.03788 |  | 0.93 | 1.05 | 0.040957 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | BEECRK4 | 0.96304 | 0.92516 | -0.03788 |  | 0.93 | 1.05 | 0.044127 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | BEECRK4 | 0.96304 | 0.92516 | -0.03788 |  | 0.93 | 1.05 | 0.044127 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | BEECRK4 | 0.96304 | 0.92516 | -0.03788 |  | 0.93 | 1.05 | 0.054637 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | BEECRK4 | 0.96304 | 0.92516 | -0.03788 |  | 0.93 | 1.05 | 0.060597 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | BEECRK4 | 0.96304 | 0.92516 | -0.03788 |  | 0.93 | 1.05 | 0.044286 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | BEECRK4 | 0.96304 | 0.92516 | -0.03788 |  | 0.93 | 1.05 | 0.059107 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | BEECRK4 | 0.96304 | 0.92516 | -0.03788 |  | 0.93 | 1.05 | 0.052698 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | BEECRK4 | 0.96304 | 0.92516 | -0.03788 |  | 0.93 | 1.05 | 0.067422 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | BEECRK4 | 0.96304 | 0.92516 | -0.03788 |  | 0.93 | 1.05 | 0.053768 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | BEECRK4 | 0.96304 | 0.92516 | -0.03788 |  | 0.93 | 1.05 | 0.03909 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | BEECRK4 | 0.96742 | 0.92792 | -0.0395 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | BEECRK4 | 0.96742 | 0.92792 | -0.0395 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | BEECRK4 | 0.96742 | 0.92792 | -0.0395 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | BEECRK4 | 0.96742 | 0.92792 | -0.0395 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | BEECRK4 | 0.96742 | 0.92792 | -0.0395 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | BEECRK4 | 0.96742 | 0.92792 | -0.0395 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | BEECRK4 | 0.96742 | 0.92792 | -0.0395 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | BEECRK4 | 0.96742 | 0.92792 | -0.0395 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | BEECRK4 | 0.96742 | 0.92792 | -0.0395 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | BEECRK4 | 0.96742 | 0.92792 | -0.0395 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | BEECRK4 | 0.96742 | 0.92792 | -0.0395 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | BEECRK4 | 0.96742 | 0.92792 | -0.0395 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | BEECRK4 | 0.96742 | 0.92792 | -0.0395 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | BEECRK4 | 0.96742 | 0.92792 | -0.0395 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | BEECRK4 | 0.96742 | 0.92792 | -0.0395 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | BEECRK4 | 0.96742 | 0.92792 | -0.0395 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | BEECRK4 | 0.96742 | 0.92792 | -0.0395 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | BEECRK4 | 0.96742 | 0.92792 | -0.0395 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | BEECRK4 | 0.96742 | 0.92792 | -0.0395 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | BEECRK4 | 0.96742 | 0.92792 | -0.0395 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | BEECRK4 | 0.96742 | 0.92792 | -0.0395 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | BEECRK4 | 0.96742 | 0.92792 | -0.0395 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | BEECRK4 | 0.96742 | 0.92792 | -0.0395 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | BEECRK4 | 0.96742 | 0.92792 | -0.0395 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | BEECRK4 | 0.96742 | 0.92792 | -0.0395 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | BEECRK4 | 0.96742 | 0.92792 | -0.0395 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | BEECRK4 | 0.96742 | 0.92792 | -0.0395 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | BEECRK4 | 0.96742 | 0.92792 | -0.0395 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | BEELER 3 | 0.94029 | 0.88839 | -0.051893 |  | 0.9 | 1.05 | 0.046736 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | BEELER 3 | 0.94029 | 0.88839 | -0.051893 |  | 0.9 | 1.05 | 0.030145 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | BELTONS5 | 0.99329 | 0.91521 | -0.078082 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | BELTONS5 | 0.99329 | 0.91521 | -0.078082 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | BELTONS5 | 0.99329 | 0.91521 | -0.078082 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | BELTONS5 | 0.99329 | 0.91521 | -0.078082 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | BELTONS5 | 0.99329 | 0.91521 | -0.078082 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | BELTONS5 | 0.99329 | 0.91521 | -0.078082 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | BELTONS5 | 0.99329 | 0.91521 | -0.078082 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | BELTONS5 | 0.99329 | 0.91521 | -0.078082 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | BELTONS5 | 0.99329 | 0.91521 | -0.078082 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | BELTONS5 | 0.99329 | 0.91521 | -0.078082 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | BELTONS5 | 0.99329 | 0.91521 | -0.078082 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | BELTONS5 | 0.99329 | 0.91521 | -0.078082 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | BELTONS5 | 0.99329 | 0.91521 | -0.078082 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | BELTONS5 | 0.99329 | 0.91521 | -0.078082 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | BELTONS5 | 0.99329 | 0.91521 | -0.078082 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | BELTONS5 | 0.99329 | 0.91521 | -0.078082 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | BELTONS5 | 0.99329 | 0.91521 | -0.078082 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | BELTONS5 | 0.99329 | 0.91521 | -0.078082 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | BELTONS5 | 0.99329 | 0.91521 | -0.078082 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | BELTONS5 | 0.99329 | 0.91521 | -0.078082 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | BELTONS5 | 0.99329 | 0.91521 | -0.078082 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | BELTONS5 | 0.99329 | 0.91521 | -0.078082 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | BELTONS5 | 0.99329 | 0.91521 | -0.078082 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | BELTONS5 | 0.99329 | 0.91521 | -0.078082 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | BELTONS5 | 0.99329 | 0.91521 | -0.078082 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | BELTONS5 | 0.99329 | 0.91521 | -0.078082 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | BELTONS5 | 0.99329 | 0.91521 | -0.078082 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | BELTONS5 | 0.99329 | 0.91521 | -0.078082 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | BENTLEY4 | 0.98482 | 0.92917 | -0.055652 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | BENTLEY4 | 0.98482 | 0.92917 | -0.055652 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | BENTLEY4 | 0.98482 | 0.92917 | -0.055652 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | BENTLEY4 | 0.98482 | 0.92917 | -0.055652 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | BENTLEY4 | 0.98482 | 0.92917 | -0.055652 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | BENTLEY4 | 0.98482 | 0.92917 | -0.055652 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | BENTLEY4 | 0.98482 | 0.92917 | -0.055652 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | BENTLEY4 | 0.98482 | 0.92917 | -0.055652 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | BENTLEY4 | 0.98482 | 0.92917 | -0.055652 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | BENTLEY4 | 0.98482 | 0.92917 | -0.055652 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | BENTLEY4 | 0.98482 | 0.92917 | -0.055652 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | BENTLEY4 | 0.98482 | 0.92917 | -0.055652 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | BENTLEY4 | 0.98482 | 0.92917 | -0.055652 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | BENTLEY4 | 0.98482 | 0.92917 | -0.055652 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | BENTLEY4 | 0.98482 | 0.92917 | -0.055652 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | BENTLEY4 | 0.98482 | 0.92917 | -0.055652 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | BENTLEY4 | 0.98482 | 0.92917 | -0.055652 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | BENTLEY4 | 0.98482 | 0.92917 | -0.055652 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | BENTLEY4 | 0.98482 | 0.92917 | -0.055652 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | BENTLEY4 | 0.98482 | 0.92917 | -0.055652 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | BENTLEY4 | 0.98482 | 0.92917 | -0.055652 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | BENTLEY4 | 0.98482 | 0.92917 | -0.055652 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | BENTLEY4 | 0.98482 | 0.92917 | -0.055652 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | BENTLEY4 | 0.98482 | 0.92917 | -0.055652 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | BENTLEY4 | 0.98482 | 0.92917 | -0.055652 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | BENTLEY4 | 0.98482 | 0.92917 | -0.055652 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | BENTLEY4 | 0.98482 | 0.92917 | -0.055652 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | BENTLEY4 | 0.98482 | 0.92917 | -0.055652 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | BENTVJ_5 | 0.98824 | 0.91845 | -0.069791 |  | 0.92 | 1.05 | 0.032166 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | BENTVJ_5 | 0.98824 | 0.91845 | -0.069791 |  | 0.92 | 1.05 | 0.040299 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | BENTVJ_5 | 0.98824 | 0.91845 | -0.069791 |  | 0.92 | 1.05 | 0.087845 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | BENTVJ_5 | 0.98824 | 0.91845 | -0.069791 |  | 0.92 | 1.05 | 0.076211 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | BENTVJ_5 | 0.98824 | 0.91845 | -0.069791 |  | 0.92 | 1.05 | 0.069331 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | BENTVJ_5 | 0.98824 | 0.91845 | -0.069791 |  | 0.92 | 1.05 | 0.035943 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | BENTVJ_5 | 0.98824 | 0.91845 | -0.069791 |  | 0.92 | 1.05 | 0.034061 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | BENTVJ_5 | 0.98824 | 0.91845 | -0.069791 |  | 0.92 | 1.05 | 0.16354 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | BENTVJ_5 | 0.98824 | 0.91845 | -0.069791 |  | 0.92 | 1.05 | 0.045005 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | BENTVJ_5 | 0.98824 | 0.91845 | -0.069791 |  | 0.92 | 1.05 | 0.13572 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | BENTVJ_5 | 0.98824 | 0.91845 | -0.069791 |  | 0.92 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | BENTVJ_5 | 0.98824 | 0.91845 | -0.069791 |  | 0.92 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | BENTVJ_5 | 0.98824 | 0.91845 | -0.069791 |  | 0.92 | 1.05 | 0.06894 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | BENTVJ_5 | 0.98824 | 0.91845 | -0.069791 |  | 0.92 | 1.05 | 0.034713 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | BENTVJ_5 | 0.98824 | 0.91845 | -0.069791 |  | 0.92 | 1.05 | 0.035229 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | BENTVJ_5 | 0.98881 | 0.9194 | -0.069413 |  | 0.92 | 1.05 | 0.040299 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | BENTVJ_5 | 0.98881 | 0.9194 | -0.069413 |  | 0.92 | 1.05 | 0.087845 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | BENTVJ_5 | 0.98881 | 0.9194 | -0.069413 |  | 0.92 | 1.05 | 0.076211 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | BENTVJ_5 | 0.98881 | 0.9194 | -0.069413 |  | 0.92 | 1.05 | 0.069331 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | BENTVJ_5 | 0.98881 | 0.9194 | -0.069413 |  | 0.92 | 1.05 | 0.035943 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | BENTVJ_5 | 0.98881 | 0.9194 | -0.069413 |  | 0.92 | 1.05 | 0.034061 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | BENTVJ_5 | 0.98881 | 0.9194 | -0.069413 |  | 0.92 | 1.05 | 0.16354 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | BENTVJ_5 | 0.98881 | 0.9194 | -0.069413 |  | 0.92 | 1.05 | 0.045005 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | BENTVJ_5 | 0.98881 | 0.9194 | -0.069413 |  | 0.92 | 1.05 | 0.13572 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | BENTVJ_5 | 0.98881 | 0.9194 | -0.069413 |  | 0.92 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | BENTVJ_5 | 0.98881 | 0.9194 | -0.069413 |  | 0.92 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | BENTVJ_5 | 0.98881 | 0.9194 | -0.069413 |  | 0.92 | 1.05 | 0.06894 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | BENTVJ_5 | 0.98881 | 0.9194 | -0.069413 |  | 0.92 | 1.05 | 0.034713 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | BENTVJ_5 | 0.98881 | 0.9194 | -0.069413 |  | 0.92 | 1.05 | 0.035229 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | BENT_SL5 | 0.9883 | 0.91861 | -0.069688 |  | 0.92 | 1.05 | 0.032166 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | BENT_SL5 | 0.9883 | 0.91861 | -0.069688 |  | 0.92 | 1.05 | 0.040299 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | BENT_SL5 | 0.9883 | 0.91861 | -0.069688 |  | 0.92 | 1.05 | 0.087845 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | BENT_SL5 | 0.9883 | 0.91861 | -0.069688 |  | 0.92 | 1.05 | 0.076211 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | BENT_SL5 | 0.9883 | 0.91861 | -0.069688 |  | 0.92 | 1.05 | 0.069331 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | BENT_SL5 | 0.9883 | 0.91861 | -0.069688 |  | 0.92 | 1.05 | 0.035943 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | BENT_SL5 | 0.9883 | 0.91861 | -0.069688 |  | 0.92 | 1.05 | 0.034061 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | BENT_SL5 | 0.9883 | 0.91861 | -0.069688 |  | 0.92 | 1.05 | 0.16354 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | BENT_SL5 | 0.9883 | 0.91861 | -0.069688 |  | 0.92 | 1.05 | 0.045005 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | BENT_SL5 | 0.9883 | 0.91861 | -0.069688 |  | 0.92 | 1.05 | 0.13572 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | BENT_SL5 | 0.9883 | 0.91861 | -0.069688 |  | 0.92 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | BENT_SL5 | 0.9883 | 0.91861 | -0.069688 |  | 0.92 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | BENT_SL5 | 0.9883 | 0.91861 | -0.069688 |  | 0.92 | 1.05 | 0.06894 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | BENT_SL5 | 0.9883 | 0.91861 | -0.069688 |  | 0.92 | 1.05 | 0.034713 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | BENT_SL5 | 0.9883 | 0.91861 | -0.069688 |  | 0.92 | 1.05 | 0.035229 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | BENT_SL5 | 0.98887 | 0.91956 | -0.069311 |  | 0.92 | 1.05 | 0.040299 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | BENT_SL5 | 0.98887 | 0.91956 | -0.069311 |  | 0.92 | 1.05 | 0.087845 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | BENT_SL5 | 0.98887 | 0.91956 | -0.069311 |  | 0.92 | 1.05 | 0.076211 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | BENT_SL5 | 0.98887 | 0.91956 | -0.069311 |  | 0.92 | 1.05 | 0.069331 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | BENT_SL5 | 0.98887 | 0.91956 | -0.069311 |  | 0.92 | 1.05 | 0.035943 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | BENT_SL5 | 0.98887 | 0.91956 | -0.069311 |  | 0.92 | 1.05 | 0.034061 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | BENT_SL5 | 0.98887 | 0.91956 | -0.069311 |  | 0.92 | 1.05 | 0.16354 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | BENT_SL5 | 0.98887 | 0.91956 | -0.069311 |  | 0.92 | 1.05 | 0.045005 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | BENT_SL5 | 0.98887 | 0.91956 | -0.069311 |  | 0.92 | 1.05 | 0.13572 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | BENT_SL5 | 0.98887 | 0.91956 | -0.069311 |  | 0.92 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | BENT_SL5 | 0.98887 | 0.91956 | -0.069311 |  | 0.92 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | BENT_SL5 | 0.98887 | 0.91956 | -0.069311 |  | 0.92 | 1.05 | 0.06894 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | BENT_SL5 | 0.98887 | 0.91956 | -0.069311 |  | 0.92 | 1.05 | 0.034713 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | BENT_SL5 | 0.98887 | 0.91956 | -0.069311 |  | 0.92 | 1.05 | 0.035229 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | BIRDCTY3 | 0.95811 | 0.88971 | -0.068403 |  | 0.9 | 1.05 | 0.041569 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | BIRDCTY3 | 0.95811 | 0.88971 | -0.068403 |  | 0.9 | 1.05 | 0.031515 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | BIRDCTY3 | 0.95811 | 0.88971 | -0.068403 |  | 0.9 | 1.05 | 0.031515 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | BIRDCTY3 | 0.95811 | 0.88971 | -0.068403 |  | 0.9 | 1.05 | 0.03222 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | BIRDCTY3 | 0.95811 | 0.88971 | -0.068403 |  | 0.9 | 1.05 | 0.030633 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | BIRDCTY3 | 0.95811 | 0.88971 | -0.068403 |  | 0.9 | 1.05 | 0.030061 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | BIRDCTY3 | 0.95811 | 0.88971 | -0.068403 |  | 0.9 | 1.05 | 0.031207 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | BIRDCTY3 | 0.95167 | 0.88119 | -0.070477 |  | 0.9 | 1.05 | 0.046736 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | BIRDCTY3 | 0.95167 | 0.88119 | -0.070477 |  | 0.9 | 1.05 | 0.030145 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | BIRDCTY3 | 0.95154 | 0.87439 | -0.077149 |  | 0.9 | 1.05 | 0.046736 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | BIRDCTY3 | 0.95154 | 0.87439 | -0.077149 |  | 0.9 | 1.05 | 0.030145 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | BIRDCTY3 | 0.95154 | 0.87439 | -0.07715 |  | 0.9 | 1.05 | 0.046736 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | BIRDCTY3 | 0.95154 | 0.87439 | -0.07715 |  | 0.9 | 1.05 | 0.030145 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | BIRDCTY3 | 0.95154 | 0.87439 | -0.077151 |  | 0.9 | 1.05 | 0.046736 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | BIRDCTY3 | 0.95154 | 0.87439 | -0.077151 |  | 0.9 | 1.05 | 0.030145 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | BISMARK3 | 0.96806 | 0.9276 | -0.040464 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | BISMARK3 | 0.96806 | 0.9276 | -0.040464 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | BISMARK3 | 0.96806 | 0.9276 | -0.040464 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | BISMARK3 | 0.96806 | 0.9276 | -0.040464 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | BISMARK3 | 0.96806 | 0.9276 | -0.040464 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | BISMARK3 | 0.96806 | 0.9276 | -0.040464 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | BISMARK3 | 0.96806 | 0.9276 | -0.040464 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | BISMARK3 | 0.96806 | 0.9276 | -0.040464 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | BISMARK3 | 0.96806 | 0.9276 | -0.040464 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | BISMARK3 | 0.96806 | 0.9276 | -0.040464 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | BISMARK3 | 0.96806 | 0.9276 | -0.040464 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | BISMARK3 | 0.96806 | 0.9276 | -0.040464 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | BISMARK3 | 0.96806 | 0.9276 | -0.040464 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | BISMARK3 | 0.96806 | 0.9276 | -0.040464 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | BISMARK3 | 0.96806 | 0.9276 | -0.040464 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | BISMARK3 | 0.96806 | 0.9276 | -0.040464 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | BISMARK3 | 0.96806 | 0.9276 | -0.040464 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | BISMARK3 | 0.96806 | 0.9276 | -0.040464 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | BISMARK3 | 0.96806 | 0.9276 | -0.040464 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | BISMARK3 | 0.96806 | 0.9276 | -0.040464 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | BISMARK3 | 0.97994 | 0.92887 | -0.051072 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | BISMARK3 | 0.97994 | 0.92887 | -0.051072 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | BISMARK3 | 0.97994 | 0.92887 | -0.051072 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | BISMARK3 | 0.97994 | 0.92887 | -0.051072 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | BISMARK3 | 0.97994 | 0.92887 | -0.051072 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | BISMARK3 | 0.97994 | 0.92887 | -0.051072 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | BISMARK3 | 0.97994 | 0.92887 | -0.051072 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | BISMARK3 | 0.97994 | 0.92887 | -0.051072 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | BISMARK3 | 0.97994 | 0.92887 | -0.051072 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | BISMARK3 | 0.97994 | 0.92887 | -0.051072 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | BISMARK3 | 0.97994 | 0.92887 | -0.051072 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | BISMARK3 | 0.97994 | 0.92887 | -0.051072 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | BISMARK3 | 0.97994 | 0.92887 | -0.051072 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | BISMARK3 | 0.97994 | 0.92887 | -0.051072 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | BISMARK3 | 0.97994 | 0.92887 | -0.051072 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | BISMARK3 | 0.97994 | 0.92887 | -0.051072 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | BISMARK3 | 0.97994 | 0.92887 | -0.051072 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | BISMARK3 | 0.97994 | 0.92887 | -0.051072 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | BISMARK3 | 0.97994 | 0.92887 | -0.051072 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | BISMARK3 | 0.97994 | 0.92887 | -0.051072 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | BISMARK3 | 0.97994 | 0.92887 | -0.051072 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | BISMARK3 | 0.97994 | 0.92887 | -0.051072 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | BISMARK3 | 0.97994 | 0.92887 | -0.051072 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | BISMARK3 | 0.97994 | 0.92887 | -0.051072 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | BISMARK3 | 0.97994 | 0.92887 | -0.051072 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | BISMARK3 | 0.97994 | 0.92887 | -0.051072 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | BISMARK3 | 0.97994 | 0.92887 | -0.051072 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | BISMARK3 | 0.97994 | 0.92887 | -0.051072 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | BLSPW 5 | 0.99121 | 0.92939 | -0.06182 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | BLSPW 5 | 0.99121 | 0.92939 | -0.06182 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | BLSPW 5 | 0.99121 | 0.92939 | -0.06182 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | BLSPW 5 | 0.99121 | 0.92939 | -0.06182 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | BLSPW 5 | 0.99121 | 0.92939 | -0.06182 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | BLSPW 5 | 0.99121 | 0.92939 | -0.06182 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | BLSPW 5 | 0.99121 | 0.92939 | -0.06182 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | BLSPW 5 | 0.99121 | 0.92939 | -0.06182 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | BLSPW 5 | 0.99121 | 0.92939 | -0.06182 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | BLSPW 5 | 0.99121 | 0.92939 | -0.06182 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | BLSPW 5 | 0.99121 | 0.92939 | -0.06182 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | BLSPW 5 | 0.99121 | 0.92939 | -0.06182 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | BLSPW 5 | 0.99121 | 0.92939 | -0.06182 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | BLSPW 5 | 0.99121 | 0.92939 | -0.06182 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | BLSPW 5 | 0.99121 | 0.92939 | -0.06182 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | BLSPW 5 | 0.99121 | 0.92939 | -0.06182 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | BLSPW 5 | 0.99121 | 0.92939 | -0.06182 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | BLSPW 5 | 0.99121 | 0.92939 | -0.06182 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | BLSPW 5 | 0.99121 | 0.92939 | -0.06182 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | BLSPW 5 | 0.99121 | 0.92939 | -0.06182 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | BLSPW 5 | 0.99121 | 0.92939 | -0.06182 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | BLSPW 5 | 0.99121 | 0.92939 | -0.06182 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | BLSPW 5 | 0.99121 | 0.92939 | -0.06182 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | BLSPW 5 | 0.99121 | 0.92939 | -0.06182 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | BLSPW 5 | 0.99121 | 0.92939 | -0.06182 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | BLSPW 5 | 0.99121 | 0.92939 | -0.06182 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | BLSPW 5 | 0.99121 | 0.92939 | -0.06182 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | BLSPW 5 | 0.99121 | 0.92939 | -0.06182 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | BNSF 5 | 0.99959 | 0.91905 | -0.080533 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | BNSF 5 | 0.99959 | 0.91905 | -0.080533 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | BNSF 5 | 0.99959 | 0.91905 | -0.080533 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | BNSF 5 | 0.99959 | 0.91905 | -0.080533 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | BNSF 5 | 0.99959 | 0.91905 | -0.080533 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | BNSF 5 | 0.99959 | 0.91905 | -0.080533 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | BNSF 5 | 0.99959 | 0.91905 | -0.080533 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | BNSF 5 | 0.99959 | 0.91905 | -0.080533 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | BNSF 5 | 0.99959 | 0.91905 | -0.080533 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | BNSF 5 | 0.99959 | 0.91905 | -0.080533 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | BNSF 5 | 0.99959 | 0.91905 | -0.080533 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | BNSF 5 | 0.99959 | 0.91905 | -0.080533 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | BNSF 5 | 0.99959 | 0.91905 | -0.080533 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | BNSF 5 | 0.99959 | 0.91905 | -0.080533 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | BNSF 5 | 0.99959 | 0.91905 | -0.080533 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | BNSF 5 | 0.99959 | 0.91905 | -0.080533 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | BNSF 5 | 0.99959 | 0.91905 | -0.080533 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | BNSF 5 | 0.99959 | 0.91905 | -0.080533 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | BNSF 5 | 0.99959 | 0.91905 | -0.080533 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | BNSF 5 | 0.99959 | 0.91905 | -0.080533 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | BNSF 5 | 0.99959 | 0.91905 | -0.080533 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | BNSF 5 | 0.99959 | 0.91905 | -0.080533 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | BNSF 5 | 0.99959 | 0.91905 | -0.080533 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | BNSF 5 | 0.99959 | 0.91905 | -0.080533 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | BNSF 5 | 0.99959 | 0.91905 | -0.080533 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | BNSF 5 | 0.99959 | 0.91905 | -0.080533 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | BNSF 5 | 0.99959 | 0.91905 | -0.080533 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | BNSF 5 | 0.99959 | 0.91905 | -0.080533 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | BONITA 3 | 0.96282 | 0.91895 | -0.043869 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | BONITA 3 | 0.96282 | 0.91895 | -0.043869 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | BONITA 3 | 0.96282 | 0.91895 | -0.043869 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | BONITA 3 | 0.96282 | 0.91895 | -0.043869 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | BONITA 3 | 0.96282 | 0.91895 | -0.043869 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | BONITA 3 | 0.96282 | 0.91895 | -0.043869 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | BONITA 3 | 0.96282 | 0.91895 | -0.043869 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | BONITA 3 | 0.96282 | 0.91895 | -0.043869 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | BONITA 3 | 0.96282 | 0.91895 | -0.043869 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | BONITA 3 | 0.96282 | 0.91895 | -0.043869 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | BONITA 3 | 0.96282 | 0.91895 | -0.043869 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | BONITA 3 | 0.96282 | 0.91895 | -0.043869 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | BONITA 3 | 0.96282 | 0.91895 | -0.043869 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | BONITA 3 | 0.96282 | 0.91895 | -0.043869 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | BONITA 3 | 0.96282 | 0.91895 | -0.043869 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | BONITA 3 | 0.96282 | 0.91895 | -0.043869 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | BONITA 3 | 0.96282 | 0.91895 | -0.043869 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | BONITA 3 | 0.96282 | 0.91895 | -0.043869 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | BONITA 3 | 0.96282 | 0.91895 | -0.043869 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | BONITA 3 | 0.96282 | 0.91895 | -0.043869 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | BONITA 3 | 0.97386 | 0.9257 | -0.048168 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | BONITA 3 | 0.97386 | 0.9257 | -0.048168 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | BONITA 3 | 0.97386 | 0.9257 | -0.048168 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | BONITA 3 | 0.97386 | 0.9257 | -0.048168 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | BONITA 3 | 0.97386 | 0.9257 | -0.048168 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | BONITA 3 | 0.97386 | 0.9257 | -0.048168 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | BONITA 3 | 0.97386 | 0.9257 | -0.048168 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | BONITA 3 | 0.97386 | 0.9257 | -0.048168 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | BONITA 3 | 0.97386 | 0.9257 | -0.048168 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | BONITA 3 | 0.97386 | 0.9257 | -0.048168 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | BONITA 3 | 0.97386 | 0.9257 | -0.048168 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | BONITA 3 | 0.97386 | 0.9257 | -0.048168 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | BONITA 3 | 0.97386 | 0.9257 | -0.048168 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | BONITA 3 | 0.97386 | 0.9257 | -0.048168 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | BONITA 3 | 0.97386 | 0.9257 | -0.048168 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | BONITA 3 | 0.97386 | 0.9257 | -0.048168 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | BONITA 3 | 0.97386 | 0.9257 | -0.048168 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | BONITA 3 | 0.97386 | 0.9257 | -0.048168 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | BONITA 3 | 0.97386 | 0.9257 | -0.048168 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | BONITA 3 | 0.97386 | 0.9257 | -0.048168 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | BONITA 3 | 0.97839 | 0.90468 | -0.073718 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | BONITA 3 | 0.97839 | 0.90468 | -0.073718 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | BONITA 3 | 0.97839 | 0.90468 | -0.073718 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | BONITA 3 | 0.97839 | 0.90468 | -0.073718 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | BONITA 3 | 0.97839 | 0.90468 | -0.073718 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | BONITA 3 | 0.97839 | 0.90468 | -0.073718 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | BONITA 3 | 0.97839 | 0.90468 | -0.073718 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | BONITA 3 | 0.97839 | 0.90468 | -0.073718 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | BONITA 3 | 0.97839 | 0.90468 | -0.073718 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | BONITA 3 | 0.97839 | 0.90468 | -0.073718 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | BONITA 3 | 0.97839 | 0.90468 | -0.073718 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | BONITA 3 | 0.97839 | 0.90468 | -0.073718 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | BONITA 3 | 0.97839 | 0.90468 | -0.073718 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | BONITA 3 | 0.97839 | 0.90468 | -0.073718 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | BONITA 3 | 0.97839 | 0.90468 | -0.073718 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | BONITA 3 | 0.97839 | 0.90468 | -0.073718 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | BONITA 3 | 0.97839 | 0.90468 | -0.073718 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | BONITA 3 | 0.97839 | 0.90468 | -0.073718 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | BONITA 3 | 0.97839 | 0.90468 | -0.073718 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | BONITA 3 | 0.97839 | 0.90468 | -0.073718 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | BONITA 3 | 0.97839 | 0.90468 | -0.073718 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | BONITA 3 | 0.97839 | 0.90468 | -0.073718 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | BONITA 3 | 0.97839 | 0.90468 | -0.073718 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | BONITA 3 | 0.97839 | 0.90468 | -0.073718 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | BONITA 3 | 0.97839 | 0.90468 | -0.073718 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | BONITA 3 | 0.97839 | 0.90468 | -0.073718 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | BONITA 3 | 0.97839 | 0.90468 | -0.073718 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | BONITA 3 | 0.97839 | 0.90468 | -0.073718 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | BONITA 3 | 0.96933 | 0.92919 | -0.04014 |  | 0.93 | 1.05 | 0.03768 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | BONITA 3 | 0.96933 | 0.92919 | -0.04014 |  | 0.93 | 1.05 | 0.054649 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | BONITA 3 | 0.96933 | 0.92919 | -0.04014 |  | 0.93 | 1.05 | 0.041275 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | BONITA 3 | 0.96933 | 0.92919 | -0.04014 |  | 0.93 | 1.05 | 0.032793 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | BONITA 3 | 0.96933 | 0.92919 | -0.04014 |  | 0.93 | 1.05 | 0.043592 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | BONITA 3 | 0.96933 | 0.92919 | -0.04014 |  | 0.93 | 1.05 | 0.040246 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | BONITA 3 | 0.96933 | 0.92919 | -0.04014 |  | 0.93 | 1.05 | 0.030207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | BONITA 3 | 0.96933 | 0.92919 | -0.04014 |  | 0.93 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | BONITA 3 | 0.96933 | 0.92919 | -0.04014 |  | 0.93 | 1.05 | 0.069525 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | BONITA 3 | 0.96933 | 0.92919 | -0.04014 |  | 0.93 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | BONITA 3 | 0.96933 | 0.92919 | -0.04014 |  | 0.93 | 1.05 | 0.032357 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | BONITA 3 | 0.96933 | 0.92919 | -0.04014 |  | 0.93 | 1.05 | 0.033611 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | BONITA 3 | 0.96933 | 0.92919 | -0.04014 |  | 0.93 | 1.05 | 0.030163 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | BONITA 3 | 0.96933 | 0.92919 | -0.04014 |  | 0.93 | 1.05 | 0.042714 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | BONITA 3 | 0.96933 | 0.92919 | -0.04014 |  | 0.93 | 1.05 | 0.042627 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | BONITA 3 | 0.96933 | 0.92919 | -0.04014 |  | 0.93 | 1.05 | 0.032319 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | BONITA 3 | 0.96933 | 0.92919 | -0.04014 |  | 0.93 | 1.05 | 0.034532 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | BONITA 3 | 0.96933 | 0.92919 | -0.04014 |  | 0.93 | 1.05 | 0.030438 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | BONITA 3 | 0.96933 | 0.92919 | -0.04014 |  | 0.93 | 1.05 | 0.035207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | BONITA 3 | 0.96933 | 0.92919 | -0.04014 |  | 0.93 | 1.05 | 0.030949 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | BREWSTR3 | 0.96888 | 0.89495 | -0.073929 |  | 0.9 | 1.05 | 0.041569 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | BREWSTR3 | 0.96888 | 0.89495 | -0.073929 |  | 0.9 | 1.05 | 0.031515 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | BREWSTR3 | 0.96888 | 0.89495 | -0.073929 |  | 0.9 | 1.05 | 0.031515 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | BREWSTR3 | 0.96888 | 0.89495 | -0.073929 |  | 0.9 | 1.05 | 0.03222 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | BREWSTR3 | 0.96888 | 0.89495 | -0.073929 |  | 0.9 | 1.05 | 0.030633 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | BREWSTR3 | 0.96888 | 0.89495 | -0.073929 |  | 0.9 | 1.05 | 0.030061 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | BREWSTR3 | 0.96888 | 0.89495 | -0.073929 |  | 0.9 | 1.05 | 0.031207 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | BREWSTR3 | 0.96935 | 0.89823 | -0.071117 |  | 0.9 | 1.05 | 0.041569 | P42:345:NPPD:BKR-MAC-3304:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | BREWSTR3 | 0.96935 | 0.89823 | -0.071117 |  | 0.9 | 1.05 | 0.031515 | P42:345:NPPD:BKR-MAC-3304:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | BREWSTR3 | 0.96935 | 0.89823 | -0.071117 |  | 0.9 | 1.05 | 0.031515 | P42:345:NPPD:BKR-MAC-3304:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | BREWSTR3 | 0.96935 | 0.89823 | -0.071117 |  | 0.9 | 1.05 | 0.03222 | P42:345:NPPD:BKR-MAC-3304:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | BREWSTR3 | 0.96935 | 0.89823 | -0.071117 |  | 0.9 | 1.05 | 0.030633 | P42:345:NPPD:BKR-MAC-3304:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | BREWSTR3 | 0.96935 | 0.89823 | -0.071117 |  | 0.9 | 1.05 | 0.030061 | P42:345:NPPD:BKR-MAC-3304:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | BREWSTR3 | 0.96935 | 0.89823 | -0.071117 |  | 0.9 | 1.05 | 0.031207 | P42:345:NPPD:BKR-MAC-3304:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | BREWSTR3 | 0.96942 | 0.89571 | -0.073715 |  | 0.9 | 1.05 | 0.046736 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | BREWSTR3 | 0.96942 | 0.89571 | -0.073715 |  | 0.9 | 1.05 | 0.030145 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | BREWSTR3 | 0.96942 | 0.89571 | -0.073715 |  | 0.9 | 1.05 | 0.046736 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | BREWSTR3 | 0.96942 | 0.89571 | -0.073715 |  | 0.9 | 1.05 | 0.030145 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | BREWSTR3 | 0.96943 | 0.89571 | -0.073717 |  | 0.9 | 1.05 | 0.046736 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | BREWSTR3 | 0.96943 | 0.89571 | -0.073717 |  | 0.9 | 1.05 | 0.030145 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | BRKRIDG5 | 0.96136 | 0.92264 | -0.038712 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | BRKRIDG5 | 0.96136 | 0.92264 | -0.038712 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | BRKRIDG5 | 0.96136 | 0.92264 | -0.038712 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | BRKRIDG5 | 0.96136 | 0.92264 | -0.038712 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | BRKRIDG5 | 0.96136 | 0.92264 | -0.038712 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | BRKRIDG5 | 0.96136 | 0.92264 | -0.038712 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | BRKRIDG5 | 0.96136 | 0.92264 | -0.038712 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | BRKRIDG5 | 0.96136 | 0.92264 | -0.038712 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | BRKRIDG5 | 0.96136 | 0.92264 | -0.038712 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | BRKRIDG5 | 0.96136 | 0.92264 | -0.038712 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | BRKRIDG5 | 0.96136 | 0.92264 | -0.038712 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | BRKRIDG5 | 0.96136 | 0.92264 | -0.038712 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | BRKRIDG5 | 0.96136 | 0.92264 | -0.038712 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | BRKRIDG5 | 0.96136 | 0.92264 | -0.038712 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | BRKRIDG5 | 0.96136 | 0.92264 | -0.038712 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | BRKRIDG5 | 0.96136 | 0.92264 | -0.038712 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | BRKRIDG5 | 0.96136 | 0.92264 | -0.038712 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | BRKRIDG5 | 0.96136 | 0.92264 | -0.038712 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | BRKRIDG5 | 0.96136 | 0.92264 | -0.038712 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | BRKRIDG5 | 0.96136 | 0.92264 | -0.038712 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | BRKRIDG5 | 0.9697 | 0.92645 | -0.043248 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | BRKRIDG5 | 0.9697 | 0.92645 | -0.043248 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | BRKRIDG5 | 0.9697 | 0.92645 | -0.043248 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | BRKRIDG5 | 0.9697 | 0.92645 | -0.043248 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | BRKRIDG5 | 0.9697 | 0.92645 | -0.043248 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | BRKRIDG5 | 0.9697 | 0.92645 | -0.043248 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | BRKRIDG5 | 0.9697 | 0.92645 | -0.043248 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | BRKRIDG5 | 0.9697 | 0.92645 | -0.043248 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | BRKRIDG5 | 0.9697 | 0.92645 | -0.043248 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | BRKRIDG5 | 0.9697 | 0.92645 | -0.043248 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | BRKRIDG5 | 0.9697 | 0.92645 | -0.043248 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | BRKRIDG5 | 0.9697 | 0.92645 | -0.043248 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | BRKRIDG5 | 0.9697 | 0.92645 | -0.043248 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | BRKRIDG5 | 0.9697 | 0.92645 | -0.043248 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | BRKRIDG5 | 0.9697 | 0.92645 | -0.043248 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | BRKRIDG5 | 0.9697 | 0.92645 | -0.043248 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | BRKRIDG5 | 0.9697 | 0.92645 | -0.043248 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | BRKRIDG5 | 0.9697 | 0.92645 | -0.043248 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | BRKRIDG5 | 0.9697 | 0.92645 | -0.043248 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | BRKRIDG5 | 0.9697 | 0.92645 | -0.043248 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | BRKRIDG5 | 0.9722 | 0.90459 | -0.067611 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | BRKRIDG5 | 0.9722 | 0.90459 | -0.067611 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | BRKRIDG5 | 0.9722 | 0.90459 | -0.067611 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | BRKRIDG5 | 0.9722 | 0.90459 | -0.067611 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | BRKRIDG5 | 0.9722 | 0.90459 | -0.067611 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | BRKRIDG5 | 0.9722 | 0.90459 | -0.067611 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | BRKRIDG5 | 0.9722 | 0.90459 | -0.067611 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | BRKRIDG5 | 0.9722 | 0.90459 | -0.067611 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | BRKRIDG5 | 0.9722 | 0.90459 | -0.067611 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | BRKRIDG5 | 0.9722 | 0.90459 | -0.067611 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | BRKRIDG5 | 0.9722 | 0.90459 | -0.067611 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | BRKRIDG5 | 0.9722 | 0.90459 | -0.067611 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | BRKRIDG5 | 0.9722 | 0.90459 | -0.067611 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | BRKRIDG5 | 0.9722 | 0.90459 | -0.067611 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | BRKRIDG5 | 0.9722 | 0.90459 | -0.067611 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | BRKRIDG5 | 0.9722 | 0.90459 | -0.067611 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | BRKRIDG5 | 0.9722 | 0.90459 | -0.067611 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | BRKRIDG5 | 0.9722 | 0.90459 | -0.067611 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | BRKRIDG5 | 0.9722 | 0.90459 | -0.067611 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | BRKRIDG5 | 0.9722 | 0.90459 | -0.067611 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | BRKRIDG5 | 0.9722 | 0.90459 | -0.067611 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | BRKRIDG5 | 0.9722 | 0.90459 | -0.067611 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | BRKRIDG5 | 0.9722 | 0.90459 | -0.067611 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | BRKRIDG5 | 0.9722 | 0.90459 | -0.067611 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | BRKRIDG5 | 0.9722 | 0.90459 | -0.067611 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | BRKRIDG5 | 0.9722 | 0.90459 | -0.067611 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | BRKRIDG5 | 0.9722 | 0.90459 | -0.067611 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | BRKRIDG5 | 0.9722 | 0.90459 | -0.067611 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | BRKRIDG5 | 0.96592 | 0.92942 | -0.0365 |  | 0.93 | 1.05 | 0.03768 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | BRKRIDG5 | 0.96592 | 0.92942 | -0.0365 |  | 0.93 | 1.05 | 0.054649 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | BRKRIDG5 | 0.96592 | 0.92942 | -0.0365 |  | 0.93 | 1.05 | 0.041275 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | BRKRIDG5 | 0.96592 | 0.92942 | -0.0365 |  | 0.93 | 1.05 | 0.032793 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | BRKRIDG5 | 0.96592 | 0.92942 | -0.0365 |  | 0.93 | 1.05 | 0.043592 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | BRKRIDG5 | 0.96592 | 0.92942 | -0.0365 |  | 0.93 | 1.05 | 0.040246 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | BRKRIDG5 | 0.96592 | 0.92942 | -0.0365 |  | 0.93 | 1.05 | 0.030207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | BRKRIDG5 | 0.96592 | 0.92942 | -0.0365 |  | 0.93 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | BRKRIDG5 | 0.96592 | 0.92942 | -0.0365 |  | 0.93 | 1.05 | 0.069525 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | BRKRIDG5 | 0.96592 | 0.92942 | -0.0365 |  | 0.93 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | BRKRIDG5 | 0.96592 | 0.92942 | -0.0365 |  | 0.93 | 1.05 | 0.032357 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | BRKRIDG5 | 0.96592 | 0.92942 | -0.0365 |  | 0.93 | 1.05 | 0.033611 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | BRKRIDG5 | 0.96592 | 0.92942 | -0.0365 |  | 0.93 | 1.05 | 0.030163 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | BRKRIDG5 | 0.96592 | 0.92942 | -0.0365 |  | 0.93 | 1.05 | 0.042714 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | BRKRIDG5 | 0.96592 | 0.92942 | -0.0365 |  | 0.93 | 1.05 | 0.042627 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | BRKRIDG5 | 0.96592 | 0.92942 | -0.0365 |  | 0.93 | 1.05 | 0.032319 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | BRKRIDG5 | 0.96592 | 0.92942 | -0.0365 |  | 0.93 | 1.05 | 0.034532 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | BRKRIDG5 | 0.96592 | 0.92942 | -0.0365 |  | 0.93 | 1.05 | 0.030438 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | BRKRIDG5 | 0.96592 | 0.92942 | -0.0365 |  | 0.93 | 1.05 | 0.035207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | BRKRIDG5 | 0.96592 | 0.92942 | -0.0365 |  | 0.93 | 1.05 | 0.030949 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | BUCYRUS5 | 0.97745 | 0.92975 | -0.047705 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | BUCYRUS5 | 0.97745 | 0.92975 | -0.047705 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | BUCYRUS5 | 0.97745 | 0.92975 | -0.047705 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | BUCYRUS5 | 0.97745 | 0.92975 | -0.047705 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | BUCYRUS5 | 0.97745 | 0.92975 | -0.047705 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | BUCYRUS5 | 0.97745 | 0.92975 | -0.047705 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | BUCYRUS5 | 0.97745 | 0.92975 | -0.047705 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | BUCYRUS5 | 0.97745 | 0.92975 | -0.047705 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | BUCYRUS5 | 0.97745 | 0.92975 | -0.047705 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | BUCYRUS5 | 0.97745 | 0.92975 | -0.047705 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | BUCYRUS5 | 0.97745 | 0.92975 | -0.047705 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | BUCYRUS5 | 0.97745 | 0.92975 | -0.047705 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | BUCYRUS5 | 0.97745 | 0.92975 | -0.047705 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | BUCYRUS5 | 0.97745 | 0.92975 | -0.047705 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | BUCYRUS5 | 0.97745 | 0.92975 | -0.047705 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | BUCYRUS5 | 0.97745 | 0.92975 | -0.047705 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | BUCYRUS5 | 0.97745 | 0.92975 | -0.047705 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | BUCYRUS5 | 0.97745 | 0.92975 | -0.047705 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | BUCYRUS5 | 0.97745 | 0.92975 | -0.047705 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | BUCYRUS5 | 0.97745 | 0.92975 | -0.047705 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | BUCYRUS5 | 0.99058 | 0.90554 | -0.085031 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | BUCYRUS5 | 0.99058 | 0.90554 | -0.085031 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | BUCYRUS5 | 0.99058 | 0.90554 | -0.085031 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | BUCYRUS5 | 0.99058 | 0.90554 | -0.085031 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | BUCYRUS5 | 0.99058 | 0.90554 | -0.085031 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | BUCYRUS5 | 0.99058 | 0.90554 | -0.085031 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | BUCYRUS5 | 0.99058 | 0.90554 | -0.085031 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | BUCYRUS5 | 0.99058 | 0.90554 | -0.085031 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | BUCYRUS5 | 0.99058 | 0.90554 | -0.085031 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | BUCYRUS5 | 0.99058 | 0.90554 | -0.085031 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | BUCYRUS5 | 0.99058 | 0.90554 | -0.085031 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | BUCYRUS5 | 0.99058 | 0.90554 | -0.085031 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | BUCYRUS5 | 0.99058 | 0.90554 | -0.085031 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | BUCYRUS5 | 0.99058 | 0.90554 | -0.085031 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | BUCYRUS5 | 0.99058 | 0.90554 | -0.085031 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | BUCYRUS5 | 0.99058 | 0.90554 | -0.085031 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | BUCYRUS5 | 0.99058 | 0.90554 | -0.085031 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | BUCYRUS5 | 0.99058 | 0.90554 | -0.085031 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | BUCYRUS5 | 0.99058 | 0.90554 | -0.085031 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | BUCYRUS5 | 0.99058 | 0.90554 | -0.085031 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | BUCYRUS5 | 0.99058 | 0.90554 | -0.085031 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | BUCYRUS5 | 0.99058 | 0.90554 | -0.085031 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | BUCYRUS5 | 0.99058 | 0.90554 | -0.085031 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | BUCYRUS5 | 0.99058 | 0.90554 | -0.085031 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | BUCYRUS5 | 0.99058 | 0.90554 | -0.085031 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | BUCYRUS5 | 0.99058 | 0.90554 | -0.085031 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | BUCYRUS5 | 0.99058 | 0.90554 | -0.085031 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | BUCYRUS5 | 0.99058 | 0.90554 | -0.085031 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | BUFFALO7 | 0.98797 | 0.94829 | -0.039681 |  | 0.95 | 1.05 | 0.077434 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.02 MVAR switched shunt at BUFFALO7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | BUFFALO7 | 0.98797 | 0.94829 | -0.039681 |  | 0.95 | 1.05 | 0.032924 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.02 MVAR switched shunt at BUFFALO7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | BUFFALO7 | 0.98797 | 0.94829 | -0.039681 |  | 0.95 | 1.05 | 0.032924 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.02 MVAR switched shunt at BUFFALO7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | BUFFALO7 | 0.98797 | 0.94829 | -0.039681 |  | 0.95 | 1.05 | 0.032685 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.02 MVAR switched shunt at BUFFALO7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | BUFFALO7 | 0.98797 | 0.94829 | -0.039681 |  | 0.95 | 1.05 | 0.030104 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.02 MVAR switched shunt at BUFFALO7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | BUFFALO7 | 0.98797 | 0.94829 | -0.039681 |  | 0.95 | 1.05 | 0.036404 | Single 523097 HITCHLAND7 345 523823 CARPENTER7 345 1 | Add 0.02 MVAR switched shunt at BUFFALO7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | BUFFALO7 | 0.98797 | 0.94829 | -0.039681 |  | 0.95 | 1.05 | 0.077434 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.02 MVAR switched shunt at BUFFALO7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | BUFFALO7 | 0.98797 | 0.94829 | -0.039681 |  | 0.95 | 1.05 | 0.032924 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.02 MVAR switched shunt at BUFFALO7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | BUFFALO7 | 0.98797 | 0.94829 | -0.039681 |  | 0.95 | 1.05 | 0.032924 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.02 MVAR switched shunt at BUFFALO7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | BUFFALO7 | 0.98797 | 0.94829 | -0.039681 |  | 0.95 | 1.05 | 0.032685 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.02 MVAR switched shunt at BUFFALO7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | BUFFALO7 | 0.98797 | 0.94829 | -0.039681 |  | 0.95 | 1.05 | 0.030104 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.02 MVAR switched shunt at BUFFALO7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | BUFFALO7 | 0.98797 | 0.94829 | -0.039681 |  | 0.95 | 1.05 | 0.036404 | P12:345:SPS:J26:1:HITCHLAND_CARPENTER___:EHV: | Add 0.02 MVAR switched shunt at BUFFALO7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | BUFFALO7 | 0.98785 | 0.94773 | -0.04011 |  | 0.95 | 1.05 | 0.077434 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 160 MVAR switched shunt at WICHITA7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | BUFFALO7 | 0.98785 | 0.94773 | -0.04011 |  | 0.95 | 1.05 | 0.032924 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 160 MVAR switched shunt at WICHITA7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | BUFFALO7 | 0.98785 | 0.94773 | -0.04011 |  | 0.95 | 1.05 | 0.032924 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 160 MVAR switched shunt at WICHITA7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | BUFFALO7 | 0.98785 | 0.94773 | -0.04011 |  | 0.95 | 1.05 | 0.032685 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 160 MVAR switched shunt at WICHITA7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | BUFFALO7 | 0.98785 | 0.94773 | -0.04011 |  | 0.95 | 1.05 | 0.030104 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 160 MVAR switched shunt at WICHITA7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | BUFFALO7 | 0.98785 | 0.94773 | -0.04011 |  | 0.95 | 1.05 | 0.036404 | P42:345:SPS:CARPENTER-OR335:::EHV: | Add 160 MVAR switched shunt at WICHITA7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | BUFFALO7 | 0.9853 | 0.93804 | -0.04726 |  | 0.95 | 1.05 | 0.040163 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | BUFFALO7 | 0.9853 | 0.93804 | -0.04726 |  | 0.95 | 1.05 | 0.035544 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | BUFFALO7 | 0.9853 | 0.93804 | -0.04726 |  | 0.95 | 1.05 | 0.048812 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | BUFFALO7 | 0.9853 | 0.93804 | -0.04726 |  | 0.95 | 1.05 | 0.049073 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | BUFFALO7 | 0.9853 | 0.93804 | -0.04726 |  | 0.95 | 1.05 | 0.035142 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | BUFFALO7 | 0.9853 | 0.93804 | -0.04726 |  | 0.95 | 1.05 | 0.037502 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | BUFFALO7 | 0.9853 | 0.93804 | -0.04726 |  | 0.95 | 1.05 | 0.04571 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | BUFFALO7 | 0.9853 | 0.93804 | -0.04726 |  | 0.95 | 1.05 | 0.03081 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | BUFFALO7 | 0.9853 | 0.93804 | -0.04726 |  | 0.95 | 1.05 | 0.03835 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | BUFFALO7 | 0.9853 | 0.93804 | -0.04726 |  | 0.95 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | BUFFALO7 | 0.9853 | 0.93804 | -0.04726 |  | 0.95 | 1.05 | 0.064216 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | BUFFALO7 | 0.9853 | 0.93804 | -0.04726 |  | 0.95 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | BUFFALO7 | 0.9853 | 0.93804 | -0.04726 |  | 0.95 | 1.05 | 0.037545 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | BUFFALO7 | 0.9853 | 0.93804 | -0.04726 |  | 0.95 | 1.05 | 0.037793 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | BUFFALO7 | 0.9853 | 0.93804 | -0.04726 |  | 0.95 | 1.05 | 0.035866 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | BUFFALO7 | 0.9853 | 0.93804 | -0.04726 |  | 0.95 | 1.05 | 0.064223 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | BUFFALO7 | 0.9853 | 0.93804 | -0.04726 |  | 0.95 | 1.05 | 0.046439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | BUFFALO7 | 0.9853 | 0.93804 | -0.04726 |  | 0.95 | 1.05 | 0.03576 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | BUFFALO7 | 0.9853 | 0.93804 | -0.04726 |  | 0.95 | 1.05 | 0.032864 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | BUFFALO7 | 0.9853 | 0.93804 | -0.04726 |  | 0.95 | 1.05 | 0.032012 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | BUFFALO7 | 0.9853 | 0.93804 | -0.04726 |  | 0.95 | 1.05 | 0.033901 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | BUFFALO7 | 0.9853 | 0.93804 | -0.04726 |  | 0.95 | 1.05 | 0.035381 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | BUFFALO7 | 0.9876 | 0.94029 | -0.047309 |  | 0.95 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | BUFFALO7 | 0.9876 | 0.94029 | -0.047309 |  | 0.95 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | BUFFALO7 | 0.9876 | 0.94029 | -0.047309 |  | 0.95 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | BUFFALO7 | 0.9876 | 0.94029 | -0.047309 |  | 0.95 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | BUFFALO7 | 0.9876 | 0.94029 | -0.047309 |  | 0.95 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | BUFFALO7 | 0.9876 | 0.94029 | -0.047309 |  | 0.95 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | BUFFALO7 | 0.9876 | 0.94029 | -0.047309 |  | 0.95 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | BUFFALO7 | 0.9876 | 0.94029 | -0.047309 |  | 0.95 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | BUFFALO7 | 0.9876 | 0.94029 | -0.047309 |  | 0.95 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | BUFFALO7 | 0.9876 | 0.94029 | -0.047309 |  | 0.95 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | BUFFALO7 | 0.9876 | 0.94029 | -0.047309 |  | 0.95 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | BUFFALO7 | 0.9876 | 0.94029 | -0.047309 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | BUFFALO7 | 0.9876 | 0.94029 | -0.047309 |  | 0.95 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | BUFFALO7 | 0.9876 | 0.94029 | -0.047309 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | BUFFALO7 | 0.9876 | 0.94029 | -0.047309 |  | 0.95 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | BUFFALO7 | 0.9876 | 0.94029 | -0.047309 |  | 0.95 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | BUFFALO7 | 0.9876 | 0.94029 | -0.047309 |  | 0.95 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | BUFFALO7 | 0.9876 | 0.94029 | -0.047309 |  | 0.95 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | BUFFALO7 | 0.9876 | 0.94029 | -0.047309 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | BUFFALO7 | 0.9876 | 0.94029 | -0.047309 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | BUFFALO7 | 0.9876 | 0.94029 | -0.047309 |  | 0.95 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | BUFFALO7 | 0.9876 | 0.94029 | -0.047309 |  | 0.95 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | BUFFALO7 | 0.9876 | 0.94029 | -0.047309 |  | 0.95 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | BUFFALO7 | 0.9876 | 0.94029 | -0.047309 |  | 0.95 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | BUFFALO7 | 0.9876 | 0.94029 | -0.047309 |  | 0.95 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | BUFFALO7 | 0.9876 | 0.94029 | -0.047309 |  | 0.95 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | BUFFALO7 | 0.9876 | 0.94029 | -0.047309 |  | 0.95 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | BUFFALO7 | 0.9876 | 0.94029 | -0.047309 |  | 0.95 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | BUNKRDG5 | 0.98828 | 0.92273 | -0.065553 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | BUNKRDG5 | 0.98828 | 0.92273 | -0.065553 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | BUNKRDG5 | 0.98828 | 0.92273 | -0.065553 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | BUNKRDG5 | 0.98828 | 0.92273 | -0.065553 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | BUNKRDG5 | 0.98828 | 0.92273 | -0.065553 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | BUNKRDG5 | 0.98828 | 0.92273 | -0.065553 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | BUNKRDG5 | 0.98828 | 0.92273 | -0.065553 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | BUNKRDG5 | 0.98828 | 0.92273 | -0.065553 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | BUNKRDG5 | 0.98828 | 0.92273 | -0.065553 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | BUNKRDG5 | 0.98828 | 0.92273 | -0.065553 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | BUNKRDG5 | 0.98828 | 0.92273 | -0.065553 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | BUNKRDG5 | 0.98828 | 0.92273 | -0.065553 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | BUNKRDG5 | 0.98828 | 0.92273 | -0.065553 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | BUNKRDG5 | 0.98828 | 0.92273 | -0.065553 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | BUNKRDG5 | 0.98828 | 0.92273 | -0.065553 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | BUNKRDG5 | 0.98828 | 0.92273 | -0.065553 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | BUNKRDG5 | 0.98828 | 0.92273 | -0.065553 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | BUNKRDG5 | 0.98828 | 0.92273 | -0.065553 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | BUNKRDG5 | 0.98828 | 0.92273 | -0.065553 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | BUNKRDG5 | 0.98828 | 0.92273 | -0.065553 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | BUNKRDG5 | 0.98828 | 0.92273 | -0.065553 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | BUNKRDG5 | 0.98828 | 0.92273 | -0.065553 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | BUNKRDG5 | 0.98828 | 0.92273 | -0.065553 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | BUNKRDG5 | 0.98828 | 0.92273 | -0.065553 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | BUNKRDG5 | 0.98828 | 0.92273 | -0.065553 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | BUNKRDG5 | 0.98828 | 0.92273 | -0.065553 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | BUNKRDG5 | 0.98828 | 0.92273 | -0.065553 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | BUNKRDG5 | 0.98828 | 0.92273 | -0.065553 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | ASGI-2024-023 | BURNS 7 | 0.99891 | 0.94182 | -0.057088 |  | 0.95 | 1.05 | 0.030773 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-025 | BURNS 7 | 0.99891 | 0.94182 | -0.057088 |  | 0.95 | 1.05 | 0.033004 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | BURNS 7 | 0.99891 | 0.94182 | -0.057088 |  | 0.95 | 1.05 | 0.046711 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-068 | BURNS 7 | 0.99891 | 0.94182 | -0.057088 |  | 0.95 | 1.05 | 0.032369 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-071 | BURNS 7 | 0.99891 | 0.94182 | -0.057088 |  | 0.95 | 1.05 | 0.030466 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | BURNS 7 | 0.99891 | 0.94182 | -0.057088 |  | 0.95 | 1.05 | 0.04987 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | BURNS 7 | 0.99891 | 0.94182 | -0.057088 |  | 0.95 | 1.05 | 0.099365 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | BURNS 7 | 0.99891 | 0.94182 | -0.057088 |  | 0.95 | 1.05 | 0.071132 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | BURNS 7 | 0.99891 | 0.94182 | -0.057088 |  | 0.95 | 1.05 | 0.043927 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | BURNS 7 | 0.99891 | 0.94182 | -0.057088 |  | 0.95 | 1.05 | 0.030565 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | BURNS 7 | 0.99891 | 0.94182 | -0.057088 |  | 0.95 | 1.05 | 0.072847 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | BURNS 7 | 0.99891 | 0.94182 | -0.057088 |  | 0.95 | 1.05 | 0.041148 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | BURNS 7 | 0.99891 | 0.94182 | -0.057088 |  | 0.95 | 1.05 | 0.042015 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-220 | BURNS 7 | 0.99891 | 0.94182 | -0.057088 |  | 0.95 | 1.05 | 0.030318 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | BURNS 7 | 0.99891 | 0.94182 | -0.057088 |  | 0.95 | 1.05 | 0.054104 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | BURNS 7 | 0.99891 | 0.94182 | -0.057088 |  | 0.95 | 1.05 | 0.047089 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | BURNS 7 | 0.99891 | 0.94182 | -0.057088 |  | 0.95 | 1.05 | 0.040323 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | BURNS 7 | 0.99891 | 0.94182 | -0.057088 |  | 0.95 | 1.05 | 0.13688 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-241 | BURNS 7 | 0.99891 | 0.94182 | -0.057088 |  | 0.95 | 1.05 | 0.033004 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | BURNS 7 | 0.99891 | 0.94182 | -0.057088 |  | 0.95 | 1.05 | 0.040323 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | BURNS 7 | 0.99891 | 0.94182 | -0.057088 |  | 0.95 | 1.05 | 0.039752 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | BURNS 7 | 0.99891 | 0.94182 | -0.057088 |  | 0.95 | 1.05 | 0.041972 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | BURNS 7 | 0.99891 | 0.94182 | -0.057088 |  | 0.95 | 1.05 | 0.054397 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | BURNS 7 | 0.99891 | 0.94182 | -0.057088 |  | 0.95 | 1.05 | 0.073688 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | BURNS 7 | 0.99891 | 0.94182 | -0.057088 |  | 0.95 | 1.05 | 0.048904 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | BURNS 7 | 0.99891 | 0.94182 | -0.057088 |  | 0.95 | 1.05 | 0.048904 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | BURNS 7 | 0.99891 | 0.94182 | -0.057088 |  | 0.95 | 1.05 | 0.072188 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | BURNS 7 | 0.99891 | 0.94182 | -0.057088 |  | 0.95 | 1.05 | 0.042186 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | BURNS 7 | 0.99891 | 0.94182 | -0.057088 |  | 0.95 | 1.05 | 0.041423 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | BURNS 7 | 0.99891 | 0.94182 | -0.057088 |  | 0.95 | 1.05 | 0.050171 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | BURNS 7 | 0.99891 | 0.94182 | -0.057088 |  | 0.95 | 1.05 | 0.04386 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | BURNS 7 | 0.99891 | 0.94182 | -0.057088 |  | 0.95 | 1.05 | 0.050218 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | BURNS 7 | 0.99891 | 0.94182 | -0.057088 |  | 0.95 | 1.05 | 0.040041 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | BURNS 7 | 0.99891 | 0.94182 | -0.057088 |  | 0.95 | 1.05 | 0.038784 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | BURNS 7 | 0.99807 | 0.94483 | -0.053236 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | BURNS 7 | 0.99807 | 0.94483 | -0.053236 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | BURNS 7 | 0.99807 | 0.94483 | -0.053236 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | BURNS 7 | 0.99807 | 0.94483 | -0.053236 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | BURNS 7 | 0.99807 | 0.94483 | -0.053236 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | BURNS 7 | 0.99807 | 0.94483 | -0.053236 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | BURNS 7 | 0.99807 | 0.94483 | -0.053236 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | BURNS 7 | 0.99807 | 0.94483 | -0.053236 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | BURNS 7 | 0.99807 | 0.94483 | -0.053236 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | BURNS 7 | 0.99807 | 0.94483 | -0.053236 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | BURNS 7 | 0.99807 | 0.94483 | -0.053236 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | BURNS 7 | 0.99807 | 0.94483 | -0.053236 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | BURNS 7 | 0.99807 | 0.94483 | -0.053236 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | BURNS 7 | 0.99807 | 0.94483 | -0.053236 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | BURNS 7 | 0.99807 | 0.94483 | -0.053236 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | BURNS 7 | 0.99807 | 0.94483 | -0.053236 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | BURNS 7 | 0.99807 | 0.94483 | -0.053236 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | BURNS 7 | 0.99807 | 0.94483 | -0.053236 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | BURNS 7 | 0.99807 | 0.94483 | -0.053236 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | BURNS 7 | 0.99807 | 0.94483 | -0.053236 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | BURNS 7 | 0.9956 | 0.93339 | -0.06221 |  | 0.95 | 1.05 | 0.040163 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | BURNS 7 | 0.9956 | 0.93339 | -0.06221 |  | 0.95 | 1.05 | 0.035544 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | BURNS 7 | 0.9956 | 0.93339 | -0.06221 |  | 0.95 | 1.05 | 0.048812 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | BURNS 7 | 0.9956 | 0.93339 | -0.06221 |  | 0.95 | 1.05 | 0.049073 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | BURNS 7 | 0.9956 | 0.93339 | -0.06221 |  | 0.95 | 1.05 | 0.035142 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | BURNS 7 | 0.9956 | 0.93339 | -0.06221 |  | 0.95 | 1.05 | 0.037502 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | BURNS 7 | 0.9956 | 0.93339 | -0.06221 |  | 0.95 | 1.05 | 0.04571 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | BURNS 7 | 0.9956 | 0.93339 | -0.06221 |  | 0.95 | 1.05 | 0.03081 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | BURNS 7 | 0.9956 | 0.93339 | -0.06221 |  | 0.95 | 1.05 | 0.03835 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | BURNS 7 | 0.9956 | 0.93339 | -0.06221 |  | 0.95 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | BURNS 7 | 0.9956 | 0.93339 | -0.06221 |  | 0.95 | 1.05 | 0.064216 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | BURNS 7 | 0.9956 | 0.93339 | -0.06221 |  | 0.95 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | BURNS 7 | 0.9956 | 0.93339 | -0.06221 |  | 0.95 | 1.05 | 0.037545 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | BURNS 7 | 0.9956 | 0.93339 | -0.06221 |  | 0.95 | 1.05 | 0.037793 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | BURNS 7 | 0.9956 | 0.93339 | -0.06221 |  | 0.95 | 1.05 | 0.035866 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | BURNS 7 | 0.9956 | 0.93339 | -0.06221 |  | 0.95 | 1.05 | 0.064223 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | BURNS 7 | 0.9956 | 0.93339 | -0.06221 |  | 0.95 | 1.05 | 0.046439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | BURNS 7 | 0.9956 | 0.93339 | -0.06221 |  | 0.95 | 1.05 | 0.03576 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | BURNS 7 | 0.9956 | 0.93339 | -0.06221 |  | 0.95 | 1.05 | 0.032864 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | BURNS 7 | 0.9956 | 0.93339 | -0.06221 |  | 0.95 | 1.05 | 0.032012 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | BURNS 7 | 0.9956 | 0.93339 | -0.06221 |  | 0.95 | 1.05 | 0.033901 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | BURNS 7 | 0.9956 | 0.93339 | -0.06221 |  | 0.95 | 1.05 | 0.035381 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | BURNS 7 | 0.99582 | 0.94507 | -0.050741 |  | 0.95 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | BURNS 7 | 0.99582 | 0.94507 | -0.050741 |  | 0.95 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | BURNS 7 | 0.99582 | 0.94507 | -0.050741 |  | 0.95 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | BURNS 7 | 0.99582 | 0.94507 | -0.050741 |  | 0.95 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | BURNS 7 | 0.99582 | 0.94507 | -0.050741 |  | 0.95 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | BURNS 7 | 0.99582 | 0.94507 | -0.050741 |  | 0.95 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | BURNS 7 | 0.99582 | 0.94507 | -0.050741 |  | 0.95 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | BURNS 7 | 0.99582 | 0.94507 | -0.050741 |  | 0.95 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | BURNS 7 | 0.99582 | 0.94507 | -0.050741 |  | 0.95 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | BURNS 7 | 0.99582 | 0.94507 | -0.050741 |  | 0.95 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | BURNS 7 | 0.99582 | 0.94507 | -0.050741 |  | 0.95 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | BURNS 7 | 0.99582 | 0.94507 | -0.050741 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | BURNS 7 | 0.99582 | 0.94507 | -0.050741 |  | 0.95 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | BURNS 7 | 0.99582 | 0.94507 | -0.050741 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | BURNS 7 | 0.99582 | 0.94507 | -0.050741 |  | 0.95 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | BURNS 7 | 0.99582 | 0.94507 | -0.050741 |  | 0.95 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | BURNS 7 | 0.99582 | 0.94507 | -0.050741 |  | 0.95 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | BURNS 7 | 0.99582 | 0.94507 | -0.050741 |  | 0.95 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | BURNS 7 | 0.99582 | 0.94507 | -0.050741 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | BURNS 7 | 0.99582 | 0.94507 | -0.050741 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | BURNS 7 | 0.99582 | 0.94507 | -0.050741 |  | 0.95 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | BURNS 7 | 0.99582 | 0.94507 | -0.050741 |  | 0.95 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | BURNS 7 | 0.99582 | 0.94507 | -0.050741 |  | 0.95 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | BURNS 7 | 0.99582 | 0.94507 | -0.050741 |  | 0.95 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | BURNS 7 | 0.99582 | 0.94507 | -0.050741 |  | 0.95 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | BURNS 7 | 0.99582 | 0.94507 | -0.050741 |  | 0.95 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | BURNS 7 | 0.99582 | 0.94507 | -0.050741 |  | 0.95 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | BURNS 7 | 0.99582 | 0.94507 | -0.050741 |  | 0.95 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | BVRVLY 3 | 0.95745 | 0.88992 | -0.067529 |  | 0.9 | 1.05 | 0.041569 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | BVRVLY 3 | 0.95745 | 0.88992 | -0.067529 |  | 0.9 | 1.05 | 0.031515 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | BVRVLY 3 | 0.95745 | 0.88992 | -0.067529 |  | 0.9 | 1.05 | 0.031515 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | BVRVLY 3 | 0.95745 | 0.88992 | -0.067529 |  | 0.9 | 1.05 | 0.03222 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | BVRVLY 3 | 0.95745 | 0.88992 | -0.067529 |  | 0.9 | 1.05 | 0.030633 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | BVRVLY 3 | 0.95745 | 0.88992 | -0.067529 |  | 0.9 | 1.05 | 0.030061 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | BVRVLY 3 | 0.95745 | 0.88992 | -0.067529 |  | 0.9 | 1.05 | 0.031207 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | BVRVLY 3 | 0.95586 | 0.88776 | -0.068103 |  | 0.9 | 1.05 | 0.046736 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | BVRVLY 3 | 0.95586 | 0.88776 | -0.068103 |  | 0.9 | 1.05 | 0.030145 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | BVRVLY 3 | 0.95593 | 0.88195 | -0.073981 |  | 0.9 | 1.05 | 0.046736 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | BVRVLY 3 | 0.95593 | 0.88195 | -0.073981 |  | 0.9 | 1.05 | 0.030145 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | BVRVLY 3 | 0.95593 | 0.88195 | -0.073981 |  | 0.9 | 1.05 | 0.046736 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | BVRVLY 3 | 0.95593 | 0.88195 | -0.073981 |  | 0.9 | 1.05 | 0.030145 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | BVRVLY 3 | 0.95593 | 0.88195 | -0.073982 |  | 0.9 | 1.05 | 0.046736 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | BVRVLY 3 | 0.95593 | 0.88195 | -0.073982 |  | 0.9 | 1.05 | 0.030145 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | BVRVLYT3 | 0.95763 | 0.89013 | -0.067494 |  | 0.9 | 1.05 | 0.041569 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | BVRVLYT3 | 0.95763 | 0.89013 | -0.067494 |  | 0.9 | 1.05 | 0.031515 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | BVRVLYT3 | 0.95763 | 0.89013 | -0.067494 |  | 0.9 | 1.05 | 0.031515 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | BVRVLYT3 | 0.95763 | 0.89013 | -0.067494 |  | 0.9 | 1.05 | 0.03222 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | BVRVLYT3 | 0.95763 | 0.89013 | -0.067494 |  | 0.9 | 1.05 | 0.030633 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | BVRVLYT3 | 0.95763 | 0.89013 | -0.067494 |  | 0.9 | 1.05 | 0.030061 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | BVRVLYT3 | 0.95763 | 0.89013 | -0.067494 |  | 0.9 | 1.05 | 0.031207 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | BVRVLYT3 | 0.95604 | 0.88798 | -0.068066 |  | 0.9 | 1.05 | 0.046736 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | BVRVLYT3 | 0.95604 | 0.88798 | -0.068066 |  | 0.9 | 1.05 | 0.030145 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | BVRVLYT3 | 0.95611 | 0.88217 | -0.073941 |  | 0.9 | 1.05 | 0.046736 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | BVRVLYT3 | 0.95611 | 0.88217 | -0.073941 |  | 0.9 | 1.05 | 0.030145 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | BVRVLYT3 | 0.95611 | 0.88217 | -0.073941 |  | 0.9 | 1.05 | 0.046736 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | BVRVLYT3 | 0.95611 | 0.88217 | -0.073941 |  | 0.9 | 1.05 | 0.030145 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | BVRVLYT3 | 0.95611 | 0.88217 | -0.073942 |  | 0.9 | 1.05 | 0.046736 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | BVRVLYT3 | 0.95611 | 0.88217 | -0.073942 |  | 0.9 | 1.05 | 0.030145 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | CANEYRV7 | 0.98275 | 0.94027 | -0.042479 |  | 0.95 | 1.05 | 0.040163 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | CANEYRV7 | 0.98275 | 0.94027 | -0.042479 |  | 0.95 | 1.05 | 0.035544 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | CANEYRV7 | 0.98275 | 0.94027 | -0.042479 |  | 0.95 | 1.05 | 0.048812 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | CANEYRV7 | 0.98275 | 0.94027 | -0.042479 |  | 0.95 | 1.05 | 0.049073 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | CANEYRV7 | 0.98275 | 0.94027 | -0.042479 |  | 0.95 | 1.05 | 0.035142 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | CANEYRV7 | 0.98275 | 0.94027 | -0.042479 |  | 0.95 | 1.05 | 0.037502 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | CANEYRV7 | 0.98275 | 0.94027 | -0.042479 |  | 0.95 | 1.05 | 0.04571 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | CANEYRV7 | 0.98275 | 0.94027 | -0.042479 |  | 0.95 | 1.05 | 0.03081 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | CANEYRV7 | 0.98275 | 0.94027 | -0.042479 |  | 0.95 | 1.05 | 0.03835 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | CANEYRV7 | 0.98275 | 0.94027 | -0.042479 |  | 0.95 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | CANEYRV7 | 0.98275 | 0.94027 | -0.042479 |  | 0.95 | 1.05 | 0.064216 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | CANEYRV7 | 0.98275 | 0.94027 | -0.042479 |  | 0.95 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | CANEYRV7 | 0.98275 | 0.94027 | -0.042479 |  | 0.95 | 1.05 | 0.037545 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | CANEYRV7 | 0.98275 | 0.94027 | -0.042479 |  | 0.95 | 1.05 | 0.037793 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | CANEYRV7 | 0.98275 | 0.94027 | -0.042479 |  | 0.95 | 1.05 | 0.035866 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | CANEYRV7 | 0.98275 | 0.94027 | -0.042479 |  | 0.95 | 1.05 | 0.064223 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | CANEYRV7 | 0.98275 | 0.94027 | -0.042479 |  | 0.95 | 1.05 | 0.046439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | CANEYRV7 | 0.98275 | 0.94027 | -0.042479 |  | 0.95 | 1.05 | 0.03576 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | CANEYRV7 | 0.98275 | 0.94027 | -0.042479 |  | 0.95 | 1.05 | 0.032864 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | CANEYRV7 | 0.98275 | 0.94027 | -0.042479 |  | 0.95 | 1.05 | 0.032012 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | CANEYRV7 | 0.98275 | 0.94027 | -0.042479 |  | 0.95 | 1.05 | 0.033901 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | CANEYRV7 | 0.98275 | 0.94027 | -0.042479 |  | 0.95 | 1.05 | 0.035381 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | CANEYWF7 | 0.98287 | 0.94039 | -0.042484 |  | 0.95 | 1.05 | 0.040163 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | CANEYWF7 | 0.98287 | 0.94039 | -0.042484 |  | 0.95 | 1.05 | 0.035544 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | CANEYWF7 | 0.98287 | 0.94039 | -0.042484 |  | 0.95 | 1.05 | 0.048812 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | CANEYWF7 | 0.98287 | 0.94039 | -0.042484 |  | 0.95 | 1.05 | 0.049073 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | CANEYWF7 | 0.98287 | 0.94039 | -0.042484 |  | 0.95 | 1.05 | 0.035142 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | CANEYWF7 | 0.98287 | 0.94039 | -0.042484 |  | 0.95 | 1.05 | 0.037502 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | CANEYWF7 | 0.98287 | 0.94039 | -0.042484 |  | 0.95 | 1.05 | 0.04571 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | CANEYWF7 | 0.98287 | 0.94039 | -0.042484 |  | 0.95 | 1.05 | 0.03081 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | CANEYWF7 | 0.98287 | 0.94039 | -0.042484 |  | 0.95 | 1.05 | 0.03835 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | CANEYWF7 | 0.98287 | 0.94039 | -0.042484 |  | 0.95 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | CANEYWF7 | 0.98287 | 0.94039 | -0.042484 |  | 0.95 | 1.05 | 0.064216 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | CANEYWF7 | 0.98287 | 0.94039 | -0.042484 |  | 0.95 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | CANEYWF7 | 0.98287 | 0.94039 | -0.042484 |  | 0.95 | 1.05 | 0.037545 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | CANEYWF7 | 0.98287 | 0.94039 | -0.042484 |  | 0.95 | 1.05 | 0.037793 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | CANEYWF7 | 0.98287 | 0.94039 | -0.042484 |  | 0.95 | 1.05 | 0.035866 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | CANEYWF7 | 0.98287 | 0.94039 | -0.042484 |  | 0.95 | 1.05 | 0.064223 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | CANEYWF7 | 0.98287 | 0.94039 | -0.042484 |  | 0.95 | 1.05 | 0.046439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | CANEYWF7 | 0.98287 | 0.94039 | -0.042484 |  | 0.95 | 1.05 | 0.03576 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | CANEYWF7 | 0.98287 | 0.94039 | -0.042484 |  | 0.95 | 1.05 | 0.032864 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | CANEYWF7 | 0.98287 | 0.94039 | -0.042484 |  | 0.95 | 1.05 | 0.032012 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | CANEYWF7 | 0.98287 | 0.94039 | -0.042484 |  | 0.95 | 1.05 | 0.033901 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | CANEYWF7 | 0.98287 | 0.94039 | -0.042484 |  | 0.95 | 1.05 | 0.035381 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | CARB-KW 3 | 0.97142 | 0.91123 | -0.060192 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | CARB-KW 3 | 0.97142 | 0.91123 | -0.060192 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | CARB-KW 3 | 0.97142 | 0.91123 | -0.060192 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | CARB-KW 3 | 0.97142 | 0.91123 | -0.060192 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | CARB-KW 3 | 0.97142 | 0.91123 | -0.060192 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | CARB-KW 3 | 0.97142 | 0.91123 | -0.060192 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | CARB-KW 3 | 0.97142 | 0.91123 | -0.060192 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | CARB-KW 3 | 0.97142 | 0.91123 | -0.060192 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | CARB-KW 3 | 0.97142 | 0.91123 | -0.060192 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | CARB-KW 3 | 0.97142 | 0.91123 | -0.060192 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | CARB-KW 3 | 0.97142 | 0.91123 | -0.060192 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | CARB-KW 3 | 0.97142 | 0.91123 | -0.060192 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | CARB-KW 3 | 0.97142 | 0.91123 | -0.060192 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | CARB-KW 3 | 0.97142 | 0.91123 | -0.060192 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | CARB-KW 3 | 0.97142 | 0.91123 | -0.060192 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | CARB-KW 3 | 0.97142 | 0.91123 | -0.060192 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | CARB-KW 3 | 0.97142 | 0.91123 | -0.060192 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | CARB-KW 3 | 0.97142 | 0.91123 | -0.060192 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | CARB-KW 3 | 0.97142 | 0.91123 | -0.060192 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | CARB-KW 3 | 0.97142 | 0.91123 | -0.060192 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | CARB-KW 3 | 0.97142 | 0.91123 | -0.060192 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | CARB-KW 3 | 0.97142 | 0.91123 | -0.060192 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | CARB-KW 3 | 0.97142 | 0.91123 | -0.060192 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | CARB-KW 3 | 0.97142 | 0.91123 | -0.060192 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | CARB-KW 3 | 0.97142 | 0.91123 | -0.060192 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | CARB-KW 3 | 0.97142 | 0.91123 | -0.060192 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | CARB-KW 3 | 0.97142 | 0.91123 | -0.060192 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | CARB-KW 3 | 0.97142 | 0.91123 | -0.060192 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | CEDARNL5 | 1.0058 | 0.92459 | -0.081185 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | CEDARNL5 | 1.0058 | 0.92459 | -0.081185 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | CEDARNL5 | 1.0058 | 0.92459 | -0.081185 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | CEDARNL5 | 1.0058 | 0.92459 | -0.081185 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | CEDARNL5 | 1.0058 | 0.92459 | -0.081185 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | CEDARNL5 | 1.0058 | 0.92459 | -0.081185 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | CEDARNL5 | 1.0058 | 0.92459 | -0.081185 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | CEDARNL5 | 1.0058 | 0.92459 | -0.081185 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | CEDARNL5 | 1.0058 | 0.92459 | -0.081185 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | CEDARNL5 | 1.0058 | 0.92459 | -0.081185 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | CEDARNL5 | 1.0058 | 0.92459 | -0.081185 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | CEDARNL5 | 1.0058 | 0.92459 | -0.081185 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | CEDARNL5 | 1.0058 | 0.92459 | -0.081185 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | CEDARNL5 | 1.0058 | 0.92459 | -0.081185 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | CEDARNL5 | 1.0058 | 0.92459 | -0.081185 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | CEDARNL5 | 1.0058 | 0.92459 | -0.081185 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | CEDARNL5 | 1.0058 | 0.92459 | -0.081185 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | CEDARNL5 | 1.0058 | 0.92459 | -0.081185 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | CEDARNL5 | 1.0058 | 0.92459 | -0.081185 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | CEDARNL5 | 1.0058 | 0.92459 | -0.081185 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | CEDARNL5 | 1.0058 | 0.92459 | -0.081185 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | CEDARNL5 | 1.0058 | 0.92459 | -0.081185 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | CEDARNL5 | 1.0058 | 0.92459 | -0.081185 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | CEDARNL5 | 1.0058 | 0.92459 | -0.081185 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | CEDARNL5 | 1.0058 | 0.92459 | -0.081185 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | CEDARNL5 | 1.0058 | 0.92459 | -0.081185 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | CEDARNL5 | 1.0058 | 0.92459 | -0.081185 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | CEDARNL5 | 1.0058 | 0.92459 | -0.081185 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | CEDRCRK5 | 0.96888 | 0.92799 | -0.040898 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | CEDRCRK5 | 0.96888 | 0.92799 | -0.040898 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | CEDRCRK5 | 0.96888 | 0.92799 | -0.040898 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | CEDRCRK5 | 0.96888 | 0.92799 | -0.040898 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | CEDRCRK5 | 0.96888 | 0.92799 | -0.040898 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | CEDRCRK5 | 0.96888 | 0.92799 | -0.040898 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | CEDRCRK5 | 0.96888 | 0.92799 | -0.040898 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | CEDRCRK5 | 0.96888 | 0.92799 | -0.040898 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | CEDRCRK5 | 0.96888 | 0.92799 | -0.040898 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | CEDRCRK5 | 0.96888 | 0.92799 | -0.040898 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | CEDRCRK5 | 0.96888 | 0.92799 | -0.040898 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | CEDRCRK5 | 0.96888 | 0.92799 | -0.040898 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | CEDRCRK5 | 0.96888 | 0.92799 | -0.040898 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | CEDRCRK5 | 0.96888 | 0.92799 | -0.040898 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | CEDRCRK5 | 0.96888 | 0.92799 | -0.040898 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | CEDRCRK5 | 0.96888 | 0.92799 | -0.040898 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | CEDRCRK5 | 0.96888 | 0.92799 | -0.040898 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | CEDRCRK5 | 0.96888 | 0.92799 | -0.040898 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | CEDRCRK5 | 0.96888 | 0.92799 | -0.040898 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | CEDRCRK5 | 0.96888 | 0.92799 | -0.040898 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | CEDRCRK5 | 0.98237 | 0.91434 | -0.068025 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | CEDRCRK5 | 0.98237 | 0.91434 | -0.068025 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | CEDRCRK5 | 0.98237 | 0.91434 | -0.068025 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | CEDRCRK5 | 0.98237 | 0.91434 | -0.068025 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | CEDRCRK5 | 0.98237 | 0.91434 | -0.068025 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | CEDRCRK5 | 0.98237 | 0.91434 | -0.068025 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | CEDRCRK5 | 0.98237 | 0.91434 | -0.068025 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | CEDRCRK5 | 0.98237 | 0.91434 | -0.068025 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | CEDRCRK5 | 0.98237 | 0.91434 | -0.068025 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | CEDRCRK5 | 0.98237 | 0.91434 | -0.068025 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | CEDRCRK5 | 0.98237 | 0.91434 | -0.068025 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | CEDRCRK5 | 0.98237 | 0.91434 | -0.068025 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | CEDRCRK5 | 0.98237 | 0.91434 | -0.068025 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | CEDRCRK5 | 0.98237 | 0.91434 | -0.068025 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | CEDRCRK5 | 0.98237 | 0.91434 | -0.068025 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | CEDRCRK5 | 0.98237 | 0.91434 | -0.068025 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | CEDRCRK5 | 0.98237 | 0.91434 | -0.068025 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | CEDRCRK5 | 0.98237 | 0.91434 | -0.068025 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | CEDRCRK5 | 0.98237 | 0.91434 | -0.068025 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | CEDRCRK5 | 0.98237 | 0.91434 | -0.068025 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | CEDRCRK5 | 0.98237 | 0.91434 | -0.068025 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | CEDRCRK5 | 0.98237 | 0.91434 | -0.068025 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | CEDRCRK5 | 0.98237 | 0.91434 | -0.068025 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | CEDRCRK5 | 0.98237 | 0.91434 | -0.068025 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | CEDRCRK5 | 0.98237 | 0.91434 | -0.068025 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | CEDRCRK5 | 0.98237 | 0.91434 | -0.068025 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | CEDRCRK5 | 0.98237 | 0.91434 | -0.068025 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | CEDRCRK5 | 0.98237 | 0.91434 | -0.068025 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | CENTENL5 | 1.0086 | 0.9179 | -0.090749 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | CENTENL5 | 1.0086 | 0.9179 | -0.090749 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | CENTENL5 | 1.0086 | 0.9179 | -0.090749 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | CENTENL5 | 1.0086 | 0.9179 | -0.090749 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | CENTENL5 | 1.0086 | 0.9179 | -0.090749 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | CENTENL5 | 1.0086 | 0.9179 | -0.090749 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | CENTENL5 | 1.0086 | 0.9179 | -0.090749 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | CENTENL5 | 1.0086 | 0.9179 | -0.090749 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | CENTENL5 | 1.0086 | 0.9179 | -0.090749 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | CENTENL5 | 1.0086 | 0.9179 | -0.090749 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | CENTENL5 | 1.0086 | 0.9179 | -0.090749 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | CENTENL5 | 1.0086 | 0.9179 | -0.090749 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | CENTENL5 | 1.0086 | 0.9179 | -0.090749 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | CENTENL5 | 1.0086 | 0.9179 | -0.090749 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | CENTENL5 | 1.0086 | 0.9179 | -0.090749 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | CENTENL5 | 1.0086 | 0.9179 | -0.090749 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | CENTENL5 | 1.0086 | 0.9179 | -0.090749 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | CENTENL5 | 1.0086 | 0.9179 | -0.090749 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | CENTENL5 | 1.0086 | 0.9179 | -0.090749 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | CENTENL5 | 1.0086 | 0.9179 | -0.090749 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | CENTENL5 | 1.0086 | 0.9179 | -0.090749 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | CENTENL5 | 1.0086 | 0.9179 | -0.090749 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | CENTENL5 | 1.0086 | 0.9179 | -0.090749 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | CENTENL5 | 1.0086 | 0.9179 | -0.090749 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | CENTENL5 | 1.0086 | 0.9179 | -0.090749 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | CENTENL5 | 1.0086 | 0.9179 | -0.090749 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | CENTENL5 | 1.0086 | 0.9179 | -0.090749 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | CENTENL5 | 1.0086 | 0.9179 | -0.090749 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | CHAMSPR7 | 0.97734 | 0.91437 | -0.062969 |  | 0.92 | 1.05 | 0.030712 | P23:345:GRDA:TONNECE CB9580:::EHV: | Add 0.4 MVAR switched shunt at TONTITN7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | CHAMSPR7 | 0.97734 | 0.91437 | -0.062969 |  | 0.92 | 1.05 | 0.038311 | P23:345:GRDA:TONNECE CB9580:::EHV: | Add 0.4 MVAR switched shunt at TONTITN7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | CHAMSPR7 | 0.97734 | 0.91437 | -0.062969 |  | 0.92 | 1.05 | 0.061498 | P23:345:GRDA:TONNECE CB9580:::EHV: | Add 0.4 MVAR switched shunt at TONTITN7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | CHAMSPR7 | 0.97734 | 0.91437 | -0.062969 |  | 0.92 | 1.05 | 0.070613 | P23:345:GRDA:TONNECE CB9580:::EHV: | Add 0.4 MVAR switched shunt at TONTITN7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | CHAMSPR7 | 0.97734 | 0.91437 | -0.062969 |  | 0.92 | 1.05 | 0.037457 | P23:345:GRDA:TONNECE CB9580:::EHV: | Add 0.4 MVAR switched shunt at TONTITN7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | CHAMSPR7 | 0.97734 | 0.91437 | -0.062969 |  | 0.92 | 1.05 | 0.15352 | P23:345:GRDA:TONNECE CB9580:::EHV: | Add 0.4 MVAR switched shunt at TONTITN7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | CHAMSPR7 | 0.97734 | 0.91437 | -0.062969 |  | 0.92 | 1.05 | 0.062033 | P23:345:GRDA:TONNECE CB9580:::EHV: | Add 0.4 MVAR switched shunt at TONTITN7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | CHAMSPR7 | 0.97798 | 0.91599 | -0.061986 |  | 0.92 | 1.05 | 0.038311 | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: | Add 0.4 MVAR switched shunt at TONTITN7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | CHAMSPR7 | 0.97798 | 0.91599 | -0.061986 |  | 0.92 | 1.05 | 0.058472 | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: | Add 0.4 MVAR switched shunt at TONTITN7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | CHAMSPR7 | 0.97798 | 0.91599 | -0.061986 |  | 0.92 | 1.05 | 0.070613 | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: | Add 0.4 MVAR switched shunt at TONTITN7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | CHAMSPR7 | 0.97798 | 0.91599 | -0.061986 |  | 0.92 | 1.05 | 0.036297 | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: | Add 0.4 MVAR switched shunt at TONTITN7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | CHAMSPR7 | 0.97798 | 0.91599 | -0.061986 |  | 0.92 | 1.05 | 0.15352 | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: | Add 0.4 MVAR switched shunt at TONTITN7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | CHAMSPR7 | 0.97798 | 0.91599 | -0.061986 |  | 0.92 | 1.05 | 0.060874 | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: | Add 0.4 MVAR switched shunt at TONTITN7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | CHASE 3 | 0.96291 | 0.89475 | -0.068158 |  | 0.9 | 1.05 | 0.064516 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 3.3 MVAR switched shunt at CHASE 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | CHASE 3 | 0.9269 | 0.85906 | -0.06784 |  | 0.9 | 1.05 | 0.046736 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | CHASE 3 | 0.9269 | 0.85906 | -0.06784 |  | 0.9 | 1.05 | 0.030145 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | CHASE 3 | 0.93891 | 0.86506 | -0.073844 |  | 0.9 | 1.05 | 0.046736 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | CHASE 3 | 0.93891 | 0.86506 | -0.073844 |  | 0.9 | 1.05 | 0.030145 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | CHASE 3 | 0.93891 | 0.86506 | -0.073845 |  | 0.9 | 1.05 | 0.046736 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | CHASE 3 | 0.93891 | 0.86506 | -0.073845 |  | 0.9 | 1.05 | 0.030145 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | CHASE 3 | 0.93891 | 0.86506 | -0.073845 |  | 0.9 | 1.05 | 0.046736 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | CHASE 3 | 0.93891 | 0.86506 | -0.073845 |  | 0.9 | 1.05 | 0.030145 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | CLEARVW3 | 0.969 | 0.92983 | -0.039174 |  | 0.93 | 1.05 | 0.03768 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | CLEARVW3 | 0.969 | 0.92983 | -0.039174 |  | 0.93 | 1.05 | 0.054649 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | CLEARVW3 | 0.969 | 0.92983 | -0.039174 |  | 0.93 | 1.05 | 0.041275 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | CLEARVW3 | 0.969 | 0.92983 | -0.039174 |  | 0.93 | 1.05 | 0.032793 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | CLEARVW3 | 0.969 | 0.92983 | -0.039174 |  | 0.93 | 1.05 | 0.043592 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | CLEARVW3 | 0.969 | 0.92983 | -0.039174 |  | 0.93 | 1.05 | 0.040246 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | CLEARVW3 | 0.969 | 0.92983 | -0.039174 |  | 0.93 | 1.05 | 0.030207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | CLEARVW3 | 0.969 | 0.92983 | -0.039174 |  | 0.93 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | CLEARVW3 | 0.969 | 0.92983 | -0.039174 |  | 0.93 | 1.05 | 0.069525 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | CLEARVW3 | 0.969 | 0.92983 | -0.039174 |  | 0.93 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | CLEARVW3 | 0.969 | 0.92983 | -0.039174 |  | 0.93 | 1.05 | 0.032357 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | CLEARVW3 | 0.969 | 0.92983 | -0.039174 |  | 0.93 | 1.05 | 0.033611 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | CLEARVW3 | 0.969 | 0.92983 | -0.039174 |  | 0.93 | 1.05 | 0.030163 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | CLEARVW3 | 0.969 | 0.92983 | -0.039174 |  | 0.93 | 1.05 | 0.042714 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | CLEARVW3 | 0.969 | 0.92983 | -0.039174 |  | 0.93 | 1.05 | 0.042627 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | CLEARVW3 | 0.969 | 0.92983 | -0.039174 |  | 0.93 | 1.05 | 0.032319 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | CLEARVW3 | 0.969 | 0.92983 | -0.039174 |  | 0.93 | 1.05 | 0.034532 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | CLEARVW3 | 0.969 | 0.92983 | -0.039174 |  | 0.93 | 1.05 | 0.030438 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | CLEARVW3 | 0.969 | 0.92983 | -0.039174 |  | 0.93 | 1.05 | 0.035207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | CLEARVW3 | 0.969 | 0.92983 | -0.039174 |  | 0.93 | 1.05 | 0.030949 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | CLEARVW3 | 0.96248 | 0.91788 | -0.044601 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | CLEARVW3 | 0.96248 | 0.91788 | -0.044601 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | CLEARVW3 | 0.96248 | 0.91788 | -0.044601 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | CLEARVW3 | 0.96248 | 0.91788 | -0.044601 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | CLEARVW3 | 0.96248 | 0.91788 | -0.044601 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | CLEARVW3 | 0.96248 | 0.91788 | -0.044601 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | CLEARVW3 | 0.96248 | 0.91788 | -0.044601 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | CLEARVW3 | 0.96248 | 0.91788 | -0.044601 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | CLEARVW3 | 0.96248 | 0.91788 | -0.044601 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | CLEARVW3 | 0.96248 | 0.91788 | -0.044601 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | CLEARVW3 | 0.96248 | 0.91788 | -0.044601 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | CLEARVW3 | 0.96248 | 0.91788 | -0.044601 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | CLEARVW3 | 0.96248 | 0.91788 | -0.044601 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | CLEARVW3 | 0.96248 | 0.91788 | -0.044601 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | CLEARVW3 | 0.96248 | 0.91788 | -0.044601 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | CLEARVW3 | 0.96248 | 0.91788 | -0.044601 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | CLEARVW3 | 0.96248 | 0.91788 | -0.044601 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | CLEARVW3 | 0.96248 | 0.91788 | -0.044601 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | CLEARVW3 | 0.96248 | 0.91788 | -0.044601 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | CLEARVW3 | 0.96248 | 0.91788 | -0.044601 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | CLEARVW3 | 0.97311 | 0.92392 | -0.049193 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | CLEARVW3 | 0.97311 | 0.92392 | -0.049193 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | CLEARVW3 | 0.97311 | 0.92392 | -0.049193 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | CLEARVW3 | 0.97311 | 0.92392 | -0.049193 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | CLEARVW3 | 0.97311 | 0.92392 | -0.049193 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | CLEARVW3 | 0.97311 | 0.92392 | -0.049193 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | CLEARVW3 | 0.97311 | 0.92392 | -0.049193 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | CLEARVW3 | 0.97311 | 0.92392 | -0.049193 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | CLEARVW3 | 0.97311 | 0.92392 | -0.049193 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | CLEARVW3 | 0.97311 | 0.92392 | -0.049193 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | CLEARVW3 | 0.97311 | 0.92392 | -0.049193 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | CLEARVW3 | 0.97311 | 0.92392 | -0.049193 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | CLEARVW3 | 0.97311 | 0.92392 | -0.049193 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | CLEARVW3 | 0.97311 | 0.92392 | -0.049193 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | CLEARVW3 | 0.97311 | 0.92392 | -0.049193 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | CLEARVW3 | 0.97311 | 0.92392 | -0.049193 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | CLEARVW3 | 0.97311 | 0.92392 | -0.049193 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | CLEARVW3 | 0.97311 | 0.92392 | -0.049193 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | CLEARVW3 | 0.97311 | 0.92392 | -0.049193 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | CLEARVW3 | 0.97311 | 0.92392 | -0.049193 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | CLEARVW3 | 0.9791 | 0.90998 | -0.069121 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | CLEARVW3 | 0.9791 | 0.90998 | -0.069121 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | CLEARVW3 | 0.9791 | 0.90998 | -0.069121 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | CLEARVW3 | 0.9791 | 0.90998 | -0.069121 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | CLEARVW3 | 0.9791 | 0.90998 | -0.069121 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | CLEARVW3 | 0.9791 | 0.90998 | -0.069121 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | CLEARVW3 | 0.9791 | 0.90998 | -0.069121 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | CLEARVW3 | 0.9791 | 0.90998 | -0.069121 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | CLEARVW3 | 0.9791 | 0.90998 | -0.069121 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | CLEARVW3 | 0.9791 | 0.90998 | -0.069121 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | CLEARVW3 | 0.9791 | 0.90998 | -0.069121 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | CLEARVW3 | 0.9791 | 0.90998 | -0.069121 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | CLEARVW3 | 0.9791 | 0.90998 | -0.069121 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | CLEARVW3 | 0.9791 | 0.90998 | -0.069121 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | CLEARVW3 | 0.9791 | 0.90998 | -0.069121 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | CLEARVW3 | 0.9791 | 0.90998 | -0.069121 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | CLEARVW3 | 0.9791 | 0.90998 | -0.069121 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | CLEARVW3 | 0.9791 | 0.90998 | -0.069121 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | CLEARVW3 | 0.9791 | 0.90998 | -0.069121 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | CLEARVW3 | 0.9791 | 0.90998 | -0.069121 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | CLEARVW3 | 0.9791 | 0.90998 | -0.069121 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | CLEARVW3 | 0.9791 | 0.90998 | -0.069121 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | CLEARVW3 | 0.9791 | 0.90998 | -0.069121 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | CLEARVW3 | 0.9791 | 0.90998 | -0.069121 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | CLEARVW3 | 0.9791 | 0.90998 | -0.069121 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | CLEARVW3 | 0.9791 | 0.90998 | -0.069121 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | CLEARVW3 | 0.9791 | 0.90998 | -0.069121 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | CLEARVW3 | 0.9791 | 0.90998 | -0.069121 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | CLEARVW3 | 0.9683 | 0.92814 | -0.040166 |  | 0.93 | 1.05 | 0.03768 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | CLEARVW3 | 0.9683 | 0.92814 | -0.040166 |  | 0.93 | 1.05 | 0.054649 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | CLEARVW3 | 0.9683 | 0.92814 | -0.040166 |  | 0.93 | 1.05 | 0.041275 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | CLEARVW3 | 0.9683 | 0.92814 | -0.040166 |  | 0.93 | 1.05 | 0.032793 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | CLEARVW3 | 0.9683 | 0.92814 | -0.040166 |  | 0.93 | 1.05 | 0.043592 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | CLEARVW3 | 0.9683 | 0.92814 | -0.040166 |  | 0.93 | 1.05 | 0.040246 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | CLEARVW3 | 0.9683 | 0.92814 | -0.040166 |  | 0.93 | 1.05 | 0.030207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | CLEARVW3 | 0.9683 | 0.92814 | -0.040166 |  | 0.93 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | CLEARVW3 | 0.9683 | 0.92814 | -0.040166 |  | 0.93 | 1.05 | 0.069525 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | CLEARVW3 | 0.9683 | 0.92814 | -0.040166 |  | 0.93 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | CLEARVW3 | 0.9683 | 0.92814 | -0.040166 |  | 0.93 | 1.05 | 0.032357 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | CLEARVW3 | 0.9683 | 0.92814 | -0.040166 |  | 0.93 | 1.05 | 0.033611 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | CLEARVW3 | 0.9683 | 0.92814 | -0.040166 |  | 0.93 | 1.05 | 0.030163 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | CLEARVW3 | 0.9683 | 0.92814 | -0.040166 |  | 0.93 | 1.05 | 0.042714 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | CLEARVW3 | 0.9683 | 0.92814 | -0.040166 |  | 0.93 | 1.05 | 0.042627 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | CLEARVW3 | 0.9683 | 0.92814 | -0.040166 |  | 0.93 | 1.05 | 0.032319 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | CLEARVW3 | 0.9683 | 0.92814 | -0.040166 |  | 0.93 | 1.05 | 0.034532 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | CLEARVW3 | 0.9683 | 0.92814 | -0.040166 |  | 0.93 | 1.05 | 0.030438 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | CLEARVW3 | 0.9683 | 0.92814 | -0.040166 |  | 0.93 | 1.05 | 0.035207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | CLEARVW3 | 0.9683 | 0.92814 | -0.040166 |  | 0.93 | 1.05 | 0.030949 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | CLIFTON3 | 0.94839 | 0.8909 | -0.057487 |  | 0.9 | 1.05 | 0.0326 | Single 539805 ELMCREEK7 345 640600 DAYKIN3 345 1 | Add 2 MVAR switched shunt at CLIFTON3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | CLIFTON3 | 0.94839 | 0.8909 | -0.057487 |  | 0.9 | 1.05 | 0.030348 | Single 539805 ELMCREEK7 345 640600 DAYKIN3 345 1 | Add 2 MVAR switched shunt at CLIFTON3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | CLIFTON3 | 0.94839 | 0.8909 | -0.057487 |  | 0.9 | 1.05 | 0.031036 | Single 539805 ELMCREEK7 345 640600 DAYKIN3 345 1 | Add 2 MVAR switched shunt at CLIFTON3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | CLIFTON3 | 0.94839 | 0.8909 | -0.057487 |  | 0.9 | 1.05 | 0.030059 | Single 539805 ELMCREEK7 345 640600 DAYKIN3 345 1 | Add 2 MVAR switched shunt at CLIFTON3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | CLIFTON3 | 0.94839 | 0.8909 | -0.057487 |  | 0.9 | 1.05 | 0.030059 | Single 539805 ELMCREEK7 345 640600 DAYKIN3 345 1 | Add 2 MVAR switched shunt at CLIFTON3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | CLIFTON3 | 0.94839 | 0.8909 | -0.057487 |  | 0.9 | 1.05 | 0.030771 | Single 539805 ELMCREEK7 345 640600 DAYKIN3 345 1 | Add 2 MVAR switched shunt at CLIFTON3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | CLIFTON3 | 0.94839 | 0.8909 | -0.057487 |  | 0.9 | 1.05 | 0.030685 | Single 539805 ELMCREEK7 345 640600 DAYKIN3 345 1 | Add 2 MVAR switched shunt at CLIFTON3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | CLINTON5 | 0.98299 | 0.90685 | -0.076144 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | CLINTON5 | 0.98299 | 0.90685 | -0.076144 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | CLINTON5 | 0.98299 | 0.90685 | -0.076144 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | CLINTON5 | 0.98299 | 0.90685 | -0.076144 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | CLINTON5 | 0.98299 | 0.90685 | -0.076144 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | CLINTON5 | 0.98299 | 0.90685 | -0.076144 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | CLINTON5 | 0.98299 | 0.90685 | -0.076144 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | CLINTON5 | 0.98299 | 0.90685 | -0.076144 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | CLINTON5 | 0.98299 | 0.90685 | -0.076144 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | CLINTON5 | 0.98299 | 0.90685 | -0.076144 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | CLINTON5 | 0.98299 | 0.90685 | -0.076144 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | CLINTON5 | 0.98299 | 0.90685 | -0.076144 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | CLINTON5 | 0.98299 | 0.90685 | -0.076144 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | CLINTON5 | 0.98299 | 0.90685 | -0.076144 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | CLINTON5 | 0.98299 | 0.90685 | -0.076144 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | CLINTON5 | 0.98299 | 0.90685 | -0.076144 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | CLINTON5 | 0.98299 | 0.90685 | -0.076144 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | CLINTON5 | 0.98299 | 0.90685 | -0.076144 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | CLINTON5 | 0.98299 | 0.90685 | -0.076144 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | CLINTON5 | 0.98299 | 0.90685 | -0.076144 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | CLINTON5 | 0.98299 | 0.90685 | -0.076144 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | CLINTON5 | 0.98299 | 0.90685 | -0.076144 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | CLINTON5 | 0.98299 | 0.90685 | -0.076144 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | CLINTON5 | 0.98299 | 0.90685 | -0.076144 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | CLINTON5 | 0.98299 | 0.90685 | -0.076144 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | CLINTON5 | 0.98299 | 0.90685 | -0.076144 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | CLINTON5 | 0.98299 | 0.90685 | -0.076144 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | CLINTON5 | 0.98299 | 0.90685 | -0.076144 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | CNTRVIL5 | 0.99298 | 0.92364 | -0.069334 |  | 0.93 | 1.05 | 0.03768 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | CNTRVIL5 | 0.99298 | 0.92364 | -0.069334 |  | 0.93 | 1.05 | 0.054649 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | CNTRVIL5 | 0.99298 | 0.92364 | -0.069334 |  | 0.93 | 1.05 | 0.041275 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | CNTRVIL5 | 0.99298 | 0.92364 | -0.069334 |  | 0.93 | 1.05 | 0.032793 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | CNTRVIL5 | 0.99298 | 0.92364 | -0.069334 |  | 0.93 | 1.05 | 0.043592 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | CNTRVIL5 | 0.99298 | 0.92364 | -0.069334 |  | 0.93 | 1.05 | 0.040246 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | CNTRVIL5 | 0.99298 | 0.92364 | -0.069334 |  | 0.93 | 1.05 | 0.030207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | CNTRVIL5 | 0.99298 | 0.92364 | -0.069334 |  | 0.93 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | CNTRVIL5 | 0.99298 | 0.92364 | -0.069334 |  | 0.93 | 1.05 | 0.069525 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | CNTRVIL5 | 0.99298 | 0.92364 | -0.069334 |  | 0.93 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | CNTRVIL5 | 0.99298 | 0.92364 | -0.069334 |  | 0.93 | 1.05 | 0.032357 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | CNTRVIL5 | 0.99298 | 0.92364 | -0.069334 |  | 0.93 | 1.05 | 0.033611 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | CNTRVIL5 | 0.99298 | 0.92364 | -0.069334 |  | 0.93 | 1.05 | 0.030163 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | CNTRVIL5 | 0.99298 | 0.92364 | -0.069334 |  | 0.93 | 1.05 | 0.042714 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | CNTRVIL5 | 0.99298 | 0.92364 | -0.069334 |  | 0.93 | 1.05 | 0.042627 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | CNTRVIL5 | 0.99298 | 0.92364 | -0.069334 |  | 0.93 | 1.05 | 0.032319 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | CNTRVIL5 | 0.99298 | 0.92364 | -0.069334 |  | 0.93 | 1.05 | 0.034532 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | CNTRVIL5 | 0.99298 | 0.92364 | -0.069334 |  | 0.93 | 1.05 | 0.030438 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | CNTRVIL5 | 0.99298 | 0.92364 | -0.069334 |  | 0.93 | 1.05 | 0.035207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | CNTRVIL5 | 0.99298 | 0.92364 | -0.069334 |  | 0.93 | 1.05 | 0.030949 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | CNTRVIL5 | 0.99364 | 0.92485 | -0.068794 |  | 0.93 | 1.05 | 0.03768 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | CNTRVIL5 | 0.99364 | 0.92485 | -0.068794 |  | 0.93 | 1.05 | 0.054649 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | CNTRVIL5 | 0.99364 | 0.92485 | -0.068794 |  | 0.93 | 1.05 | 0.041275 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | CNTRVIL5 | 0.99364 | 0.92485 | -0.068794 |  | 0.93 | 1.05 | 0.032793 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | CNTRVIL5 | 0.99364 | 0.92485 | -0.068794 |  | 0.93 | 1.05 | 0.043592 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | CNTRVIL5 | 0.99364 | 0.92485 | -0.068794 |  | 0.93 | 1.05 | 0.040246 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | CNTRVIL5 | 0.99364 | 0.92485 | -0.068794 |  | 0.93 | 1.05 | 0.030207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | CNTRVIL5 | 0.99364 | 0.92485 | -0.068794 |  | 0.93 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | CNTRVIL5 | 0.99364 | 0.92485 | -0.068794 |  | 0.93 | 1.05 | 0.069525 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | CNTRVIL5 | 0.99364 | 0.92485 | -0.068794 |  | 0.93 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | CNTRVIL5 | 0.99364 | 0.92485 | -0.068794 |  | 0.93 | 1.05 | 0.032357 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | CNTRVIL5 | 0.99364 | 0.92485 | -0.068794 |  | 0.93 | 1.05 | 0.033611 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | CNTRVIL5 | 0.99364 | 0.92485 | -0.068794 |  | 0.93 | 1.05 | 0.030163 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | CNTRVIL5 | 0.99364 | 0.92485 | -0.068794 |  | 0.93 | 1.05 | 0.042714 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | CNTRVIL5 | 0.99364 | 0.92485 | -0.068794 |  | 0.93 | 1.05 | 0.042627 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | CNTRVIL5 | 0.99364 | 0.92485 | -0.068794 |  | 0.93 | 1.05 | 0.032319 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | CNTRVIL5 | 0.99364 | 0.92485 | -0.068794 |  | 0.93 | 1.05 | 0.034532 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | CNTRVIL5 | 0.99364 | 0.92485 | -0.068794 |  | 0.93 | 1.05 | 0.030438 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | CNTRVIL5 | 0.99364 | 0.92485 | -0.068794 |  | 0.93 | 1.05 | 0.035207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | CNTRVIL5 | 0.99364 | 0.92485 | -0.068794 |  | 0.93 | 1.05 | 0.030949 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | ASGI-2024-023 | CNTRVIL5 | 0.99926 | 0.92549 | -0.073775 |  | 0.93 | 1.05 | 0.030773 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-025 | CNTRVIL5 | 0.99926 | 0.92549 | -0.073775 |  | 0.93 | 1.05 | 0.033004 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | CNTRVIL5 | 0.99926 | 0.92549 | -0.073775 |  | 0.93 | 1.05 | 0.046711 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-068 | CNTRVIL5 | 0.99926 | 0.92549 | -0.073775 |  | 0.93 | 1.05 | 0.032369 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-071 | CNTRVIL5 | 0.99926 | 0.92549 | -0.073775 |  | 0.93 | 1.05 | 0.030466 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | CNTRVIL5 | 0.99926 | 0.92549 | -0.073775 |  | 0.93 | 1.05 | 0.04987 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | CNTRVIL5 | 0.99926 | 0.92549 | -0.073775 |  | 0.93 | 1.05 | 0.099365 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | CNTRVIL5 | 0.99926 | 0.92549 | -0.073775 |  | 0.93 | 1.05 | 0.071132 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | CNTRVIL5 | 0.99926 | 0.92549 | -0.073775 |  | 0.93 | 1.05 | 0.043927 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | CNTRVIL5 | 0.99926 | 0.92549 | -0.073775 |  | 0.93 | 1.05 | 0.030565 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | CNTRVIL5 | 0.99926 | 0.92549 | -0.073775 |  | 0.93 | 1.05 | 0.072847 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | CNTRVIL5 | 0.99926 | 0.92549 | -0.073775 |  | 0.93 | 1.05 | 0.041148 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | CNTRVIL5 | 0.99926 | 0.92549 | -0.073775 |  | 0.93 | 1.05 | 0.042015 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-220 | CNTRVIL5 | 0.99926 | 0.92549 | -0.073775 |  | 0.93 | 1.05 | 0.030318 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | CNTRVIL5 | 0.99926 | 0.92549 | -0.073775 |  | 0.93 | 1.05 | 0.054104 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | CNTRVIL5 | 0.99926 | 0.92549 | -0.073775 |  | 0.93 | 1.05 | 0.047089 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | CNTRVIL5 | 0.99926 | 0.92549 | -0.073775 |  | 0.93 | 1.05 | 0.040323 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | CNTRVIL5 | 0.99926 | 0.92549 | -0.073775 |  | 0.93 | 1.05 | 0.13688 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-241 | CNTRVIL5 | 0.99926 | 0.92549 | -0.073775 |  | 0.93 | 1.05 | 0.033004 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | CNTRVIL5 | 0.99926 | 0.92549 | -0.073775 |  | 0.93 | 1.05 | 0.040323 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | CNTRVIL5 | 0.99926 | 0.92549 | -0.073775 |  | 0.93 | 1.05 | 0.039752 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | CNTRVIL5 | 0.99926 | 0.92549 | -0.073775 |  | 0.93 | 1.05 | 0.041972 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | CNTRVIL5 | 0.99926 | 0.92549 | -0.073775 |  | 0.93 | 1.05 | 0.054397 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | CNTRVIL5 | 0.99926 | 0.92549 | -0.073775 |  | 0.93 | 1.05 | 0.073688 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | CNTRVIL5 | 0.99926 | 0.92549 | -0.073775 |  | 0.93 | 1.05 | 0.048904 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | CNTRVIL5 | 0.99926 | 0.92549 | -0.073775 |  | 0.93 | 1.05 | 0.048904 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | CNTRVIL5 | 0.99926 | 0.92549 | -0.073775 |  | 0.93 | 1.05 | 0.072188 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | CNTRVIL5 | 0.99926 | 0.92549 | -0.073775 |  | 0.93 | 1.05 | 0.042186 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | CNTRVIL5 | 0.99926 | 0.92549 | -0.073775 |  | 0.93 | 1.05 | 0.041423 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | CNTRVIL5 | 0.99926 | 0.92549 | -0.073775 |  | 0.93 | 1.05 | 0.050171 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | CNTRVIL5 | 0.99926 | 0.92549 | -0.073775 |  | 0.93 | 1.05 | 0.04386 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | CNTRVIL5 | 0.99926 | 0.92549 | -0.073775 |  | 0.93 | 1.05 | 0.050218 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | CNTRVIL5 | 0.99926 | 0.92549 | -0.073775 |  | 0.93 | 1.05 | 0.040041 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | CNTRVIL5 | 0.99926 | 0.92549 | -0.073775 |  | 0.93 | 1.05 | 0.038784 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | CNTRVIL5 | 0.98923 | 0.92594 | -0.063295 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | CNTRVIL5 | 0.98923 | 0.92594 | -0.063295 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | CNTRVIL5 | 0.98923 | 0.92594 | -0.063295 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | CNTRVIL5 | 0.98923 | 0.92594 | -0.063295 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | CNTRVIL5 | 0.98923 | 0.92594 | -0.063295 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | CNTRVIL5 | 0.98923 | 0.92594 | -0.063295 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | CNTRVIL5 | 0.98923 | 0.92594 | -0.063295 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | CNTRVIL5 | 0.98923 | 0.92594 | -0.063295 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | CNTRVIL5 | 0.98923 | 0.92594 | -0.063295 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | CNTRVIL5 | 0.98923 | 0.92594 | -0.063295 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | CNTRVIL5 | 0.98923 | 0.92594 | -0.063295 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | CNTRVIL5 | 0.98923 | 0.92594 | -0.063295 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | CNTRVIL5 | 0.98923 | 0.92594 | -0.063295 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | CNTRVIL5 | 0.98923 | 0.92594 | -0.063295 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | CNTRVIL5 | 0.98923 | 0.92594 | -0.063295 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | CNTRVIL5 | 0.98923 | 0.92594 | -0.063295 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | CNTRVIL5 | 0.98923 | 0.92594 | -0.063295 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | CNTRVIL5 | 0.98923 | 0.92594 | -0.063295 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | CNTRVIL5 | 0.98923 | 0.92594 | -0.063295 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | CNTRVIL5 | 0.98923 | 0.92594 | -0.063295 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | CNTRVIL5 | 0.99506 | 0.91073 | -0.084327 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | CNTRVIL5 | 0.99506 | 0.91073 | -0.084327 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | CNTRVIL5 | 0.99506 | 0.91073 | -0.084327 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | CNTRVIL5 | 0.99506 | 0.91073 | -0.084327 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | CNTRVIL5 | 0.99506 | 0.91073 | -0.084327 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | CNTRVIL5 | 0.99506 | 0.91073 | -0.084327 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | CNTRVIL5 | 0.99506 | 0.91073 | -0.084327 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | CNTRVIL5 | 0.99506 | 0.91073 | -0.084327 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | CNTRVIL5 | 0.99506 | 0.91073 | -0.084327 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | CNTRVIL5 | 0.99506 | 0.91073 | -0.084327 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | CNTRVIL5 | 0.99506 | 0.91073 | -0.084327 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | CNTRVIL5 | 0.99506 | 0.91073 | -0.084327 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | CNTRVIL5 | 0.99506 | 0.91073 | -0.084327 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | CNTRVIL5 | 0.99506 | 0.91073 | -0.084327 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | CNTRVIL5 | 0.99506 | 0.91073 | -0.084327 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | CNTRVIL5 | 0.99506 | 0.91073 | -0.084327 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | CNTRVIL5 | 0.99506 | 0.91073 | -0.084327 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | CNTRVIL5 | 0.99506 | 0.91073 | -0.084327 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | CNTRVIL5 | 0.99506 | 0.91073 | -0.084327 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | CNTRVIL5 | 0.99506 | 0.91073 | -0.084327 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | CNTRVIL5 | 0.99506 | 0.91073 | -0.084327 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | CNTRVIL5 | 0.99506 | 0.91073 | -0.084327 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | CNTRVIL5 | 0.99506 | 0.91073 | -0.084327 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | CNTRVIL5 | 0.99506 | 0.91073 | -0.084327 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | CNTRVIL5 | 0.99506 | 0.91073 | -0.084327 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | CNTRVIL5 | 0.99506 | 0.91073 | -0.084327 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | CNTRVIL5 | 0.99506 | 0.91073 | -0.084327 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | CNTRVIL5 | 0.99506 | 0.91073 | -0.084327 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | COLBY_PUMP3 | 0.96404 | 0.89191 | -0.072132 |  | 0.9 | 1.05 | 0.041569 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | COLBY_PUMP3 | 0.96404 | 0.89191 | -0.072132 |  | 0.9 | 1.05 | 0.031515 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | COLBY_PUMP3 | 0.96404 | 0.89191 | -0.072132 |  | 0.9 | 1.05 | 0.031515 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | COLBY_PUMP3 | 0.96404 | 0.89191 | -0.072132 |  | 0.9 | 1.05 | 0.03222 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | COLBY_PUMP3 | 0.96404 | 0.89191 | -0.072132 |  | 0.9 | 1.05 | 0.030633 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | COLBY_PUMP3 | 0.96404 | 0.89191 | -0.072132 |  | 0.9 | 1.05 | 0.030061 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | COLBY_PUMP3 | 0.96404 | 0.89191 | -0.072132 |  | 0.9 | 1.05 | 0.031207 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | COLBY_PUMP3 | 0.96444 | 0.8953 | -0.06914 |  | 0.9 | 1.05 | 0.041569 | P42:345:NPPD:BKR-MAC-3304:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | COLBY_PUMP3 | 0.96444 | 0.8953 | -0.06914 |  | 0.9 | 1.05 | 0.031515 | P42:345:NPPD:BKR-MAC-3304:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | COLBY_PUMP3 | 0.96444 | 0.8953 | -0.06914 |  | 0.9 | 1.05 | 0.031515 | P42:345:NPPD:BKR-MAC-3304:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | COLBY_PUMP3 | 0.96444 | 0.8953 | -0.06914 |  | 0.9 | 1.05 | 0.03222 | P42:345:NPPD:BKR-MAC-3304:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | COLBY_PUMP3 | 0.96444 | 0.8953 | -0.06914 |  | 0.9 | 1.05 | 0.030633 | P42:345:NPPD:BKR-MAC-3304:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | COLBY_PUMP3 | 0.96444 | 0.8953 | -0.06914 |  | 0.9 | 1.05 | 0.030061 | P42:345:NPPD:BKR-MAC-3304:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | COLBY_PUMP3 | 0.96444 | 0.8953 | -0.06914 |  | 0.9 | 1.05 | 0.031207 | P42:345:NPPD:BKR-MAC-3304:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | COLBY_PUMP3 | 0.96444 | 0.8953 | -0.06914 |  | 0.9 | 1.05 | 0.041569 | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | COLBY_PUMP3 | 0.96444 | 0.8953 | -0.06914 |  | 0.9 | 1.05 | 0.031515 | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | COLBY_PUMP3 | 0.96444 | 0.8953 | -0.06914 |  | 0.9 | 1.05 | 0.031515 | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | COLBY_PUMP3 | 0.96444 | 0.8953 | -0.06914 |  | 0.9 | 1.05 | 0.03222 | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | COLBY_PUMP3 | 0.96444 | 0.8953 | -0.06914 |  | 0.9 | 1.05 | 0.030633 | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | COLBY_PUMP3 | 0.96444 | 0.8953 | -0.06914 |  | 0.9 | 1.05 | 0.030061 | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | COLBY_PUMP3 | 0.96444 | 0.8953 | -0.06914 |  | 0.9 | 1.05 | 0.031207 | P12:345:MIDW-NPPD:POSTROCK7-AXTELL3:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | COLBY_PUMP3 | 0.96556 | 0.8967 | -0.068863 |  | 0.9 | 1.05 | 0.041569 | Single 530583 POSTROCK7 345 640527 MACON3 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | COLBY_PUMP3 | 0.96556 | 0.8967 | -0.068863 |  | 0.9 | 1.05 | 0.031515 | Single 530583 POSTROCK7 345 640527 MACON3 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | COLBY_PUMP3 | 0.96556 | 0.8967 | -0.068863 |  | 0.9 | 1.05 | 0.031515 | Single 530583 POSTROCK7 345 640527 MACON3 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | COLBY_PUMP3 | 0.96556 | 0.8967 | -0.068863 |  | 0.9 | 1.05 | 0.03222 | Single 530583 POSTROCK7 345 640527 MACON3 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | COLBY_PUMP3 | 0.96556 | 0.8967 | -0.068863 |  | 0.9 | 1.05 | 0.030633 | Single 530583 POSTROCK7 345 640527 MACON3 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | COLBY_PUMP3 | 0.96556 | 0.8967 | -0.068863 |  | 0.9 | 1.05 | 0.030061 | Single 530583 POSTROCK7 345 640527 MACON3 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | COLBY_PUMP3 | 0.96556 | 0.8967 | -0.068863 |  | 0.9 | 1.05 | 0.031207 | Single 530583 POSTROCK7 345 640527 MACON3 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | COLBY_PUMP3 | 0.96503 | 0.89529 | -0.069731 |  | 0.9 | 1.05 | 0.041569 | Single 640065 AXTELL3 345 640527 MACON3 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | COLBY_PUMP3 | 0.96503 | 0.89529 | -0.069731 |  | 0.9 | 1.05 | 0.031515 | Single 640065 AXTELL3 345 640527 MACON3 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | COLBY_PUMP3 | 0.96503 | 0.89529 | -0.069731 |  | 0.9 | 1.05 | 0.031515 | Single 640065 AXTELL3 345 640527 MACON3 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | COLBY_PUMP3 | 0.96503 | 0.89529 | -0.069731 |  | 0.9 | 1.05 | 0.03222 | Single 640065 AXTELL3 345 640527 MACON3 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | COLBY_PUMP3 | 0.96503 | 0.89529 | -0.069731 |  | 0.9 | 1.05 | 0.030633 | Single 640065 AXTELL3 345 640527 MACON3 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | COLBY_PUMP3 | 0.96503 | 0.89529 | -0.069731 |  | 0.9 | 1.05 | 0.030061 | Single 640065 AXTELL3 345 640527 MACON3 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | COLBY_PUMP3 | 0.96503 | 0.89529 | -0.069731 |  | 0.9 | 1.05 | 0.031207 | Single 640065 AXTELL3 345 640527 MACON3 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | COLLEGE5 | 0.96405 | 0.92311 | -0.040944 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | COLLEGE5 | 0.96405 | 0.92311 | -0.040944 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | COLLEGE5 | 0.96405 | 0.92311 | -0.040944 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | COLLEGE5 | 0.96405 | 0.92311 | -0.040944 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | COLLEGE5 | 0.96405 | 0.92311 | -0.040944 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | COLLEGE5 | 0.96405 | 0.92311 | -0.040944 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | COLLEGE5 | 0.96405 | 0.92311 | -0.040944 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | COLLEGE5 | 0.96405 | 0.92311 | -0.040944 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | COLLEGE5 | 0.96405 | 0.92311 | -0.040944 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | COLLEGE5 | 0.96405 | 0.92311 | -0.040944 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | COLLEGE5 | 0.96405 | 0.92311 | -0.040944 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | COLLEGE5 | 0.96405 | 0.92311 | -0.040944 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | COLLEGE5 | 0.96405 | 0.92311 | -0.040944 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | COLLEGE5 | 0.96405 | 0.92311 | -0.040944 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | COLLEGE5 | 0.96405 | 0.92311 | -0.040944 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | COLLEGE5 | 0.96405 | 0.92311 | -0.040944 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | COLLEGE5 | 0.96405 | 0.92311 | -0.040944 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | COLLEGE5 | 0.96405 | 0.92311 | -0.040944 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | COLLEGE5 | 0.96405 | 0.92311 | -0.040944 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | COLLEGE5 | 0.96405 | 0.92311 | -0.040944 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | COLLEGE5 | 0.97374 | 0.92838 | -0.045353 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | COLLEGE5 | 0.97374 | 0.92838 | -0.045353 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | COLLEGE5 | 0.97374 | 0.92838 | -0.045353 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | COLLEGE5 | 0.97374 | 0.92838 | -0.045353 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | COLLEGE5 | 0.97374 | 0.92838 | -0.045353 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | COLLEGE5 | 0.97374 | 0.92838 | -0.045353 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | COLLEGE5 | 0.97374 | 0.92838 | -0.045353 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | COLLEGE5 | 0.97374 | 0.92838 | -0.045353 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | COLLEGE5 | 0.97374 | 0.92838 | -0.045353 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | COLLEGE5 | 0.97374 | 0.92838 | -0.045353 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | COLLEGE5 | 0.97374 | 0.92838 | -0.045353 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | COLLEGE5 | 0.97374 | 0.92838 | -0.045353 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | COLLEGE5 | 0.97374 | 0.92838 | -0.045353 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | COLLEGE5 | 0.97374 | 0.92838 | -0.045353 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | COLLEGE5 | 0.97374 | 0.92838 | -0.045353 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | COLLEGE5 | 0.97374 | 0.92838 | -0.045353 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | COLLEGE5 | 0.97374 | 0.92838 | -0.045353 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | COLLEGE5 | 0.97374 | 0.92838 | -0.045353 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | COLLEGE5 | 0.97374 | 0.92838 | -0.045353 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | COLLEGE5 | 0.97374 | 0.92838 | -0.045353 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | COLLEGE5 | 0.97702 | 0.90789 | -0.069128 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | COLLEGE5 | 0.97702 | 0.90789 | -0.069128 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | COLLEGE5 | 0.97702 | 0.90789 | -0.069128 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | COLLEGE5 | 0.97702 | 0.90789 | -0.069128 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | COLLEGE5 | 0.97702 | 0.90789 | -0.069128 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | COLLEGE5 | 0.97702 | 0.90789 | -0.069128 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | COLLEGE5 | 0.97702 | 0.90789 | -0.069128 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | COLLEGE5 | 0.97702 | 0.90789 | -0.069128 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | COLLEGE5 | 0.97702 | 0.90789 | -0.069128 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | COLLEGE5 | 0.97702 | 0.90789 | -0.069128 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | COLLEGE5 | 0.97702 | 0.90789 | -0.069128 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | COLLEGE5 | 0.97702 | 0.90789 | -0.069128 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | COLLEGE5 | 0.97702 | 0.90789 | -0.069128 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | COLLEGE5 | 0.97702 | 0.90789 | -0.069128 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | COLLEGE5 | 0.97702 | 0.90789 | -0.069128 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | COLLEGE5 | 0.97702 | 0.90789 | -0.069128 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | COLLEGE5 | 0.97702 | 0.90789 | -0.069128 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | COLLEGE5 | 0.97702 | 0.90789 | -0.069128 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | COLLEGE5 | 0.97702 | 0.90789 | -0.069128 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | COLLEGE5 | 0.97702 | 0.90789 | -0.069128 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | COLLEGE5 | 0.97702 | 0.90789 | -0.069128 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | COLLEGE5 | 0.97702 | 0.90789 | -0.069128 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | COLLEGE5 | 0.97702 | 0.90789 | -0.069128 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | COLLEGE5 | 0.97702 | 0.90789 | -0.069128 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | COLLEGE5 | 0.97702 | 0.90789 | -0.069128 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | COLLEGE5 | 0.97702 | 0.90789 | -0.069128 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | COLLEGE5 | 0.97702 | 0.90789 | -0.069128 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | COLLEGE5 | 0.97702 | 0.90789 | -0.069128 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | COWSKIN 4 | 0.95865 | 0.89984 | -0.058817 |  | 0.9 | 1.05 | 0.032166 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | COWSKIN 4 | 0.95865 | 0.89984 | -0.058817 |  | 0.9 | 1.05 | 0.040299 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | COWSKIN 4 | 0.95865 | 0.89984 | -0.058817 |  | 0.9 | 1.05 | 0.087845 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | COWSKIN 4 | 0.95865 | 0.89984 | -0.058817 |  | 0.9 | 1.05 | 0.076211 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | COWSKIN 4 | 0.95865 | 0.89984 | -0.058817 |  | 0.9 | 1.05 | 0.069331 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | COWSKIN 4 | 0.95865 | 0.89984 | -0.058817 |  | 0.9 | 1.05 | 0.035943 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | COWSKIN 4 | 0.95865 | 0.89984 | -0.058817 |  | 0.9 | 1.05 | 0.034061 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | COWSKIN 4 | 0.95865 | 0.89984 | -0.058817 |  | 0.9 | 1.05 | 0.16354 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | COWSKIN 4 | 0.95865 | 0.89984 | -0.058817 |  | 0.9 | 1.05 | 0.045005 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | COWSKIN 4 | 0.95865 | 0.89984 | -0.058817 |  | 0.9 | 1.05 | 0.13572 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | COWSKIN 4 | 0.95865 | 0.89984 | -0.058817 |  | 0.9 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | COWSKIN 4 | 0.95865 | 0.89984 | -0.058817 |  | 0.9 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | COWSKIN 4 | 0.95865 | 0.89984 | -0.058817 |  | 0.9 | 1.05 | 0.06894 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | COWSKIN 4 | 0.95865 | 0.89984 | -0.058817 |  | 0.9 | 1.05 | 0.034713 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | COWSKIN 4 | 0.95865 | 0.89984 | -0.058817 |  | 0.9 | 1.05 | 0.035229 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | COWSKIN2 | 0.94677 | 0.8909 | -0.055864 |  | 0.9 | 1.05 | 0.032166 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | COWSKIN2 | 0.94677 | 0.8909 | -0.055864 |  | 0.9 | 1.05 | 0.040299 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | COWSKIN2 | 0.94677 | 0.8909 | -0.055864 |  | 0.9 | 1.05 | 0.087845 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | COWSKIN2 | 0.94677 | 0.8909 | -0.055864 |  | 0.9 | 1.05 | 0.076211 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | COWSKIN2 | 0.94677 | 0.8909 | -0.055864 |  | 0.9 | 1.05 | 0.069331 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | COWSKIN2 | 0.94677 | 0.8909 | -0.055864 |  | 0.9 | 1.05 | 0.035943 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | COWSKIN2 | 0.94677 | 0.8909 | -0.055864 |  | 0.9 | 1.05 | 0.034061 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | COWSKIN2 | 0.94677 | 0.8909 | -0.055864 |  | 0.9 | 1.05 | 0.16354 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | COWSKIN2 | 0.94677 | 0.8909 | -0.055864 |  | 0.9 | 1.05 | 0.045005 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | COWSKIN2 | 0.94677 | 0.8909 | -0.055864 |  | 0.9 | 1.05 | 0.13572 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | COWSKIN2 | 0.94677 | 0.8909 | -0.055864 |  | 0.9 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | COWSKIN2 | 0.94677 | 0.8909 | -0.055864 |  | 0.9 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | COWSKIN2 | 0.94677 | 0.8909 | -0.055864 |  | 0.9 | 1.05 | 0.06894 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | COWSKIN2 | 0.94677 | 0.8909 | -0.055864 |  | 0.9 | 1.05 | 0.034713 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | COWSKIN2 | 0.94677 | 0.8909 | -0.055864 |  | 0.9 | 1.05 | 0.035229 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | COWSKIN2 | 0.94712 | 0.89169 | -0.055431 |  | 0.9 | 1.05 | 0.040299 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | COWSKIN2 | 0.94712 | 0.89169 | -0.055431 |  | 0.9 | 1.05 | 0.087845 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | COWSKIN2 | 0.94712 | 0.89169 | -0.055431 |  | 0.9 | 1.05 | 0.076211 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | COWSKIN2 | 0.94712 | 0.89169 | -0.055431 |  | 0.9 | 1.05 | 0.069331 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | COWSKIN2 | 0.94712 | 0.89169 | -0.055431 |  | 0.9 | 1.05 | 0.035943 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | COWSKIN2 | 0.94712 | 0.89169 | -0.055431 |  | 0.9 | 1.05 | 0.034061 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | COWSKIN2 | 0.94712 | 0.89169 | -0.055431 |  | 0.9 | 1.05 | 0.16354 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | COWSKIN2 | 0.94712 | 0.89169 | -0.055431 |  | 0.9 | 1.05 | 0.045005 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | COWSKIN2 | 0.94712 | 0.89169 | -0.055431 |  | 0.9 | 1.05 | 0.13572 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | COWSKIN2 | 0.94712 | 0.89169 | -0.055431 |  | 0.9 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | COWSKIN2 | 0.94712 | 0.89169 | -0.055431 |  | 0.9 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | COWSKIN2 | 0.94712 | 0.89169 | -0.055431 |  | 0.9 | 1.05 | 0.06894 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | COWSKIN2 | 0.94712 | 0.89169 | -0.055431 |  | 0.9 | 1.05 | 0.034713 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | COWSKIN2 | 0.94712 | 0.89169 | -0.055431 |  | 0.9 | 1.05 | 0.035229 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | COWSKIN2 | 0.9414 | 0.89233 | -0.049073 |  | 0.9 | 1.05 | 0.030712 | P23:345:GRDA:TONNECE CB9580:::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | COWSKIN2 | 0.9414 | 0.89233 | -0.049073 |  | 0.9 | 1.05 | 0.038311 | P23:345:GRDA:TONNECE CB9580:::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | COWSKIN2 | 0.9414 | 0.89233 | -0.049073 |  | 0.9 | 1.05 | 0.061498 | P23:345:GRDA:TONNECE CB9580:::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | COWSKIN2 | 0.9414 | 0.89233 | -0.049073 |  | 0.9 | 1.05 | 0.070613 | P23:345:GRDA:TONNECE CB9580:::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | COWSKIN2 | 0.9414 | 0.89233 | -0.049073 |  | 0.9 | 1.05 | 0.037457 | P23:345:GRDA:TONNECE CB9580:::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | COWSKIN2 | 0.9414 | 0.89233 | -0.049073 |  | 0.9 | 1.05 | 0.15352 | P23:345:GRDA:TONNECE CB9580:::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | COWSKIN2 | 0.9414 | 0.89233 | -0.049073 |  | 0.9 | 1.05 | 0.062033 | P23:345:GRDA:TONNECE CB9580:::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | COWSKIN2 | 0.94733 | 0.895 | -0.052324 |  | 0.9 | 1.05 | 0.032166 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | COWSKIN2 | 0.94733 | 0.895 | -0.052324 |  | 0.9 | 1.05 | 0.040299 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | COWSKIN2 | 0.94733 | 0.895 | -0.052324 |  | 0.9 | 1.05 | 0.055405 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | COWSKIN2 | 0.94733 | 0.895 | -0.052324 |  | 0.9 | 1.05 | 0.076211 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | COWSKIN2 | 0.94733 | 0.895 | -0.052324 |  | 0.9 | 1.05 | 0.069331 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | COWSKIN2 | 0.94733 | 0.895 | -0.052324 |  | 0.9 | 1.05 | 0.035943 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | COWSKIN2 | 0.94733 | 0.895 | -0.052324 |  | 0.9 | 1.05 | 0.034061 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | COWSKIN2 | 0.94733 | 0.895 | -0.052324 |  | 0.9 | 1.05 | 0.082012 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | COWSKIN2 | 0.94733 | 0.895 | -0.052324 |  | 0.9 | 1.05 | 0.045005 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | COWSKIN2 | 0.94733 | 0.895 | -0.052324 |  | 0.9 | 1.05 | 0.13572 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | COWSKIN2 | 0.94733 | 0.895 | -0.052324 |  | 0.9 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | COWSKIN2 | 0.94733 | 0.895 | -0.052324 |  | 0.9 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | COWSKIN2 | 0.94733 | 0.895 | -0.052324 |  | 0.9 | 1.05 | 0.06894 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | COWSKIN2 | 0.94733 | 0.895 | -0.052324 |  | 0.9 | 1.05 | 0.034713 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | COWSKIN2 | 0.94733 | 0.895 | -0.052324 |  | 0.9 | 1.05 | 0.035229 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | COWSKIN2 | 0.94272 | 0.89508 | -0.047638 |  | 0.9 | 1.05 | 0.038311 | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | COWSKIN2 | 0.94272 | 0.89508 | -0.047638 |  | 0.9 | 1.05 | 0.058472 | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | COWSKIN2 | 0.94272 | 0.89508 | -0.047638 |  | 0.9 | 1.05 | 0.070613 | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | COWSKIN2 | 0.94272 | 0.89508 | -0.047638 |  | 0.9 | 1.05 | 0.036297 | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | COWSKIN2 | 0.94272 | 0.89508 | -0.047638 |  | 0.9 | 1.05 | 0.15352 | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | COWSKIN2 | 0.94272 | 0.89508 | -0.047638 |  | 0.9 | 1.05 | 0.060874 | P12:345:GRDA:GRDA1 7-TONECE7:::EHV: | Add 24 MVAR switched shunt at GROVE 4 138 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | CPK446 5 | 0.96851 | 0.91431 | -0.054198 |  | 0.925 | 1.05 | 0.032166 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | CPK446 5 | 0.96851 | 0.91431 | -0.054198 |  | 0.925 | 1.05 | 0.040299 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | CPK446 5 | 0.96851 | 0.91431 | -0.054198 |  | 0.925 | 1.05 | 0.087845 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | CPK446 5 | 0.96851 | 0.91431 | -0.054198 |  | 0.925 | 1.05 | 0.076211 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | CPK446 5 | 0.96851 | 0.91431 | -0.054198 |  | 0.925 | 1.05 | 0.069331 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | CPK446 5 | 0.96851 | 0.91431 | -0.054198 |  | 0.925 | 1.05 | 0.035943 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | CPK446 5 | 0.96851 | 0.91431 | -0.054198 |  | 0.925 | 1.05 | 0.034061 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | CPK446 5 | 0.96851 | 0.91431 | -0.054198 |  | 0.925 | 1.05 | 0.16354 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | CPK446 5 | 0.96851 | 0.91431 | -0.054198 |  | 0.925 | 1.05 | 0.045005 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | CPK446 5 | 0.96851 | 0.91431 | -0.054198 |  | 0.925 | 1.05 | 0.13572 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | CPK446 5 | 0.96851 | 0.91431 | -0.054198 |  | 0.925 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | CPK446 5 | 0.96851 | 0.91431 | -0.054198 |  | 0.925 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | CPK446 5 | 0.96851 | 0.91431 | -0.054198 |  | 0.925 | 1.05 | 0.06894 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | CPK446 5 | 0.96851 | 0.91431 | -0.054198 |  | 0.925 | 1.05 | 0.034713 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | CPK446 5 | 0.96851 | 0.91431 | -0.054198 |  | 0.925 | 1.05 | 0.035229 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | CPK446 5 | 0.97028 | 0.91663 | -0.053648 |  | 0.925 | 1.05 | 0.040299 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | CPK446 5 | 0.97028 | 0.91663 | -0.053648 |  | 0.925 | 1.05 | 0.087845 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | CPK446 5 | 0.97028 | 0.91663 | -0.053648 |  | 0.925 | 1.05 | 0.076211 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | CPK446 5 | 0.97028 | 0.91663 | -0.053648 |  | 0.925 | 1.05 | 0.069331 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | CPK446 5 | 0.97028 | 0.91663 | -0.053648 |  | 0.925 | 1.05 | 0.035943 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | CPK446 5 | 0.97028 | 0.91663 | -0.053648 |  | 0.925 | 1.05 | 0.034061 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | CPK446 5 | 0.97028 | 0.91663 | -0.053648 |  | 0.925 | 1.05 | 0.16354 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | CPK446 5 | 0.97028 | 0.91663 | -0.053648 |  | 0.925 | 1.05 | 0.045005 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | CPK446 5 | 0.97028 | 0.91663 | -0.053648 |  | 0.925 | 1.05 | 0.13572 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | CPK446 5 | 0.97028 | 0.91663 | -0.053648 |  | 0.925 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | CPK446 5 | 0.97028 | 0.91663 | -0.053648 |  | 0.925 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | CPK446 5 | 0.97028 | 0.91663 | -0.053648 |  | 0.925 | 1.05 | 0.06894 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | CPK446 5 | 0.97028 | 0.91663 | -0.053648 |  | 0.925 | 1.05 | 0.034713 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | CPK446 5 | 0.97028 | 0.91663 | -0.053648 |  | 0.925 | 1.05 | 0.035229 | P23:345:AECI:7BLACKBERRY:6_2::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | CPK446 5 | 0.9692 | 0.91953 | -0.049669 |  | 0.925 | 1.05 | 0.032166 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | CPK446 5 | 0.9692 | 0.91953 | -0.049669 |  | 0.925 | 1.05 | 0.040299 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | CPK446 5 | 0.9692 | 0.91953 | -0.049669 |  | 0.925 | 1.05 | 0.055405 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | CPK446 5 | 0.9692 | 0.91953 | -0.049669 |  | 0.925 | 1.05 | 0.076211 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | CPK446 5 | 0.9692 | 0.91953 | -0.049669 |  | 0.925 | 1.05 | 0.069331 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | CPK446 5 | 0.9692 | 0.91953 | -0.049669 |  | 0.925 | 1.05 | 0.035943 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | CPK446 5 | 0.9692 | 0.91953 | -0.049669 |  | 0.925 | 1.05 | 0.034061 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | CPK446 5 | 0.9692 | 0.91953 | -0.049669 |  | 0.925 | 1.05 | 0.082012 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | CPK446 5 | 0.9692 | 0.91953 | -0.049669 |  | 0.925 | 1.05 | 0.045005 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | CPK446 5 | 0.9692 | 0.91953 | -0.049669 |  | 0.925 | 1.05 | 0.13572 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | CPK446 5 | 0.9692 | 0.91953 | -0.049669 |  | 0.925 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | CPK446 5 | 0.9692 | 0.91953 | -0.049669 |  | 0.925 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | CPK446 5 | 0.9692 | 0.91953 | -0.049669 |  | 0.925 | 1.05 | 0.06894 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | CPK446 5 | 0.9692 | 0.91953 | -0.049669 |  | 0.925 | 1.05 | 0.034713 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | CPK446 5 | 0.9692 | 0.91953 | -0.049669 |  | 0.925 | 1.05 | 0.035229 | P23:345:AECI:7BLACKBERRY:653::: | Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 21 MVAR switched shunt at MON383 5 161 kV; Add 0.09 MVAR switched shunt at NOL435 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | CPK446 5 | 0.96953 | 0.92252 | -0.047011 |  | 0.925 | 1.05 | 0.046659 | P23:345:AECI:7MORGAN:322::: | Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | CPK446 5 | 0.96953 | 0.92252 | -0.047011 |  | 0.925 | 1.05 | 0.04228 | P23:345:AECI:7MORGAN:322::: | Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | CPK446 5 | 0.96953 | 0.92252 | -0.047011 |  | 0.925 | 1.05 | 0.041735 | P23:345:AECI:7MORGAN:322::: | Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | CPK446 5 | 0.96953 | 0.92252 | -0.047011 |  | 0.925 | 1.05 | 0.031826 | P23:345:AECI:7MORGAN:322::: | Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | CPK446 5 | 0.96953 | 0.92252 | -0.047011 |  | 0.925 | 1.05 | 0.065625 | P23:345:AECI:7MORGAN:322::: | Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | CPK446 5 | 0.96953 | 0.92252 | -0.047011 |  | 0.925 | 1.05 | 0.052176 | P23:345:AECI:7MORGAN:322::: | Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | CPK446 5 | 0.96953 | 0.92252 | -0.047011 |  | 0.925 | 1.05 | 0.041722 | P23:345:AECI:7MORGAN:322::: | Add 16 MVAR switched shunt at CPK446 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | CPK446 5 | 0.97039 | 0.9197 | -0.050689 |  | 0.925 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | CPK446 5 | 0.97039 | 0.9197 | -0.050689 |  | 0.925 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | CPK446 5 | 0.97039 | 0.9197 | -0.050689 |  | 0.925 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | CPK446 5 | 0.97039 | 0.9197 | -0.050689 |  | 0.925 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | CPK446 5 | 0.97039 | 0.9197 | -0.050689 |  | 0.925 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | CPK446 5 | 0.97039 | 0.9197 | -0.050689 |  | 0.925 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | CPK446 5 | 0.97039 | 0.9197 | -0.050689 |  | 0.925 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | CPK446 5 | 0.97039 | 0.9197 | -0.050689 |  | 0.925 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | CPK446 5 | 0.97039 | 0.9197 | -0.050689 |  | 0.925 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | CPK446 5 | 0.97039 | 0.9197 | -0.050689 |  | 0.925 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | CPK446 5 | 0.97039 | 0.9197 | -0.050689 |  | 0.925 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | CPK446 5 | 0.97039 | 0.9197 | -0.050689 |  | 0.925 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | CPK446 5 | 0.97039 | 0.9197 | -0.050689 |  | 0.925 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | CPK446 5 | 0.97039 | 0.9197 | -0.050689 |  | 0.925 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | CPK446 5 | 0.97039 | 0.9197 | -0.050689 |  | 0.925 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | CPK446 5 | 0.97039 | 0.9197 | -0.050689 |  | 0.925 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | CPK446 5 | 0.97039 | 0.9197 | -0.050689 |  | 0.925 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | CPK446 5 | 0.97039 | 0.9197 | -0.050689 |  | 0.925 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | CPK446 5 | 0.97039 | 0.9197 | -0.050689 |  | 0.925 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | CPK446 5 | 0.97039 | 0.9197 | -0.050689 |  | 0.925 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | CPK446 5 | 0.97039 | 0.9197 | -0.050689 |  | 0.925 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | CPK446 5 | 0.97039 | 0.9197 | -0.050689 |  | 0.925 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | CPK446 5 | 0.97039 | 0.9197 | -0.050689 |  | 0.925 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | CPK446 5 | 0.97039 | 0.9197 | -0.050689 |  | 0.925 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | CPK446 5 | 0.97039 | 0.9197 | -0.050689 |  | 0.925 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | CPK446 5 | 0.97039 | 0.9197 | -0.050689 |  | 0.925 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | CPK446 5 | 0.97039 | 0.9197 | -0.050689 |  | 0.925 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | CPK446 5 | 0.97039 | 0.9197 | -0.050689 |  | 0.925 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | CRAIG 5 | 0.96802 | 0.92811 | -0.039913 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | CRAIG 5 | 0.96802 | 0.92811 | -0.039913 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | CRAIG 5 | 0.96802 | 0.92811 | -0.039913 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | CRAIG 5 | 0.96802 | 0.92811 | -0.039913 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | CRAIG 5 | 0.96802 | 0.92811 | -0.039913 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | CRAIG 5 | 0.96802 | 0.92811 | -0.039913 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | CRAIG 5 | 0.96802 | 0.92811 | -0.039913 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | CRAIG 5 | 0.96802 | 0.92811 | -0.039913 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | CRAIG 5 | 0.96802 | 0.92811 | -0.039913 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | CRAIG 5 | 0.96802 | 0.92811 | -0.039913 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | CRAIG 5 | 0.96802 | 0.92811 | -0.039913 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | CRAIG 5 | 0.96802 | 0.92811 | -0.039913 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | CRAIG 5 | 0.96802 | 0.92811 | -0.039913 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | CRAIG 5 | 0.96802 | 0.92811 | -0.039913 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | CRAIG 5 | 0.96802 | 0.92811 | -0.039913 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | CRAIG 5 | 0.96802 | 0.92811 | -0.039913 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | CRAIG 5 | 0.96802 | 0.92811 | -0.039913 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | CRAIG 5 | 0.96802 | 0.92811 | -0.039913 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | CRAIG 5 | 0.96802 | 0.92811 | -0.039913 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | CRAIG 5 | 0.96802 | 0.92811 | -0.039913 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | CRAIG 5 | 0.98091 | 0.91439 | -0.066518 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | CRAIG 5 | 0.98091 | 0.91439 | -0.066518 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | CRAIG 5 | 0.98091 | 0.91439 | -0.066518 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | CRAIG 5 | 0.98091 | 0.91439 | -0.066518 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | CRAIG 5 | 0.98091 | 0.91439 | -0.066518 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | CRAIG 5 | 0.98091 | 0.91439 | -0.066518 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | CRAIG 5 | 0.98091 | 0.91439 | -0.066518 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | CRAIG 5 | 0.98091 | 0.91439 | -0.066518 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | CRAIG 5 | 0.98091 | 0.91439 | -0.066518 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | CRAIG 5 | 0.98091 | 0.91439 | -0.066518 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | CRAIG 5 | 0.98091 | 0.91439 | -0.066518 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | CRAIG 5 | 0.98091 | 0.91439 | -0.066518 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | CRAIG 5 | 0.98091 | 0.91439 | -0.066518 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | CRAIG 5 | 0.98091 | 0.91439 | -0.066518 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | CRAIG 5 | 0.98091 | 0.91439 | -0.066518 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | CRAIG 5 | 0.98091 | 0.91439 | -0.066518 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | CRAIG 5 | 0.98091 | 0.91439 | -0.066518 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | CRAIG 5 | 0.98091 | 0.91439 | -0.066518 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | CRAIG 5 | 0.98091 | 0.91439 | -0.066518 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | CRAIG 5 | 0.98091 | 0.91439 | -0.066518 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | CRAIG 5 | 0.98091 | 0.91439 | -0.066518 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | CRAIG 5 | 0.98091 | 0.91439 | -0.066518 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | CRAIG 5 | 0.98091 | 0.91439 | -0.066518 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | CRAIG 5 | 0.98091 | 0.91439 | -0.066518 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | CRAIG 5 | 0.98091 | 0.91439 | -0.066518 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | CRAIG 5 | 0.98091 | 0.91439 | -0.066518 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | CRAIG 5 | 0.98091 | 0.91439 | -0.066518 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | CRAIG 5 | 0.98091 | 0.91439 | -0.066518 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | CRAIG 7 | 0.9684 | 0.9327 | -0.035705 |  | 0.95 | 1.05 | 0.03768 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | CRAIG 7 | 0.9684 | 0.9327 | -0.035705 |  | 0.95 | 1.05 | 0.054649 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | CRAIG 7 | 0.9684 | 0.9327 | -0.035705 |  | 0.95 | 1.05 | 0.041275 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | CRAIG 7 | 0.9684 | 0.9327 | -0.035705 |  | 0.95 | 1.05 | 0.032793 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | CRAIG 7 | 0.9684 | 0.9327 | -0.035705 |  | 0.95 | 1.05 | 0.043592 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | CRAIG 7 | 0.9684 | 0.9327 | -0.035705 |  | 0.95 | 1.05 | 0.040246 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | CRAIG 7 | 0.9684 | 0.9327 | -0.035705 |  | 0.95 | 1.05 | 0.030207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | CRAIG 7 | 0.9684 | 0.9327 | -0.035705 |  | 0.95 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | CRAIG 7 | 0.9684 | 0.9327 | -0.035705 |  | 0.95 | 1.05 | 0.069525 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | CRAIG 7 | 0.9684 | 0.9327 | -0.035705 |  | 0.95 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | CRAIG 7 | 0.9684 | 0.9327 | -0.035705 |  | 0.95 | 1.05 | 0.032357 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | CRAIG 7 | 0.9684 | 0.9327 | -0.035705 |  | 0.95 | 1.05 | 0.033611 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | CRAIG 7 | 0.9684 | 0.9327 | -0.035705 |  | 0.95 | 1.05 | 0.030163 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | CRAIG 7 | 0.9684 | 0.9327 | -0.035705 |  | 0.95 | 1.05 | 0.042714 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | CRAIG 7 | 0.9684 | 0.9327 | -0.035705 |  | 0.95 | 1.05 | 0.042627 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | CRAIG 7 | 0.9684 | 0.9327 | -0.035705 |  | 0.95 | 1.05 | 0.032319 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | CRAIG 7 | 0.9684 | 0.9327 | -0.035705 |  | 0.95 | 1.05 | 0.034532 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | CRAIG 7 | 0.9684 | 0.9327 | -0.035705 |  | 0.95 | 1.05 | 0.030438 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | CRAIG 7 | 0.9684 | 0.9327 | -0.035705 |  | 0.95 | 1.05 | 0.035207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | CRAIG 7 | 0.9684 | 0.9327 | -0.035705 |  | 0.95 | 1.05 | 0.030949 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | CRAIG 7 | 0.96246 | 0.92196 | -0.040503 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | CRAIG 7 | 0.96246 | 0.92196 | -0.040503 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | CRAIG 7 | 0.96246 | 0.92196 | -0.040503 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | CRAIG 7 | 0.96246 | 0.92196 | -0.040503 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | CRAIG 7 | 0.96246 | 0.92196 | -0.040503 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | CRAIG 7 | 0.96246 | 0.92196 | -0.040503 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | CRAIG 7 | 0.96246 | 0.92196 | -0.040503 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | CRAIG 7 | 0.96246 | 0.92196 | -0.040503 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | CRAIG 7 | 0.96246 | 0.92196 | -0.040503 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | CRAIG 7 | 0.96246 | 0.92196 | -0.040503 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | CRAIG 7 | 0.96246 | 0.92196 | -0.040503 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | CRAIG 7 | 0.96246 | 0.92196 | -0.040503 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | CRAIG 7 | 0.96246 | 0.92196 | -0.040503 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | CRAIG 7 | 0.96246 | 0.92196 | -0.040503 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | CRAIG 7 | 0.96246 | 0.92196 | -0.040503 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | CRAIG 7 | 0.96246 | 0.92196 | -0.040503 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | CRAIG 7 | 0.96246 | 0.92196 | -0.040503 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | CRAIG 7 | 0.96246 | 0.92196 | -0.040503 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | CRAIG 7 | 0.96246 | 0.92196 | -0.040503 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | CRAIG 7 | 0.96246 | 0.92196 | -0.040503 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | CRAIG 7 | 0.97211 | 0.92762 | -0.044487 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | CRAIG 7 | 0.97211 | 0.92762 | -0.044487 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | CRAIG 7 | 0.97211 | 0.92762 | -0.044487 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | CRAIG 7 | 0.97211 | 0.92762 | -0.044487 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | CRAIG 7 | 0.97211 | 0.92762 | -0.044487 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | CRAIG 7 | 0.97211 | 0.92762 | -0.044487 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | CRAIG 7 | 0.97211 | 0.92762 | -0.044487 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | CRAIG 7 | 0.97211 | 0.92762 | -0.044487 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | CRAIG 7 | 0.97211 | 0.92762 | -0.044487 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | CRAIG 7 | 0.97211 | 0.92762 | -0.044487 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | CRAIG 7 | 0.97211 | 0.92762 | -0.044487 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | CRAIG 7 | 0.97211 | 0.92762 | -0.044487 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | CRAIG 7 | 0.97211 | 0.92762 | -0.044487 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | CRAIG 7 | 0.97211 | 0.92762 | -0.044487 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | CRAIG 7 | 0.97211 | 0.92762 | -0.044487 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | CRAIG 7 | 0.97211 | 0.92762 | -0.044487 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | CRAIG 7 | 0.97211 | 0.92762 | -0.044487 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | CRAIG 7 | 0.97211 | 0.92762 | -0.044487 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | CRAIG 7 | 0.97211 | 0.92762 | -0.044487 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | CRAIG 7 | 0.97211 | 0.92762 | -0.044487 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | CRAIG 7 | 0.97747 | 0.91373 | -0.063744 |  | 0.95 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | CRAIG 7 | 0.97747 | 0.91373 | -0.063744 |  | 0.95 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | CRAIG 7 | 0.97747 | 0.91373 | -0.063744 |  | 0.95 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | CRAIG 7 | 0.97747 | 0.91373 | -0.063744 |  | 0.95 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | CRAIG 7 | 0.97747 | 0.91373 | -0.063744 |  | 0.95 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | CRAIG 7 | 0.97747 | 0.91373 | -0.063744 |  | 0.95 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | CRAIG 7 | 0.97747 | 0.91373 | -0.063744 |  | 0.95 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | CRAIG 7 | 0.97747 | 0.91373 | -0.063744 |  | 0.95 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | CRAIG 7 | 0.97747 | 0.91373 | -0.063744 |  | 0.95 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | CRAIG 7 | 0.97747 | 0.91373 | -0.063744 |  | 0.95 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | CRAIG 7 | 0.97747 | 0.91373 | -0.063744 |  | 0.95 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | CRAIG 7 | 0.97747 | 0.91373 | -0.063744 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | CRAIG 7 | 0.97747 | 0.91373 | -0.063744 |  | 0.95 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | CRAIG 7 | 0.97747 | 0.91373 | -0.063744 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | CRAIG 7 | 0.97747 | 0.91373 | -0.063744 |  | 0.95 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | CRAIG 7 | 0.97747 | 0.91373 | -0.063744 |  | 0.95 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | CRAIG 7 | 0.97747 | 0.91373 | -0.063744 |  | 0.95 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | CRAIG 7 | 0.97747 | 0.91373 | -0.063744 |  | 0.95 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | CRAIG 7 | 0.97747 | 0.91373 | -0.063744 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | CRAIG 7 | 0.97747 | 0.91373 | -0.063744 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | CRAIG 7 | 0.97747 | 0.91373 | -0.063744 |  | 0.95 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | CRAIG 7 | 0.97747 | 0.91373 | -0.063744 |  | 0.95 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | CRAIG 7 | 0.97747 | 0.91373 | -0.063744 |  | 0.95 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | CRAIG 7 | 0.97747 | 0.91373 | -0.063744 |  | 0.95 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | CRAIG 7 | 0.97747 | 0.91373 | -0.063744 |  | 0.95 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | CRAIG 7 | 0.97747 | 0.91373 | -0.063744 |  | 0.95 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | CRAIG 7 | 0.97747 | 0.91373 | -0.063744 |  | 0.95 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | CRAIG 7 | 0.97747 | 0.91373 | -0.063744 |  | 0.95 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | CRAIG 7 | 0.96778 | 0.93109 | -0.036689 |  | 0.95 | 1.05 | 0.03768 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | CRAIG 7 | 0.96778 | 0.93109 | -0.036689 |  | 0.95 | 1.05 | 0.054649 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | CRAIG 7 | 0.96778 | 0.93109 | -0.036689 |  | 0.95 | 1.05 | 0.041275 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | CRAIG 7 | 0.96778 | 0.93109 | -0.036689 |  | 0.95 | 1.05 | 0.032793 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | CRAIG 7 | 0.96778 | 0.93109 | -0.036689 |  | 0.95 | 1.05 | 0.043592 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | CRAIG 7 | 0.96778 | 0.93109 | -0.036689 |  | 0.95 | 1.05 | 0.040246 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | CRAIG 7 | 0.96778 | 0.93109 | -0.036689 |  | 0.95 | 1.05 | 0.030207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | CRAIG 7 | 0.96778 | 0.93109 | -0.036689 |  | 0.95 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | CRAIG 7 | 0.96778 | 0.93109 | -0.036689 |  | 0.95 | 1.05 | 0.069525 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | CRAIG 7 | 0.96778 | 0.93109 | -0.036689 |  | 0.95 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | CRAIG 7 | 0.96778 | 0.93109 | -0.036689 |  | 0.95 | 1.05 | 0.032357 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | CRAIG 7 | 0.96778 | 0.93109 | -0.036689 |  | 0.95 | 1.05 | 0.033611 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | CRAIG 7 | 0.96778 | 0.93109 | -0.036689 |  | 0.95 | 1.05 | 0.030163 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | CRAIG 7 | 0.96778 | 0.93109 | -0.036689 |  | 0.95 | 1.05 | 0.042714 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | CRAIG 7 | 0.96778 | 0.93109 | -0.036689 |  | 0.95 | 1.05 | 0.042627 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | CRAIG 7 | 0.96778 | 0.93109 | -0.036689 |  | 0.95 | 1.05 | 0.032319 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | CRAIG 7 | 0.96778 | 0.93109 | -0.036689 |  | 0.95 | 1.05 | 0.034532 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | CRAIG 7 | 0.96778 | 0.93109 | -0.036689 |  | 0.95 | 1.05 | 0.030438 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | CRAIG 7 | 0.96778 | 0.93109 | -0.036689 |  | 0.95 | 1.05 | 0.035207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | CRAIG 7 | 0.96778 | 0.93109 | -0.036689 |  | 0.95 | 1.05 | 0.030949 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | CRAIG_CAP 5 | 0.96908 | 0.92913 | -0.039956 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | CRAIG_CAP 5 | 0.96908 | 0.92913 | -0.039956 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | CRAIG_CAP 5 | 0.96908 | 0.92913 | -0.039956 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | CRAIG_CAP 5 | 0.96908 | 0.92913 | -0.039956 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | CRAIG_CAP 5 | 0.96908 | 0.92913 | -0.039956 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | CRAIG_CAP 5 | 0.96908 | 0.92913 | -0.039956 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | CRAIG_CAP 5 | 0.96908 | 0.92913 | -0.039956 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | CRAIG_CAP 5 | 0.96908 | 0.92913 | -0.039956 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | CRAIG_CAP 5 | 0.96908 | 0.92913 | -0.039956 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | CRAIG_CAP 5 | 0.96908 | 0.92913 | -0.039956 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | CRAIG_CAP 5 | 0.96908 | 0.92913 | -0.039956 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | CRAIG_CAP 5 | 0.96908 | 0.92913 | -0.039956 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | CRAIG_CAP 5 | 0.96908 | 0.92913 | -0.039956 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | CRAIG_CAP 5 | 0.96908 | 0.92913 | -0.039956 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | CRAIG_CAP 5 | 0.96908 | 0.92913 | -0.039956 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | CRAIG_CAP 5 | 0.96908 | 0.92913 | -0.039956 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | CRAIG_CAP 5 | 0.96908 | 0.92913 | -0.039956 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | CRAIG_CAP 5 | 0.96908 | 0.92913 | -0.039956 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | CRAIG_CAP 5 | 0.96908 | 0.92913 | -0.039956 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | CRAIG_CAP 5 | 0.96908 | 0.92913 | -0.039956 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | CRAIG_CAP 5 | 0.98198 | 0.91539 | -0.066591 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | CRAIG_CAP 5 | 0.98198 | 0.91539 | -0.066591 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | CRAIG_CAP 5 | 0.98198 | 0.91539 | -0.066591 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | CRAIG_CAP 5 | 0.98198 | 0.91539 | -0.066591 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | CRAIG_CAP 5 | 0.98198 | 0.91539 | -0.066591 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | CRAIG_CAP 5 | 0.98198 | 0.91539 | -0.066591 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | CRAIG_CAP 5 | 0.98198 | 0.91539 | -0.066591 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | CRAIG_CAP 5 | 0.98198 | 0.91539 | -0.066591 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | CRAIG_CAP 5 | 0.98198 | 0.91539 | -0.066591 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | CRAIG_CAP 5 | 0.98198 | 0.91539 | -0.066591 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | CRAIG_CAP 5 | 0.98198 | 0.91539 | -0.066591 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | CRAIG_CAP 5 | 0.98198 | 0.91539 | -0.066591 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | CRAIG_CAP 5 | 0.98198 | 0.91539 | -0.066591 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | CRAIG_CAP 5 | 0.98198 | 0.91539 | -0.066591 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | CRAIG_CAP 5 | 0.98198 | 0.91539 | -0.066591 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | CRAIG_CAP 5 | 0.98198 | 0.91539 | -0.066591 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | CRAIG_CAP 5 | 0.98198 | 0.91539 | -0.066591 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | CRAIG_CAP 5 | 0.98198 | 0.91539 | -0.066591 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | CRAIG_CAP 5 | 0.98198 | 0.91539 | -0.066591 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | CRAIG_CAP 5 | 0.98198 | 0.91539 | -0.066591 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | CRAIG_CAP 5 | 0.98198 | 0.91539 | -0.066591 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | CRAIG_CAP 5 | 0.98198 | 0.91539 | -0.066591 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | CRAIG_CAP 5 | 0.98198 | 0.91539 | -0.066591 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | CRAIG_CAP 5 | 0.98198 | 0.91539 | -0.066591 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | CRAIG_CAP 5 | 0.98198 | 0.91539 | -0.066591 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | CRAIG_CAP 5 | 0.98198 | 0.91539 | -0.066591 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | CRAIG_CAP 5 | 0.98198 | 0.91539 | -0.066591 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | CRAIG_CAP 5 | 0.98198 | 0.91539 | -0.066591 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | CRAWFOR2 | 0.96411 | 0.92098 | -0.043126 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | CRAWFOR2 | 0.96411 | 0.92098 | -0.043126 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | CRAWFOR2 | 0.96411 | 0.92098 | -0.043126 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | CRAWFOR2 | 0.96411 | 0.92098 | -0.043126 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | CRAWFOR2 | 0.96411 | 0.92098 | -0.043126 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | CRAWFOR2 | 0.96411 | 0.92098 | -0.043126 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | CRAWFOR2 | 0.96411 | 0.92098 | -0.043126 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | CRAWFOR2 | 0.96411 | 0.92098 | -0.043126 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | CRAWFOR2 | 0.96411 | 0.92098 | -0.043126 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | CRAWFOR2 | 0.96411 | 0.92098 | -0.043126 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | CRAWFOR2 | 0.96411 | 0.92098 | -0.043126 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | CRAWFOR2 | 0.96411 | 0.92098 | -0.043126 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | CRAWFOR2 | 0.96411 | 0.92098 | -0.043126 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | CRAWFOR2 | 0.96411 | 0.92098 | -0.043126 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | CRAWFOR2 | 0.96411 | 0.92098 | -0.043126 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | CRAWFOR2 | 0.96411 | 0.92098 | -0.043126 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | CRAWFOR2 | 0.96411 | 0.92098 | -0.043126 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | CRAWFOR2 | 0.96411 | 0.92098 | -0.043126 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | CRAWFOR2 | 0.96411 | 0.92098 | -0.043126 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | CRAWFOR2 | 0.96411 | 0.92098 | -0.043126 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | CRAWFOR2 | 0.96411 | 0.92098 | -0.043126 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | CRAWFOR2 | 0.96411 | 0.92098 | -0.043126 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | CRAWFOR2 | 0.96411 | 0.92098 | -0.043126 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | CRAWFOR2 | 0.96411 | 0.92098 | -0.043126 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | CRAWFOR2 | 0.96411 | 0.92098 | -0.043126 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | CRAWFOR2 | 0.96411 | 0.92098 | -0.043126 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | CRAWFOR2 | 0.96411 | 0.92098 | -0.043126 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | CRAWFOR2 | 0.96411 | 0.92098 | -0.043126 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | CSTFRAN3 | 0.95892 | 0.88973 | -0.069189 |  | 0.9 | 1.05 | 0.041569 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | CSTFRAN3 | 0.95892 | 0.88973 | -0.069189 |  | 0.9 | 1.05 | 0.031515 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | CSTFRAN3 | 0.95892 | 0.88973 | -0.069189 |  | 0.9 | 1.05 | 0.031515 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | CSTFRAN3 | 0.95892 | 0.88973 | -0.069189 |  | 0.9 | 1.05 | 0.03222 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | CSTFRAN3 | 0.95892 | 0.88973 | -0.069189 |  | 0.9 | 1.05 | 0.030633 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | CSTFRAN3 | 0.95892 | 0.88973 | -0.069189 |  | 0.9 | 1.05 | 0.030061 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | CSTFRAN3 | 0.95892 | 0.88973 | -0.069189 |  | 0.9 | 1.05 | 0.031207 | P42:345:NPPD:BKR-AXT-3306:::: | Add 25 MVAR switched shunt at ATWOOD 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | CSTFRAN3 | 0.94758 | 0.87481 | -0.072766 |  | 0.9 | 1.05 | 0.046736 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | CSTFRAN3 | 0.94758 | 0.87481 | -0.072766 |  | 0.9 | 1.05 | 0.030145 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | CSTFRAN3 | 0.94731 | 0.8671 | -0.080213 |  | 0.9 | 1.05 | 0.046736 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | CSTFRAN3 | 0.94731 | 0.8671 | -0.080213 |  | 0.9 | 1.05 | 0.030145 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | CSTFRAN3 | 0.94731 | 0.8671 | -0.080213 |  | 0.9 | 1.05 | 0.046736 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | CSTFRAN3 | 0.94731 | 0.8671 | -0.080213 |  | 0.9 | 1.05 | 0.030145 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | CSTFRAN3 | 0.94731 | 0.8671 | -0.080214 |  | 0.9 | 1.05 | 0.046736 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | CSTFRAN3 | 0.94731 | 0.8671 | -0.080214 |  | 0.9 | 1.05 | 0.030145 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | DAD368 5 | 0.97809 | 0.91586 | -0.062239 |  | 0.925 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | DAD368 5 | 0.97809 | 0.91586 | -0.062239 |  | 0.925 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | DAD368 5 | 0.97809 | 0.91586 | -0.062239 |  | 0.925 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | DAD368 5 | 0.97809 | 0.91586 | -0.062239 |  | 0.925 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | DAD368 5 | 0.97809 | 0.91586 | -0.062239 |  | 0.925 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | DAD368 5 | 0.97809 | 0.91586 | -0.062239 |  | 0.925 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | DAD368 5 | 0.97809 | 0.91586 | -0.062239 |  | 0.925 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | DAD368 5 | 0.97809 | 0.91586 | -0.062239 |  | 0.925 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | DAD368 5 | 0.97809 | 0.91586 | -0.062239 |  | 0.925 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | DAD368 5 | 0.97809 | 0.91586 | -0.062239 |  | 0.925 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | DAD368 5 | 0.97809 | 0.91586 | -0.062239 |  | 0.925 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | DAD368 5 | 0.97809 | 0.91586 | -0.062239 |  | 0.925 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | DAD368 5 | 0.97809 | 0.91586 | -0.062239 |  | 0.925 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | DAD368 5 | 0.97809 | 0.91586 | -0.062239 |  | 0.925 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | DAD368 5 | 0.97809 | 0.91586 | -0.062239 |  | 0.925 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | DAD368 5 | 0.97809 | 0.91586 | -0.062239 |  | 0.925 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | DAD368 5 | 0.97809 | 0.91586 | -0.062239 |  | 0.925 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | DAD368 5 | 0.97809 | 0.91586 | -0.062239 |  | 0.925 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | DAD368 5 | 0.97809 | 0.91586 | -0.062239 |  | 0.925 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | DAD368 5 | 0.97809 | 0.91586 | -0.062239 |  | 0.925 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | DAD368 5 | 0.97809 | 0.91586 | -0.062239 |  | 0.925 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | DAD368 5 | 0.97809 | 0.91586 | -0.062239 |  | 0.925 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | DAD368 5 | 0.97809 | 0.91586 | -0.062239 |  | 0.925 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | DAD368 5 | 0.97809 | 0.91586 | -0.062239 |  | 0.925 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | DAD368 5 | 0.97809 | 0.91586 | -0.062239 |  | 0.925 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | DAD368 5 | 0.97809 | 0.91586 | -0.062239 |  | 0.925 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | DAD368 5 | 0.97809 | 0.91586 | -0.062239 |  | 0.925 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | DAD368 5 | 0.97809 | 0.91586 | -0.062239 |  | 0.925 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | ASGI-2024-023 | DAKOTA_5 | 1.001 | 0.92889 | -0.072092 |  | 0.93 | 1.05 | 0.030773 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-025 | DAKOTA_5 | 1.001 | 0.92889 | -0.072092 |  | 0.93 | 1.05 | 0.033004 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | DAKOTA_5 | 1.001 | 0.92889 | -0.072092 |  | 0.93 | 1.05 | 0.046711 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-068 | DAKOTA_5 | 1.001 | 0.92889 | -0.072092 |  | 0.93 | 1.05 | 0.032369 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-071 | DAKOTA_5 | 1.001 | 0.92889 | -0.072092 |  | 0.93 | 1.05 | 0.030466 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | DAKOTA_5 | 1.001 | 0.92889 | -0.072092 |  | 0.93 | 1.05 | 0.04987 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | DAKOTA_5 | 1.001 | 0.92889 | -0.072092 |  | 0.93 | 1.05 | 0.099365 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | DAKOTA_5 | 1.001 | 0.92889 | -0.072092 |  | 0.93 | 1.05 | 0.071132 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | DAKOTA_5 | 1.001 | 0.92889 | -0.072092 |  | 0.93 | 1.05 | 0.043927 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | DAKOTA_5 | 1.001 | 0.92889 | -0.072092 |  | 0.93 | 1.05 | 0.030565 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | DAKOTA_5 | 1.001 | 0.92889 | -0.072092 |  | 0.93 | 1.05 | 0.072847 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | DAKOTA_5 | 1.001 | 0.92889 | -0.072092 |  | 0.93 | 1.05 | 0.041148 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | DAKOTA_5 | 1.001 | 0.92889 | -0.072092 |  | 0.93 | 1.05 | 0.042015 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-220 | DAKOTA_5 | 1.001 | 0.92889 | -0.072092 |  | 0.93 | 1.05 | 0.030318 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | DAKOTA_5 | 1.001 | 0.92889 | -0.072092 |  | 0.93 | 1.05 | 0.054104 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | DAKOTA_5 | 1.001 | 0.92889 | -0.072092 |  | 0.93 | 1.05 | 0.047089 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | DAKOTA_5 | 1.001 | 0.92889 | -0.072092 |  | 0.93 | 1.05 | 0.040323 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | DAKOTA_5 | 1.001 | 0.92889 | -0.072092 |  | 0.93 | 1.05 | 0.13688 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-241 | DAKOTA_5 | 1.001 | 0.92889 | -0.072092 |  | 0.93 | 1.05 | 0.033004 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | DAKOTA_5 | 1.001 | 0.92889 | -0.072092 |  | 0.93 | 1.05 | 0.040323 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | DAKOTA_5 | 1.001 | 0.92889 | -0.072092 |  | 0.93 | 1.05 | 0.039752 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | DAKOTA_5 | 1.001 | 0.92889 | -0.072092 |  | 0.93 | 1.05 | 0.041972 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | DAKOTA_5 | 1.001 | 0.92889 | -0.072092 |  | 0.93 | 1.05 | 0.054397 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | DAKOTA_5 | 1.001 | 0.92889 | -0.072092 |  | 0.93 | 1.05 | 0.073688 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | DAKOTA_5 | 1.001 | 0.92889 | -0.072092 |  | 0.93 | 1.05 | 0.048904 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | DAKOTA_5 | 1.001 | 0.92889 | -0.072092 |  | 0.93 | 1.05 | 0.048904 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | DAKOTA_5 | 1.001 | 0.92889 | -0.072092 |  | 0.93 | 1.05 | 0.072188 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | DAKOTA_5 | 1.001 | 0.92889 | -0.072092 |  | 0.93 | 1.05 | 0.042186 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | DAKOTA_5 | 1.001 | 0.92889 | -0.072092 |  | 0.93 | 1.05 | 0.041423 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | DAKOTA_5 | 1.001 | 0.92889 | -0.072092 |  | 0.93 | 1.05 | 0.050171 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | DAKOTA_5 | 1.001 | 0.92889 | -0.072092 |  | 0.93 | 1.05 | 0.04386 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | DAKOTA_5 | 1.001 | 0.92889 | -0.072092 |  | 0.93 | 1.05 | 0.050218 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | DAKOTA_5 | 1.001 | 0.92889 | -0.072092 |  | 0.93 | 1.05 | 0.040041 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | DAKOTA_5 | 1.001 | 0.92889 | -0.072092 |  | 0.93 | 1.05 | 0.038784 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 42 MVAR switched shunt at CNTRVIL5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | DIGHTON3 | 0.9615 | 0.89591 | -0.06559 |  | 0.9 | 1.05 | 0.045977 | Single 531449 HOLCOMB7 345 531465 SETAB7 345 1 | Add 1 MVAR switched shunt at DIGHTON3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | DIGHTON3 | 0.9615 | 0.89591 | -0.06559 |  | 0.9 | 1.05 | 0.045977 | P12:345:SUNC:SETAB-HOLCOMB::531449-531465(1):EHV: | Add 1 MVAR switched shunt at DIGHTON3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | EAST ST3 | 0.94163 | 0.85205 | -0.089587 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | EAST ST3 | 0.94163 | 0.85205 | -0.089587 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | EAST ST3 | 0.94163 | 0.85205 | -0.089587 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | EAST ST3 | 0.94163 | 0.85205 | -0.089587 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | EAST ST3 | 0.94163 | 0.85205 | -0.089587 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | EAST ST3 | 0.94163 | 0.85205 | -0.089587 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | EAST ST3 | 0.94163 | 0.85205 | -0.089587 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | EAST ST3 | 0.94163 | 0.85205 | -0.089587 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | EAST ST3 | 0.94163 | 0.85205 | -0.089587 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | EAST ST3 | 0.94163 | 0.85205 | -0.089587 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | EAST ST3 | 0.94163 | 0.85205 | -0.089587 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | EAST ST3 | 0.94163 | 0.85205 | -0.089587 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | EAST ST3 | 0.94163 | 0.85205 | -0.089587 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | EAST ST3 | 0.94163 | 0.85205 | -0.089587 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | EAST ST3 | 0.94163 | 0.85205 | -0.089587 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | EAST ST3 | 0.94163 | 0.85205 | -0.089587 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | EAST ST3 | 0.94163 | 0.85205 | -0.089587 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | EAST ST3 | 0.94163 | 0.85205 | -0.089587 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | EAST ST3 | 0.94163 | 0.85205 | -0.089587 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | EAST ST3 | 0.94163 | 0.85205 | -0.089587 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | EAST ST3 | 0.94163 | 0.85205 | -0.089587 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | EAST ST3 | 0.94163 | 0.85205 | -0.089587 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | EAST ST3 | 0.94163 | 0.85205 | -0.089587 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | EAST ST3 | 0.94163 | 0.85205 | -0.089587 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | EAST ST3 | 0.94163 | 0.85205 | -0.089587 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | EAST ST3 | 0.94163 | 0.85205 | -0.089587 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | EAST ST3 | 0.94163 | 0.85205 | -0.089587 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | EAST ST3 | 0.94163 | 0.85205 | -0.089587 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | ECNTRTN5 | 0.98889 | 0.91969 | -0.069195 |  | 0.92 | 1.05 | 0.032166 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | ECNTRTN5 | 0.98889 | 0.91969 | -0.069195 |  | 0.92 | 1.05 | 0.040299 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | ECNTRTN5 | 0.98889 | 0.91969 | -0.069195 |  | 0.92 | 1.05 | 0.087845 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | ECNTRTN5 | 0.98889 | 0.91969 | -0.069195 |  | 0.92 | 1.05 | 0.076211 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | ECNTRTN5 | 0.98889 | 0.91969 | -0.069195 |  | 0.92 | 1.05 | 0.069331 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | ECNTRTN5 | 0.98889 | 0.91969 | -0.069195 |  | 0.92 | 1.05 | 0.035943 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | ECNTRTN5 | 0.98889 | 0.91969 | -0.069195 |  | 0.92 | 1.05 | 0.034061 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | ECNTRTN5 | 0.98889 | 0.91969 | -0.069195 |  | 0.92 | 1.05 | 0.16354 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | ECNTRTN5 | 0.98889 | 0.91969 | -0.069195 |  | 0.92 | 1.05 | 0.045005 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | ECNTRTN5 | 0.98889 | 0.91969 | -0.069195 |  | 0.92 | 1.05 | 0.13572 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | ECNTRTN5 | 0.98889 | 0.91969 | -0.069195 |  | 0.92 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | ECNTRTN5 | 0.98889 | 0.91969 | -0.069195 |  | 0.92 | 1.05 | 0.037472 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | ECNTRTN5 | 0.98889 | 0.91969 | -0.069195 |  | 0.92 | 1.05 | 0.06894 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | ECNTRTN5 | 0.98889 | 0.91969 | -0.069195 |  | 0.92 | 1.05 | 0.034713 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | ECNTRTN5 | 0.98889 | 0.91969 | -0.069195 |  | 0.92 | 1.05 | 0.035229 | P23:345:AECI:7BLACKBERRY:6_3::: | Add 16 MVAR switched shunt at SIBLEYRD5 161 kV; Add 24 MVAR switched shunt at GROVE 4 138 kV; Add 15 MVAR switched shunt at NEO184 5 161 kV; Add 21 MVAR switched shunt at MON383 5 161 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | EDWRDVL5 | 0.97596 | 0.92134 | -0.054614 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | EDWRDVL5 | 0.97596 | 0.92134 | -0.054614 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | EDWRDVL5 | 0.97596 | 0.92134 | -0.054614 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | EDWRDVL5 | 0.97596 | 0.92134 | -0.054614 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | EDWRDVL5 | 0.97596 | 0.92134 | -0.054614 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | EDWRDVL5 | 0.97596 | 0.92134 | -0.054614 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | EDWRDVL5 | 0.97596 | 0.92134 | -0.054614 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | EDWRDVL5 | 0.97596 | 0.92134 | -0.054614 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | EDWRDVL5 | 0.97596 | 0.92134 | -0.054614 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | EDWRDVL5 | 0.97596 | 0.92134 | -0.054614 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | EDWRDVL5 | 0.97596 | 0.92134 | -0.054614 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | EDWRDVL5 | 0.97596 | 0.92134 | -0.054614 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | EDWRDVL5 | 0.97596 | 0.92134 | -0.054614 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | EDWRDVL5 | 0.97596 | 0.92134 | -0.054614 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | EDWRDVL5 | 0.97596 | 0.92134 | -0.054614 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | EDWRDVL5 | 0.97596 | 0.92134 | -0.054614 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | EDWRDVL5 | 0.97596 | 0.92134 | -0.054614 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | EDWRDVL5 | 0.97596 | 0.92134 | -0.054614 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | EDWRDVL5 | 0.97596 | 0.92134 | -0.054614 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | EDWRDVL5 | 0.97596 | 0.92134 | -0.054614 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | EDWRDVL5 | 0.97596 | 0.92134 | -0.054614 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | EDWRDVL5 | 0.97596 | 0.92134 | -0.054614 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | EDWRDVL5 | 0.97596 | 0.92134 | -0.054614 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | EDWRDVL5 | 0.97596 | 0.92134 | -0.054614 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | EDWRDVL5 | 0.97596 | 0.92134 | -0.054614 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | EDWRDVL5 | 0.97596 | 0.92134 | -0.054614 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | EDWRDVL5 | 0.97596 | 0.92134 | -0.054614 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | EDWRDVL5 | 0.97596 | 0.92134 | -0.054614 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | EEUREKA3 | 0.97371 | 0.905 | -0.068712 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | EEUREKA3 | 0.97371 | 0.905 | -0.068712 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | EEUREKA3 | 0.97371 | 0.905 | -0.068712 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | EEUREKA3 | 0.97371 | 0.905 | -0.068712 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | EEUREKA3 | 0.97371 | 0.905 | -0.068712 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | EEUREKA3 | 0.97371 | 0.905 | -0.068712 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | EEUREKA3 | 0.97371 | 0.905 | -0.068712 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | EEUREKA3 | 0.97371 | 0.905 | -0.068712 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | EEUREKA3 | 0.97371 | 0.905 | -0.068712 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | EEUREKA3 | 0.97371 | 0.905 | -0.068712 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | EEUREKA3 | 0.97371 | 0.905 | -0.068712 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | EEUREKA3 | 0.97371 | 0.905 | -0.068712 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | EEUREKA3 | 0.97371 | 0.905 | -0.068712 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | EEUREKA3 | 0.97371 | 0.905 | -0.068712 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | EEUREKA3 | 0.97371 | 0.905 | -0.068712 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | EEUREKA3 | 0.97371 | 0.905 | -0.068712 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | EEUREKA3 | 0.97371 | 0.905 | -0.068712 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | EEUREKA3 | 0.97371 | 0.905 | -0.068712 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | EEUREKA3 | 0.97371 | 0.905 | -0.068712 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | EEUREKA3 | 0.97371 | 0.905 | -0.068712 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | EEUREKA3 | 0.97371 | 0.905 | -0.068712 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | EEUREKA3 | 0.97371 | 0.905 | -0.068712 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | EEUREKA3 | 0.97371 | 0.905 | -0.068712 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | EEUREKA3 | 0.97371 | 0.905 | -0.068712 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | EEUREKA3 | 0.97371 | 0.905 | -0.068712 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | EEUREKA3 | 0.97371 | 0.905 | -0.068712 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | EEUREKA3 | 0.97371 | 0.905 | -0.068712 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | EEUREKA3 | 0.97371 | 0.905 | -0.068712 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | ELKRVR17 | 0.98764 | 0.94697 | -0.040675 |  | 0.95 | 1.05 | 0.040027 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | ELKRVR17 | 0.98764 | 0.94697 | -0.040675 |  | 0.95 | 1.05 | 0.090773 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | ELKRVR17 | 0.98764 | 0.94697 | -0.040675 |  | 0.95 | 1.05 | 0.034521 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | ELKRVR17 | 0.98764 | 0.94697 | -0.040675 |  | 0.95 | 1.05 | 0.038035 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | ELKRVR17 | 0.98764 | 0.94697 | -0.040675 |  | 0.95 | 1.05 | 0.048856 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | ELKRVR17 | 0.98764 | 0.94697 | -0.040675 |  | 0.95 | 1.05 | 0.048856 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | ELKRVR17 | 0.98764 | 0.94697 | -0.040675 |  | 0.95 | 1.05 | 0.050618 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | ELKRVR17 | 0.98764 | 0.94697 | -0.040675 |  | 0.95 | 1.05 | 0.04163 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | ELKRVR17 | 0.98764 | 0.94697 | -0.040675 |  | 0.95 | 1.05 | 0.043776 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | ELKRVR17 | 0.98764 | 0.94697 | -0.040675 |  | 0.95 | 1.05 | 0.034868 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | ELKRVR17 | 0.98764 | 0.94697 | -0.040675 |  | 0.95 | 1.05 | 0.031975 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | ELKRVR17 | 0.98764 | 0.94697 | -0.040675 |  | 0.95 | 1.05 | 0.037422 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | ELKRVR17 | 0.98764 | 0.94697 | -0.040675 |  | 0.95 | 1.05 | 0.050095 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | ELKRVR17 | 0.97943 | 0.93304 | -0.046384 |  | 0.95 | 1.05 | 0.040163 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | ELKRVR17 | 0.97943 | 0.93304 | -0.046384 |  | 0.95 | 1.05 | 0.035544 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | ELKRVR17 | 0.97943 | 0.93304 | -0.046384 |  | 0.95 | 1.05 | 0.048812 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | ELKRVR17 | 0.97943 | 0.93304 | -0.046384 |  | 0.95 | 1.05 | 0.049073 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | ELKRVR17 | 0.97943 | 0.93304 | -0.046384 |  | 0.95 | 1.05 | 0.035142 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | ELKRVR17 | 0.97943 | 0.93304 | -0.046384 |  | 0.95 | 1.05 | 0.037502 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | ELKRVR17 | 0.97943 | 0.93304 | -0.046384 |  | 0.95 | 1.05 | 0.04571 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | ELKRVR17 | 0.97943 | 0.93304 | -0.046384 |  | 0.95 | 1.05 | 0.03081 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | ELKRVR17 | 0.97943 | 0.93304 | -0.046384 |  | 0.95 | 1.05 | 0.03835 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | ELKRVR17 | 0.97943 | 0.93304 | -0.046384 |  | 0.95 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | ELKRVR17 | 0.97943 | 0.93304 | -0.046384 |  | 0.95 | 1.05 | 0.064216 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | ELKRVR17 | 0.97943 | 0.93304 | -0.046384 |  | 0.95 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | ELKRVR17 | 0.97943 | 0.93304 | -0.046384 |  | 0.95 | 1.05 | 0.037545 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | ELKRVR17 | 0.97943 | 0.93304 | -0.046384 |  | 0.95 | 1.05 | 0.037793 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | ELKRVR17 | 0.97943 | 0.93304 | -0.046384 |  | 0.95 | 1.05 | 0.035866 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | ELKRVR17 | 0.97943 | 0.93304 | -0.046384 |  | 0.95 | 1.05 | 0.064223 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | ELKRVR17 | 0.97943 | 0.93304 | -0.046384 |  | 0.95 | 1.05 | 0.046439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | ELKRVR17 | 0.97943 | 0.93304 | -0.046384 |  | 0.95 | 1.05 | 0.03576 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | ELKRVR17 | 0.97943 | 0.93304 | -0.046384 |  | 0.95 | 1.05 | 0.032864 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | ELKRVR17 | 0.97943 | 0.93304 | -0.046384 |  | 0.95 | 1.05 | 0.032012 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | ELKRVR17 | 0.97943 | 0.93304 | -0.046384 |  | 0.95 | 1.05 | 0.033901 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | ELKRVR17 | 0.97943 | 0.93304 | -0.046384 |  | 0.95 | 1.05 | 0.035381 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | ELKRVR17 | 0.99198 | 0.94715 | -0.044833 |  | 0.95 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | ELKRVR17 | 0.99198 | 0.94715 | -0.044833 |  | 0.95 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | ELKRVR17 | 0.99198 | 0.94715 | -0.044833 |  | 0.95 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | ELKRVR17 | 0.99198 | 0.94715 | -0.044833 |  | 0.95 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | ELKRVR17 | 0.99198 | 0.94715 | -0.044833 |  | 0.95 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | ELKRVR17 | 0.99198 | 0.94715 | -0.044833 |  | 0.95 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | ELKRVR17 | 0.99198 | 0.94715 | -0.044833 |  | 0.95 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | ELKRVR17 | 0.99198 | 0.94715 | -0.044833 |  | 0.95 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | ELKRVR17 | 0.99198 | 0.94715 | -0.044833 |  | 0.95 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | ELKRVR17 | 0.99198 | 0.94715 | -0.044833 |  | 0.95 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | ELKRVR17 | 0.99198 | 0.94715 | -0.044833 |  | 0.95 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | ELKRVR17 | 0.99198 | 0.94715 | -0.044833 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | ELKRVR17 | 0.99198 | 0.94715 | -0.044833 |  | 0.95 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | ELKRVR17 | 0.99198 | 0.94715 | -0.044833 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | ELKRVR17 | 0.99198 | 0.94715 | -0.044833 |  | 0.95 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | ELKRVR17 | 0.99198 | 0.94715 | -0.044833 |  | 0.95 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | ELKRVR17 | 0.99198 | 0.94715 | -0.044833 |  | 0.95 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | ELKRVR17 | 0.99198 | 0.94715 | -0.044833 |  | 0.95 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | ELKRVR17 | 0.99198 | 0.94715 | -0.044833 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | ELKRVR17 | 0.99198 | 0.94715 | -0.044833 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | ELKRVR17 | 0.99198 | 0.94715 | -0.044833 |  | 0.95 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | ELKRVR17 | 0.99198 | 0.94715 | -0.044833 |  | 0.95 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | ELKRVR17 | 0.99198 | 0.94715 | -0.044833 |  | 0.95 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | ELKRVR17 | 0.99198 | 0.94715 | -0.044833 |  | 0.95 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | ELKRVR17 | 0.99198 | 0.94715 | -0.044833 |  | 0.95 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | ELKRVR17 | 0.99198 | 0.94715 | -0.044833 |  | 0.95 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | ELKRVR17 | 0.99198 | 0.94715 | -0.044833 |  | 0.95 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | ELKRVR17 | 0.99198 | 0.94715 | -0.044833 |  | 0.95 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | ELLIS 2 | 0.93089 | 0.86605 | -0.064845 |  | 0.9 | 1.05 | 0.046736 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | ELLIS 2 | 0.93089 | 0.86605 | -0.064845 |  | 0.9 | 1.05 | 0.030145 | P23:345:SUNC:SB_BRK482:::EHV: | Add 32.8 MVAR switched shunt at NSI TAP3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | ELLIS 2 | 0.93647 | 0.86715 | -0.069312 |  | 0.9 | 1.05 | 0.046736 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | ELLIS 2 | 0.93647 | 0.86715 | -0.069312 |  | 0.9 | 1.05 | 0.030145 | Single 531451 MINGO7 345 531465 SETAB7 345 1 | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | ELLIS 2 | 0.93647 | 0.86716 | -0.069312 |  | 0.9 | 1.05 | 0.046736 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | ELLIS 2 | 0.93647 | 0.86716 | -0.069312 |  | 0.9 | 1.05 | 0.030145 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | ELLIS 2 | 0.93647 | 0.86716 | -0.069313 |  | 0.9 | 1.05 | 0.046736 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | ELLIS 2 | 0.93647 | 0.86716 | -0.069313 |  | 0.9 | 1.05 | 0.030145 | P23:115-345:SUNC:MO_BRK188:::HV: | Add 3.2 MVAR switched shunt at BIRDCTY3 115 kV; Add 20 MVAR switched shunt at RANSOM 3 115 kV; Add 12 MVAR switched shunt at GOODCTY3 115 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | EUDORA 3 | 0.96594 | 0.92786 | -0.038083 |  | 0.93 | 1.05 | 0.03768 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | EUDORA 3 | 0.96594 | 0.92786 | -0.038083 |  | 0.93 | 1.05 | 0.054649 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | EUDORA 3 | 0.96594 | 0.92786 | -0.038083 |  | 0.93 | 1.05 | 0.041275 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | EUDORA 3 | 0.96594 | 0.92786 | -0.038083 |  | 0.93 | 1.05 | 0.032793 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | EUDORA 3 | 0.96594 | 0.92786 | -0.038083 |  | 0.93 | 1.05 | 0.043592 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | EUDORA 3 | 0.96594 | 0.92786 | -0.038083 |  | 0.93 | 1.05 | 0.040246 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | EUDORA 3 | 0.96594 | 0.92786 | -0.038083 |  | 0.93 | 1.05 | 0.030207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | EUDORA 3 | 0.96594 | 0.92786 | -0.038083 |  | 0.93 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | EUDORA 3 | 0.96594 | 0.92786 | -0.038083 |  | 0.93 | 1.05 | 0.069525 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | EUDORA 3 | 0.96594 | 0.92786 | -0.038083 |  | 0.93 | 1.05 | 0.032056 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | EUDORA 3 | 0.96594 | 0.92786 | -0.038083 |  | 0.93 | 1.05 | 0.032357 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | EUDORA 3 | 0.96594 | 0.92786 | -0.038083 |  | 0.93 | 1.05 | 0.033611 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | EUDORA 3 | 0.96594 | 0.92786 | -0.038083 |  | 0.93 | 1.05 | 0.030163 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | EUDORA 3 | 0.96594 | 0.92786 | -0.038083 |  | 0.93 | 1.05 | 0.042714 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | EUDORA 3 | 0.96594 | 0.92786 | -0.038083 |  | 0.93 | 1.05 | 0.042627 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | EUDORA 3 | 0.96594 | 0.92786 | -0.038083 |  | 0.93 | 1.05 | 0.032319 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | EUDORA 3 | 0.96594 | 0.92786 | -0.038083 |  | 0.93 | 1.05 | 0.034532 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | EUDORA 3 | 0.96594 | 0.92786 | -0.038083 |  | 0.93 | 1.05 | 0.030438 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | EUDORA 3 | 0.96594 | 0.92786 | -0.038083 |  | 0.93 | 1.05 | 0.035207 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | EUDORA 3 | 0.96594 | 0.92786 | -0.038083 |  | 0.93 | 1.05 | 0.030949 | Single 542981 LACYGNE7 345 765571 G21-029-TAP 345 1 | Add 177 MVAR switched shunt at SWISVAL7 345 kV; Add 316 MVAR switched shunt at W.GRDNR7 345 kV; Add 213 MVAR switched shunt at STILWEL7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | EUDORA 3 | 0.96065 | 0.91688 | -0.043768 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | EUDORA 3 | 0.96065 | 0.91688 | -0.043768 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | EUDORA 3 | 0.96065 | 0.91688 | -0.043768 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | EUDORA 3 | 0.96065 | 0.91688 | -0.043768 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | EUDORA 3 | 0.96065 | 0.91688 | -0.043768 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | EUDORA 3 | 0.96065 | 0.91688 | -0.043768 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | EUDORA 3 | 0.96065 | 0.91688 | -0.043768 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | EUDORA 3 | 0.96065 | 0.91688 | -0.043768 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | EUDORA 3 | 0.96065 | 0.91688 | -0.043768 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | EUDORA 3 | 0.96065 | 0.91688 | -0.043768 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | EUDORA 3 | 0.96065 | 0.91688 | -0.043768 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | EUDORA 3 | 0.96065 | 0.91688 | -0.043768 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | EUDORA 3 | 0.96065 | 0.91688 | -0.043768 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | EUDORA 3 | 0.96065 | 0.91688 | -0.043768 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | EUDORA 3 | 0.96065 | 0.91688 | -0.043768 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | EUDORA 3 | 0.96065 | 0.91688 | -0.043768 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | EUDORA 3 | 0.96065 | 0.91688 | -0.043768 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | EUDORA 3 | 0.96065 | 0.91688 | -0.043768 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | EUDORA 3 | 0.96065 | 0.91688 | -0.043768 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | EUDORA 3 | 0.96065 | 0.91688 | -0.043768 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | EUDORA 3 | 0.96939 | 0.92159 | -0.047807 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | EUDORA 3 | 0.96939 | 0.92159 | -0.047807 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | EUDORA 3 | 0.96939 | 0.92159 | -0.047807 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | EUDORA 3 | 0.96939 | 0.92159 | -0.047807 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | EUDORA 3 | 0.96939 | 0.92159 | -0.047807 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | EUDORA 3 | 0.96939 | 0.92159 | -0.047807 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | EUDORA 3 | 0.96939 | 0.92159 | -0.047807 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | EUDORA 3 | 0.96939 | 0.92159 | -0.047807 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | EUDORA 3 | 0.96939 | 0.92159 | -0.047807 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | EUDORA 3 | 0.96939 | 0.92159 | -0.047807 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | EUDORA 3 | 0.96939 | 0.92159 | -0.047807 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | EUDORA 3 | 0.96939 | 0.92159 | -0.047807 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | EUDORA 3 | 0.96939 | 0.92159 | -0.047807 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | EUDORA 3 | 0.96939 | 0.92159 | -0.047807 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | EUDORA 3 | 0.96939 | 0.92159 | -0.047807 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | EUDORA 3 | 0.96939 | 0.92159 | -0.047807 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | EUDORA 3 | 0.96939 | 0.92159 | -0.047807 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | EUDORA 3 | 0.96939 | 0.92159 | -0.047807 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | EUDORA 3 | 0.96939 | 0.92159 | -0.047807 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | EUDORA 3 | 0.96939 | 0.92159 | -0.047807 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | EUDORA 3 | 0.97558 | 0.91275 | -0.062826 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | EUDORA 3 | 0.97558 | 0.91275 | -0.062826 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | EUDORA 3 | 0.97558 | 0.91275 | -0.062826 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | EUDORA 3 | 0.97558 | 0.91275 | -0.062826 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | EUDORA 3 | 0.97558 | 0.91275 | -0.062826 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | EUDORA 3 | 0.97558 | 0.91275 | -0.062826 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | EUDORA 3 | 0.97558 | 0.91275 | -0.062826 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | EUDORA 3 | 0.97558 | 0.91275 | -0.062826 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | EUDORA 3 | 0.97558 | 0.91275 | -0.062826 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | EUDORA 3 | 0.97558 | 0.91275 | -0.062826 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | EUDORA 3 | 0.97558 | 0.91275 | -0.062826 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | EUDORA 3 | 0.97558 | 0.91275 | -0.062826 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | EUDORA 3 | 0.97558 | 0.91275 | -0.062826 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | EUDORA 3 | 0.97558 | 0.91275 | -0.062826 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | EUDORA 3 | 0.97558 | 0.91275 | -0.062826 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | EUDORA 3 | 0.97558 | 0.91275 | -0.062826 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | EUDORA 3 | 0.97558 | 0.91275 | -0.062826 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | EUDORA 3 | 0.97558 | 0.91275 | -0.062826 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | EUDORA 3 | 0.97558 | 0.91275 | -0.062826 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | EUDORA 3 | 0.97558 | 0.91275 | -0.062826 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | EUDORA 3 | 0.97558 | 0.91275 | -0.062826 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | EUDORA 3 | 0.97558 | 0.91275 | -0.062826 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | EUDORA 3 | 0.97558 | 0.91275 | -0.062826 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | EUDORA 3 | 0.97558 | 0.91275 | -0.062826 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | EUDORA 3 | 0.97558 | 0.91275 | -0.062826 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | EUDORA 3 | 0.97558 | 0.91275 | -0.062826 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | EUDORA 3 | 0.97558 | 0.91275 | -0.062826 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | EUDORA 3 | 0.97558 | 0.91275 | -0.062826 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | EUDORA 3 | 0.96536 | 0.92626 | -0.039106 |  | 0.93 | 1.05 | 0.03768 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | EUDORA 3 | 0.96536 | 0.92626 | -0.039106 |  | 0.93 | 1.05 | 0.054649 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | EUDORA 3 | 0.96536 | 0.92626 | -0.039106 |  | 0.93 | 1.05 | 0.041275 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | EUDORA 3 | 0.96536 | 0.92626 | -0.039106 |  | 0.93 | 1.05 | 0.032793 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | EUDORA 3 | 0.96536 | 0.92626 | -0.039106 |  | 0.93 | 1.05 | 0.043592 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | EUDORA 3 | 0.96536 | 0.92626 | -0.039106 |  | 0.93 | 1.05 | 0.040246 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | EUDORA 3 | 0.96536 | 0.92626 | -0.039106 |  | 0.93 | 1.05 | 0.030207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | EUDORA 3 | 0.96536 | 0.92626 | -0.039106 |  | 0.93 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | EUDORA 3 | 0.96536 | 0.92626 | -0.039106 |  | 0.93 | 1.05 | 0.069525 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | EUDORA 3 | 0.96536 | 0.92626 | -0.039106 |  | 0.93 | 1.05 | 0.032056 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | EUDORA 3 | 0.96536 | 0.92626 | -0.039106 |  | 0.93 | 1.05 | 0.032357 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | EUDORA 3 | 0.96536 | 0.92626 | -0.039106 |  | 0.93 | 1.05 | 0.033611 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | EUDORA 3 | 0.96536 | 0.92626 | -0.039106 |  | 0.93 | 1.05 | 0.030163 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | EUDORA 3 | 0.96536 | 0.92626 | -0.039106 |  | 0.93 | 1.05 | 0.042714 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | EUDORA 3 | 0.96536 | 0.92626 | -0.039106 |  | 0.93 | 1.05 | 0.042627 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | EUDORA 3 | 0.96536 | 0.92626 | -0.039106 |  | 0.93 | 1.05 | 0.032319 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | EUDORA 3 | 0.96536 | 0.92626 | -0.039106 |  | 0.93 | 1.05 | 0.034532 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | EUDORA 3 | 0.96536 | 0.92626 | -0.039106 |  | 0.93 | 1.05 | 0.030438 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | EUDORA 3 | 0.96536 | 0.92626 | -0.039106 |  | 0.93 | 1.05 | 0.035207 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | EUDORA 3 | 0.96536 | 0.92626 | -0.039106 |  | 0.93 | 1.05 | 0.030949 | Single 542968 STILWEL7 345 765571 G21-029-TAP 345 1 | None
Voltage | 04ALL | 2 | 29SP | V | ASGI-2024-023 | EXPED WF7 | 1.0022 | 0.94491 | -0.057275 |  | 0.95 | 1.05 | 0.030773 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-025 | EXPED WF7 | 1.0022 | 0.94491 | -0.057275 |  | 0.95 | 1.05 | 0.033004 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | EXPED WF7 | 1.0022 | 0.94491 | -0.057275 |  | 0.95 | 1.05 | 0.046711 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-068 | EXPED WF7 | 1.0022 | 0.94491 | -0.057275 |  | 0.95 | 1.05 | 0.032369 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-071 | EXPED WF7 | 1.0022 | 0.94491 | -0.057275 |  | 0.95 | 1.05 | 0.030466 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | EXPED WF7 | 1.0022 | 0.94491 | -0.057275 |  | 0.95 | 1.05 | 0.04987 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | EXPED WF7 | 1.0022 | 0.94491 | -0.057275 |  | 0.95 | 1.05 | 0.099365 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | EXPED WF7 | 1.0022 | 0.94491 | -0.057275 |  | 0.95 | 1.05 | 0.071132 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | EXPED WF7 | 1.0022 | 0.94491 | -0.057275 |  | 0.95 | 1.05 | 0.043927 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | EXPED WF7 | 1.0022 | 0.94491 | -0.057275 |  | 0.95 | 1.05 | 0.030565 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | EXPED WF7 | 1.0022 | 0.94491 | -0.057275 |  | 0.95 | 1.05 | 0.072847 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | EXPED WF7 | 1.0022 | 0.94491 | -0.057275 |  | 0.95 | 1.05 | 0.041148 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | EXPED WF7 | 1.0022 | 0.94491 | -0.057275 |  | 0.95 | 1.05 | 0.042015 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-220 | EXPED WF7 | 1.0022 | 0.94491 | -0.057275 |  | 0.95 | 1.05 | 0.030318 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | EXPED WF7 | 1.0022 | 0.94491 | -0.057275 |  | 0.95 | 1.05 | 0.054104 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | EXPED WF7 | 1.0022 | 0.94491 | -0.057275 |  | 0.95 | 1.05 | 0.047089 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | EXPED WF7 | 1.0022 | 0.94491 | -0.057275 |  | 0.95 | 1.05 | 0.040323 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | EXPED WF7 | 1.0022 | 0.94491 | -0.057275 |  | 0.95 | 1.05 | 0.13688 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-241 | EXPED WF7 | 1.0022 | 0.94491 | -0.057275 |  | 0.95 | 1.05 | 0.033004 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | EXPED WF7 | 1.0022 | 0.94491 | -0.057275 |  | 0.95 | 1.05 | 0.040323 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | EXPED WF7 | 1.0022 | 0.94491 | -0.057275 |  | 0.95 | 1.05 | 0.039752 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | EXPED WF7 | 1.0022 | 0.94491 | -0.057275 |  | 0.95 | 1.05 | 0.041972 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | EXPED WF7 | 1.0022 | 0.94491 | -0.057275 |  | 0.95 | 1.05 | 0.054397 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | EXPED WF7 | 1.0022 | 0.94491 | -0.057275 |  | 0.95 | 1.05 | 0.073688 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | EXPED WF7 | 1.0022 | 0.94491 | -0.057275 |  | 0.95 | 1.05 | 0.048904 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | EXPED WF7 | 1.0022 | 0.94491 | -0.057275 |  | 0.95 | 1.05 | 0.048904 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | EXPED WF7 | 1.0022 | 0.94491 | -0.057275 |  | 0.95 | 1.05 | 0.072188 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | EXPED WF7 | 1.0022 | 0.94491 | -0.057275 |  | 0.95 | 1.05 | 0.042186 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | EXPED WF7 | 1.0022 | 0.94491 | -0.057275 |  | 0.95 | 1.05 | 0.041423 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | EXPED WF7 | 1.0022 | 0.94491 | -0.057275 |  | 0.95 | 1.05 | 0.050171 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | EXPED WF7 | 1.0022 | 0.94491 | -0.057275 |  | 0.95 | 1.05 | 0.04386 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | EXPED WF7 | 1.0022 | 0.94491 | -0.057275 |  | 0.95 | 1.05 | 0.050218 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | EXPED WF7 | 1.0022 | 0.94491 | -0.057275 |  | 0.95 | 1.05 | 0.040041 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | EXPED WF7 | 1.0022 | 0.94491 | -0.057275 |  | 0.95 | 1.05 | 0.038784 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | EXPED WF7 | 1.0013 | 0.94793 | -0.05341 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | EXPED WF7 | 1.0013 | 0.94793 | -0.05341 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | EXPED WF7 | 1.0013 | 0.94793 | -0.05341 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | EXPED WF7 | 1.0013 | 0.94793 | -0.05341 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | EXPED WF7 | 1.0013 | 0.94793 | -0.05341 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | EXPED WF7 | 1.0013 | 0.94793 | -0.05341 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | EXPED WF7 | 1.0013 | 0.94793 | -0.05341 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | EXPED WF7 | 1.0013 | 0.94793 | -0.05341 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | EXPED WF7 | 1.0013 | 0.94793 | -0.05341 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | EXPED WF7 | 1.0013 | 0.94793 | -0.05341 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | EXPED WF7 | 1.0013 | 0.94793 | -0.05341 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | EXPED WF7 | 1.0013 | 0.94793 | -0.05341 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | EXPED WF7 | 1.0013 | 0.94793 | -0.05341 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | EXPED WF7 | 1.0013 | 0.94793 | -0.05341 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | EXPED WF7 | 1.0013 | 0.94793 | -0.05341 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | EXPED WF7 | 1.0013 | 0.94793 | -0.05341 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | EXPED WF7 | 1.0013 | 0.94793 | -0.05341 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | EXPED WF7 | 1.0013 | 0.94793 | -0.05341 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | EXPED WF7 | 1.0013 | 0.94793 | -0.05341 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | EXPED WF7 | 1.0013 | 0.94793 | -0.05341 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | EXPED WF7 | 0.99886 | 0.93645 | -0.062414 |  | 0.95 | 1.05 | 0.040163 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | EXPED WF7 | 0.99886 | 0.93645 | -0.062414 |  | 0.95 | 1.05 | 0.035544 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | EXPED WF7 | 0.99886 | 0.93645 | -0.062414 |  | 0.95 | 1.05 | 0.048812 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | EXPED WF7 | 0.99886 | 0.93645 | -0.062414 |  | 0.95 | 1.05 | 0.049073 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | EXPED WF7 | 0.99886 | 0.93645 | -0.062414 |  | 0.95 | 1.05 | 0.035142 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | EXPED WF7 | 0.99886 | 0.93645 | -0.062414 |  | 0.95 | 1.05 | 0.037502 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | EXPED WF7 | 0.99886 | 0.93645 | -0.062414 |  | 0.95 | 1.05 | 0.04571 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | EXPED WF7 | 0.99886 | 0.93645 | -0.062414 |  | 0.95 | 1.05 | 0.03081 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | EXPED WF7 | 0.99886 | 0.93645 | -0.062414 |  | 0.95 | 1.05 | 0.03835 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | EXPED WF7 | 0.99886 | 0.93645 | -0.062414 |  | 0.95 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | EXPED WF7 | 0.99886 | 0.93645 | -0.062414 |  | 0.95 | 1.05 | 0.064216 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | EXPED WF7 | 0.99886 | 0.93645 | -0.062414 |  | 0.95 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | EXPED WF7 | 0.99886 | 0.93645 | -0.062414 |  | 0.95 | 1.05 | 0.037545 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | EXPED WF7 | 0.99886 | 0.93645 | -0.062414 |  | 0.95 | 1.05 | 0.037793 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | EXPED WF7 | 0.99886 | 0.93645 | -0.062414 |  | 0.95 | 1.05 | 0.035866 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | EXPED WF7 | 0.99886 | 0.93645 | -0.062414 |  | 0.95 | 1.05 | 0.064223 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | EXPED WF7 | 0.99886 | 0.93645 | -0.062414 |  | 0.95 | 1.05 | 0.046439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | EXPED WF7 | 0.99886 | 0.93645 | -0.062414 |  | 0.95 | 1.05 | 0.03576 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | EXPED WF7 | 0.99886 | 0.93645 | -0.062414 |  | 0.95 | 1.05 | 0.032864 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | EXPED WF7 | 0.99886 | 0.93645 | -0.062414 |  | 0.95 | 1.05 | 0.032012 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | EXPED WF7 | 0.99886 | 0.93645 | -0.062414 |  | 0.95 | 1.05 | 0.033901 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | EXPED WF7 | 0.99886 | 0.93645 | -0.062414 |  | 0.95 | 1.05 | 0.035381 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | EXPED WF7 | 0.99908 | 0.94818 | -0.050908 |  | 0.95 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | EXPED WF7 | 0.99908 | 0.94818 | -0.050908 |  | 0.95 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | EXPED WF7 | 0.99908 | 0.94818 | -0.050908 |  | 0.95 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | EXPED WF7 | 0.99908 | 0.94818 | -0.050908 |  | 0.95 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | EXPED WF7 | 0.99908 | 0.94818 | -0.050908 |  | 0.95 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | EXPED WF7 | 0.99908 | 0.94818 | -0.050908 |  | 0.95 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | EXPED WF7 | 0.99908 | 0.94818 | -0.050908 |  | 0.95 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | EXPED WF7 | 0.99908 | 0.94818 | -0.050908 |  | 0.95 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | EXPED WF7 | 0.99908 | 0.94818 | -0.050908 |  | 0.95 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | EXPED WF7 | 0.99908 | 0.94818 | -0.050908 |  | 0.95 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | EXPED WF7 | 0.99908 | 0.94818 | -0.050908 |  | 0.95 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | EXPED WF7 | 0.99908 | 0.94818 | -0.050908 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | EXPED WF7 | 0.99908 | 0.94818 | -0.050908 |  | 0.95 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | EXPED WF7 | 0.99908 | 0.94818 | -0.050908 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | EXPED WF7 | 0.99908 | 0.94818 | -0.050908 |  | 0.95 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | EXPED WF7 | 0.99908 | 0.94818 | -0.050908 |  | 0.95 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | EXPED WF7 | 0.99908 | 0.94818 | -0.050908 |  | 0.95 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | EXPED WF7 | 0.99908 | 0.94818 | -0.050908 |  | 0.95 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | EXPED WF7 | 0.99908 | 0.94818 | -0.050908 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | EXPED WF7 | 0.99908 | 0.94818 | -0.050908 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | EXPED WF7 | 0.99908 | 0.94818 | -0.050908 |  | 0.95 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | EXPED WF7 | 0.99908 | 0.94818 | -0.050908 |  | 0.95 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | EXPED WF7 | 0.99908 | 0.94818 | -0.050908 |  | 0.95 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | EXPED WF7 | 0.99908 | 0.94818 | -0.050908 |  | 0.95 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | EXPED WF7 | 0.99908 | 0.94818 | -0.050908 |  | 0.95 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | EXPED WF7 | 0.99908 | 0.94818 | -0.050908 |  | 0.95 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | EXPED WF7 | 0.99908 | 0.94818 | -0.050908 |  | 0.95 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | EXPED WF7 | 0.99908 | 0.94818 | -0.050908 |  | 0.95 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | FAIRGDS3 | 0.96465 | 0.92366 | -0.040992 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | FAIRGDS3 | 0.96465 | 0.92366 | -0.040992 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | FAIRGDS3 | 0.96465 | 0.92366 | -0.040992 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | FAIRGDS3 | 0.96465 | 0.92366 | -0.040992 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | FAIRGDS3 | 0.96465 | 0.92366 | -0.040992 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | FAIRGDS3 | 0.96465 | 0.92366 | -0.040992 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | FAIRGDS3 | 0.96465 | 0.92366 | -0.040992 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | FAIRGDS3 | 0.96465 | 0.92366 | -0.040992 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | FAIRGDS3 | 0.96465 | 0.92366 | -0.040992 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | FAIRGDS3 | 0.96465 | 0.92366 | -0.040992 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | FAIRGDS3 | 0.96465 | 0.92366 | -0.040992 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | FAIRGDS3 | 0.96465 | 0.92366 | -0.040992 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | FAIRGDS3 | 0.96465 | 0.92366 | -0.040992 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | FAIRGDS3 | 0.96465 | 0.92366 | -0.040992 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | FAIRGDS3 | 0.96465 | 0.92366 | -0.040992 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | FAIRGDS3 | 0.96465 | 0.92366 | -0.040992 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | FAIRGDS3 | 0.96465 | 0.92366 | -0.040992 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | FAIRGDS3 | 0.96465 | 0.92366 | -0.040992 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | FAIRGDS3 | 0.96465 | 0.92366 | -0.040992 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | FAIRGDS3 | 0.96465 | 0.92366 | -0.040992 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | FAIRGDS3 | 0.97089 | 0.92685 | -0.044042 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | FAIRGDS3 | 0.97089 | 0.92685 | -0.044042 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | FAIRGDS3 | 0.97089 | 0.92685 | -0.044042 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | FAIRGDS3 | 0.97089 | 0.92685 | -0.044042 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | FAIRGDS3 | 0.97089 | 0.92685 | -0.044042 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | FAIRGDS3 | 0.97089 | 0.92685 | -0.044042 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | FAIRGDS3 | 0.97089 | 0.92685 | -0.044042 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | FAIRGDS3 | 0.97089 | 0.92685 | -0.044042 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | FAIRGDS3 | 0.97089 | 0.92685 | -0.044042 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | FAIRGDS3 | 0.97089 | 0.92685 | -0.044042 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | FAIRGDS3 | 0.97089 | 0.92685 | -0.044042 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | FAIRGDS3 | 0.97089 | 0.92685 | -0.044042 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | FAIRGDS3 | 0.97089 | 0.92685 | -0.044042 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | FAIRGDS3 | 0.97089 | 0.92685 | -0.044042 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | FAIRGDS3 | 0.97089 | 0.92685 | -0.044042 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | FAIRGDS3 | 0.97089 | 0.92685 | -0.044042 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | FAIRGDS3 | 0.97089 | 0.92685 | -0.044042 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | FAIRGDS3 | 0.97089 | 0.92685 | -0.044042 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | FAIRGDS3 | 0.97089 | 0.92685 | -0.044042 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | FAIRGDS3 | 0.97089 | 0.92685 | -0.044042 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | FAIRGDS3 | 0.97725 | 0.92429 | -0.052969 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | FAIRGDS3 | 0.97725 | 0.92429 | -0.052969 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | FAIRGDS3 | 0.97725 | 0.92429 | -0.052969 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | FAIRGDS3 | 0.97725 | 0.92429 | -0.052969 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | FAIRGDS3 | 0.97725 | 0.92429 | -0.052969 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | FAIRGDS3 | 0.97725 | 0.92429 | -0.052969 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | FAIRGDS3 | 0.97725 | 0.92429 | -0.052969 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | FAIRGDS3 | 0.97725 | 0.92429 | -0.052969 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | FAIRGDS3 | 0.97725 | 0.92429 | -0.052969 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | FAIRGDS3 | 0.97725 | 0.92429 | -0.052969 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | FAIRGDS3 | 0.97725 | 0.92429 | -0.052969 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | FAIRGDS3 | 0.97725 | 0.92429 | -0.052969 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | FAIRGDS3 | 0.97725 | 0.92429 | -0.052969 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | FAIRGDS3 | 0.97725 | 0.92429 | -0.052969 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | FAIRGDS3 | 0.97725 | 0.92429 | -0.052969 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | FAIRGDS3 | 0.97725 | 0.92429 | -0.052969 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | FAIRGDS3 | 0.97725 | 0.92429 | -0.052969 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | FAIRGDS3 | 0.97725 | 0.92429 | -0.052969 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | FAIRGDS3 | 0.97725 | 0.92429 | -0.052969 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | FAIRGDS3 | 0.97725 | 0.92429 | -0.052969 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | FAIRGDS3 | 0.97725 | 0.92429 | -0.052969 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | FAIRGDS3 | 0.97725 | 0.92429 | -0.052969 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | FAIRGDS3 | 0.97725 | 0.92429 | -0.052969 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | FAIRGDS3 | 0.97725 | 0.92429 | -0.052969 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | FAIRGDS3 | 0.97725 | 0.92429 | -0.052969 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | FAIRGDS3 | 0.97725 | 0.92429 | -0.052969 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | FAIRGDS3 | 0.97725 | 0.92429 | -0.052969 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | FAIRGDS3 | 0.97725 | 0.92429 | -0.052969 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | FINNEY 7 | 1.0309 | 1.0611 | 0.03028 |  | 0.9 | 1.05 | 0.064516 | P23:345:SUNC:HLC_BRK282:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | FINNEY 7 | 1.0329 | 1.0606 | 0.027697 |  | 0.9 | 1.05 | 0.064516 | Single 523853 FINNEY7 345 531449 HOLCOMB7 345 1 | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | FINNEY 7 | 1.0329 | 1.0606 | 0.027697 |  | 0.9 | 1.05 | 0.064516 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | FINNEY 7 | 1.0329 | 1.0606 | 0.027697 |  | 0.9 | 1.05 | 0.064516 | P12:345:SPS:J04:1:FINNEY_HOLCOMB___:EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | FINNEY 7 | 1.0151 | 1.0542 | 0.039079 |  | 0.9 | 1.05 | 0.064516 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 23 MVAR switched shunt at FINNEY 7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | FLORENC3 | 0.96673 | 0.89997 | -0.066757 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | FLORENC3 | 0.96673 | 0.89997 | -0.066757 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | FLORENC3 | 0.96673 | 0.89997 | -0.066757 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | FLORENC3 | 0.96673 | 0.89997 | -0.066757 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | FLORENC3 | 0.96673 | 0.89997 | -0.066757 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | FLORENC3 | 0.96673 | 0.89997 | -0.066757 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | FLORENC3 | 0.96673 | 0.89997 | -0.066757 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | FLORENC3 | 0.96673 | 0.89997 | -0.066757 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | FLORENC3 | 0.96673 | 0.89997 | -0.066757 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | FLORENC3 | 0.96673 | 0.89997 | -0.066757 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | FLORENC3 | 0.96673 | 0.89997 | -0.066757 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | FLORENC3 | 0.96673 | 0.89997 | -0.066757 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | FLORENC3 | 0.96673 | 0.89997 | -0.066757 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | FLORENC3 | 0.96673 | 0.89997 | -0.066757 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | FLORENC3 | 0.96673 | 0.89997 | -0.066757 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | FLORENC3 | 0.96673 | 0.89997 | -0.066757 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | FLORENC3 | 0.96673 | 0.89997 | -0.066757 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | FLORENC3 | 0.96673 | 0.89997 | -0.066757 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | FLORENC3 | 0.96673 | 0.89997 | -0.066757 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | FLORENC3 | 0.96673 | 0.89997 | -0.066757 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | FLORENC3 | 0.96673 | 0.89997 | -0.066757 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | FLORENC3 | 0.96673 | 0.89997 | -0.066757 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | FLORENC3 | 0.96673 | 0.89997 | -0.066757 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | FLORENC3 | 0.96673 | 0.89997 | -0.066757 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | FLORENC3 | 0.96673 | 0.89997 | -0.066757 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | FLORENC3 | 0.96673 | 0.89997 | -0.066757 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | FLORENC3 | 0.96673 | 0.89997 | -0.066757 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | FLORENC3 | 0.96673 | 0.89997 | -0.066757 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | FMC 3 | 0.96812 | 0.92771 | -0.040406 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | FMC 3 | 0.96812 | 0.92771 | -0.040406 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | FMC 3 | 0.96812 | 0.92771 | -0.040406 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | FMC 3 | 0.96812 | 0.92771 | -0.040406 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | FMC 3 | 0.96812 | 0.92771 | -0.040406 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | FMC 3 | 0.96812 | 0.92771 | -0.040406 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | FMC 3 | 0.96812 | 0.92771 | -0.040406 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | FMC 3 | 0.96812 | 0.92771 | -0.040406 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | FMC 3 | 0.96812 | 0.92771 | -0.040406 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | FMC 3 | 0.96812 | 0.92771 | -0.040406 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | FMC 3 | 0.96812 | 0.92771 | -0.040406 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | FMC 3 | 0.96812 | 0.92771 | -0.040406 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | FMC 3 | 0.96812 | 0.92771 | -0.040406 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | FMC 3 | 0.96812 | 0.92771 | -0.040406 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | FMC 3 | 0.96812 | 0.92771 | -0.040406 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | FMC 3 | 0.96812 | 0.92771 | -0.040406 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | FMC 3 | 0.96812 | 0.92771 | -0.040406 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | FMC 3 | 0.96812 | 0.92771 | -0.040406 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | FMC 3 | 0.96812 | 0.92771 | -0.040406 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | FMC 3 | 0.96812 | 0.92771 | -0.040406 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | FMC 3 | 0.97973 | 0.92908 | -0.050648 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | FMC 3 | 0.97973 | 0.92908 | -0.050648 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | FMC 3 | 0.97973 | 0.92908 | -0.050648 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | FMC 3 | 0.97973 | 0.92908 | -0.050648 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | FMC 3 | 0.97973 | 0.92908 | -0.050648 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | FMC 3 | 0.97973 | 0.92908 | -0.050648 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | FMC 3 | 0.97973 | 0.92908 | -0.050648 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | FMC 3 | 0.97973 | 0.92908 | -0.050648 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | FMC 3 | 0.97973 | 0.92908 | -0.050648 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | FMC 3 | 0.97973 | 0.92908 | -0.050648 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | FMC 3 | 0.97973 | 0.92908 | -0.050648 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | FMC 3 | 0.97973 | 0.92908 | -0.050648 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | FMC 3 | 0.97973 | 0.92908 | -0.050648 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | FMC 3 | 0.97973 | 0.92908 | -0.050648 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | FMC 3 | 0.97973 | 0.92908 | -0.050648 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | FMC 3 | 0.97973 | 0.92908 | -0.050648 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | FMC 3 | 0.97973 | 0.92908 | -0.050648 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | FMC 3 | 0.97973 | 0.92908 | -0.050648 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | FMC 3 | 0.97973 | 0.92908 | -0.050648 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | FMC 3 | 0.97973 | 0.92908 | -0.050648 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | FMC 3 | 0.97973 | 0.92908 | -0.050648 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | FMC 3 | 0.97973 | 0.92908 | -0.050648 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | FMC 3 | 0.97973 | 0.92908 | -0.050648 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | FMC 3 | 0.97973 | 0.92908 | -0.050648 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | FMC 3 | 0.97973 | 0.92908 | -0.050648 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | FMC 3 | 0.97973 | 0.92908 | -0.050648 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | FMC 3 | 0.97973 | 0.92908 | -0.050648 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | FMC 3 | 0.97973 | 0.92908 | -0.050648 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | FOREST 5 | 0.98556 | 0.92166 | -0.063901 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | FOREST 5 | 0.98556 | 0.92166 | -0.063901 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | FOREST 5 | 0.98556 | 0.92166 | -0.063901 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | FOREST 5 | 0.98556 | 0.92166 | -0.063901 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | FOREST 5 | 0.98556 | 0.92166 | -0.063901 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | FOREST 5 | 0.98556 | 0.92166 | -0.063901 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | FOREST 5 | 0.98556 | 0.92166 | -0.063901 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | FOREST 5 | 0.98556 | 0.92166 | -0.063901 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | FOREST 5 | 0.98556 | 0.92166 | -0.063901 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | FOREST 5 | 0.98556 | 0.92166 | -0.063901 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | FOREST 5 | 0.98556 | 0.92166 | -0.063901 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | FOREST 5 | 0.98556 | 0.92166 | -0.063901 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | FOREST 5 | 0.98556 | 0.92166 | -0.063901 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | FOREST 5 | 0.98556 | 0.92166 | -0.063901 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | FOREST 5 | 0.98556 | 0.92166 | -0.063901 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | FOREST 5 | 0.98556 | 0.92166 | -0.063901 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | FOREST 5 | 0.98556 | 0.92166 | -0.063901 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | FOREST 5 | 0.98556 | 0.92166 | -0.063901 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | FOREST 5 | 0.98556 | 0.92166 | -0.063901 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | FOREST 5 | 0.98556 | 0.92166 | -0.063901 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | FOREST 5 | 0.98556 | 0.92166 | -0.063901 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | FOREST 5 | 0.98556 | 0.92166 | -0.063901 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | FOREST 5 | 0.98556 | 0.92166 | -0.063901 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | FOREST 5 | 0.98556 | 0.92166 | -0.063901 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | FOREST 5 | 0.98556 | 0.92166 | -0.063901 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | FOREST 5 | 0.98556 | 0.92166 | -0.063901 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | FOREST 5 | 0.98556 | 0.92166 | -0.063901 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | FOREST 5 | 0.98556 | 0.92166 | -0.063901 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | FR4 XMF1 345 | 0.99694 | 0.94492 | -0.052015 |  | 0.95 | 1.05 | 0.040027 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | FR4 XMF1 345 | 0.99694 | 0.94492 | -0.052015 |  | 0.95 | 1.05 | 0.090773 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | FR4 XMF1 345 | 0.99694 | 0.94492 | -0.052015 |  | 0.95 | 1.05 | 0.034521 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | FR4 XMF1 345 | 0.99694 | 0.94492 | -0.052015 |  | 0.95 | 1.05 | 0.038035 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | FR4 XMF1 345 | 0.99694 | 0.94492 | -0.052015 |  | 0.95 | 1.05 | 0.048856 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | FR4 XMF1 345 | 0.99694 | 0.94492 | -0.052015 |  | 0.95 | 1.05 | 0.048856 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | FR4 XMF1 345 | 0.99694 | 0.94492 | -0.052015 |  | 0.95 | 1.05 | 0.050618 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | FR4 XMF1 345 | 0.99694 | 0.94492 | -0.052015 |  | 0.95 | 1.05 | 0.04163 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | FR4 XMF1 345 | 0.99694 | 0.94492 | -0.052015 |  | 0.95 | 1.05 | 0.043776 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | FR4 XMF1 345 | 0.99694 | 0.94492 | -0.052015 |  | 0.95 | 1.05 | 0.034868 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | FR4 XMF1 345 | 0.99694 | 0.94492 | -0.052015 |  | 0.95 | 1.05 | 0.031975 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | FR4 XMF1 345 | 0.99694 | 0.94492 | -0.052015 |  | 0.95 | 1.05 | 0.037422 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | FR4 XMF1 345 | 0.99694 | 0.94492 | -0.052015 |  | 0.95 | 1.05 | 0.050095 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | FR4 XMF1 345 | 0.99421 | 0.9423 | -0.051908 |  | 0.95 | 1.05 | 0.094783 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | FR4 XMF1 345 | 0.99421 | 0.9423 | -0.051908 |  | 0.95 | 1.05 | 0.03645 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | FR4 XMF1 345 | 0.99421 | 0.9423 | -0.051908 |  | 0.95 | 1.05 | 0.04755 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | FR4 XMF1 345 | 0.99421 | 0.9423 | -0.051908 |  | 0.95 | 1.05 | 0.06097 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | FR4 XMF1 345 | 0.99421 | 0.9423 | -0.051908 |  | 0.95 | 1.05 | 0.061051 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | FR4 XMF1 345 | 0.99421 | 0.9423 | -0.051908 |  | 0.95 | 1.05 | 0.04456 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | FR4 XMF1 345 | 0.99421 | 0.9423 | -0.051908 |  | 0.95 | 1.05 | 0.048811 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | FR4 XMF1 345 | 0.99421 | 0.9423 | -0.051908 |  | 0.95 | 1.05 | 0.13004 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | FR4 XMF1 345 | 0.99421 | 0.9423 | -0.051908 |  | 0.95 | 1.05 | 0.049018 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | FR4 XMF1 345 | 0.99421 | 0.9423 | -0.051908 |  | 0.95 | 1.05 | 0.059524 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | FR4 XMF1 345 | 0.99421 | 0.9423 | -0.051908 |  | 0.95 | 1.05 | 0.059524 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | FR4 XMF1 345 | 0.99421 | 0.9423 | -0.051908 |  | 0.95 | 1.05 | 0.05974 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | FR4 XMF1 345 | 0.99421 | 0.9423 | -0.051908 |  | 0.95 | 1.05 | 0.076949 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | FR4 XMF1 345 | 0.99421 | 0.9423 | -0.051908 |  | 0.95 | 1.05 | 0.042157 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | FR4 XMF1 345 | 0.99421 | 0.9423 | -0.051908 |  | 0.95 | 1.05 | 0.040957 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | FR4 XMF1 345 | 0.99421 | 0.9423 | -0.051908 |  | 0.95 | 1.05 | 0.044127 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | FR4 XMF1 345 | 0.99421 | 0.9423 | -0.051908 |  | 0.95 | 1.05 | 0.044127 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | FR4 XMF1 345 | 0.99421 | 0.9423 | -0.051908 |  | 0.95 | 1.05 | 0.054637 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | FR4 XMF1 345 | 0.99421 | 0.9423 | -0.051908 |  | 0.95 | 1.05 | 0.060597 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | FR4 XMF1 345 | 0.99421 | 0.9423 | -0.051908 |  | 0.95 | 1.05 | 0.044286 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | FR4 XMF1 345 | 0.99421 | 0.9423 | -0.051908 |  | 0.95 | 1.05 | 0.059107 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | FR4 XMF1 345 | 0.99421 | 0.9423 | -0.051908 |  | 0.95 | 1.05 | 0.052698 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | FR4 XMF1 345 | 0.99421 | 0.9423 | -0.051908 |  | 0.95 | 1.05 | 0.067422 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | FR4 XMF1 345 | 0.99421 | 0.9423 | -0.051908 |  | 0.95 | 1.05 | 0.053768 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | FR4 XMF1 345 | 0.99421 | 0.9423 | -0.051908 |  | 0.95 | 1.05 | 0.03909 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | FR4345KV-TAP | 0.99687 | 0.94486 | -0.052011 |  | 0.95 | 1.05 | 0.040027 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | FR4345KV-TAP | 0.99687 | 0.94486 | -0.052011 |  | 0.95 | 1.05 | 0.090773 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | FR4345KV-TAP | 0.99687 | 0.94486 | -0.052011 |  | 0.95 | 1.05 | 0.034521 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | FR4345KV-TAP | 0.99687 | 0.94486 | -0.052011 |  | 0.95 | 1.05 | 0.038035 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | FR4345KV-TAP | 0.99687 | 0.94486 | -0.052011 |  | 0.95 | 1.05 | 0.048856 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | FR4345KV-TAP | 0.99687 | 0.94486 | -0.052011 |  | 0.95 | 1.05 | 0.048856 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | FR4345KV-TAP | 0.99687 | 0.94486 | -0.052011 |  | 0.95 | 1.05 | 0.050618 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | FR4345KV-TAP | 0.99687 | 0.94486 | -0.052011 |  | 0.95 | 1.05 | 0.04163 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | FR4345KV-TAP | 0.99687 | 0.94486 | -0.052011 |  | 0.95 | 1.05 | 0.043776 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | FR4345KV-TAP | 0.99687 | 0.94486 | -0.052011 |  | 0.95 | 1.05 | 0.034868 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | FR4345KV-TAP | 0.99687 | 0.94486 | -0.052011 |  | 0.95 | 1.05 | 0.031975 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | FR4345KV-TAP | 0.99687 | 0.94486 | -0.052011 |  | 0.95 | 1.05 | 0.037422 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | FR4345KV-TAP | 0.99687 | 0.94486 | -0.052011 |  | 0.95 | 1.05 | 0.050095 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | FR4345KV-TAP | 0.99414 | 0.94223 | -0.051905 |  | 0.95 | 1.05 | 0.094783 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | FR4345KV-TAP | 0.99414 | 0.94223 | -0.051905 |  | 0.95 | 1.05 | 0.03645 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | FR4345KV-TAP | 0.99414 | 0.94223 | -0.051905 |  | 0.95 | 1.05 | 0.04755 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | FR4345KV-TAP | 0.99414 | 0.94223 | -0.051905 |  | 0.95 | 1.05 | 0.06097 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | FR4345KV-TAP | 0.99414 | 0.94223 | -0.051905 |  | 0.95 | 1.05 | 0.061051 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | FR4345KV-TAP | 0.99414 | 0.94223 | -0.051905 |  | 0.95 | 1.05 | 0.04456 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | FR4345KV-TAP | 0.99414 | 0.94223 | -0.051905 |  | 0.95 | 1.05 | 0.048811 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | FR4345KV-TAP | 0.99414 | 0.94223 | -0.051905 |  | 0.95 | 1.05 | 0.13004 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | FR4345KV-TAP | 0.99414 | 0.94223 | -0.051905 |  | 0.95 | 1.05 | 0.049018 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | FR4345KV-TAP | 0.99414 | 0.94223 | -0.051905 |  | 0.95 | 1.05 | 0.059524 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | FR4345KV-TAP | 0.99414 | 0.94223 | -0.051905 |  | 0.95 | 1.05 | 0.059524 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | FR4345KV-TAP | 0.99414 | 0.94223 | -0.051905 |  | 0.95 | 1.05 | 0.05974 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | FR4345KV-TAP | 0.99414 | 0.94223 | -0.051905 |  | 0.95 | 1.05 | 0.076949 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | FR4345KV-TAP | 0.99414 | 0.94223 | -0.051905 |  | 0.95 | 1.05 | 0.042157 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | FR4345KV-TAP | 0.99414 | 0.94223 | -0.051905 |  | 0.95 | 1.05 | 0.040957 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | FR4345KV-TAP | 0.99414 | 0.94223 | -0.051905 |  | 0.95 | 1.05 | 0.044127 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | FR4345KV-TAP | 0.99414 | 0.94223 | -0.051905 |  | 0.95 | 1.05 | 0.044127 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | FR4345KV-TAP | 0.99414 | 0.94223 | -0.051905 |  | 0.95 | 1.05 | 0.054637 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | FR4345KV-TAP | 0.99414 | 0.94223 | -0.051905 |  | 0.95 | 1.05 | 0.060597 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | FR4345KV-TAP | 0.99414 | 0.94223 | -0.051905 |  | 0.95 | 1.05 | 0.044286 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | FR4345KV-TAP | 0.99414 | 0.94223 | -0.051905 |  | 0.95 | 1.05 | 0.059107 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | FR4345KV-TAP | 0.99414 | 0.94223 | -0.051905 |  | 0.95 | 1.05 | 0.052698 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | FR4345KV-TAP | 0.99414 | 0.94223 | -0.051905 |  | 0.95 | 1.05 | 0.067422 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | FR4345KV-TAP | 0.99414 | 0.94223 | -0.051905 |  | 0.95 | 1.05 | 0.053768 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | FR4345KV-TAP | 0.99414 | 0.94223 | -0.051905 |  | 0.95 | 1.05 | 0.03909 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | FREESTATE3 | 0.96584 | 0.92523 | -0.040612 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | FREESTATE3 | 0.96584 | 0.92523 | -0.040612 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | FREESTATE3 | 0.96584 | 0.92523 | -0.040612 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | FREESTATE3 | 0.96584 | 0.92523 | -0.040612 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | FREESTATE3 | 0.96584 | 0.92523 | -0.040612 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | FREESTATE3 | 0.96584 | 0.92523 | -0.040612 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | FREESTATE3 | 0.96584 | 0.92523 | -0.040612 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | FREESTATE3 | 0.96584 | 0.92523 | -0.040612 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | FREESTATE3 | 0.96584 | 0.92523 | -0.040612 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | FREESTATE3 | 0.96584 | 0.92523 | -0.040612 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | FREESTATE3 | 0.96584 | 0.92523 | -0.040612 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | FREESTATE3 | 0.96584 | 0.92523 | -0.040612 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | FREESTATE3 | 0.96584 | 0.92523 | -0.040612 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | FREESTATE3 | 0.96584 | 0.92523 | -0.040612 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | FREESTATE3 | 0.96584 | 0.92523 | -0.040612 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | FREESTATE3 | 0.96584 | 0.92523 | -0.040612 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | FREESTATE3 | 0.96584 | 0.92523 | -0.040612 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | FREESTATE3 | 0.96584 | 0.92523 | -0.040612 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | FREESTATE3 | 0.96584 | 0.92523 | -0.040612 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | FREESTATE3 | 0.96584 | 0.92523 | -0.040612 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | FREESTATE3 | 0.97171 | 0.92821 | -0.043492 |  | 0.93 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | FREESTATE3 | 0.97171 | 0.92821 | -0.043492 |  | 0.93 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | FREESTATE3 | 0.97171 | 0.92821 | -0.043492 |  | 0.93 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | FREESTATE3 | 0.97171 | 0.92821 | -0.043492 |  | 0.93 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | FREESTATE3 | 0.97171 | 0.92821 | -0.043492 |  | 0.93 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | FREESTATE3 | 0.97171 | 0.92821 | -0.043492 |  | 0.93 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | FREESTATE3 | 0.97171 | 0.92821 | -0.043492 |  | 0.93 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | FREESTATE3 | 0.97171 | 0.92821 | -0.043492 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | FREESTATE3 | 0.97171 | 0.92821 | -0.043492 |  | 0.93 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | FREESTATE3 | 0.97171 | 0.92821 | -0.043492 |  | 0.93 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | FREESTATE3 | 0.97171 | 0.92821 | -0.043492 |  | 0.93 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | FREESTATE3 | 0.97171 | 0.92821 | -0.043492 |  | 0.93 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | FREESTATE3 | 0.97171 | 0.92821 | -0.043492 |  | 0.93 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | FREESTATE3 | 0.97171 | 0.92821 | -0.043492 |  | 0.93 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | FREESTATE3 | 0.97171 | 0.92821 | -0.043492 |  | 0.93 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | FREESTATE3 | 0.97171 | 0.92821 | -0.043492 |  | 0.93 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | FREESTATE3 | 0.97171 | 0.92821 | -0.043492 |  | 0.93 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | FREESTATE3 | 0.97171 | 0.92821 | -0.043492 |  | 0.93 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | FREESTATE3 | 0.97171 | 0.92821 | -0.043492 |  | 0.93 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | FREESTATE3 | 0.97171 | 0.92821 | -0.043492 |  | 0.93 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | FREESTATE3 | 0.97754 | 0.92624 | -0.051298 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | FREESTATE3 | 0.97754 | 0.92624 | -0.051298 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | FREESTATE3 | 0.97754 | 0.92624 | -0.051298 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | FREESTATE3 | 0.97754 | 0.92624 | -0.051298 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | FREESTATE3 | 0.97754 | 0.92624 | -0.051298 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | FREESTATE3 | 0.97754 | 0.92624 | -0.051298 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | FREESTATE3 | 0.97754 | 0.92624 | -0.051298 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | FREESTATE3 | 0.97754 | 0.92624 | -0.051298 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | FREESTATE3 | 0.97754 | 0.92624 | -0.051298 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | FREESTATE3 | 0.97754 | 0.92624 | -0.051298 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | FREESTATE3 | 0.97754 | 0.92624 | -0.051298 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | FREESTATE3 | 0.97754 | 0.92624 | -0.051298 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | FREESTATE3 | 0.97754 | 0.92624 | -0.051298 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | FREESTATE3 | 0.97754 | 0.92624 | -0.051298 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | FREESTATE3 | 0.97754 | 0.92624 | -0.051298 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | FREESTATE3 | 0.97754 | 0.92624 | -0.051298 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | FREESTATE3 | 0.97754 | 0.92624 | -0.051298 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | FREESTATE3 | 0.97754 | 0.92624 | -0.051298 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | FREESTATE3 | 0.97754 | 0.92624 | -0.051298 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | FREESTATE3 | 0.97754 | 0.92624 | -0.051298 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | FREESTATE3 | 0.97754 | 0.92624 | -0.051298 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | FREESTATE3 | 0.97754 | 0.92624 | -0.051298 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | FREESTATE3 | 0.97754 | 0.92624 | -0.051298 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | FREESTATE3 | 0.97754 | 0.92624 | -0.051298 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | FREESTATE3 | 0.97754 | 0.92624 | -0.051298 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | FREESTATE3 | 0.97754 | 0.92624 | -0.051298 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | FREESTATE3 | 0.97754 | 0.92624 | -0.051298 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | FREESTATE3 | 0.97754 | 0.92624 | -0.051298 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | G15052_1 | 0.95862 | 0.89198 | -0.066636 |  | 0.95 | 1.05 | 0.040027 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | G15052_1 | 0.95862 | 0.89198 | -0.066636 |  | 0.95 | 1.05 | 0.090773 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | G15052_1 | 0.95862 | 0.89198 | -0.066636 |  | 0.95 | 1.05 | 0.034521 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | G15052_1 | 0.95862 | 0.89198 | -0.066636 |  | 0.95 | 1.05 | 0.038035 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | G15052_1 | 0.95862 | 0.89198 | -0.066636 |  | 0.95 | 1.05 | 0.048856 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | G15052_1 | 0.95862 | 0.89198 | -0.066636 |  | 0.95 | 1.05 | 0.048856 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | G15052_1 | 0.95862 | 0.89198 | -0.066636 |  | 0.95 | 1.05 | 0.050618 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | G15052_1 | 0.95862 | 0.89198 | -0.066636 |  | 0.95 | 1.05 | 0.04163 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | G15052_1 | 0.95862 | 0.89198 | -0.066636 |  | 0.95 | 1.05 | 0.043776 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | G15052_1 | 0.95862 | 0.89198 | -0.066636 |  | 0.95 | 1.05 | 0.034868 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | G15052_1 | 0.95862 | 0.89198 | -0.066636 |  | 0.95 | 1.05 | 0.031975 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | G15052_1 | 0.95862 | 0.89198 | -0.066636 |  | 0.95 | 1.05 | 0.037422 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | G15052_1 | 0.95862 | 0.89198 | -0.066636 |  | 0.95 | 1.05 | 0.050095 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-025 | G15052_1 | 0.95713 | 0.90787 | -0.049255 |  | 0.95 | 1.05 | 0.032597 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | G15052_1 | 0.95713 | 0.90787 | -0.049255 |  | 0.95 | 1.05 | 0.089211 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-068 | G15052_1 | 0.95713 | 0.90787 | -0.049255 |  | 0.95 | 1.05 | 0.031361 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | G15052_1 | 0.95713 | 0.90787 | -0.049255 |  | 0.95 | 1.05 | 0.033436 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | G15052_1 | 0.95713 | 0.90787 | -0.049255 |  | 0.95 | 1.05 | 0.034144 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | G15052_1 | 0.95713 | 0.90787 | -0.049255 |  | 0.95 | 1.05 | 0.072573 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | G15052_1 | 0.95713 | 0.90787 | -0.049255 |  | 0.95 | 1.05 | 0.038878 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | G15052_1 | 0.95713 | 0.90787 | -0.049255 |  | 0.95 | 1.05 | 0.038509 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | G15052_1 | 0.95713 | 0.90787 | -0.049255 |  | 0.95 | 1.05 | 0.052231 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | G15052_1 | 0.95713 | 0.90787 | -0.049255 |  | 0.95 | 1.05 | 0.058153 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | G15052_1 | 0.95713 | 0.90787 | -0.049255 |  | 0.95 | 1.05 | 0.066569 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | G15052_1 | 0.95713 | 0.90787 | -0.049255 |  | 0.95 | 1.05 | 0.054479 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | G15052_1 | 0.95713 | 0.90787 | -0.049255 |  | 0.95 | 1.05 | 0.077846 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-241 | G15052_1 | 0.95713 | 0.90787 | -0.049255 |  | 0.95 | 1.05 | 0.032597 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | G15052_1 | 0.95713 | 0.90787 | -0.049255 |  | 0.95 | 1.05 | 0.077846 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | G15052_1 | 0.95713 | 0.90787 | -0.049255 |  | 0.95 | 1.05 | 0.082936 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | G15052_1 | 0.95713 | 0.90787 | -0.049255 |  | 0.95 | 1.05 | 0.078825 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | G15052_1 | 0.95713 | 0.90787 | -0.049255 |  | 0.95 | 1.05 | 0.038428 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | G15052_1 | 0.95713 | 0.90787 | -0.049255 |  | 0.95 | 1.05 | 0.045466 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | G15052_1 | 0.95713 | 0.90787 | -0.049255 |  | 0.95 | 1.05 | 0.045466 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | G15052_1 | 0.95713 | 0.90787 | -0.049255 |  | 0.95 | 1.05 | 0.036682 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | G15052_1 | 0.95713 | 0.90787 | -0.049255 |  | 0.95 | 1.05 | 0.074387 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | G15052_1 | 0.95713 | 0.90787 | -0.049255 |  | 0.95 | 1.05 | 0.051904 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | G15052_1 | 0.95713 | 0.90787 | -0.049255 |  | 0.95 | 1.05 | 0.063745 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | G15052_1 | 0.95713 | 0.90787 | -0.049255 |  | 0.95 | 1.05 | 0.061907 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | G15052_1 | 0.95713 | 0.90787 | -0.049255 |  | 0.95 | 1.05 | 0.066186 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | G15052_1 | 0.95713 | 0.90787 | -0.049255 |  | 0.95 | 1.05 | 0.068783 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | G15052_1 | 0.95713 | 0.90787 | -0.049255 |  | 0.95 | 1.05 | 0.045506 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-025 | G15052_1 | 0.95724 | 0.90842 | -0.048825 |  | 0.95 | 1.05 | 0.032597 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | G15052_1 | 0.95724 | 0.90842 | -0.048825 |  | 0.95 | 1.05 | 0.089211 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-068 | G15052_1 | 0.95724 | 0.90842 | -0.048825 |  | 0.95 | 1.05 | 0.031361 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | G15052_1 | 0.95724 | 0.90842 | -0.048825 |  | 0.95 | 1.05 | 0.033436 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | G15052_1 | 0.95724 | 0.90842 | -0.048825 |  | 0.95 | 1.05 | 0.034144 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | G15052_1 | 0.95724 | 0.90842 | -0.048825 |  | 0.95 | 1.05 | 0.072573 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | G15052_1 | 0.95724 | 0.90842 | -0.048825 |  | 0.95 | 1.05 | 0.038878 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | G15052_1 | 0.95724 | 0.90842 | -0.048825 |  | 0.95 | 1.05 | 0.038509 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | G15052_1 | 0.95724 | 0.90842 | -0.048825 |  | 0.95 | 1.05 | 0.052231 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | G15052_1 | 0.95724 | 0.90842 | -0.048825 |  | 0.95 | 1.05 | 0.058153 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | G15052_1 | 0.95724 | 0.90842 | -0.048825 |  | 0.95 | 1.05 | 0.066569 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | G15052_1 | 0.95724 | 0.90842 | -0.048825 |  | 0.95 | 1.05 | 0.054479 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | G15052_1 | 0.95724 | 0.90842 | -0.048825 |  | 0.95 | 1.05 | 0.077846 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-241 | G15052_1 | 0.95724 | 0.90842 | -0.048825 |  | 0.95 | 1.05 | 0.032597 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | G15052_1 | 0.95724 | 0.90842 | -0.048825 |  | 0.95 | 1.05 | 0.077846 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | G15052_1 | 0.95724 | 0.90842 | -0.048825 |  | 0.95 | 1.05 | 0.082936 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | G15052_1 | 0.95724 | 0.90842 | -0.048825 |  | 0.95 | 1.05 | 0.078825 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | G15052_1 | 0.95724 | 0.90842 | -0.048825 |  | 0.95 | 1.05 | 0.038428 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | G15052_1 | 0.95724 | 0.90842 | -0.048825 |  | 0.95 | 1.05 | 0.045466 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | G15052_1 | 0.95724 | 0.90842 | -0.048825 |  | 0.95 | 1.05 | 0.045466 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | G15052_1 | 0.95724 | 0.90842 | -0.048825 |  | 0.95 | 1.05 | 0.036682 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | G15052_1 | 0.95724 | 0.90842 | -0.048825 |  | 0.95 | 1.05 | 0.074387 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | G15052_1 | 0.95724 | 0.90842 | -0.048825 |  | 0.95 | 1.05 | 0.051904 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | G15052_1 | 0.95724 | 0.90842 | -0.048825 |  | 0.95 | 1.05 | 0.063745 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | G15052_1 | 0.95724 | 0.90842 | -0.048825 |  | 0.95 | 1.05 | 0.061907 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | G15052_1 | 0.95724 | 0.90842 | -0.048825 |  | 0.95 | 1.05 | 0.066186 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | G15052_1 | 0.95724 | 0.90842 | -0.048825 |  | 0.95 | 1.05 | 0.068783 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | G15052_1 | 0.95724 | 0.90842 | -0.048825 |  | 0.95 | 1.05 | 0.045506 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-025 | G15052_1 | 0.95854 | 0.91044 | -0.048101 |  | 0.95 | 1.05 | 0.032597 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | G15052_1 | 0.95854 | 0.91044 | -0.048101 |  | 0.95 | 1.05 | 0.089211 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-068 | G15052_1 | 0.95854 | 0.91044 | -0.048101 |  | 0.95 | 1.05 | 0.031361 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | G15052_1 | 0.95854 | 0.91044 | -0.048101 |  | 0.95 | 1.05 | 0.033436 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | G15052_1 | 0.95854 | 0.91044 | -0.048101 |  | 0.95 | 1.05 | 0.034144 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | G15052_1 | 0.95854 | 0.91044 | -0.048101 |  | 0.95 | 1.05 | 0.072573 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | G15052_1 | 0.95854 | 0.91044 | -0.048101 |  | 0.95 | 1.05 | 0.038878 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | G15052_1 | 0.95854 | 0.91044 | -0.048101 |  | 0.95 | 1.05 | 0.038509 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | G15052_1 | 0.95854 | 0.91044 | -0.048101 |  | 0.95 | 1.05 | 0.052231 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | G15052_1 | 0.95854 | 0.91044 | -0.048101 |  | 0.95 | 1.05 | 0.058153 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | G15052_1 | 0.95854 | 0.91044 | -0.048101 |  | 0.95 | 1.05 | 0.066569 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | G15052_1 | 0.95854 | 0.91044 | -0.048101 |  | 0.95 | 1.05 | 0.054479 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | G15052_1 | 0.95854 | 0.91044 | -0.048101 |  | 0.95 | 1.05 | 0.077846 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-241 | G15052_1 | 0.95854 | 0.91044 | -0.048101 |  | 0.95 | 1.05 | 0.032597 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | G15052_1 | 0.95854 | 0.91044 | -0.048101 |  | 0.95 | 1.05 | 0.077846 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | G15052_1 | 0.95854 | 0.91044 | -0.048101 |  | 0.95 | 1.05 | 0.082936 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | G15052_1 | 0.95854 | 0.91044 | -0.048101 |  | 0.95 | 1.05 | 0.078825 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | G15052_1 | 0.95854 | 0.91044 | -0.048101 |  | 0.95 | 1.05 | 0.038428 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | G15052_1 | 0.95854 | 0.91044 | -0.048101 |  | 0.95 | 1.05 | 0.045466 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | G15052_1 | 0.95854 | 0.91044 | -0.048101 |  | 0.95 | 1.05 | 0.045466 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | G15052_1 | 0.95854 | 0.91044 | -0.048101 |  | 0.95 | 1.05 | 0.036682 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | G15052_1 | 0.95854 | 0.91044 | -0.048101 |  | 0.95 | 1.05 | 0.074387 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | G15052_1 | 0.95854 | 0.91044 | -0.048101 |  | 0.95 | 1.05 | 0.051904 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | G15052_1 | 0.95854 | 0.91044 | -0.048101 |  | 0.95 | 1.05 | 0.063745 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | G15052_1 | 0.95854 | 0.91044 | -0.048101 |  | 0.95 | 1.05 | 0.061907 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | G15052_1 | 0.95854 | 0.91044 | -0.048101 |  | 0.95 | 1.05 | 0.066186 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | G15052_1 | 0.95854 | 0.91044 | -0.048101 |  | 0.95 | 1.05 | 0.068783 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | G15052_1 | 0.95854 | 0.91044 | -0.048101 |  | 0.95 | 1.05 | 0.045506 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | G15052_1 | 0.95868 | 0.89671 | -0.061966 |  | 0.95 | 1.05 | 0.040163 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | G15052_1 | 0.95868 | 0.89671 | -0.061966 |  | 0.95 | 1.05 | 0.035544 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | G15052_1 | 0.95868 | 0.89671 | -0.061966 |  | 0.95 | 1.05 | 0.048812 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | G15052_1 | 0.95868 | 0.89671 | -0.061966 |  | 0.95 | 1.05 | 0.049073 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | G15052_1 | 0.95868 | 0.89671 | -0.061966 |  | 0.95 | 1.05 | 0.035142 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | G15052_1 | 0.95868 | 0.89671 | -0.061966 |  | 0.95 | 1.05 | 0.037502 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | G15052_1 | 0.95868 | 0.89671 | -0.061966 |  | 0.95 | 1.05 | 0.04571 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | G15052_1 | 0.95868 | 0.89671 | -0.061966 |  | 0.95 | 1.05 | 0.03081 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | G15052_1 | 0.95868 | 0.89671 | -0.061966 |  | 0.95 | 1.05 | 0.03835 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | G15052_1 | 0.95868 | 0.89671 | -0.061966 |  | 0.95 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | G15052_1 | 0.95868 | 0.89671 | -0.061966 |  | 0.95 | 1.05 | 0.064216 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | G15052_1 | 0.95868 | 0.89671 | -0.061966 |  | 0.95 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | G15052_1 | 0.95868 | 0.89671 | -0.061966 |  | 0.95 | 1.05 | 0.037545 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | G15052_1 | 0.95868 | 0.89671 | -0.061966 |  | 0.95 | 1.05 | 0.037793 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | G15052_1 | 0.95868 | 0.89671 | -0.061966 |  | 0.95 | 1.05 | 0.035866 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | G15052_1 | 0.95868 | 0.89671 | -0.061966 |  | 0.95 | 1.05 | 0.064223 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | G15052_1 | 0.95868 | 0.89671 | -0.061966 |  | 0.95 | 1.05 | 0.046439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | G15052_1 | 0.95868 | 0.89671 | -0.061966 |  | 0.95 | 1.05 | 0.03576 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | G15052_1 | 0.95868 | 0.89671 | -0.061966 |  | 0.95 | 1.05 | 0.032864 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | G15052_1 | 0.95868 | 0.89671 | -0.061966 |  | 0.95 | 1.05 | 0.032012 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | G15052_1 | 0.95868 | 0.89671 | -0.061966 |  | 0.95 | 1.05 | 0.033901 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | G15052_1 | 0.95868 | 0.89671 | -0.061966 |  | 0.95 | 1.05 | 0.035381 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | G15052_T | 0.95862 | 0.89198 | -0.066636 |  | 0.95 | 1.05 | 0.040027 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | G15052_T | 0.95862 | 0.89198 | -0.066636 |  | 0.95 | 1.05 | 0.090773 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | G15052_T | 0.95862 | 0.89198 | -0.066636 |  | 0.95 | 1.05 | 0.034521 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | G15052_T | 0.95862 | 0.89198 | -0.066636 |  | 0.95 | 1.05 | 0.038035 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | G15052_T | 0.95862 | 0.89198 | -0.066636 |  | 0.95 | 1.05 | 0.048856 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | G15052_T | 0.95862 | 0.89198 | -0.066636 |  | 0.95 | 1.05 | 0.048856 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | G15052_T | 0.95862 | 0.89198 | -0.066636 |  | 0.95 | 1.05 | 0.050618 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | G15052_T | 0.95862 | 0.89198 | -0.066636 |  | 0.95 | 1.05 | 0.04163 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | G15052_T | 0.95862 | 0.89198 | -0.066636 |  | 0.95 | 1.05 | 0.043776 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | G15052_T | 0.95862 | 0.89198 | -0.066636 |  | 0.95 | 1.05 | 0.034868 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | G15052_T | 0.95862 | 0.89198 | -0.066636 |  | 0.95 | 1.05 | 0.031975 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | G15052_T | 0.95862 | 0.89198 | -0.066636 |  | 0.95 | 1.05 | 0.037422 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | G15052_T | 0.95862 | 0.89198 | -0.066636 |  | 0.95 | 1.05 | 0.050095 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | G15052_T | 0.97459 | 0.94428 | -0.030308 |  | 0.95 | 1.05 | 0.094783 | System Intact | Add 45 MVAR SVC at G15052_T 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | G15052_T | 0.97459 | 0.94428 | -0.030308 |  | 0.95 | 1.05 | 0.03645 | System Intact | Add 45 MVAR SVC at G15052_T 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | G15052_T | 0.97459 | 0.94428 | -0.030308 |  | 0.95 | 1.05 | 0.04755 | System Intact | Add 45 MVAR SVC at G15052_T 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | G15052_T | 0.97459 | 0.94428 | -0.030308 |  | 0.95 | 1.05 | 0.06097 | System Intact | Add 45 MVAR SVC at G15052_T 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | G15052_T | 0.97459 | 0.94428 | -0.030308 |  | 0.95 | 1.05 | 0.061051 | System Intact | Add 45 MVAR SVC at G15052_T 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | G15052_T | 0.97459 | 0.94428 | -0.030308 |  | 0.95 | 1.05 | 0.04456 | System Intact | Add 45 MVAR SVC at G15052_T 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | G15052_T | 0.97459 | 0.94428 | -0.030308 |  | 0.95 | 1.05 | 0.048811 | System Intact | Add 45 MVAR SVC at G15052_T 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | G15052_T | 0.97459 | 0.94428 | -0.030308 |  | 0.95 | 1.05 | 0.13004 | System Intact | Add 45 MVAR SVC at G15052_T 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | G15052_T | 0.97459 | 0.94428 | -0.030308 |  | 0.95 | 1.05 | 0.049018 | System Intact | Add 45 MVAR SVC at G15052_T 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | G15052_T | 0.97459 | 0.94428 | -0.030308 |  | 0.95 | 1.05 | 0.059524 | System Intact | Add 45 MVAR SVC at G15052_T 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | G15052_T | 0.97459 | 0.94428 | -0.030308 |  | 0.95 | 1.05 | 0.059524 | System Intact | Add 45 MVAR SVC at G15052_T 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | G15052_T | 0.97459 | 0.94428 | -0.030308 |  | 0.95 | 1.05 | 0.05974 | System Intact | Add 45 MVAR SVC at G15052_T 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | G15052_T | 0.97459 | 0.94428 | -0.030308 |  | 0.95 | 1.05 | 0.076949 | System Intact | Add 45 MVAR SVC at G15052_T 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | G15052_T | 0.97459 | 0.94428 | -0.030308 |  | 0.95 | 1.05 | 0.042157 | System Intact | Add 45 MVAR SVC at G15052_T 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | G15052_T | 0.97459 | 0.94428 | -0.030308 |  | 0.95 | 1.05 | 0.040957 | System Intact | Add 45 MVAR SVC at G15052_T 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | G15052_T | 0.97459 | 0.94428 | -0.030308 |  | 0.95 | 1.05 | 0.044127 | System Intact | Add 45 MVAR SVC at G15052_T 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | G15052_T | 0.97459 | 0.94428 | -0.030308 |  | 0.95 | 1.05 | 0.044127 | System Intact | Add 45 MVAR SVC at G15052_T 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | G15052_T | 0.97459 | 0.94428 | -0.030308 |  | 0.95 | 1.05 | 0.054637 | System Intact | Add 45 MVAR SVC at G15052_T 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | G15052_T | 0.97459 | 0.94428 | -0.030308 |  | 0.95 | 1.05 | 0.060597 | System Intact | Add 45 MVAR SVC at G15052_T 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | G15052_T | 0.97459 | 0.94428 | -0.030308 |  | 0.95 | 1.05 | 0.044286 | System Intact | Add 45 MVAR SVC at G15052_T 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | G15052_T | 0.97459 | 0.94428 | -0.030308 |  | 0.95 | 1.05 | 0.059107 | System Intact | Add 45 MVAR SVC at G15052_T 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | G15052_T | 0.97459 | 0.94428 | -0.030308 |  | 0.95 | 1.05 | 0.052698 | System Intact | Add 45 MVAR SVC at G15052_T 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | G15052_T | 0.97459 | 0.94428 | -0.030308 |  | 0.95 | 1.05 | 0.067422 | System Intact | Add 45 MVAR SVC at G15052_T 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | G15052_T | 0.97459 | 0.94428 | -0.030308 |  | 0.95 | 1.05 | 0.053768 | System Intact | Add 45 MVAR SVC at G15052_T 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | G15052_T | 0.97459 | 0.94428 | -0.030308 |  | 0.95 | 1.05 | 0.03909 | System Intact | Add 45 MVAR SVC at G15052_T 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-025 | G15052_T | 0.95713 | 0.90787 | -0.049255 |  | 0.95 | 1.05 | 0.032597 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | G15052_T | 0.95713 | 0.90787 | -0.049255 |  | 0.95 | 1.05 | 0.089211 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-068 | G15052_T | 0.95713 | 0.90787 | -0.049255 |  | 0.95 | 1.05 | 0.031361 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | G15052_T | 0.95713 | 0.90787 | -0.049255 |  | 0.95 | 1.05 | 0.033436 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | G15052_T | 0.95713 | 0.90787 | -0.049255 |  | 0.95 | 1.05 | 0.034144 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | G15052_T | 0.95713 | 0.90787 | -0.049255 |  | 0.95 | 1.05 | 0.072573 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | G15052_T | 0.95713 | 0.90787 | -0.049255 |  | 0.95 | 1.05 | 0.038878 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | G15052_T | 0.95713 | 0.90787 | -0.049255 |  | 0.95 | 1.05 | 0.038509 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | G15052_T | 0.95713 | 0.90787 | -0.049255 |  | 0.95 | 1.05 | 0.052231 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | G15052_T | 0.95713 | 0.90787 | -0.049255 |  | 0.95 | 1.05 | 0.058153 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | G15052_T | 0.95713 | 0.90787 | -0.049255 |  | 0.95 | 1.05 | 0.066569 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | G15052_T | 0.95713 | 0.90787 | -0.049255 |  | 0.95 | 1.05 | 0.054479 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | G15052_T | 0.95713 | 0.90787 | -0.049255 |  | 0.95 | 1.05 | 0.077846 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-241 | G15052_T | 0.95713 | 0.90787 | -0.049255 |  | 0.95 | 1.05 | 0.032597 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | G15052_T | 0.95713 | 0.90787 | -0.049255 |  | 0.95 | 1.05 | 0.077846 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | G15052_T | 0.95713 | 0.90787 | -0.049255 |  | 0.95 | 1.05 | 0.082936 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | G15052_T | 0.95713 | 0.90787 | -0.049255 |  | 0.95 | 1.05 | 0.078825 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | G15052_T | 0.95713 | 0.90787 | -0.049255 |  | 0.95 | 1.05 | 0.038428 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | G15052_T | 0.95713 | 0.90787 | -0.049255 |  | 0.95 | 1.05 | 0.045466 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | G15052_T | 0.95713 | 0.90787 | -0.049255 |  | 0.95 | 1.05 | 0.045466 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | G15052_T | 0.95713 | 0.90787 | -0.049255 |  | 0.95 | 1.05 | 0.036682 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | G15052_T | 0.95713 | 0.90787 | -0.049255 |  | 0.95 | 1.05 | 0.074387 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | G15052_T | 0.95713 | 0.90787 | -0.049255 |  | 0.95 | 1.05 | 0.051904 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | G15052_T | 0.95713 | 0.90787 | -0.049255 |  | 0.95 | 1.05 | 0.063745 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | G15052_T | 0.95713 | 0.90787 | -0.049255 |  | 0.95 | 1.05 | 0.061907 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | G15052_T | 0.95713 | 0.90787 | -0.049255 |  | 0.95 | 1.05 | 0.066186 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | G15052_T | 0.95713 | 0.90787 | -0.049255 |  | 0.95 | 1.05 | 0.068783 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | G15052_T | 0.95713 | 0.90787 | -0.049255 |  | 0.95 | 1.05 | 0.045506 | Single 532798 VIOLA7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-025 | G15052_T | 0.95724 | 0.90842 | -0.048825 |  | 0.95 | 1.05 | 0.032597 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | G15052_T | 0.95724 | 0.90842 | -0.048825 |  | 0.95 | 1.05 | 0.089211 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-068 | G15052_T | 0.95724 | 0.90842 | -0.048825 |  | 0.95 | 1.05 | 0.031361 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | G15052_T | 0.95724 | 0.90842 | -0.048825 |  | 0.95 | 1.05 | 0.033436 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | G15052_T | 0.95724 | 0.90842 | -0.048825 |  | 0.95 | 1.05 | 0.034144 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | G15052_T | 0.95724 | 0.90842 | -0.048825 |  | 0.95 | 1.05 | 0.072573 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | G15052_T | 0.95724 | 0.90842 | -0.048825 |  | 0.95 | 1.05 | 0.038878 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | G15052_T | 0.95724 | 0.90842 | -0.048825 |  | 0.95 | 1.05 | 0.038509 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | G15052_T | 0.95724 | 0.90842 | -0.048825 |  | 0.95 | 1.05 | 0.052231 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | G15052_T | 0.95724 | 0.90842 | -0.048825 |  | 0.95 | 1.05 | 0.058153 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | G15052_T | 0.95724 | 0.90842 | -0.048825 |  | 0.95 | 1.05 | 0.066569 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | G15052_T | 0.95724 | 0.90842 | -0.048825 |  | 0.95 | 1.05 | 0.054479 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | G15052_T | 0.95724 | 0.90842 | -0.048825 |  | 0.95 | 1.05 | 0.077846 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-241 | G15052_T | 0.95724 | 0.90842 | -0.048825 |  | 0.95 | 1.05 | 0.032597 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | G15052_T | 0.95724 | 0.90842 | -0.048825 |  | 0.95 | 1.05 | 0.077846 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | G15052_T | 0.95724 | 0.90842 | -0.048825 |  | 0.95 | 1.05 | 0.082936 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | G15052_T | 0.95724 | 0.90842 | -0.048825 |  | 0.95 | 1.05 | 0.078825 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | G15052_T | 0.95724 | 0.90842 | -0.048825 |  | 0.95 | 1.05 | 0.038428 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | G15052_T | 0.95724 | 0.90842 | -0.048825 |  | 0.95 | 1.05 | 0.045466 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | G15052_T | 0.95724 | 0.90842 | -0.048825 |  | 0.95 | 1.05 | 0.045466 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | G15052_T | 0.95724 | 0.90842 | -0.048825 |  | 0.95 | 1.05 | 0.036682 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | G15052_T | 0.95724 | 0.90842 | -0.048825 |  | 0.95 | 1.05 | 0.074387 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | G15052_T | 0.95724 | 0.90842 | -0.048825 |  | 0.95 | 1.05 | 0.051904 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | G15052_T | 0.95724 | 0.90842 | -0.048825 |  | 0.95 | 1.05 | 0.063745 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | G15052_T | 0.95724 | 0.90842 | -0.048825 |  | 0.95 | 1.05 | 0.061907 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | G15052_T | 0.95724 | 0.90842 | -0.048825 |  | 0.95 | 1.05 | 0.066186 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | G15052_T | 0.95724 | 0.90842 | -0.048825 |  | 0.95 | 1.05 | 0.068783 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | G15052_T | 0.95724 | 0.90842 | -0.048825 |  | 0.95 | 1.05 | 0.045506 | Single 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-025 | G15052_T | 0.95854 | 0.91044 | -0.048101 |  | 0.95 | 1.05 | 0.032597 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | G15052_T | 0.95854 | 0.91044 | -0.048101 |  | 0.95 | 1.05 | 0.089211 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-068 | G15052_T | 0.95854 | 0.91044 | -0.048101 |  | 0.95 | 1.05 | 0.031361 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | G15052_T | 0.95854 | 0.91044 | -0.048101 |  | 0.95 | 1.05 | 0.033436 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | G15052_T | 0.95854 | 0.91044 | -0.048101 |  | 0.95 | 1.05 | 0.034144 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | G15052_T | 0.95854 | 0.91044 | -0.048101 |  | 0.95 | 1.05 | 0.072573 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | G15052_T | 0.95854 | 0.91044 | -0.048101 |  | 0.95 | 1.05 | 0.038878 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | G15052_T | 0.95854 | 0.91044 | -0.048101 |  | 0.95 | 1.05 | 0.038509 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | G15052_T | 0.95854 | 0.91044 | -0.048101 |  | 0.95 | 1.05 | 0.052231 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | G15052_T | 0.95854 | 0.91044 | -0.048101 |  | 0.95 | 1.05 | 0.058153 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | G15052_T | 0.95854 | 0.91044 | -0.048101 |  | 0.95 | 1.05 | 0.066569 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | G15052_T | 0.95854 | 0.91044 | -0.048101 |  | 0.95 | 1.05 | 0.054479 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | G15052_T | 0.95854 | 0.91044 | -0.048101 |  | 0.95 | 1.05 | 0.077846 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-241 | G15052_T | 0.95854 | 0.91044 | -0.048101 |  | 0.95 | 1.05 | 0.032597 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | G15052_T | 0.95854 | 0.91044 | -0.048101 |  | 0.95 | 1.05 | 0.077846 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | G15052_T | 0.95854 | 0.91044 | -0.048101 |  | 0.95 | 1.05 | 0.082936 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | G15052_T | 0.95854 | 0.91044 | -0.048101 |  | 0.95 | 1.05 | 0.078825 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | G15052_T | 0.95854 | 0.91044 | -0.048101 |  | 0.95 | 1.05 | 0.038428 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | G15052_T | 0.95854 | 0.91044 | -0.048101 |  | 0.95 | 1.05 | 0.045466 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | G15052_T | 0.95854 | 0.91044 | -0.048101 |  | 0.95 | 1.05 | 0.045466 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | G15052_T | 0.95854 | 0.91044 | -0.048101 |  | 0.95 | 1.05 | 0.036682 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | G15052_T | 0.95854 | 0.91044 | -0.048101 |  | 0.95 | 1.05 | 0.074387 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | G15052_T | 0.95854 | 0.91044 | -0.048101 |  | 0.95 | 1.05 | 0.051904 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | G15052_T | 0.95854 | 0.91044 | -0.048101 |  | 0.95 | 1.05 | 0.063745 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | G15052_T | 0.95854 | 0.91044 | -0.048101 |  | 0.95 | 1.05 | 0.061907 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | G15052_T | 0.95854 | 0.91044 | -0.048101 |  | 0.95 | 1.05 | 0.066186 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | G15052_T | 0.95854 | 0.91044 | -0.048101 |  | 0.95 | 1.05 | 0.068783 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | G15052_T | 0.95854 | 0.91044 | -0.048101 |  | 0.95 | 1.05 | 0.045506 | P42:345:OKGE:SB_REOW7319:::EHV: | Add 280 MVAR SVC at G15052_1 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | G15052_T | 0.95868 | 0.89671 | -0.061966 |  | 0.95 | 1.05 | 0.040163 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | G15052_T | 0.95868 | 0.89671 | -0.061966 |  | 0.95 | 1.05 | 0.035544 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | G15052_T | 0.95868 | 0.89671 | -0.061966 |  | 0.95 | 1.05 | 0.048812 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | G15052_T | 0.95868 | 0.89671 | -0.061966 |  | 0.95 | 1.05 | 0.049073 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | G15052_T | 0.95868 | 0.89671 | -0.061966 |  | 0.95 | 1.05 | 0.035142 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | G15052_T | 0.95868 | 0.89671 | -0.061966 |  | 0.95 | 1.05 | 0.037502 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | G15052_T | 0.95868 | 0.89671 | -0.061966 |  | 0.95 | 1.05 | 0.04571 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | G15052_T | 0.95868 | 0.89671 | -0.061966 |  | 0.95 | 1.05 | 0.03081 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | G15052_T | 0.95868 | 0.89671 | -0.061966 |  | 0.95 | 1.05 | 0.03835 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | G15052_T | 0.95868 | 0.89671 | -0.061966 |  | 0.95 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | G15052_T | 0.95868 | 0.89671 | -0.061966 |  | 0.95 | 1.05 | 0.064216 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | G15052_T | 0.95868 | 0.89671 | -0.061966 |  | 0.95 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | G15052_T | 0.95868 | 0.89671 | -0.061966 |  | 0.95 | 1.05 | 0.037545 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | G15052_T | 0.95868 | 0.89671 | -0.061966 |  | 0.95 | 1.05 | 0.037793 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | G15052_T | 0.95868 | 0.89671 | -0.061966 |  | 0.95 | 1.05 | 0.035866 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | G15052_T | 0.95868 | 0.89671 | -0.061966 |  | 0.95 | 1.05 | 0.064223 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | G15052_T | 0.95868 | 0.89671 | -0.061966 |  | 0.95 | 1.05 | 0.046439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | G15052_T | 0.95868 | 0.89671 | -0.061966 |  | 0.95 | 1.05 | 0.03576 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | G15052_T | 0.95868 | 0.89671 | -0.061966 |  | 0.95 | 1.05 | 0.032864 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | G15052_T | 0.95868 | 0.89671 | -0.061966 |  | 0.95 | 1.05 | 0.032012 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | G15052_T | 0.95868 | 0.89671 | -0.061966 |  | 0.95 | 1.05 | 0.033901 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | G15052_T | 0.95868 | 0.89671 | -0.061966 |  | 0.95 | 1.05 | 0.035381 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | G16-111-TAP | 0.96502 | 0.91932 | -0.045699 |  | 0.95 | 1.05 | 0.064516 | P23:345:SUNC:HLC_BRK188:::EHV: | Add 86 MVAR switched shunt at POSTROCK7 345 kV; Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | ASGI-2024-023 | G16-111-TAP | 0.9665 | 0.92256 | -0.043947 |  | 0.95 | 1.05 | 0.030773 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-025 | G16-111-TAP | 0.9665 | 0.92256 | -0.043947 |  | 0.95 | 1.05 | 0.033004 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | G16-111-TAP | 0.9665 | 0.92256 | -0.043947 |  | 0.95 | 1.05 | 0.046711 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-068 | G16-111-TAP | 0.9665 | 0.92256 | -0.043947 |  | 0.95 | 1.05 | 0.032369 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-071 | G16-111-TAP | 0.9665 | 0.92256 | -0.043947 |  | 0.95 | 1.05 | 0.030466 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | G16-111-TAP | 0.9665 | 0.92256 | -0.043947 |  | 0.95 | 1.05 | 0.04987 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | G16-111-TAP | 0.9665 | 0.92256 | -0.043947 |  | 0.95 | 1.05 | 0.099365 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | G16-111-TAP | 0.9665 | 0.92256 | -0.043947 |  | 0.95 | 1.05 | 0.071132 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | G16-111-TAP | 0.9665 | 0.92256 | -0.043947 |  | 0.95 | 1.05 | 0.043927 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | G16-111-TAP | 0.9665 | 0.92256 | -0.043947 |  | 0.95 | 1.05 | 0.030565 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | G16-111-TAP | 0.9665 | 0.92256 | -0.043947 |  | 0.95 | 1.05 | 0.072847 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | G16-111-TAP | 0.9665 | 0.92256 | -0.043947 |  | 0.95 | 1.05 | 0.041148 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | G16-111-TAP | 0.9665 | 0.92256 | -0.043947 |  | 0.95 | 1.05 | 0.042015 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-220 | G16-111-TAP | 0.9665 | 0.92256 | -0.043947 |  | 0.95 | 1.05 | 0.030318 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | G16-111-TAP | 0.9665 | 0.92256 | -0.043947 |  | 0.95 | 1.05 | 0.054104 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | G16-111-TAP | 0.9665 | 0.92256 | -0.043947 |  | 0.95 | 1.05 | 0.047089 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | G16-111-TAP | 0.9665 | 0.92256 | -0.043947 |  | 0.95 | 1.05 | 0.040323 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | G16-111-TAP | 0.9665 | 0.92256 | -0.043947 |  | 0.95 | 1.05 | 0.13688 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-241 | G16-111-TAP | 0.9665 | 0.92256 | -0.043947 |  | 0.95 | 1.05 | 0.033004 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | G16-111-TAP | 0.9665 | 0.92256 | -0.043947 |  | 0.95 | 1.05 | 0.040323 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | G16-111-TAP | 0.9665 | 0.92256 | -0.043947 |  | 0.95 | 1.05 | 0.039752 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | G16-111-TAP | 0.9665 | 0.92256 | -0.043947 |  | 0.95 | 1.05 | 0.041972 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | G16-111-TAP | 0.9665 | 0.92256 | -0.043947 |  | 0.95 | 1.05 | 0.054397 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | G16-111-TAP | 0.9665 | 0.92256 | -0.043947 |  | 0.95 | 1.05 | 0.073688 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | G16-111-TAP | 0.9665 | 0.92256 | -0.043947 |  | 0.95 | 1.05 | 0.048904 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | G16-111-TAP | 0.9665 | 0.92256 | -0.043947 |  | 0.95 | 1.05 | 0.048904 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | G16-111-TAP | 0.9665 | 0.92256 | -0.043947 |  | 0.95 | 1.05 | 0.072188 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | G16-111-TAP | 0.9665 | 0.92256 | -0.043947 |  | 0.95 | 1.05 | 0.042186 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | G16-111-TAP | 0.9665 | 0.92256 | -0.043947 |  | 0.95 | 1.05 | 0.041423 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | G16-111-TAP | 0.9665 | 0.92256 | -0.043947 |  | 0.95 | 1.05 | 0.050171 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | G16-111-TAP | 0.9665 | 0.92256 | -0.043947 |  | 0.95 | 1.05 | 0.04386 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | G16-111-TAP | 0.9665 | 0.92256 | -0.043947 |  | 0.95 | 1.05 | 0.050218 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | G16-111-TAP | 0.9665 | 0.92256 | -0.043947 |  | 0.95 | 1.05 | 0.040041 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | G16-111-TAP | 0.9665 | 0.92256 | -0.043947 |  | 0.95 | 1.05 | 0.038784 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Add 150 MVAR SVC at G16-111-TAP 345 kV; Add 0.12 MVAR switched shunt at LACYGNE11_7 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | G16-111-TAP | 0.96952 | 0.94485 | -0.02467 |  | 0.95 | 1.05 | 0.045092 | System Intact | Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | G16-111-TAP | 0.96952 | 0.94485 | -0.02467 |  | 0.95 | 1.05 | 0.040734 | System Intact | Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | G16-111-TAP | 0.96952 | 0.94485 | -0.02467 |  | 0.95 | 1.05 | 0.044854 | System Intact | Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | G16-111-TAP | 0.96952 | 0.94485 | -0.02467 |  | 0.95 | 1.05 | 0.030809 | System Intact | Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | G16-111-TAP | 0.96952 | 0.94485 | -0.02467 |  | 0.95 | 1.05 | 0.032849 | System Intact | Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | G16-111-TAP | 0.96952 | 0.94485 | -0.02467 |  | 0.95 | 1.05 | 0.035693 | System Intact | Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | G16-111-TAP | 0.96952 | 0.94485 | -0.02467 |  | 0.95 | 1.05 | 0.040831 | System Intact | Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | G16-111-TAP | 0.96952 | 0.94485 | -0.02467 |  | 0.95 | 1.05 | 0.033699 | System Intact | Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | G16-111-TAP | 0.96952 | 0.94485 | -0.02467 |  | 0.95 | 1.05 | 0.043016 | System Intact | Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | G16-111-TAP | 0.96952 | 0.94485 | -0.02467 |  | 0.95 | 1.05 | 0.043016 | System Intact | Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | G16-111-TAP | 0.96952 | 0.94485 | -0.02467 |  | 0.95 | 1.05 | 0.044165 | System Intact | Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | G16-111-TAP | 0.96952 | 0.94485 | -0.02467 |  | 0.95 | 1.05 | 0.043416 | System Intact | Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | G16-111-TAP | 0.96952 | 0.94485 | -0.02467 |  | 0.95 | 1.05 | 0.041617 | System Intact | Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | G16-111-TAP | 0.96952 | 0.94485 | -0.02467 |  | 0.95 | 1.05 | 0.032965 | System Intact | Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | G16-111-TAP | 0.96952 | 0.94485 | -0.02467 |  | 0.95 | 1.05 | 0.037792 | System Intact | Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | G16-111-TAP | 0.96952 | 0.94485 | -0.02467 |  | 0.95 | 1.05 | 0.037025 | System Intact | Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | G16-111-TAP | 0.96952 | 0.94485 | -0.02467 |  | 0.95 | 1.05 | 0.038471 | System Intact | Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | G16-111-TAP | 0.96952 | 0.94485 | -0.02467 |  | 0.95 | 1.05 | 0.04141 | System Intact | Add 150 MVAR SVC at G16-111-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | G16-111-TAP | 0.96459 | 0.92277 | -0.041827 |  | 0.95 | 1.05 | 0.03768 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | G16-111-TAP | 0.96459 | 0.92277 | -0.041827 |  | 0.95 | 1.05 | 0.054649 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | G16-111-TAP | 0.96459 | 0.92277 | -0.041827 |  | 0.95 | 1.05 | 0.041275 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | G16-111-TAP | 0.96459 | 0.92277 | -0.041827 |  | 0.95 | 1.05 | 0.032793 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | G16-111-TAP | 0.96459 | 0.92277 | -0.041827 |  | 0.95 | 1.05 | 0.043592 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | G16-111-TAP | 0.96459 | 0.92277 | -0.041827 |  | 0.95 | 1.05 | 0.040246 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | G16-111-TAP | 0.96459 | 0.92277 | -0.041827 |  | 0.95 | 1.05 | 0.030207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | G16-111-TAP | 0.96459 | 0.92277 | -0.041827 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | G16-111-TAP | 0.96459 | 0.92277 | -0.041827 |  | 0.95 | 1.05 | 0.069525 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | G16-111-TAP | 0.96459 | 0.92277 | -0.041827 |  | 0.95 | 1.05 | 0.032056 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | G16-111-TAP | 0.96459 | 0.92277 | -0.041827 |  | 0.95 | 1.05 | 0.032357 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | G16-111-TAP | 0.96459 | 0.92277 | -0.041827 |  | 0.95 | 1.05 | 0.033611 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | G16-111-TAP | 0.96459 | 0.92277 | -0.041827 |  | 0.95 | 1.05 | 0.030163 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | G16-111-TAP | 0.96459 | 0.92277 | -0.041827 |  | 0.95 | 1.05 | 0.042714 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | G16-111-TAP | 0.96459 | 0.92277 | -0.041827 |  | 0.95 | 1.05 | 0.042627 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | G16-111-TAP | 0.96459 | 0.92277 | -0.041827 |  | 0.95 | 1.05 | 0.032319 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | G16-111-TAP | 0.96459 | 0.92277 | -0.041827 |  | 0.95 | 1.05 | 0.034532 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | G16-111-TAP | 0.96459 | 0.92277 | -0.041827 |  | 0.95 | 1.05 | 0.030438 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | G16-111-TAP | 0.96459 | 0.92277 | -0.041827 |  | 0.95 | 1.05 | 0.035207 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | G16-111-TAP | 0.96459 | 0.92277 | -0.041827 |  | 0.95 | 1.05 | 0.030949 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | G16-111-TAP | 0.96841 | 0.9214 | -0.047011 |  | 0.95 | 1.05 | 0.040163 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | G16-111-TAP | 0.96841 | 0.9214 | -0.047011 |  | 0.95 | 1.05 | 0.035544 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | G16-111-TAP | 0.96841 | 0.9214 | -0.047011 |  | 0.95 | 1.05 | 0.048812 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | G16-111-TAP | 0.96841 | 0.9214 | -0.047011 |  | 0.95 | 1.05 | 0.049073 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | G16-111-TAP | 0.96841 | 0.9214 | -0.047011 |  | 0.95 | 1.05 | 0.035142 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | G16-111-TAP | 0.96841 | 0.9214 | -0.047011 |  | 0.95 | 1.05 | 0.037502 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | G16-111-TAP | 0.96841 | 0.9214 | -0.047011 |  | 0.95 | 1.05 | 0.04571 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | G16-111-TAP | 0.96841 | 0.9214 | -0.047011 |  | 0.95 | 1.05 | 0.03081 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | G16-111-TAP | 0.96841 | 0.9214 | -0.047011 |  | 0.95 | 1.05 | 0.03835 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | G16-111-TAP | 0.96841 | 0.9214 | -0.047011 |  | 0.95 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | G16-111-TAP | 0.96841 | 0.9214 | -0.047011 |  | 0.95 | 1.05 | 0.064216 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | G16-111-TAP | 0.96841 | 0.9214 | -0.047011 |  | 0.95 | 1.05 | 0.036728 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | G16-111-TAP | 0.96841 | 0.9214 | -0.047011 |  | 0.95 | 1.05 | 0.037545 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | G16-111-TAP | 0.96841 | 0.9214 | -0.047011 |  | 0.95 | 1.05 | 0.037793 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | G16-111-TAP | 0.96841 | 0.9214 | -0.047011 |  | 0.95 | 1.05 | 0.035866 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | G16-111-TAP | 0.96841 | 0.9214 | -0.047011 |  | 0.95 | 1.05 | 0.064223 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | G16-111-TAP | 0.96841 | 0.9214 | -0.047011 |  | 0.95 | 1.05 | 0.046439 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | G16-111-TAP | 0.96841 | 0.9214 | -0.047011 |  | 0.95 | 1.05 | 0.03576 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | G16-111-TAP | 0.96841 | 0.9214 | -0.047011 |  | 0.95 | 1.05 | 0.032864 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | G16-111-TAP | 0.96841 | 0.9214 | -0.047011 |  | 0.95 | 1.05 | 0.032012 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | G16-111-TAP | 0.96841 | 0.9214 | -0.047011 |  | 0.95 | 1.05 | 0.033901 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | G16-111-TAP | 0.96841 | 0.9214 | -0.047011 |  | 0.95 | 1.05 | 0.035381 | P51:25:WERE:WOLFCRK7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | G16-111-TAP | 0.9567 | 0.87875 | -0.077952 |  | 0.95 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | G16-111-TAP | 0.9567 | 0.87875 | -0.077952 |  | 0.95 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | G16-111-TAP | 0.9567 | 0.87875 | -0.077952 |  | 0.95 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | G16-111-TAP | 0.9567 | 0.87875 | -0.077952 |  | 0.95 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | G16-111-TAP | 0.9567 | 0.87875 | -0.077952 |  | 0.95 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | G16-111-TAP | 0.9567 | 0.87875 | -0.077952 |  | 0.95 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | G16-111-TAP | 0.9567 | 0.87875 | -0.077952 |  | 0.95 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | G16-111-TAP | 0.9567 | 0.87875 | -0.077952 |  | 0.95 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | G16-111-TAP | 0.9567 | 0.87875 | -0.077952 |  | 0.95 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | G16-111-TAP | 0.9567 | 0.87875 | -0.077952 |  | 0.95 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | G16-111-TAP | 0.9567 | 0.87875 | -0.077952 |  | 0.95 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | G16-111-TAP | 0.9567 | 0.87875 | -0.077952 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | G16-111-TAP | 0.9567 | 0.87875 | -0.077952 |  | 0.95 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | G16-111-TAP | 0.9567 | 0.87875 | -0.077952 |  | 0.95 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | G16-111-TAP | 0.9567 | 0.87875 | -0.077952 |  | 0.95 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | G16-111-TAP | 0.9567 | 0.87875 | -0.077952 |  | 0.95 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | G16-111-TAP | 0.9567 | 0.87875 | -0.077952 |  | 0.95 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | G16-111-TAP | 0.9567 | 0.87875 | -0.077952 |  | 0.95 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | G16-111-TAP | 0.9567 | 0.87875 | -0.077952 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | G16-111-TAP | 0.9567 | 0.87875 | -0.077952 |  | 0.95 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | G16-111-TAP | 0.9567 | 0.87875 | -0.077952 |  | 0.95 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | G16-111-TAP | 0.9567 | 0.87875 | -0.077952 |  | 0.95 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | G16-111-TAP | 0.9567 | 0.87875 | -0.077952 |  | 0.95 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | G16-111-TAP | 0.9567 | 0.87875 | -0.077952 |  | 0.95 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | G16-111-TAP | 0.9567 | 0.87875 | -0.077952 |  | 0.95 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | G16-111-TAP | 0.9567 | 0.87875 | -0.077952 |  | 0.95 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | G16-111-TAP | 0.9567 | 0.87875 | -0.077952 |  | 0.95 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | G16-111-TAP | 0.9567 | 0.87875 | -0.077952 |  | 0.95 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | G17-108-TAP | 0.98496 | 0.90853 | -0.076432 |  | 0.93 | 1.05 | 0.041213 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | G17-108-TAP | 0.98496 | 0.90853 | -0.076432 |  | 0.93 | 1.05 | 0.03588 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-117 | G17-108-TAP | 0.98496 | 0.90853 | -0.076432 |  | 0.93 | 1.05 | 0.051041 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | G17-108-TAP | 0.98496 | 0.90853 | -0.076432 |  | 0.93 | 1.05 | 0.047378 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | G17-108-TAP | 0.98496 | 0.90853 | -0.076432 |  | 0.93 | 1.05 | 0.035491 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | G17-108-TAP | 0.98496 | 0.90853 | -0.076432 |  | 0.93 | 1.05 | 0.045743 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | G17-108-TAP | 0.98496 | 0.90853 | -0.076432 |  | 0.93 | 1.05 | 0.048376 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | G17-108-TAP | 0.98496 | 0.90853 | -0.076432 |  | 0.93 | 1.05 | 0.03234 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | G17-108-TAP | 0.98496 | 0.90853 | -0.076432 |  | 0.93 | 1.05 | 0.033222 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | G17-108-TAP | 0.98496 | 0.90853 | -0.076432 |  | 0.93 | 1.05 | 0.045881 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | G17-108-TAP | 0.98496 | 0.90853 | -0.076432 |  | 0.93 | 1.05 | 0.035721 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | G17-108-TAP | 0.98496 | 0.90853 | -0.076432 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-240 | G17-108-TAP | 0.98496 | 0.90853 | -0.076432 |  | 0.93 | 1.05 | 0.057484 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | G17-108-TAP | 0.98496 | 0.90853 | -0.076432 |  | 0.93 | 1.05 | 0.038608 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | G17-108-TAP | 0.98496 | 0.90853 | -0.076432 |  | 0.93 | 1.05 | 0.040033 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | G17-108-TAP | 0.98496 | 0.90853 | -0.076432 |  | 0.93 | 1.05 | 0.038037 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | G17-108-TAP | 0.98496 | 0.90853 | -0.076432 |  | 0.93 | 1.05 | 0.038524 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | G17-108-TAP | 0.98496 | 0.90853 | -0.076432 |  | 0.93 | 1.05 | 0.051398 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | G17-108-TAP | 0.98496 | 0.90853 | -0.076432 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | G17-108-TAP | 0.98496 | 0.90853 | -0.076432 |  | 0.93 | 1.05 | 0.036069 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | G17-108-TAP | 0.98496 | 0.90853 | -0.076432 |  | 0.93 | 1.05 | 0.047786 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | G17-108-TAP | 0.98496 | 0.90853 | -0.076432 |  | 0.93 | 1.05 | 0.036423 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | G17-108-TAP | 0.98496 | 0.90853 | -0.076432 |  | 0.93 | 1.05 | 0.032432 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | G17-108-TAP | 0.98496 | 0.90853 | -0.076432 |  | 0.93 | 1.05 | 0.037955 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | G17-108-TAP | 0.98496 | 0.90853 | -0.076432 |  | 0.93 | 1.05 | 0.034547 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | G17-108-TAP | 0.98496 | 0.90853 | -0.076432 |  | 0.93 | 1.05 | 0.039208 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | G17-108-TAP | 0.98496 | 0.90853 | -0.076432 |  | 0.93 | 1.05 | 0.037145 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | G17-108-TAP | 0.98496 | 0.90853 | -0.076432 |  | 0.93 | 1.05 | 0.03062 | P51:13:WERE:EMPEC 7:EHV: | None
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | G18-128-TAP | 0.98038 | 0.916 | -0.064379 |  | 0.95 | 1.05 | 0.040027 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-154 | G18-128-TAP | 0.98038 | 0.916 | -0.064379 |  | 0.95 | 1.05 | 0.090773 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | G18-128-TAP | 0.98038 | 0.916 | -0.064379 |  | 0.95 | 1.05 | 0.034521 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | G18-128-TAP | 0.98038 | 0.916 | -0.064379 |  | 0.95 | 1.05 | 0.038035 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | G18-128-TAP | 0.98038 | 0.916 | -0.064379 |  | 0.95 | 1.05 | 0.048856 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | G18-128-TAP | 0.98038 | 0.916 | -0.064379 |  | 0.95 | 1.05 | 0.048856 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | G18-128-TAP | 0.98038 | 0.916 | -0.064379 |  | 0.95 | 1.05 | 0.050618 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | G18-128-TAP | 0.98038 | 0.916 | -0.064379 |  | 0.95 | 1.05 | 0.04163 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | G18-128-TAP | 0.98038 | 0.916 | -0.064379 |  | 0.95 | 1.05 | 0.043776 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | G18-128-TAP | 0.98038 | 0.916 | -0.064379 |  | 0.95 | 1.05 | 0.034868 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | G18-128-TAP | 0.98038 | 0.916 | -0.064379 |  | 0.95 | 1.05 | 0.031975 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | G18-128-TAP | 0.98038 | 0.916 | -0.064379 |  | 0.95 | 1.05 | 0.037422 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | G18-128-TAP | 0.98038 | 0.916 | -0.064379 |  | 0.95 | 1.05 | 0.050095 | P42:345:OKGE:SB_DGSE7313:::EHV: | Add 0.02 MVAR switched shunt at TV1MNDV4 138 kV; Add 280 MVAR SVC at G15052_1 345 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | G18-128-TAP | 0.97365 | 0.91175 | -0.061905 |  | 0.95 | 1.05 | 0.094783 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | G18-128-TAP | 0.97365 | 0.91175 | -0.061905 |  | 0.95 | 1.05 | 0.03645 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | G18-128-TAP | 0.97365 | 0.91175 | -0.061905 |  | 0.95 | 1.05 | 0.04755 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | G18-128-TAP | 0.97365 | 0.91175 | -0.061905 |  | 0.95 | 1.05 | 0.06097 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | G18-128-TAP | 0.97365 | 0.91175 | -0.061905 |  | 0.95 | 1.05 | 0.061051 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | G18-128-TAP | 0.97365 | 0.91175 | -0.061905 |  | 0.95 | 1.05 | 0.04456 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-219 | G18-128-TAP | 0.97365 | 0.91175 | -0.061905 |  | 0.95 | 1.05 | 0.048811 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-235 | G18-128-TAP | 0.97365 | 0.91175 | -0.061905 |  | 0.95 | 1.05 | 0.13004 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-236 | G18-128-TAP | 0.97365 | 0.91175 | -0.061905 |  | 0.95 | 1.05 | 0.049018 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-239 | G18-128-TAP | 0.97365 | 0.91175 | -0.061905 |  | 0.95 | 1.05 | 0.059524 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-252 | G18-128-TAP | 0.97365 | 0.91175 | -0.061905 |  | 0.95 | 1.05 | 0.059524 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-254 | G18-128-TAP | 0.97365 | 0.91175 | -0.061905 |  | 0.95 | 1.05 | 0.05974 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-255 | G18-128-TAP | 0.97365 | 0.91175 | -0.061905 |  | 0.95 | 1.05 | 0.076949 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-268 | G18-128-TAP | 0.97365 | 0.91175 | -0.061905 |  | 0.95 | 1.05 | 0.042157 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-294 | G18-128-TAP | 0.97365 | 0.91175 | -0.061905 |  | 0.95 | 1.05 | 0.040957 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-296 | G18-128-TAP | 0.97365 | 0.91175 | -0.061905 |  | 0.95 | 1.05 | 0.044127 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-297 | G18-128-TAP | 0.97365 | 0.91175 | -0.061905 |  | 0.95 | 1.05 | 0.044127 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-318 | G18-128-TAP | 0.97365 | 0.91175 | -0.061905 |  | 0.95 | 1.05 | 0.054637 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-333 | G18-128-TAP | 0.97365 | 0.91175 | -0.061905 |  | 0.95 | 1.05 | 0.060597 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-338 | G18-128-TAP | 0.97365 | 0.91175 | -0.061905 |  | 0.95 | 1.05 | 0.044286 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-344 | G18-128-TAP | 0.97365 | 0.91175 | -0.061905 |  | 0.95 | 1.05 | 0.059107 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-360 | G18-128-TAP | 0.97365 | 0.91175 | -0.061905 |  | 0.95 | 1.05 | 0.052698 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-361 | G18-128-TAP | 0.97365 | 0.91175 | -0.061905 |  | 0.95 | 1.05 | 0.067422 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-362 | G18-128-TAP | 0.97365 | 0.91175 | -0.061905 |  | 0.95 | 1.05 | 0.053768 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-373 | G18-128-TAP | 0.97365 | 0.91175 | -0.061905 |  | 0.95 | 1.05 | 0.03909 | Single 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Add 150 MVAR switched shunt at NEOSHO 4 138 kV; Add 3 MVAR switched shunt at NEOSHOS2 69 kV; Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-056 | G18-128-TAP | 0.98054 | 0.93366 | -0.046878 |  | 0.95 | 1.05 | 0.094783 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-113 | G18-128-TAP | 0.98054 | 0.93366 | -0.046878 |  | 0.95 | 1.05 | 0.03645 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-118 | G18-128-TAP | 0.98054 | 0.93366 | -0.046878 |  | 0.95 | 1.05 | 0.04755 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-120 | G18-128-TAP | 0.98054 | 0.93366 | -0.046878 |  | 0.95 | 1.05 | 0.06097 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-171 | G18-128-TAP | 0.98054 | 0.93366 | -0.046878 |  | 0.95 | 1.05 | 0.061051 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV
Voltage | 04ALL | 2 | 29SP | V | GEN-2024-204 | G18-128-TAP | 0.98054 | 0.93366 | -0.046878 |  | 0.95 | 1.05 | 0.04456 | Single 515621 OPENSKY7 345 560053 G15052_T 345 1 | Add 295 MVAR switched shunt at G18-128-TAP 345 kV